Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G18-128-TAP | 0.98054 | 0.93366 | -0.046878 |  | 0.95 | 1.05 | 0.048811 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G18-128-TAP | 0.98054 | 0.93366 | -0.046878 |  | 0.95 | 1.05 | 0.13004 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G18-128-TAP | 0.98054 | 0.93366 | -0.046878 |  | 0.95 | 1.05 | 0.049018 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G18-128-TAP | 0.98054 | 0.93366 | -0.046878 |  | 0.95 | 1.05 | 0.059524 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G18-128-TAP | 0.98054 | 0.93366 | -0.046878 |  | 0.95 | 1.05 | 0.059524 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G18-128-TAP | 0.98054 | 0.93366 | -0.046878 |  | 0.95 | 1.05 | 0.05974 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G18-128-TAP | 0.98054 | 0.93366 | -0.046878 |  | 0.95 | 1.05 | 0.076949 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G18-128-TAP | 0.98054 | 0.93366 | -0.046878 |  | 0.95 | 1.05 | 0.042157 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G18-128-TAP | 0.98054 | 0.93366 | -0.046878 |  | 0.95 | 1.05 | 0.040957 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | G18-128-TAP | 0.98054 | 0.93366 | -0.046878 |  | 0.95 | 1.05 | 0.044127 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | G18-128-TAP | 0.98054 | 0.93366 | -0.046878 |  | 0.95 | 1.05 | 0.044127 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G18-128-TAP | 0.98054 | 0.93366 | -0.046878 |  | 0.95 | 1.05 | 0.054637 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G18-128-TAP | 0.98054 | 0.93366 | -0.046878 |  | 0.95 | 1.05 | 0.060597 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | G18-128-TAP | 0.98054 | 0.93366 | -0.046878 |  | 0.95 | 1.05 | 0.044286 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G18-128-TAP | 0.98054 | 0.93366 | -0.046878 |  | 0.95 | 1.05 | 0.059107 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G18-128-TAP | 0.98054 | 0.93366 | -0.046878 |  | 0.95 | 1.05 | 0.052698 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G18-128-TAP | 0.98054 | 0.93366 | -0.046878 |  | 0.95 | 1.05 | 0.067422 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G18-128-TAP | 0.98054 | 0.93366 | -0.046878 |  | 0.95 | 1.05 | 0.053768 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | G18-128-TAP | 0.98054 | 0.93366 | -0.046878 |  | 0.95 | 1.05 | 0.03909 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G18-128-TAP | 0.98343 | 0.93954 | -0.04389 |  | 0.95 | 1.05 | 0.094783 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | G18-128-TAP | 0.98343 | 0.93954 | -0.04389 |  | 0.95 | 1.05 | 0.03645 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G18-128-TAP | 0.98343 | 0.93954 | -0.04389 |  | 0.95 | 1.05 | 0.04755 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G18-128-TAP | 0.98343 | 0.93954 | -0.04389 |  | 0.95 | 1.05 | 0.06097 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G18-128-TAP | 0.98343 | 0.93954 | -0.04389 |  | 0.95 | 1.05 | 0.061051 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | G18-128-TAP | 0.98343 | 0.93954 | -0.04389 |  | 0.95 | 1.05 | 0.04456 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G18-128-TAP | 0.98343 | 0.93954 | -0.04389 |  | 0.95 | 1.05 | 0.048811 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G18-128-TAP | 0.98343 | 0.93954 | -0.04389 |  | 0.95 | 1.05 | 0.13004 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G18-128-TAP | 0.98343 | 0.93954 | -0.04389 |  | 0.95 | 1.05 | 0.049018 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G18-128-TAP | 0.98343 | 0.93954 | -0.04389 |  | 0.95 | 1.05 | 0.059524 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G18-128-TAP | 0.98343 | 0.93954 | -0.04389 |  | 0.95 | 1.05 | 0.059524 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G18-128-TAP | 0.98343 | 0.93954 | -0.04389 |  | 0.95 | 1.05 | 0.05974 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G18-128-TAP | 0.98343 | 0.93954 | -0.04389 |  | 0.95 | 1.05 | 0.076949 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G18-128-TAP | 0.98343 | 0.93954 | -0.04389 |  | 0.95 | 1.05 | 0.042157 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G18-128-TAP | 0.98343 | 0.93954 | -0.04389 |  | 0.95 | 1.05 | 0.040957 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | G18-128-TAP | 0.98343 | 0.93954 | -0.04389 |  | 0.95 | 1.05 | 0.044127 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | G18-128-TAP | 0.98343 | 0.93954 | -0.04389 |  | 0.95 | 1.05 | 0.044127 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G18-128-TAP | 0.98343 | 0.93954 | -0.04389 |  | 0.95 | 1.05 | 0.054637 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G18-128-TAP | 0.98343 | 0.93954 | -0.04389 |  | 0.95 | 1.05 | 0.060597 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | G18-128-TAP | 0.98343 | 0.93954 | -0.04389 |  | 0.95 | 1.05 | 0.044286 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G18-128-TAP | 0.98343 | 0.93954 | -0.04389 |  | 0.95 | 1.05 | 0.059107 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G18-128-TAP | 0.98343 | 0.93954 | -0.04389 |  | 0.95 | 1.05 | 0.052698 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G18-128-TAP | 0.98343 | 0.93954 | -0.04389 |  | 0.95 | 1.05 | 0.067422 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G18-128-TAP | 0.98343 | 0.93954 | -0.04389 |  | 0.95 | 1.05 | 0.053768 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | G18-128-TAP | 0.98343 | 0.93954 | -0.04389 |  | 0.95 | 1.05 | 0.03909 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G18-128-TAP | 0.98352 | 0.94139 | -0.042132 |  | 0.95 | 1.05 | 0.094783 | P42:345:OKGE:SB_OPKY7388:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | G18-128-TAP | 0.98352 | 0.94139 | -0.042132 |  | 0.95 | 1.05 | 0.03645 | P42:345:OKGE:SB_OPKY7388:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G18-128-TAP | 0.98352 | 0.94139 | -0.042132 |  | 0.95 | 1.05 | 0.04755 | P42:345:OKGE:SB_OPKY7388:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G18-128-TAP | 0.98352 | 0.94139 | -0.042132 |  | 0.95 | 1.05 | 0.06097 | P42:345:OKGE:SB_OPKY7388:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G18-128-TAP | 0.98352 | 0.94139 | -0.042132 |  | 0.95 | 1.05 | 0.061051 | P42:345:OKGE:SB_OPKY7388:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | G18-128-TAP | 0.98352 | 0.94139 | -0.042132 |  | 0.95 | 1.05 | 0.04456 | P42:345:OKGE:SB_OPKY7388:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G18-128-TAP | 0.98352 | 0.94139 | -0.042132 |  | 0.95 | 1.05 | 0.048811 | P42:345:OKGE:SB_OPKY7388:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G18-128-TAP | 0.98352 | 0.94139 | -0.042132 |  | 0.95 | 1.05 | 0.13004 | P42:345:OKGE:SB_OPKY7388:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G18-128-TAP | 0.98352 | 0.94139 | -0.042132 |  | 0.95 | 1.05 | 0.049018 | P42:345:OKGE:SB_OPKY7388:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G18-128-TAP | 0.98352 | 0.94139 | -0.042132 |  | 0.95 | 1.05 | 0.059524 | P42:345:OKGE:SB_OPKY7388:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G18-128-TAP | 0.98352 | 0.94139 | -0.042132 |  | 0.95 | 1.05 | 0.059524 | P42:345:OKGE:SB_OPKY7388:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G18-128-TAP | 0.98352 | 0.94139 | -0.042132 |  | 0.95 | 1.05 | 0.05974 | P42:345:OKGE:SB_OPKY7388:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G18-128-TAP | 0.98352 | 0.94139 | -0.042132 |  | 0.95 | 1.05 | 0.076949 | P42:345:OKGE:SB_OPKY7388:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G18-128-TAP | 0.98352 | 0.94139 | -0.042132 |  | 0.95 | 1.05 | 0.042157 | P42:345:OKGE:SB_OPKY7388:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G18-128-TAP | 0.98352 | 0.94139 | -0.042132 |  | 0.95 | 1.05 | 0.040957 | P42:345:OKGE:SB_OPKY7388:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | G18-128-TAP | 0.98352 | 0.94139 | -0.042132 |  | 0.95 | 1.05 | 0.044127 | P42:345:OKGE:SB_OPKY7388:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | G18-128-TAP | 0.98352 | 0.94139 | -0.042132 |  | 0.95 | 1.05 | 0.044127 | P42:345:OKGE:SB_OPKY7388:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G18-128-TAP | 0.98352 | 0.94139 | -0.042132 |  | 0.95 | 1.05 | 0.054637 | P42:345:OKGE:SB_OPKY7388:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G18-128-TAP | 0.98352 | 0.94139 | -0.042132 |  | 0.95 | 1.05 | 0.060597 | P42:345:OKGE:SB_OPKY7388:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | G18-128-TAP | 0.98352 | 0.94139 | -0.042132 |  | 0.95 | 1.05 | 0.044286 | P42:345:OKGE:SB_OPKY7388:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G18-128-TAP | 0.98352 | 0.94139 | -0.042132 |  | 0.95 | 1.05 | 0.059107 | P42:345:OKGE:SB_OPKY7388:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G18-128-TAP | 0.98352 | 0.94139 | -0.042132 |  | 0.95 | 1.05 | 0.052698 | P42:345:OKGE:SB_OPKY7388:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G18-128-TAP | 0.98352 | 0.94139 | -0.042132 |  | 0.95 | 1.05 | 0.067422 | P42:345:OKGE:SB_OPKY7388:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G18-128-TAP | 0.98352 | 0.94139 | -0.042132 |  | 0.95 | 1.05 | 0.053768 | P42:345:OKGE:SB_OPKY7388:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | G18-128-TAP | 0.98352 | 0.94139 | -0.042132 |  | 0.95 | 1.05 | 0.03909 | P42:345:OKGE:SB_OPKY7388:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | G20-007-TAP | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.030773 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | G20-007-TAP | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G20-007-TAP | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.046711 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | G20-007-TAP | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.032369 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | G20-007-TAP | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.030466 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | G20-007-TAP | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.04987 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G20-007-TAP | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.099365 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G20-007-TAP | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.071132 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G20-007-TAP | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.043927 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G20-007-TAP | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.030565 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G20-007-TAP | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.072847 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | G20-007-TAP | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.041148 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G20-007-TAP | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.042015 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | G20-007-TAP | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.030318 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G20-007-TAP | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.054104 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G20-007-TAP | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.047089 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G20-007-TAP | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G20-007-TAP | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.13688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | G20-007-TAP | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G20-007-TAP | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G20-007-TAP | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.039752 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G20-007-TAP | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.041972 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G20-007-TAP | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.054397 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G20-007-TAP | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.073688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | G20-007-TAP | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | G20-007-TAP | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G20-007-TAP | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.072188 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G20-007-TAP | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.042186 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | G20-007-TAP | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.041423 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G20-007-TAP | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.050171 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G20-007-TAP | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.04386 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G20-007-TAP | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.050218 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G20-007-TAP | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.040041 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | G20-007-TAP | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.038784 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G20-007-TAP | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G20-007-TAP | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G20-007-TAP | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G20-007-TAP | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G20-007-TAP | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G20-007-TAP | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G20-007-TAP | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G20-007-TAP | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G20-007-TAP | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G20-007-TAP | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G20-007-TAP | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G20-007-TAP | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G20-007-TAP | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G20-007-TAP | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G20-007-TAP | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G20-007-TAP | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G20-007-TAP | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G20-007-TAP | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G20-007-TAP | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G20-007-TAP | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G20-007-TAP | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | G20-007-TAP | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G20-007-TAP | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G20-007-TAP | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G20-007-TAP | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G20-007-TAP | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G20-007-TAP | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | G20-007-TAP | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G20-007-TAP | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G20-007-TAP | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G20-007-TAP | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G20-007-TAP | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G20-007-TAP | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G20-007-TAP | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G20-007-TAP | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G20-007-TAP | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G20-007-TAP | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G20-007-TAP | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | G20-007-TAP | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | G20-007-TAP | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G20-007-TAP | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G20-007-TAP | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | G20-007-TAP | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G20-007-TAP | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G20-007-TAP | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G20-007-TAP | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G20-007-TAP | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | G20-007-TAP | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G20-072-TAP | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | G20-072-TAP | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G20-072-TAP | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G20-072-TAP | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G20-072-TAP | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G20-072-TAP | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G20-072-TAP | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | G20-072-TAP | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G20-072-TAP | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G20-072-TAP | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G20-072-TAP | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G20-072-TAP | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G20-072-TAP | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G20-072-TAP | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G20-072-TAP | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G20-072-TAP | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G20-072-TAP | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G20-072-TAP | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | G20-072-TAP | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | G20-072-TAP | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G20-072-TAP | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G20-072-TAP | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | G20-072-TAP | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G20-072-TAP | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G20-072-TAP | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G20-072-TAP | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G20-072-TAP | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | G20-072-TAP | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G20-073-TAP | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | G20-073-TAP | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G20-073-TAP | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G20-073-TAP | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G20-073-TAP | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G20-073-TAP | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G20-073-TAP | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | G20-073-TAP | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G20-073-TAP | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G20-073-TAP | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G20-073-TAP | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G20-073-TAP | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G20-073-TAP | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G20-073-TAP | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G20-073-TAP | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G20-073-TAP | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G20-073-TAP | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G20-073-TAP | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | G20-073-TAP | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | G20-073-TAP | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G20-073-TAP | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G20-073-TAP | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | G20-073-TAP | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G20-073-TAP | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G20-073-TAP | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G20-073-TAP | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G20-073-TAP | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | G20-073-TAP | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G21-029-TAP | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G21-029-TAP | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G21-029-TAP | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G21-029-TAP | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G21-029-TAP | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G21-029-TAP | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G21-029-TAP | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G21-029-TAP | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G21-029-TAP | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G21-029-TAP | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G21-029-TAP | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G21-029-TAP | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G21-029-TAP | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G21-029-TAP | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G21-029-TAP | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G21-029-TAP | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G21-029-TAP | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G21-029-TAP | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G21-029-TAP | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G21-029-TAP | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | G21-029-TAP | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.030773 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | G21-029-TAP | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G21-029-TAP | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.046711 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | G21-029-TAP | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.032369 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | G21-029-TAP | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.030466 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | G21-029-TAP | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.04987 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G21-029-TAP | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.099365 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G21-029-TAP | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.071132 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G21-029-TAP | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.043927 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G21-029-TAP | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.030565 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G21-029-TAP | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.072847 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | G21-029-TAP | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.041148 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G21-029-TAP | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.042015 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | G21-029-TAP | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.030318 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G21-029-TAP | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.054104 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G21-029-TAP | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.047089 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G21-029-TAP | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G21-029-TAP | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.13688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | G21-029-TAP | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G21-029-TAP | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G21-029-TAP | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.039752 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G21-029-TAP | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.041972 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G21-029-TAP | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.054397 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G21-029-TAP | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.073688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | G21-029-TAP | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | G21-029-TAP | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G21-029-TAP | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.072188 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G21-029-TAP | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.042186 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | G21-029-TAP | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.041423 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G21-029-TAP | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.050171 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G21-029-TAP | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.04386 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G21-029-TAP | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.050218 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G21-029-TAP | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.040041 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | G21-029-TAP | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.038784 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G21-029-TAP | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G21-029-TAP | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G21-029-TAP | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G21-029-TAP | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G21-029-TAP | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G21-029-TAP | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G21-029-TAP | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G21-029-TAP | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G21-029-TAP | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G21-029-TAP | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G21-029-TAP | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G21-029-TAP | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G21-029-TAP | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G21-029-TAP | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G21-029-TAP | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G21-029-TAP | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G21-029-TAP | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G21-029-TAP | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G21-029-TAP | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G21-029-TAP | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G21-029-TAP | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | G21-029-TAP | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G21-029-TAP | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G21-029-TAP | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G21-029-TAP | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G21-029-TAP | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G21-029-TAP | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | G21-029-TAP | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G21-029-TAP | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G21-029-TAP | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G21-029-TAP | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G21-029-TAP | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G21-029-TAP | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G21-029-TAP | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G21-029-TAP | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G21-029-TAP | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G21-029-TAP | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G21-029-TAP | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | G21-029-TAP | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | G21-029-TAP | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G21-029-TAP | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G21-029-TAP | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | G21-029-TAP | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G21-029-TAP | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G21-029-TAP | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G21-029-TAP | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G21-029-TAP | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | G21-029-TAP | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G21-096-TAP | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | G21-096-TAP | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G21-096-TAP | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G21-096-TAP | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G21-096-TAP | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G21-096-TAP | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G21-096-TAP | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G21-096-TAP | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G21-096-TAP | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G21-096-TAP | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G21-096-TAP | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G21-096-TAP | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G21-096-TAP | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G21-096-TAP | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G21-096-TAP | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G21-096-TAP | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G21-096-TAP | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G21-096-TAP | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G21-096-TAP | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G21-096-TAP | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G21-096-TAP | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G21-096-TAP | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G22-007-TAP | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | G22-007-TAP | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G22-007-TAP | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G22-007-TAP | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G22-007-TAP | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G22-007-TAP | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G22-007-TAP | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | G22-007-TAP | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G22-007-TAP | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G22-007-TAP | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G22-007-TAP | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G22-007-TAP | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G22-007-TAP | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G22-007-TAP | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G22-007-TAP | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G22-007-TAP | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G22-007-TAP | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G22-007-TAP | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | G22-007-TAP | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | G22-007-TAP | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G22-007-TAP | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G22-007-TAP | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | G22-007-TAP | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G22-007-TAP | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G22-007-TAP | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G22-007-TAP | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G22-007-TAP | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | G22-007-TAP | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G22-013-TAP | 0.99545 | 0.94191 | -0.053541 |  | 0.95 | 1.05 | 0.040163 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G22-013-TAP | 0.99545 | 0.94191 | -0.053541 |  | 0.95 | 1.05 | 0.035142 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G22-013-TAP | 0.99545 | 0.94191 | -0.053541 |  | 0.95 | 1.05 | 0.037502 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G22-013-TAP | 0.99545 | 0.94191 | -0.053541 |  | 0.95 | 1.05 | 0.03081 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G22-013-TAP | 0.99545 | 0.94191 | -0.053541 |  | 0.95 | 1.05 | 0.03835 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G22-013-TAP | 0.99545 | 0.94191 | -0.053541 |  | 0.95 | 1.05 | 0.036728 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G22-013-TAP | 0.99545 | 0.94191 | -0.053541 |  | 0.95 | 1.05 | 0.036728 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G22-013-TAP | 0.99545 | 0.94191 | -0.053541 |  | 0.95 | 1.05 | 0.037545 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G22-013-TAP | 0.99545 | 0.94191 | -0.053541 |  | 0.95 | 1.05 | 0.037793 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G22-013-TAP | 0.99545 | 0.94191 | -0.053541 |  | 0.95 | 1.05 | 0.03576 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G22-013-TAP | 0.99545 | 0.94191 | -0.053541 |  | 0.95 | 1.05 | 0.032864 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G22-013-TAP | 0.99545 | 0.94191 | -0.053541 |  | 0.95 | 1.05 | 0.032012 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G22-013-TAP | 0.99545 | 0.94191 | -0.053541 |  | 0.95 | 1.05 | 0.033901 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G22-013-TAP | 0.99545 | 0.94191 | -0.053541 |  | 0.95 | 1.05 | 0.035381 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G22-013-TAP | 0.99545 | 0.94393 | -0.051521 |  | 0.95 | 1.05 | 0.03965 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G22-013-TAP | 0.99545 | 0.94393 | -0.051521 |  | 0.95 | 1.05 | 0.034629 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G22-013-TAP | 0.99545 | 0.94393 | -0.051521 |  | 0.95 | 1.05 | 0.036988 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G22-013-TAP | 0.99545 | 0.94393 | -0.051521 |  | 0.95 | 1.05 | 0.030296 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G22-013-TAP | 0.99545 | 0.94393 | -0.051521 |  | 0.95 | 1.05 | 0.037836 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G22-013-TAP | 0.99545 | 0.94393 | -0.051521 |  | 0.95 | 1.05 | 0.036214 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G22-013-TAP | 0.99545 | 0.94393 | -0.051521 |  | 0.95 | 1.05 | 0.036214 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G22-013-TAP | 0.99545 | 0.94393 | -0.051521 |  | 0.95 | 1.05 | 0.037031 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G22-013-TAP | 0.99545 | 0.94393 | -0.051521 |  | 0.95 | 1.05 | 0.03728 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G22-013-TAP | 0.99545 | 0.94393 | -0.051521 |  | 0.95 | 1.05 | 0.035246 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G22-013-TAP | 0.99545 | 0.94393 | -0.051521 |  | 0.95 | 1.05 | 0.03235 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G22-013-TAP | 0.99545 | 0.94393 | -0.051521 |  | 0.95 | 1.05 | 0.031498 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G22-013-TAP | 0.99545 | 0.94393 | -0.051521 |  | 0.95 | 1.05 | 0.033388 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G22-013-TAP | 0.99545 | 0.94393 | -0.051521 |  | 0.95 | 1.05 | 0.034867 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G22-013-TAP | 0.99536 | 0.94425 | -0.051112 |  | 0.95 | 1.05 | 0.03965 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G22-013-TAP | 0.99536 | 0.94425 | -0.051112 |  | 0.95 | 1.05 | 0.034629 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G22-013-TAP | 0.99536 | 0.94425 | -0.051112 |  | 0.95 | 1.05 | 0.036988 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G22-013-TAP | 0.99536 | 0.94425 | -0.051112 |  | 0.95 | 1.05 | 0.030296 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G22-013-TAP | 0.99536 | 0.94425 | -0.051112 |  | 0.95 | 1.05 | 0.037836 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G22-013-TAP | 0.99536 | 0.94425 | -0.051112 |  | 0.95 | 1.05 | 0.036214 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G22-013-TAP | 0.99536 | 0.94425 | -0.051112 |  | 0.95 | 1.05 | 0.036214 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G22-013-TAP | 0.99536 | 0.94425 | -0.051112 |  | 0.95 | 1.05 | 0.037031 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G22-013-TAP | 0.99536 | 0.94425 | -0.051112 |  | 0.95 | 1.05 | 0.03728 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G22-013-TAP | 0.99536 | 0.94425 | -0.051112 |  | 0.95 | 1.05 | 0.035246 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G22-013-TAP | 0.99536 | 0.94425 | -0.051112 |  | 0.95 | 1.05 | 0.03235 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G22-013-TAP | 0.99536 | 0.94425 | -0.051112 |  | 0.95 | 1.05 | 0.031498 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G22-013-TAP | 0.99536 | 0.94425 | -0.051112 |  | 0.95 | 1.05 | 0.033388 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G22-013-TAP | 0.99536 | 0.94425 | -0.051112 |  | 0.95 | 1.05 | 0.034867 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G22-013-TAP | 0.99536 | 0.94428 | -0.051074 |  | 0.95 | 1.05 | 0.03965 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G22-013-TAP | 0.99536 | 0.94428 | -0.051074 |  | 0.95 | 1.05 | 0.034629 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G22-013-TAP | 0.99536 | 0.94428 | -0.051074 |  | 0.95 | 1.05 | 0.036988 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G22-013-TAP | 0.99536 | 0.94428 | -0.051074 |  | 0.95 | 1.05 | 0.030296 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G22-013-TAP | 0.99536 | 0.94428 | -0.051074 |  | 0.95 | 1.05 | 0.037836 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G22-013-TAP | 0.99536 | 0.94428 | -0.051074 |  | 0.95 | 1.05 | 0.036214 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G22-013-TAP | 0.99536 | 0.94428 | -0.051074 |  | 0.95 | 1.05 | 0.036214 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G22-013-TAP | 0.99536 | 0.94428 | -0.051074 |  | 0.95 | 1.05 | 0.037031 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G22-013-TAP | 0.99536 | 0.94428 | -0.051074 |  | 0.95 | 1.05 | 0.03728 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G22-013-TAP | 0.99536 | 0.94428 | -0.051074 |  | 0.95 | 1.05 | 0.035246 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G22-013-TAP | 0.99536 | 0.94428 | -0.051074 |  | 0.95 | 1.05 | 0.03235 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G22-013-TAP | 0.99536 | 0.94428 | -0.051074 |  | 0.95 | 1.05 | 0.031498 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G22-013-TAP | 0.99536 | 0.94428 | -0.051074 |  | 0.95 | 1.05 | 0.033388 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G22-013-TAP | 0.99536 | 0.94428 | -0.051074 |  | 0.95 | 1.05 | 0.034867 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G22-013-TAP | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | G22-013-TAP | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G22-013-TAP | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G22-013-TAP | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G22-013-TAP | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G22-013-TAP | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G22-013-TAP | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | G22-013-TAP | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G22-013-TAP | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G22-013-TAP | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G22-013-TAP | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G22-013-TAP | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G22-013-TAP | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G22-013-TAP | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G22-013-TAP | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G22-013-TAP | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G22-013-TAP | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G22-013-TAP | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | G22-013-TAP | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | G22-013-TAP | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G22-013-TAP | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G22-013-TAP | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | G22-013-TAP | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G22-013-TAP | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G22-013-TAP | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G22-013-TAP | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G22-013-TAP | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | G22-013-TAP | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G22-075-TAP | 0.97821 | 0.93407 | -0.044137 |  | 0.95 | 1.05 | 0.048073 | System Intact | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G22-075-TAP | 0.97821 | 0.93407 | -0.044137 |  | 0.95 | 1.05 | 0.032207 | System Intact | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G22-075-TAP | 0.97821 | 0.93407 | -0.044137 |  | 0.95 | 1.05 | 0.032207 | System Intact | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G22-075-TAP | 0.97821 | 0.93407 | -0.044137 |  | 0.95 | 1.05 | 0.032907 | System Intact | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G22-075-TAP | 0.97821 | 0.93407 | -0.044137 |  | 0.95 | 1.05 | 0.030428 | System Intact | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G22-075-TAP | 0.97821 | 0.93407 | -0.044137 |  | 0.95 | 1.05 | 0.030314 | System Intact | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G22-075-TAP | 0.97821 | 0.93407 | -0.044137 |  | 0.95 | 1.05 | 0.032405 | System Intact | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G22-075-TAP | 0.96244 | 0.8851 | -0.077345 |  | 0.9 | 1.05 | 0.064516 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G22-075-TAP | 0.96639 | 0.89813 | -0.068266 |  | 0.9 | 1.05 | 0.0326 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G22-075-TAP | 0.96639 | 0.89813 | -0.068266 |  | 0.9 | 1.05 | 0.030348 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G22-075-TAP | 0.96639 | 0.89813 | -0.068266 |  | 0.9 | 1.05 | 0.031036 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G22-075-TAP | 0.96639 | 0.89813 | -0.068266 |  | 0.9 | 1.05 | 0.030059 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G22-075-TAP | 0.96639 | 0.89813 | -0.068266 |  | 0.9 | 1.05 | 0.030059 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G22-075-TAP | 0.96639 | 0.89813 | -0.068266 |  | 0.9 | 1.05 | 0.030771 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G22-075-TAP | 0.96639 | 0.89813 | -0.068266 |  | 0.9 | 1.05 | 0.030685 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G22-075-TAP | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | G22-075-TAP | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G22-075-TAP | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G22-075-TAP | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G22-075-TAP | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G22-075-TAP | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G22-075-TAP | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | G22-075-TAP | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G22-075-TAP | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G22-075-TAP | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G22-075-TAP | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G22-075-TAP | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G22-075-TAP | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G22-075-TAP | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G22-075-TAP | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G22-075-TAP | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G22-075-TAP | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G22-075-TAP | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | G22-075-TAP | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | G22-075-TAP | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G22-075-TAP | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G22-075-TAP | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | G22-075-TAP | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G22-075-TAP | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G22-075-TAP | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G22-075-TAP | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G22-075-TAP | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | G22-075-TAP | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G23-015-TAP | 1.0305 | 1.0602 | 0.0297 |  | 0.9 | 1.05 | 0.064516 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G23-015-TAP | 1.0325 | 1.0596 | 0.027143 |  | 0.9 | 1.05 | 0.064516 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G23-015-TAP | 1.0325 | 1.0596 | 0.027143 |  | 0.9 | 1.05 | 0.064516 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G23-015-TAP | 1.0325 | 1.0596 | 0.027143 |  | 0.9 | 1.05 | 0.064516 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G23-015-TAP | 1.0148 | 1.0528 | 0.037951 |  | 0.9 | 1.05 | 0.064516 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G23-220-TAP | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.03965 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G23-220-TAP | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.042938 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G23-220-TAP | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.032864 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G23-220-TAP | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.034629 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G23-220-TAP | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.036988 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G23-220-TAP | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.03396 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G23-220-TAP | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.030296 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G23-220-TAP | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.037836 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G23-220-TAP | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.036214 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G23-220-TAP | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.055483 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G23-220-TAP | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.036214 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G23-220-TAP | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.037031 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G23-220-TAP | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.03728 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G23-220-TAP | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.034689 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G23-220-TAP | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.033481 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G23-220-TAP | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.035246 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G23-220-TAP | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.03235 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G23-220-TAP | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.031498 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G23-220-TAP | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.033388 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G23-220-TAP | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.034867 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G23-220-TAP | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G23-220-TAP | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G23-220-TAP | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G23-220-TAP | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G23-220-TAP | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G23-220-TAP | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G23-220-TAP | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G23-220-TAP | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G23-220-TAP | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G23-220-TAP | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G23-220-TAP | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G23-220-TAP | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G23-220-TAP | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G23-220-TAP | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G23-220-TAP | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G23-220-TAP | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G23-220-TAP | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G23-220-TAP | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G23-220-TAP | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G23-220-TAP | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G23-220-TAP | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G23-220-TAP | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G23-220-TAP | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G23-220-TAP | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G23-220-TAP | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G23-220-TAP | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G23-220-TAP | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G23-220-TAP | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G23-220-TAP | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G23-220-TAP | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G23-220-TAP | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G23-220-TAP | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G23-220-TAP | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G23-220-TAP | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G23-220-TAP | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G23-220-TAP | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G23-220-TAP | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G23-220-TAP | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G23-220-TAP | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G23-220-TAP | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G23-220-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | G23-220-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G23-220-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G23-220-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G23-220-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G23-220-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G23-220-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | G23-220-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G23-220-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G23-220-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G23-220-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G23-220-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G23-220-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G23-220-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G23-220-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G23-220-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G23-220-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G23-220-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | G23-220-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | G23-220-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G23-220-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G23-220-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | G23-220-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G23-220-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G23-220-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G23-220-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G23-220-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | G23-220-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G23-220-TAP | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G23-220-TAP | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G23-220-TAP | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G23-220-TAP | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G23-220-TAP | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G23-220-TAP | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G23-220-TAP | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G23-220-TAP | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G23-220-TAP | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G23-220-TAP | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G23-220-TAP | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G23-220-TAP | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G23-220-TAP | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G23-220-TAP | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G23-220-TAP | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G23-220-TAP | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G23-220-TAP | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G23-220-TAP | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G23-220-TAP | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G23-220-TAP | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G23-221-TAP | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.03965 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G23-221-TAP | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.042938 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G23-221-TAP | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.032864 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G23-221-TAP | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.034629 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G23-221-TAP | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.036988 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G23-221-TAP | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.03396 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G23-221-TAP | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.030296 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G23-221-TAP | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.037836 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G23-221-TAP | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.036214 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G23-221-TAP | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.055483 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G23-221-TAP | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.036214 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G23-221-TAP | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.037031 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G23-221-TAP | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.03728 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G23-221-TAP | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.034689 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G23-221-TAP | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.033481 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G23-221-TAP | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.035246 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G23-221-TAP | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.03235 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G23-221-TAP | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.031498 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G23-221-TAP | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.033388 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G23-221-TAP | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.034867 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G23-221-TAP | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G23-221-TAP | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G23-221-TAP | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G23-221-TAP | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G23-221-TAP | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G23-221-TAP | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G23-221-TAP | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G23-221-TAP | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G23-221-TAP | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G23-221-TAP | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G23-221-TAP | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G23-221-TAP | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G23-221-TAP | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G23-221-TAP | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G23-221-TAP | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G23-221-TAP | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G23-221-TAP | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G23-221-TAP | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G23-221-TAP | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G23-221-TAP | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G23-221-TAP | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G23-221-TAP | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G23-221-TAP | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G23-221-TAP | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G23-221-TAP | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G23-221-TAP | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G23-221-TAP | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G23-221-TAP | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G23-221-TAP | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G23-221-TAP | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G23-221-TAP | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G23-221-TAP | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G23-221-TAP | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G23-221-TAP | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G23-221-TAP | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G23-221-TAP | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G23-221-TAP | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G23-221-TAP | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G23-221-TAP | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G23-221-TAP | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G23-221-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | G23-221-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G23-221-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G23-221-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G23-221-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G23-221-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G23-221-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | G23-221-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G23-221-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G23-221-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G23-221-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G23-221-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G23-221-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G23-221-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G23-221-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G23-221-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G23-221-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G23-221-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | G23-221-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | G23-221-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G23-221-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G23-221-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | G23-221-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G23-221-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G23-221-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G23-221-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G23-221-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | G23-221-TAP | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G23-221-TAP | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G23-221-TAP | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G23-221-TAP | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G23-221-TAP | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G23-221-TAP | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G23-221-TAP | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G23-221-TAP | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G23-221-TAP | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G23-221-TAP | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G23-221-TAP | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G23-221-TAP | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G23-221-TAP | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G23-221-TAP | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G23-221-TAP | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G23-221-TAP | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G23-221-TAP | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G23-221-TAP | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G23-221-TAP | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G23-221-TAP | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G23-221-TAP | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G24-076-TAP | 0.99539 | 0.94191 | -0.05348 |  | 0.95 | 1.05 | 0.040163 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G24-076-TAP | 0.99539 | 0.94191 | -0.05348 |  | 0.95 | 1.05 | 0.035142 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G24-076-TAP | 0.99539 | 0.94191 | -0.05348 |  | 0.95 | 1.05 | 0.037502 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G24-076-TAP | 0.99539 | 0.94191 | -0.05348 |  | 0.95 | 1.05 | 0.03081 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G24-076-TAP | 0.99539 | 0.94191 | -0.05348 |  | 0.95 | 1.05 | 0.03835 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G24-076-TAP | 0.99539 | 0.94191 | -0.05348 |  | 0.95 | 1.05 | 0.036728 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G24-076-TAP | 0.99539 | 0.94191 | -0.05348 |  | 0.95 | 1.05 | 0.036728 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G24-076-TAP | 0.99539 | 0.94191 | -0.05348 |  | 0.95 | 1.05 | 0.037545 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G24-076-TAP | 0.99539 | 0.94191 | -0.05348 |  | 0.95 | 1.05 | 0.037793 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G24-076-TAP | 0.99539 | 0.94191 | -0.05348 |  | 0.95 | 1.05 | 0.03576 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G24-076-TAP | 0.99539 | 0.94191 | -0.05348 |  | 0.95 | 1.05 | 0.032864 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G24-076-TAP | 0.99539 | 0.94191 | -0.05348 |  | 0.95 | 1.05 | 0.032012 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G24-076-TAP | 0.99539 | 0.94191 | -0.05348 |  | 0.95 | 1.05 | 0.033901 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G24-076-TAP | 0.99539 | 0.94191 | -0.05348 |  | 0.95 | 1.05 | 0.035381 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G24-076-TAP | 0.99539 | 0.94394 | -0.05145 |  | 0.95 | 1.05 | 0.03965 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G24-076-TAP | 0.99539 | 0.94394 | -0.05145 |  | 0.95 | 1.05 | 0.034629 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G24-076-TAP | 0.99539 | 0.94394 | -0.05145 |  | 0.95 | 1.05 | 0.036988 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G24-076-TAP | 0.99539 | 0.94394 | -0.05145 |  | 0.95 | 1.05 | 0.030296 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G24-076-TAP | 0.99539 | 0.94394 | -0.05145 |  | 0.95 | 1.05 | 0.037836 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G24-076-TAP | 0.99539 | 0.94394 | -0.05145 |  | 0.95 | 1.05 | 0.036214 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G24-076-TAP | 0.99539 | 0.94394 | -0.05145 |  | 0.95 | 1.05 | 0.036214 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G24-076-TAP | 0.99539 | 0.94394 | -0.05145 |  | 0.95 | 1.05 | 0.037031 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G24-076-TAP | 0.99539 | 0.94394 | -0.05145 |  | 0.95 | 1.05 | 0.03728 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G24-076-TAP | 0.99539 | 0.94394 | -0.05145 |  | 0.95 | 1.05 | 0.035246 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G24-076-TAP | 0.99539 | 0.94394 | -0.05145 |  | 0.95 | 1.05 | 0.03235 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G24-076-TAP | 0.99539 | 0.94394 | -0.05145 |  | 0.95 | 1.05 | 0.031498 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G24-076-TAP | 0.99539 | 0.94394 | -0.05145 |  | 0.95 | 1.05 | 0.033388 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G24-076-TAP | 0.99539 | 0.94394 | -0.05145 |  | 0.95 | 1.05 | 0.034867 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G24-076-TAP | 0.99529 | 0.94426 | -0.051037 |  | 0.95 | 1.05 | 0.03965 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G24-076-TAP | 0.99529 | 0.94426 | -0.051037 |  | 0.95 | 1.05 | 0.034629 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G24-076-TAP | 0.99529 | 0.94426 | -0.051037 |  | 0.95 | 1.05 | 0.036988 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G24-076-TAP | 0.99529 | 0.94426 | -0.051037 |  | 0.95 | 1.05 | 0.030296 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G24-076-TAP | 0.99529 | 0.94426 | -0.051037 |  | 0.95 | 1.05 | 0.037836 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G24-076-TAP | 0.99529 | 0.94426 | -0.051037 |  | 0.95 | 1.05 | 0.036214 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G24-076-TAP | 0.99529 | 0.94426 | -0.051037 |  | 0.95 | 1.05 | 0.036214 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G24-076-TAP | 0.99529 | 0.94426 | -0.051037 |  | 0.95 | 1.05 | 0.037031 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G24-076-TAP | 0.99529 | 0.94426 | -0.051037 |  | 0.95 | 1.05 | 0.03728 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G24-076-TAP | 0.99529 | 0.94426 | -0.051037 |  | 0.95 | 1.05 | 0.035246 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G24-076-TAP | 0.99529 | 0.94426 | -0.051037 |  | 0.95 | 1.05 | 0.03235 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G24-076-TAP | 0.99529 | 0.94426 | -0.051037 |  | 0.95 | 1.05 | 0.031498 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G24-076-TAP | 0.99529 | 0.94426 | -0.051037 |  | 0.95 | 1.05 | 0.033388 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G24-076-TAP | 0.99529 | 0.94426 | -0.051037 |  | 0.95 | 1.05 | 0.034867 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G24-076-TAP | 0.99529 | 0.94429 | -0.051001 |  | 0.95 | 1.05 | 0.03965 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G24-076-TAP | 0.99529 | 0.94429 | -0.051001 |  | 0.95 | 1.05 | 0.034629 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G24-076-TAP | 0.99529 | 0.94429 | -0.051001 |  | 0.95 | 1.05 | 0.036988 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G24-076-TAP | 0.99529 | 0.94429 | -0.051001 |  | 0.95 | 1.05 | 0.030296 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G24-076-TAP | 0.99529 | 0.94429 | -0.051001 |  | 0.95 | 1.05 | 0.037836 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G24-076-TAP | 0.99529 | 0.94429 | -0.051001 |  | 0.95 | 1.05 | 0.036214 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G24-076-TAP | 0.99529 | 0.94429 | -0.051001 |  | 0.95 | 1.05 | 0.036214 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G24-076-TAP | 0.99529 | 0.94429 | -0.051001 |  | 0.95 | 1.05 | 0.037031 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G24-076-TAP | 0.99529 | 0.94429 | -0.051001 |  | 0.95 | 1.05 | 0.03728 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G24-076-TAP | 0.99529 | 0.94429 | -0.051001 |  | 0.95 | 1.05 | 0.035246 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G24-076-TAP | 0.99529 | 0.94429 | -0.051001 |  | 0.95 | 1.05 | 0.03235 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G24-076-TAP | 0.99529 | 0.94429 | -0.051001 |  | 0.95 | 1.05 | 0.031498 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G24-076-TAP | 0.99529 | 0.94429 | -0.051001 |  | 0.95 | 1.05 | 0.033388 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G24-076-TAP | 0.99529 | 0.94429 | -0.051001 |  | 0.95 | 1.05 | 0.034867 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G24-076-TAP | 0.98876 | 0.89261 | -0.096154 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | G24-076-TAP | 0.98876 | 0.89261 | -0.096154 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G24-076-TAP | 0.98876 | 0.89261 | -0.096154 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G24-076-TAP | 0.98876 | 0.89261 | -0.096154 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G24-076-TAP | 0.98876 | 0.89261 | -0.096154 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G24-076-TAP | 0.98876 | 0.89261 | -0.096154 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G24-076-TAP | 0.98876 | 0.89261 | -0.096154 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | G24-076-TAP | 0.98876 | 0.89261 | -0.096154 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G24-076-TAP | 0.98876 | 0.89261 | -0.096154 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G24-076-TAP | 0.98876 | 0.89261 | -0.096154 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G24-076-TAP | 0.98876 | 0.89261 | -0.096154 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G24-076-TAP | 0.98876 | 0.89261 | -0.096154 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G24-076-TAP | 0.98876 | 0.89261 | -0.096154 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G24-076-TAP | 0.98876 | 0.89261 | -0.096154 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G24-076-TAP | 0.98876 | 0.89261 | -0.096154 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G24-076-TAP | 0.98876 | 0.89261 | -0.096154 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G24-076-TAP | 0.98876 | 0.89261 | -0.096154 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G24-076-TAP | 0.98876 | 0.89261 | -0.096154 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | G24-076-TAP | 0.98876 | 0.89261 | -0.096154 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | G24-076-TAP | 0.98876 | 0.89261 | -0.096154 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G24-076-TAP | 0.98876 | 0.89261 | -0.096154 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G24-076-TAP | 0.98876 | 0.89261 | -0.096154 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | G24-076-TAP | 0.98876 | 0.89261 | -0.096154 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G24-076-TAP | 0.98876 | 0.89261 | -0.096154 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G24-076-TAP | 0.98876 | 0.89261 | -0.096154 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G24-076-TAP | 0.98876 | 0.89261 | -0.096154 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G24-076-TAP | 0.98876 | 0.89261 | -0.096154 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | G24-076-TAP | 0.98876 | 0.89261 | -0.096154 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G24-129-TAP | 0.99887 | 0.94304 | -0.055829 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | G24-129-TAP | 0.99887 | 0.94304 | -0.055829 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G24-129-TAP | 0.99887 | 0.94304 | -0.055829 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G24-129-TAP | 0.99887 | 0.94304 | -0.055829 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G24-129-TAP | 0.99887 | 0.94304 | -0.055829 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G24-129-TAP | 0.99887 | 0.94304 | -0.055829 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G24-129-TAP | 0.99887 | 0.94304 | -0.055829 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | G24-129-TAP | 0.99887 | 0.94304 | -0.055829 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G24-129-TAP | 0.99887 | 0.94304 | -0.055829 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G24-129-TAP | 0.99887 | 0.94304 | -0.055829 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G24-129-TAP | 0.99887 | 0.94304 | -0.055829 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G24-129-TAP | 0.99887 | 0.94304 | -0.055829 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G24-129-TAP | 0.99887 | 0.94304 | -0.055829 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G24-129-TAP | 0.99887 | 0.94304 | -0.055829 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G24-129-TAP | 0.99887 | 0.94304 | -0.055829 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G24-129-TAP | 0.99887 | 0.94304 | -0.055829 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G24-129-TAP | 0.99887 | 0.94304 | -0.055829 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G24-129-TAP | 0.99887 | 0.94304 | -0.055829 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | G24-129-TAP | 0.99887 | 0.94304 | -0.055829 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | G24-129-TAP | 0.99887 | 0.94304 | -0.055829 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G24-129-TAP | 0.99887 | 0.94304 | -0.055829 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G24-129-TAP | 0.99887 | 0.94304 | -0.055829 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | G24-129-TAP | 0.99887 | 0.94304 | -0.055829 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G24-129-TAP | 0.99887 | 0.94304 | -0.055829 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G24-129-TAP | 0.99887 | 0.94304 | -0.055829 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G24-129-TAP | 0.99887 | 0.94304 | -0.055829 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G24-129-TAP | 0.99887 | 0.94304 | -0.055829 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | G24-129-TAP | 0.99887 | 0.94304 | -0.055829 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G24-253-TAP | 0.98061 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G24-253-TAP | 0.98061 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G24-253-TAP | 0.98061 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G24-253-TAP | 0.98061 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G24-253-TAP | 0.98061 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G24-253-TAP | 0.98061 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G24-253-TAP | 0.98061 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G24-253-TAP | 0.98061 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G24-253-TAP | 0.98061 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G24-253-TAP | 0.98061 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G24-253-TAP | 0.98061 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G24-253-TAP | 0.98061 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G24-253-TAP | 0.98061 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G24-253-TAP | 0.98061 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G24-253-TAP | 0.98061 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G24-253-TAP | 0.98061 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G24-253-TAP | 0.98061 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G24-253-TAP | 0.98061 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G24-253-TAP | 0.98061 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G24-253-TAP | 0.98061 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G24-253-TAP | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | G24-253-TAP | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G24-253-TAP | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G24-253-TAP | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G24-253-TAP | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G24-253-TAP | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G24-253-TAP | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | G24-253-TAP | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G24-253-TAP | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G24-253-TAP | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G24-253-TAP | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G24-253-TAP | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G24-253-TAP | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G24-253-TAP | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G24-253-TAP | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G24-253-TAP | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G24-253-TAP | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G24-253-TAP | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | G24-253-TAP | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | G24-253-TAP | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G24-253-TAP | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G24-253-TAP | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | G24-253-TAP | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G24-253-TAP | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G24-253-TAP | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G24-253-TAP | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G24-253-TAP | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | G24-253-TAP | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G24-276-TAP | 0.95949 | 0.92492 | -0.034575 |  | 0.95 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G24-276-TAP | 0.95949 | 0.92492 | -0.034575 |  | 0.95 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G24-276-TAP | 0.95949 | 0.92492 | -0.034575 |  | 0.95 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G24-276-TAP | 0.95949 | 0.92492 | -0.034575 |  | 0.95 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G24-276-TAP | 0.95949 | 0.92492 | -0.034575 |  | 0.95 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G24-276-TAP | 0.95949 | 0.92492 | -0.034575 |  | 0.95 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G24-276-TAP | 0.95949 | 0.92492 | -0.034575 |  | 0.95 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G24-276-TAP | 0.95949 | 0.92492 | -0.034575 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G24-276-TAP | 0.95949 | 0.92492 | -0.034575 |  | 0.95 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G24-276-TAP | 0.95949 | 0.92492 | -0.034575 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G24-276-TAP | 0.95949 | 0.92492 | -0.034575 |  | 0.95 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G24-276-TAP | 0.95949 | 0.92492 | -0.034575 |  | 0.95 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G24-276-TAP | 0.95949 | 0.92492 | -0.034575 |  | 0.95 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G24-276-TAP | 0.95949 | 0.92492 | -0.034575 |  | 0.95 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G24-276-TAP | 0.95949 | 0.92492 | -0.034575 |  | 0.95 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G24-276-TAP | 0.95949 | 0.92492 | -0.034575 |  | 0.95 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G24-276-TAP | 0.95949 | 0.92492 | -0.034575 |  | 0.95 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G24-276-TAP | 0.95949 | 0.92492 | -0.034575 |  | 0.95 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G24-276-TAP | 0.95949 | 0.92492 | -0.034575 |  | 0.95 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G24-276-TAP | 0.95949 | 0.92492 | -0.034575 |  | 0.95 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G24-276-TAP | 0.95633 | 0.91711 | -0.039221 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G24-276-TAP | 0.95633 | 0.91711 | -0.039221 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G24-276-TAP | 0.95633 | 0.91711 | -0.039221 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G24-276-TAP | 0.95633 | 0.91711 | -0.039221 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G24-276-TAP | 0.95633 | 0.91711 | -0.039221 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G24-276-TAP | 0.95633 | 0.91711 | -0.039221 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G24-276-TAP | 0.95633 | 0.91711 | -0.039221 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G24-276-TAP | 0.95633 | 0.91711 | -0.039221 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G24-276-TAP | 0.95633 | 0.91711 | -0.039221 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G24-276-TAP | 0.95633 | 0.91711 | -0.039221 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G24-276-TAP | 0.95633 | 0.91711 | -0.039221 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G24-276-TAP | 0.95633 | 0.91711 | -0.039221 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G24-276-TAP | 0.95633 | 0.91711 | -0.039221 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G24-276-TAP | 0.95633 | 0.91711 | -0.039221 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G24-276-TAP | 0.95633 | 0.91711 | -0.039221 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G24-276-TAP | 0.95633 | 0.91711 | -0.039221 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G24-276-TAP | 0.95633 | 0.91711 | -0.039221 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G24-276-TAP | 0.95633 | 0.91711 | -0.039221 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G24-276-TAP | 0.95633 | 0.91711 | -0.039221 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G24-276-TAP | 0.95633 | 0.91711 | -0.039221 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G24-276-TAP | 0.96216 | 0.91838 | -0.04378 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G24-276-TAP | 0.96216 | 0.91838 | -0.04378 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G24-276-TAP | 0.96216 | 0.91838 | -0.04378 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G24-276-TAP | 0.96216 | 0.91838 | -0.04378 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G24-276-TAP | 0.96216 | 0.91838 | -0.04378 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G24-276-TAP | 0.96216 | 0.91838 | -0.04378 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G24-276-TAP | 0.96216 | 0.91838 | -0.04378 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G24-276-TAP | 0.96216 | 0.91838 | -0.04378 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G24-276-TAP | 0.96216 | 0.91838 | -0.04378 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G24-276-TAP | 0.96216 | 0.91838 | -0.04378 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G24-276-TAP | 0.96216 | 0.91838 | -0.04378 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G24-276-TAP | 0.96216 | 0.91838 | -0.04378 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G24-276-TAP | 0.96216 | 0.91838 | -0.04378 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G24-276-TAP | 0.96216 | 0.91838 | -0.04378 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G24-276-TAP | 0.96216 | 0.91838 | -0.04378 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G24-276-TAP | 0.96216 | 0.91838 | -0.04378 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G24-276-TAP | 0.96216 | 0.91838 | -0.04378 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G24-276-TAP | 0.96216 | 0.91838 | -0.04378 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G24-276-TAP | 0.96216 | 0.91838 | -0.04378 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G24-276-TAP | 0.96216 | 0.91838 | -0.04378 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G24-276-TAP | 0.96638 | 0.91775 | -0.048626 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | G24-276-TAP | 0.96638 | 0.91775 | -0.048626 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G24-276-TAP | 0.96638 | 0.91775 | -0.048626 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G24-276-TAP | 0.96638 | 0.91775 | -0.048626 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G24-276-TAP | 0.96638 | 0.91775 | -0.048626 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G24-276-TAP | 0.96638 | 0.91775 | -0.048626 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G24-276-TAP | 0.96638 | 0.91775 | -0.048626 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | G24-276-TAP | 0.96638 | 0.91775 | -0.048626 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G24-276-TAP | 0.96638 | 0.91775 | -0.048626 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G24-276-TAP | 0.96638 | 0.91775 | -0.048626 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G24-276-TAP | 0.96638 | 0.91775 | -0.048626 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G24-276-TAP | 0.96638 | 0.91775 | -0.048626 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G24-276-TAP | 0.96638 | 0.91775 | -0.048626 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G24-276-TAP | 0.96638 | 0.91775 | -0.048626 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G24-276-TAP | 0.96638 | 0.91775 | -0.048626 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G24-276-TAP | 0.96638 | 0.91775 | -0.048626 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G24-276-TAP | 0.96638 | 0.91775 | -0.048626 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G24-276-TAP | 0.96638 | 0.91775 | -0.048626 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | G24-276-TAP | 0.96638 | 0.91775 | -0.048626 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | G24-276-TAP | 0.96638 | 0.91775 | -0.048626 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G24-276-TAP | 0.96638 | 0.91775 | -0.048626 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G24-276-TAP | 0.96638 | 0.91775 | -0.048626 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | G24-276-TAP | 0.96638 | 0.91775 | -0.048626 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G24-276-TAP | 0.96638 | 0.91775 | -0.048626 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G24-276-TAP | 0.96638 | 0.91775 | -0.048626 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G24-276-TAP | 0.96638 | 0.91775 | -0.048626 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G24-276-TAP | 0.96638 | 0.91775 | -0.048626 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | G24-276-TAP | 0.96638 | 0.91775 | -0.048626 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G24-276-TAP | 0.95909 | 0.9236 | -0.035492 |  | 0.95 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G24-276-TAP | 0.95909 | 0.9236 | -0.035492 |  | 0.95 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G24-276-TAP | 0.95909 | 0.9236 | -0.035492 |  | 0.95 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G24-276-TAP | 0.95909 | 0.9236 | -0.035492 |  | 0.95 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G24-276-TAP | 0.95909 | 0.9236 | -0.035492 |  | 0.95 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G24-276-TAP | 0.95909 | 0.9236 | -0.035492 |  | 0.95 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G24-276-TAP | 0.95909 | 0.9236 | -0.035492 |  | 0.95 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G24-276-TAP | 0.95909 | 0.9236 | -0.035492 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G24-276-TAP | 0.95909 | 0.9236 | -0.035492 |  | 0.95 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G24-276-TAP | 0.95909 | 0.9236 | -0.035492 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G24-276-TAP | 0.95909 | 0.9236 | -0.035492 |  | 0.95 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G24-276-TAP | 0.95909 | 0.9236 | -0.035492 |  | 0.95 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G24-276-TAP | 0.95909 | 0.9236 | -0.035492 |  | 0.95 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G24-276-TAP | 0.95909 | 0.9236 | -0.035492 |  | 0.95 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G24-276-TAP | 0.95909 | 0.9236 | -0.035492 |  | 0.95 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G24-276-TAP | 0.95909 | 0.9236 | -0.035492 |  | 0.95 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G24-276-TAP | 0.95909 | 0.9236 | -0.035492 |  | 0.95 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G24-276-TAP | 0.95909 | 0.9236 | -0.035492 |  | 0.95 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G24-276-TAP | 0.95909 | 0.9236 | -0.035492 |  | 0.95 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G24-276-TAP | 0.95909 | 0.9236 | -0.035492 |  | 0.95 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GARDNER5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GARDNER5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GARDNER5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GARDNER5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GARDNER5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GARDNER5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GARDNER5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GARDNER5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GARDNER5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GARDNER5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GARDNER5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GARDNER5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GARDNER5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GARDNER5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GARDNER5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GARDNER5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GARDNER5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GARDNER5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GARDNER5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GARDNER5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GARDNER5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GARDNER5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GARDNER5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GARDNER5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GARDNER5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GARDNER5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GARDNER5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GARDNER5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GARDNER5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GARDNER5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GARDNER5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GARDNER5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GARDNER5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GARDNER5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GARDNER5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GARDNER5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GARDNER5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GARDNER5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GARDNER5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GARDNER5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GARDNER5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GARDNER5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GARDNER5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GARDNER5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GARDNER5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GARDNER5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GARDNER5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GARDNER5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEARY 7 | 0.97713 | 0.93938 | -0.03775 |  | 0.95 | 1.05 | 0.03965 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEARY 7 | 0.97713 | 0.93938 | -0.03775 |  | 0.95 | 1.05 | 0.042938 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEARY 7 | 0.97713 | 0.93938 | -0.03775 |  | 0.95 | 1.05 | 0.032864 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEARY 7 | 0.97713 | 0.93938 | -0.03775 |  | 0.95 | 1.05 | 0.034629 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEARY 7 | 0.97713 | 0.93938 | -0.03775 |  | 0.95 | 1.05 | 0.036988 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEARY 7 | 0.97713 | 0.93938 | -0.03775 |  | 0.95 | 1.05 | 0.03396 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEARY 7 | 0.97713 | 0.93938 | -0.03775 |  | 0.95 | 1.05 | 0.030296 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEARY 7 | 0.97713 | 0.93938 | -0.03775 |  | 0.95 | 1.05 | 0.037836 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEARY 7 | 0.97713 | 0.93938 | -0.03775 |  | 0.95 | 1.05 | 0.036214 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEARY 7 | 0.97713 | 0.93938 | -0.03775 |  | 0.95 | 1.05 | 0.055483 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEARY 7 | 0.97713 | 0.93938 | -0.03775 |  | 0.95 | 1.05 | 0.036214 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEARY 7 | 0.97713 | 0.93938 | -0.03775 |  | 0.95 | 1.05 | 0.037031 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEARY 7 | 0.97713 | 0.93938 | -0.03775 |  | 0.95 | 1.05 | 0.03728 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEARY 7 | 0.97713 | 0.93938 | -0.03775 |  | 0.95 | 1.05 | 0.034689 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEARY 7 | 0.97713 | 0.93938 | -0.03775 |  | 0.95 | 1.05 | 0.033481 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEARY 7 | 0.97713 | 0.93938 | -0.03775 |  | 0.95 | 1.05 | 0.035246 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEARY 7 | 0.97713 | 0.93938 | -0.03775 |  | 0.95 | 1.05 | 0.03235 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEARY 7 | 0.97713 | 0.93938 | -0.03775 |  | 0.95 | 1.05 | 0.031498 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEARY 7 | 0.97713 | 0.93938 | -0.03775 |  | 0.95 | 1.05 | 0.033388 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEARY 7 | 0.97713 | 0.93938 | -0.03775 |  | 0.95 | 1.05 | 0.034867 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEARY 7 | 0.9756 | 0.93493 | -0.040666 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEARY 7 | 0.9756 | 0.93493 | -0.040666 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEARY 7 | 0.9756 | 0.93493 | -0.040666 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEARY 7 | 0.9756 | 0.93493 | -0.040666 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEARY 7 | 0.9756 | 0.93493 | -0.040666 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEARY 7 | 0.9756 | 0.93493 | -0.040666 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEARY 7 | 0.9756 | 0.93493 | -0.040666 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEARY 7 | 0.9756 | 0.93493 | -0.040666 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEARY 7 | 0.9756 | 0.93493 | -0.040666 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEARY 7 | 0.9756 | 0.93493 | -0.040666 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEARY 7 | 0.9756 | 0.93493 | -0.040666 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEARY 7 | 0.9756 | 0.93493 | -0.040666 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEARY 7 | 0.9756 | 0.93493 | -0.040666 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEARY 7 | 0.9756 | 0.93493 | -0.040666 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEARY 7 | 0.9756 | 0.93493 | -0.040666 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEARY 7 | 0.9756 | 0.93493 | -0.040666 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEARY 7 | 0.9756 | 0.93493 | -0.040666 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEARY 7 | 0.9756 | 0.93493 | -0.040666 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEARY 7 | 0.9756 | 0.93493 | -0.040666 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEARY 7 | 0.9756 | 0.93493 | -0.040666 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEARY 7 | 0.98289 | 0.93542 | -0.047474 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEARY 7 | 0.98289 | 0.93542 | -0.047474 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEARY 7 | 0.98289 | 0.93542 | -0.047474 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEARY 7 | 0.98289 | 0.93542 | -0.047474 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEARY 7 | 0.98289 | 0.93542 | -0.047474 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEARY 7 | 0.98289 | 0.93542 | -0.047474 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEARY 7 | 0.98289 | 0.93542 | -0.047474 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEARY 7 | 0.98289 | 0.93542 | -0.047474 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEARY 7 | 0.98289 | 0.93542 | -0.047474 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEARY 7 | 0.98289 | 0.93542 | -0.047474 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEARY 7 | 0.98289 | 0.93542 | -0.047474 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEARY 7 | 0.98289 | 0.93542 | -0.047474 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEARY 7 | 0.98289 | 0.93542 | -0.047474 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEARY 7 | 0.98289 | 0.93542 | -0.047474 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEARY 7 | 0.98289 | 0.93542 | -0.047474 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEARY 7 | 0.98289 | 0.93542 | -0.047474 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEARY 7 | 0.98289 | 0.93542 | -0.047474 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEARY 7 | 0.98289 | 0.93542 | -0.047474 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEARY 7 | 0.98289 | 0.93542 | -0.047474 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEARY 7 | 0.98289 | 0.93542 | -0.047474 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEARY 7 | 0.9833 | 0.91805 | -0.065253 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEARY 7 | 0.9833 | 0.91805 | -0.065253 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEARY 7 | 0.9833 | 0.91805 | -0.065253 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEARY 7 | 0.9833 | 0.91805 | -0.065253 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEARY 7 | 0.9833 | 0.91805 | -0.065253 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEARY 7 | 0.9833 | 0.91805 | -0.065253 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEARY 7 | 0.9833 | 0.91805 | -0.065253 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEARY 7 | 0.9833 | 0.91805 | -0.065253 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEARY 7 | 0.9833 | 0.91805 | -0.065253 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEARY 7 | 0.9833 | 0.91805 | -0.065253 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEARY 7 | 0.9833 | 0.91805 | -0.065253 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEARY 7 | 0.9833 | 0.91805 | -0.065253 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEARY 7 | 0.9833 | 0.91805 | -0.065253 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEARY 7 | 0.9833 | 0.91805 | -0.065253 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEARY 7 | 0.9833 | 0.91805 | -0.065253 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEARY 7 | 0.9833 | 0.91805 | -0.065253 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEARY 7 | 0.9833 | 0.91805 | -0.065253 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEARY 7 | 0.9833 | 0.91805 | -0.065253 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEARY 7 | 0.9833 | 0.91805 | -0.065253 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEARY 7 | 0.9833 | 0.91805 | -0.065253 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEARY 7 | 0.9833 | 0.91805 | -0.065253 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEARY 7 | 0.9833 | 0.91805 | -0.065253 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEARY 7 | 0.9833 | 0.91805 | -0.065253 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEARY 7 | 0.9833 | 0.91805 | -0.065253 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEARY 7 | 0.9833 | 0.91805 | -0.065253 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEARY 7 | 0.9833 | 0.91805 | -0.065253 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEARY 7 | 0.9833 | 0.91805 | -0.065253 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEARY 7 | 0.9833 | 0.91805 | -0.065253 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEARY 7 | 0.97911 | 0.9397 | -0.039409 |  | 0.95 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEARY 7 | 0.97911 | 0.9397 | -0.039409 |  | 0.95 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEARY 7 | 0.97911 | 0.9397 | -0.039409 |  | 0.95 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEARY 7 | 0.97911 | 0.9397 | -0.039409 |  | 0.95 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEARY 7 | 0.97911 | 0.9397 | -0.039409 |  | 0.95 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEARY 7 | 0.97911 | 0.9397 | -0.039409 |  | 0.95 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEARY 7 | 0.97911 | 0.9397 | -0.039409 |  | 0.95 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEARY 7 | 0.97911 | 0.9397 | -0.039409 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEARY 7 | 0.97911 | 0.9397 | -0.039409 |  | 0.95 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEARY 7 | 0.97911 | 0.9397 | -0.039409 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEARY 7 | 0.97911 | 0.9397 | -0.039409 |  | 0.95 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEARY 7 | 0.97911 | 0.9397 | -0.039409 |  | 0.95 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEARY 7 | 0.97911 | 0.9397 | -0.039409 |  | 0.95 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEARY 7 | 0.97911 | 0.9397 | -0.039409 |  | 0.95 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEARY 7 | 0.97911 | 0.9397 | -0.039409 |  | 0.95 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEARY 7 | 0.97911 | 0.9397 | -0.039409 |  | 0.95 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEARY 7 | 0.97911 | 0.9397 | -0.039409 |  | 0.95 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEARY 7 | 0.97911 | 0.9397 | -0.039409 |  | 0.95 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEARY 7 | 0.97911 | 0.9397 | -0.039409 |  | 0.95 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEARY 7 | 0.97911 | 0.9397 | -0.039409 |  | 0.95 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEM_SW 3 | 0.96494 | 0.89289 | -0.072045 |  | 0.9 | 1.05 | 0.041569 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEM_SW 3 | 0.96494 | 0.89289 | -0.072045 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEM_SW 3 | 0.96494 | 0.89289 | -0.072045 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEM_SW 3 | 0.96494 | 0.89289 | -0.072045 |  | 0.9 | 1.05 | 0.03222 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEM_SW 3 | 0.96494 | 0.89289 | -0.072045 |  | 0.9 | 1.05 | 0.030633 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEM_SW 3 | 0.96494 | 0.89289 | -0.072045 |  | 0.9 | 1.05 | 0.030061 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEM_SW 3 | 0.96494 | 0.89289 | -0.072045 |  | 0.9 | 1.05 | 0.031207 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEM_SW 3 | 0.96533 | 0.89627 | -0.069058 |  | 0.9 | 1.05 | 0.041569 | P42:345:NPPD:BKR-MAC-3304:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEM_SW 3 | 0.96533 | 0.89627 | -0.069058 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-MAC-3304:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEM_SW 3 | 0.96533 | 0.89627 | -0.069058 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-MAC-3304:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEM_SW 3 | 0.96533 | 0.89627 | -0.069058 |  | 0.9 | 1.05 | 0.03222 | P42:345:NPPD:BKR-MAC-3304:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEM_SW 3 | 0.96533 | 0.89627 | -0.069058 |  | 0.9 | 1.05 | 0.030633 | P42:345:NPPD:BKR-MAC-3304:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEM_SW 3 | 0.96533 | 0.89627 | -0.069058 |  | 0.9 | 1.05 | 0.030061 | P42:345:NPPD:BKR-MAC-3304:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEM_SW 3 | 0.96533 | 0.89627 | -0.069058 |  | 0.9 | 1.05 | 0.031207 | P42:345:NPPD:BKR-MAC-3304:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEM_SW 3 | 0.96533 | 0.89627 | -0.069058 |  | 0.9 | 1.05 | 0.041569 | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEM_SW 3 | 0.96533 | 0.89627 | -0.069058 |  | 0.9 | 1.05 | 0.031515 | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEM_SW 3 | 0.96533 | 0.89627 | -0.069058 |  | 0.9 | 1.05 | 0.031515 | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEM_SW 3 | 0.96533 | 0.89627 | -0.069058 |  | 0.9 | 1.05 | 0.03222 | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEM_SW 3 | 0.96533 | 0.89627 | -0.069058 |  | 0.9 | 1.05 | 0.030633 | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEM_SW 3 | 0.96533 | 0.89627 | -0.069058 |  | 0.9 | 1.05 | 0.030061 | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEM_SW 3 | 0.96533 | 0.89627 | -0.069058 |  | 0.9 | 1.05 | 0.031207 | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEM_SW 3 | 0.96645 | 0.89767 | -0.068781 |  | 0.9 | 1.05 | 0.041569 | Single 530583 POSTROCK7 345 640527 MACON3 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEM_SW 3 | 0.96645 | 0.89767 | -0.068781 |  | 0.9 | 1.05 | 0.031515 | Single 530583 POSTROCK7 345 640527 MACON3 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEM_SW 3 | 0.96645 | 0.89767 | -0.068781 |  | 0.9 | 1.05 | 0.031515 | Single 530583 POSTROCK7 345 640527 MACON3 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEM_SW 3 | 0.96645 | 0.89767 | -0.068781 |  | 0.9 | 1.05 | 0.03222 | Single 530583 POSTROCK7 345 640527 MACON3 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEM_SW 3 | 0.96645 | 0.89767 | -0.068781 |  | 0.9 | 1.05 | 0.030633 | Single 530583 POSTROCK7 345 640527 MACON3 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEM_SW 3 | 0.96645 | 0.89767 | -0.068781 |  | 0.9 | 1.05 | 0.030061 | Single 530583 POSTROCK7 345 640527 MACON3 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEM_SW 3 | 0.96645 | 0.89767 | -0.068781 |  | 0.9 | 1.05 | 0.031207 | Single 530583 POSTROCK7 345 640527 MACON3 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEM_SW 3 | 0.96592 | 0.89627 | -0.069648 |  | 0.9 | 1.05 | 0.041569 | Single 640065 AXTELL3 345 640527 MACON3 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEM_SW 3 | 0.96592 | 0.89627 | -0.069648 |  | 0.9 | 1.05 | 0.031515 | Single 640065 AXTELL3 345 640527 MACON3 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEM_SW 3 | 0.96592 | 0.89627 | -0.069648 |  | 0.9 | 1.05 | 0.031515 | Single 640065 AXTELL3 345 640527 MACON3 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEM_SW 3 | 0.96592 | 0.89627 | -0.069648 |  | 0.9 | 1.05 | 0.03222 | Single 640065 AXTELL3 345 640527 MACON3 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEM_SW 3 | 0.96592 | 0.89627 | -0.069648 |  | 0.9 | 1.05 | 0.030633 | Single 640065 AXTELL3 345 640527 MACON3 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEM_SW 3 | 0.96592 | 0.89627 | -0.069648 |  | 0.9 | 1.05 | 0.030061 | Single 640065 AXTELL3 345 640527 MACON3 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEM_SW 3 | 0.96592 | 0.89627 | -0.069648 |  | 0.9 | 1.05 | 0.031207 | Single 640065 AXTELL3 345 640527 MACON3 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2016-073 | 0.99002 | 0.94254 | -0.047487 |  | 0.95 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2016-073 | 0.99002 | 0.94254 | -0.047487 |  | 0.95 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2016-073 | 0.99002 | 0.94254 | -0.047487 |  | 0.95 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2016-073 | 0.99002 | 0.94254 | -0.047487 |  | 0.95 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2016-073 | 0.99002 | 0.94254 | -0.047487 |  | 0.95 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2016-073 | 0.99002 | 0.94254 | -0.047487 |  | 0.95 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2016-073 | 0.99002 | 0.94254 | -0.047487 |  | 0.95 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2016-073 | 0.99002 | 0.94254 | -0.047487 |  | 0.95 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2016-073 | 0.99002 | 0.94254 | -0.047487 |  | 0.95 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2016-073 | 0.99002 | 0.94254 | -0.047487 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2016-073 | 0.99002 | 0.94254 | -0.047487 |  | 0.95 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2016-073 | 0.99002 | 0.94254 | -0.047487 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2016-073 | 0.99002 | 0.94254 | -0.047487 |  | 0.95 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2016-073 | 0.99002 | 0.94254 | -0.047487 |  | 0.95 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2016-073 | 0.99002 | 0.94254 | -0.047487 |  | 0.95 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2016-073 | 0.99002 | 0.94254 | -0.047487 |  | 0.95 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2016-073 | 0.99002 | 0.94254 | -0.047487 |  | 0.95 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2016-073 | 0.99002 | 0.94254 | -0.047487 |  | 0.95 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2016-073 | 0.99002 | 0.94254 | -0.047487 |  | 0.95 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2016-073 | 0.99002 | 0.94254 | -0.047487 |  | 0.95 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2016-073 | 0.99002 | 0.94254 | -0.047487 |  | 0.95 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2016-073 | 0.99002 | 0.94254 | -0.047487 |  | 0.95 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2016-073 | 0.99233 | 0.94479 | -0.047535 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2016-073 | 0.99233 | 0.94479 | -0.047535 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2016-073 | 0.99233 | 0.94479 | -0.047535 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2016-073 | 0.99233 | 0.94479 | -0.047535 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2016-073 | 0.99233 | 0.94479 | -0.047535 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2016-073 | 0.99233 | 0.94479 | -0.047535 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2016-073 | 0.99233 | 0.94479 | -0.047535 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2016-073 | 0.99233 | 0.94479 | -0.047535 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2016-073 | 0.99233 | 0.94479 | -0.047535 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2016-073 | 0.99233 | 0.94479 | -0.047535 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2016-073 | 0.99233 | 0.94479 | -0.047535 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2016-073 | 0.99233 | 0.94479 | -0.047535 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2016-073 | 0.99233 | 0.94479 | -0.047535 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2016-073 | 0.99233 | 0.94479 | -0.047535 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2016-073 | 0.99233 | 0.94479 | -0.047535 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2016-073 | 0.99233 | 0.94479 | -0.047535 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2016-073 | 0.99233 | 0.94479 | -0.047535 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2016-073 | 0.99233 | 0.94479 | -0.047535 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2016-073 | 0.99233 | 0.94479 | -0.047535 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2016-073 | 0.99233 | 0.94479 | -0.047535 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2016-073 | 0.99233 | 0.94479 | -0.047535 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2016-073 | 0.99233 | 0.94479 | -0.047535 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2016-073 | 0.99233 | 0.94479 | -0.047535 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2016-073 | 0.99233 | 0.94479 | -0.047535 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2016-073 | 0.99233 | 0.94479 | -0.047535 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2016-073 | 0.99233 | 0.94479 | -0.047535 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2016-073 | 0.99233 | 0.94479 | -0.047535 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2016-073 | 0.99233 | 0.94479 | -0.047535 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2016-111 | 0.96591 | 0.92017 | -0.045742 |  | 0.95 | 1.05 | 0.064516 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | GEN-2016-111 | 0.9674 | 0.92341 | -0.043988 |  | 0.95 | 1.05 | 0.030773 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | GEN-2016-111 | 0.9674 | 0.92341 | -0.043988 |  | 0.95 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2016-111 | 0.9674 | 0.92341 | -0.043988 |  | 0.95 | 1.05 | 0.046711 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | GEN-2016-111 | 0.9674 | 0.92341 | -0.043988 |  | 0.95 | 1.05 | 0.032369 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | GEN-2016-111 | 0.9674 | 0.92341 | -0.043988 |  | 0.95 | 1.05 | 0.030466 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2016-111 | 0.9674 | 0.92341 | -0.043988 |  | 0.95 | 1.05 | 0.04987 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2016-111 | 0.9674 | 0.92341 | -0.043988 |  | 0.95 | 1.05 | 0.099365 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2016-111 | 0.9674 | 0.92341 | -0.043988 |  | 0.95 | 1.05 | 0.071132 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2016-111 | 0.9674 | 0.92341 | -0.043988 |  | 0.95 | 1.05 | 0.043927 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2016-111 | 0.9674 | 0.92341 | -0.043988 |  | 0.95 | 1.05 | 0.030565 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2016-111 | 0.9674 | 0.92341 | -0.043988 |  | 0.95 | 1.05 | 0.072847 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2016-111 | 0.9674 | 0.92341 | -0.043988 |  | 0.95 | 1.05 | 0.041148 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2016-111 | 0.9674 | 0.92341 | -0.043988 |  | 0.95 | 1.05 | 0.042015 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | GEN-2016-111 | 0.9674 | 0.92341 | -0.043988 |  | 0.95 | 1.05 | 0.030318 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2016-111 | 0.9674 | 0.92341 | -0.043988 |  | 0.95 | 1.05 | 0.054104 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2016-111 | 0.9674 | 0.92341 | -0.043988 |  | 0.95 | 1.05 | 0.047089 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2016-111 | 0.9674 | 0.92341 | -0.043988 |  | 0.95 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2016-111 | 0.9674 | 0.92341 | -0.043988 |  | 0.95 | 1.05 | 0.13688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | GEN-2016-111 | 0.9674 | 0.92341 | -0.043988 |  | 0.95 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2016-111 | 0.9674 | 0.92341 | -0.043988 |  | 0.95 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2016-111 | 0.9674 | 0.92341 | -0.043988 |  | 0.95 | 1.05 | 0.039752 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2016-111 | 0.9674 | 0.92341 | -0.043988 |  | 0.95 | 1.05 | 0.041972 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2016-111 | 0.9674 | 0.92341 | -0.043988 |  | 0.95 | 1.05 | 0.054397 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2016-111 | 0.9674 | 0.92341 | -0.043988 |  | 0.95 | 1.05 | 0.073688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2016-111 | 0.9674 | 0.92341 | -0.043988 |  | 0.95 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2016-111 | 0.9674 | 0.92341 | -0.043988 |  | 0.95 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2016-111 | 0.9674 | 0.92341 | -0.043988 |  | 0.95 | 1.05 | 0.072188 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2016-111 | 0.9674 | 0.92341 | -0.043988 |  | 0.95 | 1.05 | 0.042186 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2016-111 | 0.9674 | 0.92341 | -0.043988 |  | 0.95 | 1.05 | 0.041423 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2016-111 | 0.9674 | 0.92341 | -0.043988 |  | 0.95 | 1.05 | 0.050171 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2016-111 | 0.9674 | 0.92341 | -0.043988 |  | 0.95 | 1.05 | 0.04386 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2016-111 | 0.9674 | 0.92341 | -0.043988 |  | 0.95 | 1.05 | 0.050218 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2016-111 | 0.9674 | 0.92341 | -0.043988 |  | 0.95 | 1.05 | 0.040041 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2016-111 | 0.9674 | 0.92341 | -0.043988 |  | 0.95 | 1.05 | 0.038784 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2016-111 | 0.96549 | 0.92362 | -0.041866 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2016-111 | 0.96549 | 0.92362 | -0.041866 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2016-111 | 0.96549 | 0.92362 | -0.041866 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2016-111 | 0.96549 | 0.92362 | -0.041866 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2016-111 | 0.96549 | 0.92362 | -0.041866 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2016-111 | 0.96549 | 0.92362 | -0.041866 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2016-111 | 0.96549 | 0.92362 | -0.041866 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2016-111 | 0.96549 | 0.92362 | -0.041866 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2016-111 | 0.96549 | 0.92362 | -0.041866 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2016-111 | 0.96549 | 0.92362 | -0.041866 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2016-111 | 0.96549 | 0.92362 | -0.041866 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2016-111 | 0.96549 | 0.92362 | -0.041866 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2016-111 | 0.96549 | 0.92362 | -0.041866 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2016-111 | 0.96549 | 0.92362 | -0.041866 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2016-111 | 0.96549 | 0.92362 | -0.041866 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2016-111 | 0.96549 | 0.92362 | -0.041866 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2016-111 | 0.96549 | 0.92362 | -0.041866 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2016-111 | 0.96549 | 0.92362 | -0.041866 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2016-111 | 0.96549 | 0.92362 | -0.041866 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2016-111 | 0.96549 | 0.92362 | -0.041866 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2016-111 | 0.9693 | 0.92225 | -0.047055 |  | 0.95 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2016-111 | 0.9693 | 0.92225 | -0.047055 |  | 0.95 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2016-111 | 0.9693 | 0.92225 | -0.047055 |  | 0.95 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2016-111 | 0.9693 | 0.92225 | -0.047055 |  | 0.95 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2016-111 | 0.9693 | 0.92225 | -0.047055 |  | 0.95 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2016-111 | 0.9693 | 0.92225 | -0.047055 |  | 0.95 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2016-111 | 0.9693 | 0.92225 | -0.047055 |  | 0.95 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2016-111 | 0.9693 | 0.92225 | -0.047055 |  | 0.95 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2016-111 | 0.9693 | 0.92225 | -0.047055 |  | 0.95 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2016-111 | 0.9693 | 0.92225 | -0.047055 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2016-111 | 0.9693 | 0.92225 | -0.047055 |  | 0.95 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2016-111 | 0.9693 | 0.92225 | -0.047055 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2016-111 | 0.9693 | 0.92225 | -0.047055 |  | 0.95 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2016-111 | 0.9693 | 0.92225 | -0.047055 |  | 0.95 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2016-111 | 0.9693 | 0.92225 | -0.047055 |  | 0.95 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2016-111 | 0.9693 | 0.92225 | -0.047055 |  | 0.95 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2016-111 | 0.9693 | 0.92225 | -0.047055 |  | 0.95 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2016-111 | 0.9693 | 0.92225 | -0.047055 |  | 0.95 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2016-111 | 0.9693 | 0.92225 | -0.047055 |  | 0.95 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2016-111 | 0.9693 | 0.92225 | -0.047055 |  | 0.95 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2016-111 | 0.9693 | 0.92225 | -0.047055 |  | 0.95 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2016-111 | 0.9693 | 0.92225 | -0.047055 |  | 0.95 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2016-111 | 0.95759 | 0.87957 | -0.078025 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2016-111 | 0.95759 | 0.87957 | -0.078025 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2016-111 | 0.95759 | 0.87957 | -0.078025 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2016-111 | 0.95759 | 0.87957 | -0.078025 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2016-111 | 0.95759 | 0.87957 | -0.078025 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2016-111 | 0.95759 | 0.87957 | -0.078025 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2016-111 | 0.95759 | 0.87957 | -0.078025 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2016-111 | 0.95759 | 0.87957 | -0.078025 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2016-111 | 0.95759 | 0.87957 | -0.078025 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2016-111 | 0.95759 | 0.87957 | -0.078025 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2016-111 | 0.95759 | 0.87957 | -0.078025 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2016-111 | 0.95759 | 0.87957 | -0.078025 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2016-111 | 0.95759 | 0.87957 | -0.078025 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2016-111 | 0.95759 | 0.87957 | -0.078025 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2016-111 | 0.95759 | 0.87957 | -0.078025 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2016-111 | 0.95759 | 0.87957 | -0.078025 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2016-111 | 0.95759 | 0.87957 | -0.078025 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2016-111 | 0.95759 | 0.87957 | -0.078025 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2016-111 | 0.95759 | 0.87957 | -0.078025 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2016-111 | 0.95759 | 0.87957 | -0.078025 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2016-111 | 0.95759 | 0.87957 | -0.078025 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2016-111 | 0.95759 | 0.87957 | -0.078025 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2016-111 | 0.95759 | 0.87957 | -0.078025 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2016-111 | 0.95759 | 0.87957 | -0.078025 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2016-111 | 0.95759 | 0.87957 | -0.078025 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2016-111 | 0.95759 | 0.87957 | -0.078025 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2016-111 | 0.95759 | 0.87957 | -0.078025 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2016-111 | 0.95759 | 0.87957 | -0.078025 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2017-022 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.094783 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2017-022 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.03645 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2017-022 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.04755 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2017-022 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.06097 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2017-022 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.061051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2017-022 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.04456 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2017-022 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.048811 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2017-022 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.13004 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2017-022 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.049018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2017-022 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2017-022 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2017-022 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.05974 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2017-022 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.076949 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2017-022 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.042157 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2017-022 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.040957 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2017-022 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2017-022 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2017-022 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.054637 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2017-022 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.060597 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2017-022 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.044286 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2017-022 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.059107 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2017-022 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.052698 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2017-022 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.067422 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2017-022 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.053768 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2017-022 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.03909 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2017-022 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2017-022 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2017-022 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2017-022 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2017-022 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2017-022 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2017-022 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2017-022 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2017-022 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2017-022 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2017-022 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2017-022 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2017-022 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2017-022 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2017-022 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2017-022 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2017-022 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2017-022 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2017-022 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2017-022 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2017-022 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2017-022 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2017-022 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2017-022 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2017-022 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2017-022 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2017-022 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2017-022 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2017-022 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2017-022 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2017-022 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2017-022 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2017-022 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2017-022 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2017-022 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2017-022 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2017-022 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2017-022 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2017-022 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2017-022 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2017-022 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2017-022 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2017-022 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2017-022 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2017-022 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2017-022 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2017-022 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2017-022 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2017-022 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2017-022 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2017-086 | 0.99687 | 0.94486 | -0.052011 |  | 0.95 | 1.05 | 0.040027 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2017-086 | 0.99687 | 0.94486 | -0.052011 |  | 0.95 | 1.05 | 0.090773 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2017-086 | 0.99687 | 0.94486 | -0.052011 |  | 0.95 | 1.05 | 0.034521 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2017-086 | 0.99687 | 0.94486 | -0.052011 |  | 0.95 | 1.05 | 0.038035 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2017-086 | 0.99687 | 0.94486 | -0.052011 |  | 0.95 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2017-086 | 0.99687 | 0.94486 | -0.052011 |  | 0.95 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2017-086 | 0.99687 | 0.94486 | -0.052011 |  | 0.95 | 1.05 | 0.050618 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2017-086 | 0.99687 | 0.94486 | -0.052011 |  | 0.95 | 1.05 | 0.04163 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2017-086 | 0.99687 | 0.94486 | -0.052011 |  | 0.95 | 1.05 | 0.043776 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2017-086 | 0.99687 | 0.94486 | -0.052011 |  | 0.95 | 1.05 | 0.034868 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2017-086 | 0.99687 | 0.94486 | -0.052011 |  | 0.95 | 1.05 | 0.031975 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2017-086 | 0.99687 | 0.94486 | -0.052011 |  | 0.95 | 1.05 | 0.037422 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2017-086 | 0.99687 | 0.94486 | -0.052011 |  | 0.95 | 1.05 | 0.050095 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2017-086 | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.094783 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2017-086 | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.03645 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2017-086 | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.04755 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2017-086 | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.06097 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2017-086 | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.061051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2017-086 | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.04456 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2017-086 | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.048811 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2017-086 | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.13004 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2017-086 | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.049018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2017-086 | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2017-086 | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2017-086 | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.05974 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2017-086 | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.076949 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2017-086 | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.042157 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2017-086 | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.040957 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2017-086 | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2017-086 | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2017-086 | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.054637 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2017-086 | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.060597 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2017-086 | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.044286 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2017-086 | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.059107 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2017-086 | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.052698 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2017-086 | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.067422 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2017-086 | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.053768 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2017-086 | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.03909 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2017-108 | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2017-108 | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2017-108 | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2017-108 | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2017-108 | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2017-108 | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2017-108 | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2017-108 | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2017-108 | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2017-108 | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2017-108 | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2017-108 | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2017-108 | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2017-108 | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2017-108 | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2017-108 | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2017-108 | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2017-108 | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2017-108 | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2017-108 | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2017-108 | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2017-108 | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2017-108 | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2017-108 | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2017-108 | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2017-108 | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2017-108 | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2017-108 | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2017-195 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2017-195 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2017-195 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2017-195 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2017-195 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2017-195 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2017-195 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2017-195 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2017-195 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2017-195 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2017-195 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2017-195 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2017-195 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2017-195 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2017-195 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2017-195 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2017-195 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2017-195 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2017-195 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2017-195 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2017-195 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2017-195 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2017-195 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2017-195 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2017-195 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2017-195 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2017-195 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2017-195 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2017-195 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2017-195 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2017-195 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2017-195 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2017-195 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2017-195 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2017-195 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2017-195 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2017-195 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2017-195 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2017-195 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2017-195 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2017-195 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2017-195 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2017-195 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2017-195 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2017-195 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2017-195 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2017-195 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2017-195 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2017-195 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2017-195 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2017-195 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2017-195 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2017-195 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2017-195 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2017-195 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2017-195 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2017-195 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2017-195 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2017-195 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2017-195 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2017-195 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2017-195 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2017-195 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2017-195 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2017-195 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2017-195 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2017-195 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2017-195 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2017-195 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2017-195 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2017-195 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2017-195 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2017-195 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2017-195 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2017-195 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2017-195 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2017-195 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2017-195 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2017-195 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2017-195 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2017-195 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2017-195 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2017-195 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2017-195 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2017-195 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2017-195 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2017-195 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2017-195 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2017-195 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2017-195 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2017-195 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2017-195 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2017-195 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2017-195 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2017-195 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2017-195 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2017-195 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2017-195 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2017-195 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2017-195 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2017-195 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2017-195 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2017-195 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2017-195 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2017-195 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2017-195 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2017-195 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2017-195 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2017-220 | 0.98797 | 0.94829 | -0.039681 |  | 0.95 | 1.05 | 0.077434 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2017-220 | 0.98797 | 0.94829 | -0.039681 |  | 0.95 | 1.05 | 0.032924 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2017-220 | 0.98797 | 0.94829 | -0.039681 |  | 0.95 | 1.05 | 0.032924 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2017-220 | 0.98797 | 0.94829 | -0.039681 |  | 0.95 | 1.05 | 0.032685 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2017-220 | 0.98797 | 0.94829 | -0.039681 |  | 0.95 | 1.05 | 0.030104 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2017-220 | 0.98797 | 0.94829 | -0.039681 |  | 0.95 | 1.05 | 0.036404 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2017-220 | 0.98797 | 0.94829 | -0.039681 |  | 0.95 | 1.05 | 0.077434 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2017-220 | 0.98797 | 0.94829 | -0.039681 |  | 0.95 | 1.05 | 0.032924 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2017-220 | 0.98797 | 0.94829 | -0.039681 |  | 0.95 | 1.05 | 0.032924 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2017-220 | 0.98797 | 0.94829 | -0.039681 |  | 0.95 | 1.05 | 0.032685 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2017-220 | 0.98797 | 0.94829 | -0.039681 |  | 0.95 | 1.05 | 0.030104 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2017-220 | 0.98797 | 0.94829 | -0.039681 |  | 0.95 | 1.05 | 0.036404 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2017-220 | 0.98785 | 0.94773 | -0.04011 |  | 0.95 | 1.05 | 0.077434 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2017-220 | 0.98785 | 0.94773 | -0.04011 |  | 0.95 | 1.05 | 0.032924 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2017-220 | 0.98785 | 0.94773 | -0.04011 |  | 0.95 | 1.05 | 0.032924 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2017-220 | 0.98785 | 0.94773 | -0.04011 |  | 0.95 | 1.05 | 0.032685 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2017-220 | 0.98785 | 0.94773 | -0.04011 |  | 0.95 | 1.05 | 0.030104 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2017-220 | 0.98785 | 0.94773 | -0.04011 |  | 0.95 | 1.05 | 0.036404 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2017-220 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2017-220 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2017-220 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2017-220 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2017-220 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2017-220 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2017-220 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2017-220 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2017-220 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2017-220 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2017-220 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2017-220 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2017-220 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2017-220 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2017-220 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2017-220 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2017-220 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2017-220 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2017-220 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2017-220 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2017-220 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2017-220 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2017-220 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2017-220 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2017-220 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2017-220 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2017-220 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2017-220 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2017-220 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2017-220 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2017-220 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2017-220 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2017-220 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2017-220 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2017-220 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2017-220 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2017-220 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2017-220 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2017-220 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2017-220 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2017-220 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2017-220 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2017-220 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2017-220 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2017-220 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2017-220 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2017-220 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2017-220 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2017-220 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2017-220 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | GEN-2018-032 | 0.99937 | 0.94716 | -0.052208 |  | 0.95 | 1.05 | 0.077629 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | GEN-2018-032 | 0.99937 | 0.94716 | -0.052208 |  | 0.95 | 1.05 | 0.06446 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | GEN-2018-032 | 0.99937 | 0.94716 | -0.052208 |  | 0.95 | 1.05 | 0.066434 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | GEN-2018-032 | 0.99937 | 0.94716 | -0.052208 |  | 0.95 | 1.05 | 0.073293 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2018-032 | 0.99937 | 0.94716 | -0.052208 |  | 0.95 | 1.05 | 0.053415 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-122 | GEN-2018-032 | 0.99937 | 0.94716 | -0.052208 |  | 0.95 | 1.05 | 0.08103 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-177 | GEN-2018-032 | 0.99937 | 0.94716 | -0.052208 |  | 0.95 | 1.05 | 0.08268 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-178 | GEN-2018-032 | 0.99937 | 0.94716 | -0.052208 |  | 0.95 | 1.05 | 0.077122 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2018-032 | 0.99937 | 0.94716 | -0.052208 |  | 0.95 | 1.05 | 0.032185 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | GEN-2018-032 | 0.99937 | 0.94716 | -0.052208 |  | 0.95 | 1.05 | 0.073922 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-232 | GEN-2018-032 | 0.99937 | 0.94716 | -0.052208 |  | 0.95 | 1.05 | 0.076776 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | GEN-2018-032 | 0.99937 | 0.94716 | -0.052208 |  | 0.95 | 1.05 | 0.06446 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2018-032 | 0.99937 | 0.94716 | -0.052208 |  | 0.95 | 1.05 | 0.038841 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2018-032 | 0.99937 | 0.94716 | -0.052208 |  | 0.95 | 1.05 | 0.034687 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2018-032 | 0.99937 | 0.94716 | -0.052208 |  | 0.95 | 1.05 | 0.034687 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2018-032 | 0.99937 | 0.94716 | -0.052208 |  | 0.95 | 1.05 | 0.031574 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2018-032 | 0.99937 | 0.94716 | -0.052208 |  | 0.95 | 1.05 | 0.042889 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-376 | GEN-2018-032 | 0.99937 | 0.94716 | -0.052208 |  | 0.95 | 1.05 | 0.079908 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2018-032 | 0.99613 | 0.9483 | -0.047827 |  | 0.95 | 1.05 | 0.040299 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2018-032 | 0.99613 | 0.9483 | -0.047827 |  | 0.95 | 1.05 | 0.048812 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2018-032 | 0.99613 | 0.9483 | -0.047827 |  | 0.95 | 1.05 | 0.076211 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2018-032 | 0.99613 | 0.9483 | -0.047827 |  | 0.95 | 1.05 | 0.069331 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2018-032 | 0.99613 | 0.9483 | -0.047827 |  | 0.95 | 1.05 | 0.035943 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2018-032 | 0.99613 | 0.9483 | -0.047827 |  | 0.95 | 1.05 | 0.034061 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2018-032 | 0.99613 | 0.9483 | -0.047827 |  | 0.95 | 1.05 | 0.064216 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2018-032 | 0.99613 | 0.9483 | -0.047827 |  | 0.95 | 1.05 | 0.045005 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2018-032 | 0.99613 | 0.9483 | -0.047827 |  | 0.95 | 1.05 | 0.13572 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2018-032 | 0.99613 | 0.9483 | -0.047827 |  | 0.95 | 1.05 | 0.037472 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2018-032 | 0.99613 | 0.9483 | -0.047827 |  | 0.95 | 1.05 | 0.037472 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2018-032 | 0.99613 | 0.9483 | -0.047827 |  | 0.95 | 1.05 | 0.06894 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2018-032 | 0.99613 | 0.9483 | -0.047827 |  | 0.95 | 1.05 | 0.034713 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2018-032 | 0.99613 | 0.9483 | -0.047827 |  | 0.95 | 1.05 | 0.035229 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2018-032 | 0.9964 | 0.94985 | -0.046554 |  | 0.95 | 1.05 | 0.094783 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2018-032 | 0.9964 | 0.94985 | -0.046554 |  | 0.95 | 1.05 | 0.03645 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2018-032 | 0.9964 | 0.94985 | -0.046554 |  | 0.95 | 1.05 | 0.04755 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2018-032 | 0.9964 | 0.94985 | -0.046554 |  | 0.95 | 1.05 | 0.06097 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2018-032 | 0.9964 | 0.94985 | -0.046554 |  | 0.95 | 1.05 | 0.061051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2018-032 | 0.9964 | 0.94985 | -0.046554 |  | 0.95 | 1.05 | 0.04456 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2018-032 | 0.9964 | 0.94985 | -0.046554 |  | 0.95 | 1.05 | 0.048811 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2018-032 | 0.9964 | 0.94985 | -0.046554 |  | 0.95 | 1.05 | 0.13004 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2018-032 | 0.9964 | 0.94985 | -0.046554 |  | 0.95 | 1.05 | 0.049018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2018-032 | 0.9964 | 0.94985 | -0.046554 |  | 0.95 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2018-032 | 0.9964 | 0.94985 | -0.046554 |  | 0.95 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2018-032 | 0.9964 | 0.94985 | -0.046554 |  | 0.95 | 1.05 | 0.05974 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2018-032 | 0.9964 | 0.94985 | -0.046554 |  | 0.95 | 1.05 | 0.076949 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2018-032 | 0.9964 | 0.94985 | -0.046554 |  | 0.95 | 1.05 | 0.042157 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2018-032 | 0.9964 | 0.94985 | -0.046554 |  | 0.95 | 1.05 | 0.040957 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2018-032 | 0.9964 | 0.94985 | -0.046554 |  | 0.95 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2018-032 | 0.9964 | 0.94985 | -0.046554 |  | 0.95 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2018-032 | 0.9964 | 0.94985 | -0.046554 |  | 0.95 | 1.05 | 0.054637 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2018-032 | 0.9964 | 0.94985 | -0.046554 |  | 0.95 | 1.05 | 0.060597 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2018-032 | 0.9964 | 0.94985 | -0.046554 |  | 0.95 | 1.05 | 0.044286 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2018-032 | 0.9964 | 0.94985 | -0.046554 |  | 0.95 | 1.05 | 0.059107 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2018-032 | 0.9964 | 0.94985 | -0.046554 |  | 0.95 | 1.05 | 0.052698 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2018-032 | 0.9964 | 0.94985 | -0.046554 |  | 0.95 | 1.05 | 0.067422 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2018-032 | 0.9964 | 0.94985 | -0.046554 |  | 0.95 | 1.05 | 0.053768 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2018-032 | 0.9964 | 0.94985 | -0.046554 |  | 0.95 | 1.05 | 0.03909 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2018-032 | 0.99496 | 0.94276 | -0.052209 |  | 0.95 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2018-032 | 0.99496 | 0.94276 | -0.052209 |  | 0.95 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2018-032 | 0.99496 | 0.94276 | -0.052209 |  | 0.95 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2018-032 | 0.99496 | 0.94276 | -0.052209 |  | 0.95 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2018-032 | 0.99496 | 0.94276 | -0.052209 |  | 0.95 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2018-032 | 0.99496 | 0.94276 | -0.052209 |  | 0.95 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2018-032 | 0.99496 | 0.94276 | -0.052209 |  | 0.95 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2018-032 | 0.99496 | 0.94276 | -0.052209 |  | 0.95 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2018-032 | 0.99496 | 0.94276 | -0.052209 |  | 0.95 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2018-032 | 0.99496 | 0.94276 | -0.052209 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2018-032 | 0.99496 | 0.94276 | -0.052209 |  | 0.95 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2018-032 | 0.99496 | 0.94276 | -0.052209 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2018-032 | 0.99496 | 0.94276 | -0.052209 |  | 0.95 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2018-032 | 0.99496 | 0.94276 | -0.052209 |  | 0.95 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2018-032 | 0.99496 | 0.94276 | -0.052209 |  | 0.95 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2018-032 | 0.99496 | 0.94276 | -0.052209 |  | 0.95 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2018-032 | 0.99496 | 0.94276 | -0.052209 |  | 0.95 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2018-032 | 0.99496 | 0.94276 | -0.052209 |  | 0.95 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2018-032 | 0.99496 | 0.94276 | -0.052209 |  | 0.95 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2018-032 | 0.99496 | 0.94276 | -0.052209 |  | 0.95 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2018-032 | 0.99496 | 0.94276 | -0.052209 |  | 0.95 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2018-032 | 0.99496 | 0.94276 | -0.052209 |  | 0.95 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2018-032 | 0.99504 | 0.92478 | -0.070256 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2018-032 | 0.99504 | 0.92478 | -0.070256 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2018-032 | 0.99504 | 0.92478 | -0.070256 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2018-032 | 0.99504 | 0.92478 | -0.070256 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2018-032 | 0.99504 | 0.92478 | -0.070256 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2018-032 | 0.99504 | 0.92478 | -0.070256 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2018-032 | 0.99504 | 0.92478 | -0.070256 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2018-032 | 0.99504 | 0.92478 | -0.070256 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2018-032 | 0.99504 | 0.92478 | -0.070256 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2018-032 | 0.99504 | 0.92478 | -0.070256 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2018-032 | 0.99504 | 0.92478 | -0.070256 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2018-032 | 0.99504 | 0.92478 | -0.070256 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2018-032 | 0.99504 | 0.92478 | -0.070256 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2018-032 | 0.99504 | 0.92478 | -0.070256 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2018-032 | 0.99504 | 0.92478 | -0.070256 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2018-032 | 0.99504 | 0.92478 | -0.070256 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2018-032 | 0.99504 | 0.92478 | -0.070256 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2018-032 | 0.99504 | 0.92478 | -0.070256 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2018-032 | 0.99504 | 0.92478 | -0.070256 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2018-032 | 0.99504 | 0.92478 | -0.070256 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2018-032 | 0.99504 | 0.92478 | -0.070256 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2018-032 | 0.99504 | 0.92478 | -0.070256 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2018-032 | 0.99504 | 0.92478 | -0.070256 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2018-032 | 0.99504 | 0.92478 | -0.070256 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2018-032 | 0.99504 | 0.92478 | -0.070256 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2018-032 | 0.99504 | 0.92478 | -0.070256 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2018-032 | 0.99504 | 0.92478 | -0.070256 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2018-032 | 0.99504 | 0.92478 | -0.070256 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2018-128 | 0.9804 | 0.91602 | -0.06438 |  | 0.92 | 1.05 | 0.040027 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2018-128 | 0.9804 | 0.91602 | -0.06438 |  | 0.92 | 1.05 | 0.090773 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2018-128 | 0.9804 | 0.91602 | -0.06438 |  | 0.92 | 1.05 | 0.034521 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2018-128 | 0.9804 | 0.91602 | -0.06438 |  | 0.92 | 1.05 | 0.038035 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2018-128 | 0.9804 | 0.91602 | -0.06438 |  | 0.92 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2018-128 | 0.9804 | 0.91602 | -0.06438 |  | 0.92 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2018-128 | 0.9804 | 0.91602 | -0.06438 |  | 0.92 | 1.05 | 0.050618 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2018-128 | 0.9804 | 0.91602 | -0.06438 |  | 0.92 | 1.05 | 0.04163 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2018-128 | 0.9804 | 0.91602 | -0.06438 |  | 0.92 | 1.05 | 0.043776 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2018-128 | 0.9804 | 0.91602 | -0.06438 |  | 0.92 | 1.05 | 0.034868 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2018-128 | 0.9804 | 0.91602 | -0.06438 |  | 0.92 | 1.05 | 0.031975 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2018-128 | 0.9804 | 0.91602 | -0.06438 |  | 0.92 | 1.05 | 0.037422 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2018-128 | 0.9804 | 0.91602 | -0.06438 |  | 0.92 | 1.05 | 0.050095 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2018-128 | 0.97367 | 0.91176 | -0.061906 |  | 0.92 | 1.05 | 0.094783 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2018-128 | 0.97367 | 0.91176 | -0.061906 |  | 0.92 | 1.05 | 0.03645 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2018-128 | 0.97367 | 0.91176 | -0.061906 |  | 0.92 | 1.05 | 0.04755 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2018-128 | 0.97367 | 0.91176 | -0.061906 |  | 0.92 | 1.05 | 0.06097 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2018-128 | 0.97367 | 0.91176 | -0.061906 |  | 0.92 | 1.05 | 0.061051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2018-128 | 0.97367 | 0.91176 | -0.061906 |  | 0.92 | 1.05 | 0.04456 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2018-128 | 0.97367 | 0.91176 | -0.061906 |  | 0.92 | 1.05 | 0.048811 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2018-128 | 0.97367 | 0.91176 | -0.061906 |  | 0.92 | 1.05 | 0.13004 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2018-128 | 0.97367 | 0.91176 | -0.061906 |  | 0.92 | 1.05 | 0.049018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2018-128 | 0.97367 | 0.91176 | -0.061906 |  | 0.92 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2018-128 | 0.97367 | 0.91176 | -0.061906 |  | 0.92 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2018-128 | 0.97367 | 0.91176 | -0.061906 |  | 0.92 | 1.05 | 0.05974 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2018-128 | 0.97367 | 0.91176 | -0.061906 |  | 0.92 | 1.05 | 0.076949 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2018-128 | 0.97367 | 0.91176 | -0.061906 |  | 0.92 | 1.05 | 0.042157 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2018-128 | 0.97367 | 0.91176 | -0.061906 |  | 0.92 | 1.05 | 0.040957 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2018-128 | 0.97367 | 0.91176 | -0.061906 |  | 0.92 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2018-128 | 0.97367 | 0.91176 | -0.061906 |  | 0.92 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2018-128 | 0.97367 | 0.91176 | -0.061906 |  | 0.92 | 1.05 | 0.054637 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2018-128 | 0.97367 | 0.91176 | -0.061906 |  | 0.92 | 1.05 | 0.060597 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2018-128 | 0.97367 | 0.91176 | -0.061906 |  | 0.92 | 1.05 | 0.044286 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2018-128 | 0.97367 | 0.91176 | -0.061906 |  | 0.92 | 1.05 | 0.059107 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2018-128 | 0.97367 | 0.91176 | -0.061906 |  | 0.92 | 1.05 | 0.052698 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2018-128 | 0.97367 | 0.91176 | -0.061906 |  | 0.92 | 1.05 | 0.067422 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2018-128 | 0.97367 | 0.91176 | -0.061906 |  | 0.92 | 1.05 | 0.053768 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2018-128 | 0.97367 | 0.91176 | -0.061906 |  | 0.92 | 1.05 | 0.03909 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2019-016 | 0.97819 | 0.91595 | -0.062245 |  | 0.925 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2019-016 | 0.97819 | 0.91595 | -0.062245 |  | 0.925 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2019-016 | 0.97819 | 0.91595 | -0.062245 |  | 0.925 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2019-016 | 0.97819 | 0.91595 | -0.062245 |  | 0.925 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2019-016 | 0.97819 | 0.91595 | -0.062245 |  | 0.925 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2019-016 | 0.97819 | 0.91595 | -0.062245 |  | 0.925 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2019-016 | 0.97819 | 0.91595 | -0.062245 |  | 0.925 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2019-016 | 0.97819 | 0.91595 | -0.062245 |  | 0.925 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2019-016 | 0.97819 | 0.91595 | -0.062245 |  | 0.925 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2019-016 | 0.97819 | 0.91595 | -0.062245 |  | 0.925 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2019-016 | 0.97819 | 0.91595 | -0.062245 |  | 0.925 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2019-016 | 0.97819 | 0.91595 | -0.062245 |  | 0.925 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2019-016 | 0.97819 | 0.91595 | -0.062245 |  | 0.925 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2019-016 | 0.97819 | 0.91595 | -0.062245 |  | 0.925 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2019-016 | 0.97819 | 0.91595 | -0.062245 |  | 0.925 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2019-016 | 0.97819 | 0.91595 | -0.062245 |  | 0.925 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2019-016 | 0.97819 | 0.91595 | -0.062245 |  | 0.925 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2019-016 | 0.97819 | 0.91595 | -0.062245 |  | 0.925 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2019-016 | 0.97819 | 0.91595 | -0.062245 |  | 0.925 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2019-016 | 0.97819 | 0.91595 | -0.062245 |  | 0.925 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2019-016 | 0.97819 | 0.91595 | -0.062245 |  | 0.925 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2019-016 | 0.97819 | 0.91595 | -0.062245 |  | 0.925 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2019-016 | 0.97819 | 0.91595 | -0.062245 |  | 0.925 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2019-016 | 0.97819 | 0.91595 | -0.062245 |  | 0.925 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2019-016 | 0.97819 | 0.91595 | -0.062245 |  | 0.925 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2019-016 | 0.97819 | 0.91595 | -0.062245 |  | 0.925 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2019-016 | 0.97819 | 0.91595 | -0.062245 |  | 0.925 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2019-016 | 0.97819 | 0.91595 | -0.062245 |  | 0.925 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | GEN-2020-007 | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.030773 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | GEN-2020-007 | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2020-007 | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.046711 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | GEN-2020-007 | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.032369 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | GEN-2020-007 | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.030466 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2020-007 | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.04987 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2020-007 | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.099365 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2020-007 | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.071132 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2020-007 | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.043927 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2020-007 | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.030565 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2020-007 | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.072847 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2020-007 | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.041148 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2020-007 | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.042015 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | GEN-2020-007 | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.030318 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2020-007 | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.054104 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2020-007 | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.047089 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2020-007 | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2020-007 | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.13688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | GEN-2020-007 | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2020-007 | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2020-007 | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.039752 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2020-007 | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.041972 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2020-007 | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.054397 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2020-007 | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.073688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2020-007 | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2020-007 | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2020-007 | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.072188 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2020-007 | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.042186 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2020-007 | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.041423 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2020-007 | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.050171 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2020-007 | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.04386 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2020-007 | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.050218 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2020-007 | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.040041 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2020-007 | 0.98901 | 0.93398 | -0.055036 |  | 0.95 | 1.05 | 0.038784 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2020-007 | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2020-007 | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2020-007 | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2020-007 | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2020-007 | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2020-007 | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2020-007 | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2020-007 | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2020-007 | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2020-007 | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2020-007 | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2020-007 | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2020-007 | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2020-007 | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2020-007 | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2020-007 | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2020-007 | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2020-007 | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2020-007 | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2020-007 | 0.99783 | 0.93246 | -0.06537 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2020-007 | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2020-007 | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2020-007 | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2020-007 | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2020-007 | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2020-007 | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2020-007 | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2020-007 | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2020-007 | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2020-007 | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2020-007 | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2020-007 | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2020-007 | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2020-007 | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2020-007 | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2020-007 | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2020-007 | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2020-007 | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2020-007 | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2020-007 | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2020-007 | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2020-007 | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2020-007 | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2020-007 | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2020-007 | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2020-007 | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2020-007 | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2020-007 | 0.98874 | 0.87964 | -0.1091 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2020-057 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2020-057 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2020-057 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2020-057 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2020-057 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2020-057 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2020-057 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2020-057 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2020-057 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2020-057 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2020-057 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2020-057 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2020-057 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2020-057 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2020-057 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2020-057 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2020-057 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2020-057 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2020-057 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2020-057 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2020-057 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2020-057 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2020-057 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2020-057 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2020-057 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2020-057 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2020-057 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2020-057 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2020-057 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2020-057 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2020-057 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2020-057 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2020-057 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2020-057 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2020-057 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2020-057 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2020-057 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2020-057 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2020-057 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2020-057 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2020-057 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2020-057 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2020-057 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2020-057 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2020-057 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2020-057 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2020-057 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2020-057 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2020-057 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2020-057 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2020-057 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2020-057 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2020-057 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2020-057 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2020-057 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2020-057 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2020-057 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2020-057 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2020-057 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2020-057 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2020-057 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2020-057 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2020-057 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2020-057 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2020-057 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2020-057 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2020-057 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2020-057 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2020-057 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2020-057 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2020-057 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2020-057 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2020-057 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2020-057 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2020-057 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2020-057 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2020-057 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2020-057 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2020-057 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2020-057 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2020-057 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2020-057 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2020-057 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2020-057 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2020-057 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2020-057 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2020-057 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2020-057 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2020-057 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2020-057 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2020-057 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2020-057 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2020-057 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2020-057 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2020-057 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2020-057 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2020-057 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2020-057 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2020-057 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2020-057 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2020-057 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2020-057 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2020-057 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2020-057 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2020-057 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2020-057 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2020-057 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2020-057 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2020-058 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2020-058 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2020-058 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2020-058 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2020-058 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2020-058 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2020-058 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2020-058 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2020-058 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2020-058 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2020-058 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2020-058 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2020-058 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2020-058 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2020-058 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2020-058 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2020-058 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2020-058 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2020-058 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2020-058 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2020-058 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2020-058 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2020-058 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2020-058 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2020-058 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2020-058 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2020-058 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2020-058 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2020-058 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2020-058 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2020-058 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2020-058 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2020-058 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2020-058 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2020-058 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2020-058 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2020-058 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2020-058 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2020-058 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2020-058 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2020-058 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2020-058 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2020-058 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2020-058 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2020-058 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2020-058 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2020-058 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2020-058 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2020-058 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2020-058 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2020-058 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2020-058 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2020-058 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2020-058 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2020-058 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2020-058 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2020-058 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2020-058 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2020-058 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2020-058 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2020-058 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2020-058 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2020-058 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2020-058 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2020-058 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2020-058 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2020-058 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2020-058 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2020-058 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2020-058 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2020-058 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2020-058 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2020-058 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2020-058 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2020-058 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2020-058 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2020-058 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2020-058 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2020-058 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2020-058 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2020-058 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2020-058 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2020-058 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2020-058 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2020-058 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2020-058 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2020-058 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2020-058 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2020-058 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2020-058 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2020-058 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2020-058 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2020-058 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2020-058 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2020-058 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2020-058 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2020-058 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2020-058 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2020-058 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2020-058 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2020-058 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2020-058 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2020-058 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2020-058 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2020-058 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2020-058 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2020-058 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2020-058 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2020-072 | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2020-072 | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2020-072 | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2020-072 | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2020-072 | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2020-072 | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2020-072 | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2020-072 | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2020-072 | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2020-072 | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2020-072 | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2020-072 | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2020-072 | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2020-072 | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2020-072 | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2020-072 | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2020-072 | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2020-072 | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2020-072 | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2020-072 | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2020-072 | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2020-072 | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2020-072 | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2020-072 | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2020-072 | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2020-072 | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2020-072 | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2020-072 | 0.98603 | 0.91948 | -0.066542 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2020-073 | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2020-073 | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2020-073 | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2020-073 | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2020-073 | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2020-073 | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2020-073 | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2020-073 | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2020-073 | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2020-073 | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2020-073 | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2020-073 | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2020-073 | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2020-073 | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2020-073 | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2020-073 | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2020-073 | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2020-073 | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2020-073 | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2020-073 | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2020-073 | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2020-073 | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2020-073 | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2020-073 | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2020-073 | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2020-073 | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2020-073 | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2020-073 | 1.0104 | 0.92151 | -0.088886 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | GEN-2021-006 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.077629 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | GEN-2021-006 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.06446 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | GEN-2021-006 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.066434 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | GEN-2021-006 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.073293 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2021-006 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.053415 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-122 | GEN-2021-006 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.08103 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-177 | GEN-2021-006 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.08268 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-178 | GEN-2021-006 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.077122 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2021-006 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.032185 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | GEN-2021-006 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.073922 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-232 | GEN-2021-006 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.076776 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | GEN-2021-006 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.06446 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2021-006 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.038841 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2021-006 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.034687 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2021-006 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.034687 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2021-006 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.031574 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2021-006 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.042889 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-376 | GEN-2021-006 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.079908 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2021-006 | 0.99592 | 0.9481 | -0.047817 |  | 0.95 | 1.05 | 0.040299 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2021-006 | 0.99592 | 0.9481 | -0.047817 |  | 0.95 | 1.05 | 0.048812 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2021-006 | 0.99592 | 0.9481 | -0.047817 |  | 0.95 | 1.05 | 0.076211 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2021-006 | 0.99592 | 0.9481 | -0.047817 |  | 0.95 | 1.05 | 0.069331 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2021-006 | 0.99592 | 0.9481 | -0.047817 |  | 0.95 | 1.05 | 0.035943 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2021-006 | 0.99592 | 0.9481 | -0.047817 |  | 0.95 | 1.05 | 0.034061 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2021-006 | 0.99592 | 0.9481 | -0.047817 |  | 0.95 | 1.05 | 0.064216 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2021-006 | 0.99592 | 0.9481 | -0.047817 |  | 0.95 | 1.05 | 0.045005 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2021-006 | 0.99592 | 0.9481 | -0.047817 |  | 0.95 | 1.05 | 0.13572 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2021-006 | 0.99592 | 0.9481 | -0.047817 |  | 0.95 | 1.05 | 0.037472 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2021-006 | 0.99592 | 0.9481 | -0.047817 |  | 0.95 | 1.05 | 0.037472 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2021-006 | 0.99592 | 0.9481 | -0.047817 |  | 0.95 | 1.05 | 0.06894 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2021-006 | 0.99592 | 0.9481 | -0.047817 |  | 0.95 | 1.05 | 0.034713 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2021-006 | 0.99592 | 0.9481 | -0.047817 |  | 0.95 | 1.05 | 0.035229 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2021-006 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.094783 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2021-006 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.03645 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2021-006 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.04755 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2021-006 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.06097 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2021-006 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.061051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2021-006 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.04456 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2021-006 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.048811 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2021-006 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.13004 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2021-006 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.049018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2021-006 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2021-006 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2021-006 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.05974 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2021-006 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.076949 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2021-006 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.042157 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2021-006 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.040957 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2021-006 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2021-006 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2021-006 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.054637 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2021-006 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.060597 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2021-006 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.044286 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2021-006 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.059107 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2021-006 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.052698 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2021-006 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.067422 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2021-006 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.053768 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2021-006 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.03909 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2021-006 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2021-006 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2021-006 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2021-006 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2021-006 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2021-006 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2021-006 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2021-006 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2021-006 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2021-006 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2021-006 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2021-006 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2021-006 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2021-006 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2021-006 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2021-006 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2021-006 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2021-006 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2021-006 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2021-006 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2021-006 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2021-006 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2021-006 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2021-006 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2021-006 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2021-006 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2021-006 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2021-006 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2021-006 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2021-006 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2021-006 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2021-006 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2021-006 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2021-006 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2021-006 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2021-006 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2021-006 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2021-006 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2021-006 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2021-006 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2021-006 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2021-006 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2021-006 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2021-006 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2021-006 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2021-006 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2021-006 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2021-006 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2021-006 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2021-006 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2021-029 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2021-029 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2021-029 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2021-029 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2021-029 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2021-029 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2021-029 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2021-029 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2021-029 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2021-029 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2021-029 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2021-029 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2021-029 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2021-029 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2021-029 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2021-029 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2021-029 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2021-029 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2021-029 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2021-029 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | GEN-2021-029 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.030773 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | GEN-2021-029 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2021-029 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.046711 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | GEN-2021-029 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.032369 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | GEN-2021-029 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.030466 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2021-029 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.04987 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2021-029 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.099365 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2021-029 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.071132 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2021-029 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.043927 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2021-029 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.030565 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2021-029 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.072847 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2021-029 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.041148 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2021-029 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.042015 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | GEN-2021-029 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.030318 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2021-029 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.054104 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2021-029 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.047089 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2021-029 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2021-029 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.13688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | GEN-2021-029 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2021-029 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2021-029 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.039752 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2021-029 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.041972 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2021-029 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.054397 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2021-029 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.073688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2021-029 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2021-029 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2021-029 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.072188 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2021-029 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.042186 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2021-029 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.041423 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2021-029 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.050171 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2021-029 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.04386 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2021-029 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.050218 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2021-029 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.040041 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2021-029 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.038784 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2021-029 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2021-029 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2021-029 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2021-029 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2021-029 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2021-029 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2021-029 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2021-029 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2021-029 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2021-029 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2021-029 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2021-029 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2021-029 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2021-029 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2021-029 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2021-029 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2021-029 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2021-029 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2021-029 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2021-029 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2021-029 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2021-029 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2021-029 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2021-029 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2021-029 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2021-029 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2021-029 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2021-029 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2021-029 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2021-029 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2021-029 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2021-029 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2021-029 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2021-029 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2021-029 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2021-029 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2021-029 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2021-029 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2021-029 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2021-029 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2021-029 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2021-029 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2021-029 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2021-029 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2021-029 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2021-029 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2021-029 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2021-029 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2021-030 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2021-030 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2021-030 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2021-030 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2021-030 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2021-030 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2021-030 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2021-030 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2021-030 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2021-030 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2021-030 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2021-030 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2021-030 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2021-030 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2021-030 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2021-030 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2021-030 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2021-030 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2021-030 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2021-030 | 0.96217 | 0.92041 | -0.041761 |  | 0.95 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | GEN-2021-030 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.030773 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | GEN-2021-030 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2021-030 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.046711 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | GEN-2021-030 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.032369 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | GEN-2021-030 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.030466 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2021-030 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.04987 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2021-030 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.099365 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2021-030 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.071132 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2021-030 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.043927 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2021-030 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.030565 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2021-030 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.072847 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2021-030 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.041148 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2021-030 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.042015 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | GEN-2021-030 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.030318 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2021-030 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.054104 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2021-030 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.047089 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2021-030 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2021-030 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.13688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | GEN-2021-030 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2021-030 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2021-030 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.039752 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2021-030 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.041972 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2021-030 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.054397 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2021-030 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.073688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2021-030 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2021-030 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2021-030 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.072188 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2021-030 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.042186 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2021-030 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.041423 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2021-030 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.050171 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2021-030 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.04386 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2021-030 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.050218 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2021-030 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.040041 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2021-030 | 0.98796 | 0.9337 | -0.054254 |  | 0.95 | 1.05 | 0.038784 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2021-030 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2021-030 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2021-030 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2021-030 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2021-030 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2021-030 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2021-030 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2021-030 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2021-030 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2021-030 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2021-030 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2021-030 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2021-030 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2021-030 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2021-030 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2021-030 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2021-030 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2021-030 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2021-030 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2021-030 | 0.96654 | 0.91502 | -0.051521 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2021-030 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2021-030 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2021-030 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2021-030 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2021-030 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2021-030 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2021-030 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2021-030 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2021-030 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2021-030 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2021-030 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2021-030 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2021-030 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2021-030 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2021-030 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2021-030 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2021-030 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2021-030 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2021-030 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2021-030 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2021-030 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2021-030 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2021-030 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2021-030 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2021-030 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2021-030 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2021-030 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2021-030 | 0.98625 | 0.8771 | -0.10915 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2021-096 | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2021-096 | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2021-096 | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2021-096 | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2021-096 | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2021-096 | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2021-096 | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2021-096 | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2021-096 | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2021-096 | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2021-096 | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2021-096 | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2021-096 | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2021-096 | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2021-096 | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2021-096 | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2021-096 | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2021-096 | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2021-096 | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2021-096 | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2021-096 | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2021-096 | 0.9967 | 0.93353 | -0.063168 |  | 0.95 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2021-103 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2021-103 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2021-103 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2021-103 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2021-103 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2021-103 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2021-103 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2021-103 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2021-103 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2021-103 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2021-103 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2021-103 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2021-103 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2021-103 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2021-103 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2021-103 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2021-103 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2021-103 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2021-103 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2021-103 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2021-103 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2021-103 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2021-103 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2021-103 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2021-103 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2021-103 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2021-103 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2021-103 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2021-103 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2021-103 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2021-103 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2021-103 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2021-103 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2021-103 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2021-103 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2021-103 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2021-103 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2021-103 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2021-103 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2021-103 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2021-103 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2021-103 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2021-103 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2021-103 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2021-103 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2021-103 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2021-103 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2021-103 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2021-103 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2021-103 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2021-103 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2021-103 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2021-103 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2021-103 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2021-103 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2021-103 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2021-103 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2021-103 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2021-103 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2021-103 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2021-103 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2021-103 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2021-103 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2021-103 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2021-103 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2021-103 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2021-103 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2021-103 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2021-103 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2021-103 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2021-103 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2021-103 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2021-103 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2021-103 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2021-103 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2021-103 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2021-103 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2021-103 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2021-103 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2021-103 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2021-103 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2021-103 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2021-103 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2021-103 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2021-103 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2021-103 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2021-103 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2021-103 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2021-103 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2021-103 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2021-103 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2021-103 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2021-103 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2021-103 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2021-103 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2021-103 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2021-103 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2021-103 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2021-103 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2021-103 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2021-103 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2021-103 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2021-103 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2021-103 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2021-103 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2021-103 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2021-103 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2021-103 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2021-107 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.03965 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2021-107 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.042938 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2021-107 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.032864 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2021-107 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.034629 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2021-107 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.036988 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2021-107 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.03396 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2021-107 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.030296 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2021-107 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.037836 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2021-107 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.036214 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2021-107 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.055483 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2021-107 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.036214 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2021-107 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.037031 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2021-107 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.03728 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2021-107 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.034689 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2021-107 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.033481 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2021-107 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.035246 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2021-107 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.03235 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2021-107 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.031498 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2021-107 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.033388 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2021-107 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.034867 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2021-107 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2021-107 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2021-107 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2021-107 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2021-107 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2021-107 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2021-107 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2021-107 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2021-107 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2021-107 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2021-107 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2021-107 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2021-107 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2021-107 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2021-107 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2021-107 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2021-107 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2021-107 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2021-107 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2021-107 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2021-107 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2021-107 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2021-107 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2021-107 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2021-107 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2021-107 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2021-107 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2021-107 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2021-107 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2021-107 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2021-107 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2021-107 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2021-107 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2021-107 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2021-107 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2021-107 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2021-107 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2021-107 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2021-107 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2021-107 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2021-107 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2021-107 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2021-107 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2021-107 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2021-107 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2021-107 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2021-107 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2021-107 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2021-107 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2021-107 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2021-107 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2021-107 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2021-107 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2021-107 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2021-107 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2021-107 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2021-107 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2021-107 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2021-107 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2021-107 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2021-107 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2021-107 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2021-107 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2021-107 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2021-107 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2021-107 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2021-107 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2021-107 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2021-107 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2021-107 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2021-107 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2021-107 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2021-107 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2021-107 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2021-107 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2021-107 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2021-107 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2021-107 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2021-107 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2021-107 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2021-107 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2021-107 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2021-107 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2021-107 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2021-107 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2021-107 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2021-107 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2021-107 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2022-006 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2022-006 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2022-006 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2022-006 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2022-006 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2022-006 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2022-006 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2022-006 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2022-006 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2022-006 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2022-006 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2022-006 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2022-006 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2022-006 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2022-006 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2022-006 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2022-006 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2022-006 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2022-006 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2022-006 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2022-006 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2022-006 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2022-006 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2022-006 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2022-006 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2022-006 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2022-006 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2022-006 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2022-007 | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2022-007 | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2022-007 | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2022-007 | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2022-007 | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2022-007 | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2022-007 | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2022-007 | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2022-007 | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2022-007 | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2022-007 | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2022-007 | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2022-007 | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2022-007 | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2022-007 | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2022-007 | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2022-007 | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2022-007 | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2022-007 | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2022-007 | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2022-007 | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2022-007 | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2022-007 | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2022-007 | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2022-007 | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2022-007 | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2022-007 | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2022-007 | 0.94609 | 0.85886 | -0.087231 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2022-013 | 0.99545 | 0.94191 | -0.053541 |  | 0.95 | 1.05 | 0.040163 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2022-013 | 0.99545 | 0.94191 | -0.053541 |  | 0.95 | 1.05 | 0.035142 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2022-013 | 0.99545 | 0.94191 | -0.053541 |  | 0.95 | 1.05 | 0.037502 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2022-013 | 0.99545 | 0.94191 | -0.053541 |  | 0.95 | 1.05 | 0.03081 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2022-013 | 0.99545 | 0.94191 | -0.053541 |  | 0.95 | 1.05 | 0.03835 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2022-013 | 0.99545 | 0.94191 | -0.053541 |  | 0.95 | 1.05 | 0.036728 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2022-013 | 0.99545 | 0.94191 | -0.053541 |  | 0.95 | 1.05 | 0.036728 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2022-013 | 0.99545 | 0.94191 | -0.053541 |  | 0.95 | 1.05 | 0.037545 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2022-013 | 0.99545 | 0.94191 | -0.053541 |  | 0.95 | 1.05 | 0.037793 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2022-013 | 0.99545 | 0.94191 | -0.053541 |  | 0.95 | 1.05 | 0.03576 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2022-013 | 0.99545 | 0.94191 | -0.053541 |  | 0.95 | 1.05 | 0.032864 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2022-013 | 0.99545 | 0.94191 | -0.053541 |  | 0.95 | 1.05 | 0.032012 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2022-013 | 0.99545 | 0.94191 | -0.053541 |  | 0.95 | 1.05 | 0.033901 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2022-013 | 0.99545 | 0.94191 | -0.053541 |  | 0.95 | 1.05 | 0.035381 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2022-013 | 0.99545 | 0.94393 | -0.051521 |  | 0.95 | 1.05 | 0.03965 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2022-013 | 0.99545 | 0.94393 | -0.051521 |  | 0.95 | 1.05 | 0.034629 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2022-013 | 0.99545 | 0.94393 | -0.051521 |  | 0.95 | 1.05 | 0.036988 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2022-013 | 0.99545 | 0.94393 | -0.051521 |  | 0.95 | 1.05 | 0.030296 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2022-013 | 0.99545 | 0.94393 | -0.051521 |  | 0.95 | 1.05 | 0.037836 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2022-013 | 0.99545 | 0.94393 | -0.051521 |  | 0.95 | 1.05 | 0.036214 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2022-013 | 0.99545 | 0.94393 | -0.051521 |  | 0.95 | 1.05 | 0.036214 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2022-013 | 0.99545 | 0.94393 | -0.051521 |  | 0.95 | 1.05 | 0.037031 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2022-013 | 0.99545 | 0.94393 | -0.051521 |  | 0.95 | 1.05 | 0.03728 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2022-013 | 0.99545 | 0.94393 | -0.051521 |  | 0.95 | 1.05 | 0.035246 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2022-013 | 0.99545 | 0.94393 | -0.051521 |  | 0.95 | 1.05 | 0.03235 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2022-013 | 0.99545 | 0.94393 | -0.051521 |  | 0.95 | 1.05 | 0.031498 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2022-013 | 0.99545 | 0.94393 | -0.051521 |  | 0.95 | 1.05 | 0.033388 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2022-013 | 0.99545 | 0.94393 | -0.051521 |  | 0.95 | 1.05 | 0.034867 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2022-013 | 0.99536 | 0.94425 | -0.051112 |  | 0.95 | 1.05 | 0.03965 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2022-013 | 0.99536 | 0.94425 | -0.051112 |  | 0.95 | 1.05 | 0.034629 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2022-013 | 0.99536 | 0.94425 | -0.051112 |  | 0.95 | 1.05 | 0.036988 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2022-013 | 0.99536 | 0.94425 | -0.051112 |  | 0.95 | 1.05 | 0.030296 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2022-013 | 0.99536 | 0.94425 | -0.051112 |  | 0.95 | 1.05 | 0.037836 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2022-013 | 0.99536 | 0.94425 | -0.051112 |  | 0.95 | 1.05 | 0.036214 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2022-013 | 0.99536 | 0.94425 | -0.051112 |  | 0.95 | 1.05 | 0.036214 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2022-013 | 0.99536 | 0.94425 | -0.051112 |  | 0.95 | 1.05 | 0.037031 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2022-013 | 0.99536 | 0.94425 | -0.051112 |  | 0.95 | 1.05 | 0.03728 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2022-013 | 0.99536 | 0.94425 | -0.051112 |  | 0.95 | 1.05 | 0.035246 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2022-013 | 0.99536 | 0.94425 | -0.051112 |  | 0.95 | 1.05 | 0.03235 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2022-013 | 0.99536 | 0.94425 | -0.051112 |  | 0.95 | 1.05 | 0.031498 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2022-013 | 0.99536 | 0.94425 | -0.051112 |  | 0.95 | 1.05 | 0.033388 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2022-013 | 0.99536 | 0.94425 | -0.051112 |  | 0.95 | 1.05 | 0.034867 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2022-013 | 0.99536 | 0.94428 | -0.051074 |  | 0.95 | 1.05 | 0.03965 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2022-013 | 0.99536 | 0.94428 | -0.051074 |  | 0.95 | 1.05 | 0.034629 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2022-013 | 0.99536 | 0.94428 | -0.051074 |  | 0.95 | 1.05 | 0.036988 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2022-013 | 0.99536 | 0.94428 | -0.051074 |  | 0.95 | 1.05 | 0.030296 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2022-013 | 0.99536 | 0.94428 | -0.051074 |  | 0.95 | 1.05 | 0.037836 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2022-013 | 0.99536 | 0.94428 | -0.051074 |  | 0.95 | 1.05 | 0.036214 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2022-013 | 0.99536 | 0.94428 | -0.051074 |  | 0.95 | 1.05 | 0.036214 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2022-013 | 0.99536 | 0.94428 | -0.051074 |  | 0.95 | 1.05 | 0.037031 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2022-013 | 0.99536 | 0.94428 | -0.051074 |  | 0.95 | 1.05 | 0.03728 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2022-013 | 0.99536 | 0.94428 | -0.051074 |  | 0.95 | 1.05 | 0.035246 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2022-013 | 0.99536 | 0.94428 | -0.051074 |  | 0.95 | 1.05 | 0.03235 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2022-013 | 0.99536 | 0.94428 | -0.051074 |  | 0.95 | 1.05 | 0.031498 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2022-013 | 0.99536 | 0.94428 | -0.051074 |  | 0.95 | 1.05 | 0.033388 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2022-013 | 0.99536 | 0.94428 | -0.051074 |  | 0.95 | 1.05 | 0.034867 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2022-013 | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2022-013 | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2022-013 | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2022-013 | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2022-013 | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2022-013 | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2022-013 | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2022-013 | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2022-013 | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2022-013 | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2022-013 | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2022-013 | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2022-013 | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2022-013 | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2022-013 | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2022-013 | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2022-013 | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2022-013 | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2022-013 | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2022-013 | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2022-013 | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2022-013 | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2022-013 | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2022-013 | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2022-013 | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2022-013 | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2022-013 | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2022-013 | 0.98859 | 0.89132 | -0.097274 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2022-075 | 0.96244 | 0.8851 | -0.077345 |  | 0.9 | 1.05 | 0.064516 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2022-075 | 0.96639 | 0.89813 | -0.068266 |  | 0.9 | 1.05 | 0.0326 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2022-075 | 0.96639 | 0.89813 | -0.068266 |  | 0.9 | 1.05 | 0.030348 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2022-075 | 0.96639 | 0.89813 | -0.068266 |  | 0.9 | 1.05 | 0.031036 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2022-075 | 0.96639 | 0.89813 | -0.068266 |  | 0.9 | 1.05 | 0.030059 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2022-075 | 0.96639 | 0.89813 | -0.068266 |  | 0.9 | 1.05 | 0.030059 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2022-075 | 0.96639 | 0.89813 | -0.068266 |  | 0.9 | 1.05 | 0.030771 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2022-075 | 0.96639 | 0.89813 | -0.068266 |  | 0.9 | 1.05 | 0.030685 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2022-075 | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2022-075 | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2022-075 | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2022-075 | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2022-075 | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2022-075 | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2022-075 | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2022-075 | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2022-075 | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2022-075 | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2022-075 | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2022-075 | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2022-075 | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2022-075 | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2022-075 | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2022-075 | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2022-075 | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2022-075 | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2022-075 | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2022-075 | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2022-075 | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2022-075 | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2022-075 | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2022-075 | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2022-075 | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2022-075 | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2022-075 | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2022-075 | 0.9709 | 0.89603 | -0.07487 |  | 0.9 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2023-015 | 1.0305 | 1.0602 | 0.0297 |  | 0.9 | 1.05 | 0.064516 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2023-015 | 1.0325 | 1.0596 | 0.027143 |  | 0.9 | 1.05 | 0.064516 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2023-015 | 1.0325 | 1.0596 | 0.027143 |  | 0.9 | 1.05 | 0.064516 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2023-015 | 1.0325 | 1.0596 | 0.027143 |  | 0.9 | 1.05 | 0.064516 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2023-015 | 1.0148 | 1.0528 | 0.037951 |  | 0.9 | 1.05 | 0.064516 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2023-220 | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.03965 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2023-220 | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.042938 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2023-220 | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.032864 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2023-220 | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.034629 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2023-220 | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.036988 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2023-220 | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.03396 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2023-220 | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.030296 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2023-220 | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.037836 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2023-220 | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.036214 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2023-220 | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.055483 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2023-220 | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.036214 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2023-220 | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.037031 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2023-220 | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.03728 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2023-220 | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.034689 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2023-220 | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.033481 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2023-220 | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.035246 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2023-220 | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.03235 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2023-220 | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.031498 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2023-220 | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.033388 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2023-220 | 0.97985 | 0.92707 | -0.052786 |  | 0.95 | 1.05 | 0.034867 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2023-220 | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2023-220 | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2023-220 | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2023-220 | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2023-220 | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2023-220 | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2023-220 | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2023-220 | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2023-220 | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2023-220 | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2023-220 | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2023-220 | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2023-220 | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2023-220 | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2023-220 | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2023-220 | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2023-220 | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2023-220 | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2023-220 | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2023-220 | 0.98204 | 0.92817 | -0.053872 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2023-220 | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2023-220 | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2023-220 | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2023-220 | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2023-220 | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2023-220 | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2023-220 | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2023-220 | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2023-220 | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2023-220 | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2023-220 | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2023-220 | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2023-220 | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2023-220 | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2023-220 | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2023-220 | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2023-220 | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2023-220 | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2023-220 | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2023-220 | 0.98668 | 0.92369 | -0.06299 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2023-220 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2023-220 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2023-220 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2023-220 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2023-220 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2023-220 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2023-220 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2023-220 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2023-220 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2023-220 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2023-220 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2023-220 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2023-220 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2023-220 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2023-220 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2023-220 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2023-220 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2023-220 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2023-220 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2023-220 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2023-220 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2023-220 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2023-220 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2023-220 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2023-220 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2023-220 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2023-220 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2023-220 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2023-220 | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2023-220 | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2023-220 | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2023-220 | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2023-220 | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2023-220 | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2023-220 | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2023-220 | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2023-220 | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2023-220 | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2023-220 | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2023-220 | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2023-220 | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2023-220 | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2023-220 | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2023-220 | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2023-220 | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2023-220 | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2023-220 | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2023-220 | 0.98417 | 0.93352 | -0.050658 |  | 0.95 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2023-221 | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.03965 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2023-221 | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.042938 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2023-221 | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.032864 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2023-221 | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.034629 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2023-221 | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.036988 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2023-221 | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.03396 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2023-221 | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.030296 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2023-221 | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.037836 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2023-221 | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.036214 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2023-221 | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.055483 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2023-221 | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.036214 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2023-221 | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.037031 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2023-221 | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.03728 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2023-221 | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.034689 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2023-221 | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.033481 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2023-221 | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.035246 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2023-221 | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.03235 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2023-221 | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.031498 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2023-221 | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.033388 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2023-221 | 0.9808 | 0.92808 | -0.052723 |  | 0.95 | 1.05 | 0.034867 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2023-221 | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2023-221 | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2023-221 | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2023-221 | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2023-221 | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2023-221 | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2023-221 | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2023-221 | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2023-221 | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2023-221 | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2023-221 | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2023-221 | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2023-221 | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2023-221 | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2023-221 | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2023-221 | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2023-221 | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2023-221 | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2023-221 | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2023-221 | 0.9831 | 0.9294 | -0.053704 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2023-221 | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2023-221 | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2023-221 | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2023-221 | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2023-221 | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2023-221 | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2023-221 | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2023-221 | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2023-221 | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2023-221 | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2023-221 | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2023-221 | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2023-221 | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2023-221 | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2023-221 | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2023-221 | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2023-221 | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2023-221 | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2023-221 | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2023-221 | 0.98766 | 0.9248 | -0.062859 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2023-221 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2023-221 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2023-221 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2023-221 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2023-221 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2023-221 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2023-221 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2023-221 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2023-221 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2023-221 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2023-221 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2023-221 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2023-221 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2023-221 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2023-221 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2023-221 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2023-221 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2023-221 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2023-221 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2023-221 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2023-221 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2023-221 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2023-221 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2023-221 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2023-221 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2023-221 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2023-221 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2023-221 | 0.97546 | 0.90641 | -0.069057 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2023-221 | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2023-221 | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2023-221 | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2023-221 | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2023-221 | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2023-221 | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2023-221 | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2023-221 | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2023-221 | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2023-221 | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2023-221 | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2023-221 | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2023-221 | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2023-221 | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2023-221 | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2023-221 | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2023-221 | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2023-221 | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2023-221 | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2023-221 | 0.98519 | 0.93467 | -0.050513 |  | 0.95 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2024-076 | 0.99563 | 0.94411 | -0.051512 |  | 0.95 | 1.05 | 0.040163 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2024-076 | 0.99563 | 0.94411 | -0.051512 |  | 0.95 | 1.05 | 0.035142 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2024-076 | 0.99563 | 0.94411 | -0.051512 |  | 0.95 | 1.05 | 0.037502 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2024-076 | 0.99563 | 0.94411 | -0.051512 |  | 0.95 | 1.05 | 0.03081 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2024-076 | 0.99563 | 0.94411 | -0.051512 |  | 0.95 | 1.05 | 0.03835 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2024-076 | 0.99563 | 0.94411 | -0.051512 |  | 0.95 | 1.05 | 0.036728 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2024-076 | 0.99563 | 0.94411 | -0.051512 |  | 0.95 | 1.05 | 0.036728 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2024-076 | 0.99563 | 0.94411 | -0.051512 |  | 0.95 | 1.05 | 0.037545 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2024-076 | 0.99563 | 0.94411 | -0.051512 |  | 0.95 | 1.05 | 0.037793 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2024-076 | 0.99563 | 0.94411 | -0.051512 |  | 0.95 | 1.05 | 0.03576 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2024-076 | 0.99563 | 0.94411 | -0.051512 |  | 0.95 | 1.05 | 0.032864 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2024-076 | 0.99563 | 0.94411 | -0.051512 |  | 0.95 | 1.05 | 0.032012 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2024-076 | 0.99563 | 0.94411 | -0.051512 |  | 0.95 | 1.05 | 0.033901 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2024-076 | 0.99563 | 0.94411 | -0.051512 |  | 0.95 | 1.05 | 0.035381 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2024-076 | 0.99563 | 0.9461 | -0.04953 |  | 0.95 | 1.05 | 0.03965 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2024-076 | 0.99563 | 0.9461 | -0.04953 |  | 0.95 | 1.05 | 0.034629 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2024-076 | 0.99563 | 0.9461 | -0.04953 |  | 0.95 | 1.05 | 0.036988 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2024-076 | 0.99563 | 0.9461 | -0.04953 |  | 0.95 | 1.05 | 0.030296 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2024-076 | 0.99563 | 0.9461 | -0.04953 |  | 0.95 | 1.05 | 0.037836 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2024-076 | 0.99563 | 0.9461 | -0.04953 |  | 0.95 | 1.05 | 0.036214 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2024-076 | 0.99563 | 0.9461 | -0.04953 |  | 0.95 | 1.05 | 0.036214 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2024-076 | 0.99563 | 0.9461 | -0.04953 |  | 0.95 | 1.05 | 0.037031 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2024-076 | 0.99563 | 0.9461 | -0.04953 |  | 0.95 | 1.05 | 0.03728 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2024-076 | 0.99563 | 0.9461 | -0.04953 |  | 0.95 | 1.05 | 0.035246 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2024-076 | 0.99563 | 0.9461 | -0.04953 |  | 0.95 | 1.05 | 0.03235 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2024-076 | 0.99563 | 0.9461 | -0.04953 |  | 0.95 | 1.05 | 0.031498 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2024-076 | 0.99563 | 0.9461 | -0.04953 |  | 0.95 | 1.05 | 0.033388 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2024-076 | 0.99563 | 0.9461 | -0.04953 |  | 0.95 | 1.05 | 0.034867 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2024-076 | 0.99553 | 0.94641 | -0.049124 |  | 0.95 | 1.05 | 0.03965 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2024-076 | 0.99553 | 0.94641 | -0.049124 |  | 0.95 | 1.05 | 0.034629 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2024-076 | 0.99553 | 0.94641 | -0.049124 |  | 0.95 | 1.05 | 0.036988 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2024-076 | 0.99553 | 0.94641 | -0.049124 |  | 0.95 | 1.05 | 0.030296 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2024-076 | 0.99553 | 0.94641 | -0.049124 |  | 0.95 | 1.05 | 0.037836 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2024-076 | 0.99553 | 0.94641 | -0.049124 |  | 0.95 | 1.05 | 0.036214 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2024-076 | 0.99553 | 0.94641 | -0.049124 |  | 0.95 | 1.05 | 0.036214 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2024-076 | 0.99553 | 0.94641 | -0.049124 |  | 0.95 | 1.05 | 0.037031 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2024-076 | 0.99553 | 0.94641 | -0.049124 |  | 0.95 | 1.05 | 0.03728 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2024-076 | 0.99553 | 0.94641 | -0.049124 |  | 0.95 | 1.05 | 0.035246 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2024-076 | 0.99553 | 0.94641 | -0.049124 |  | 0.95 | 1.05 | 0.03235 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2024-076 | 0.99553 | 0.94641 | -0.049124 |  | 0.95 | 1.05 | 0.031498 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2024-076 | 0.99553 | 0.94641 | -0.049124 |  | 0.95 | 1.05 | 0.033388 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2024-076 | 0.99553 | 0.94641 | -0.049124 |  | 0.95 | 1.05 | 0.034867 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2024-076 | 0.99553 | 0.94644 | -0.049089 |  | 0.95 | 1.05 | 0.03965 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2024-076 | 0.99553 | 0.94644 | -0.049089 |  | 0.95 | 1.05 | 0.034629 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2024-076 | 0.99553 | 0.94644 | -0.049089 |  | 0.95 | 1.05 | 0.036988 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2024-076 | 0.99553 | 0.94644 | -0.049089 |  | 0.95 | 1.05 | 0.030296 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2024-076 | 0.99553 | 0.94644 | -0.049089 |  | 0.95 | 1.05 | 0.037836 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2024-076 | 0.99553 | 0.94644 | -0.049089 |  | 0.95 | 1.05 | 0.036214 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2024-076 | 0.99553 | 0.94644 | -0.049089 |  | 0.95 | 1.05 | 0.036214 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2024-076 | 0.99553 | 0.94644 | -0.049089 |  | 0.95 | 1.05 | 0.037031 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2024-076 | 0.99553 | 0.94644 | -0.049089 |  | 0.95 | 1.05 | 0.03728 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2024-076 | 0.99553 | 0.94644 | -0.049089 |  | 0.95 | 1.05 | 0.035246 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2024-076 | 0.99553 | 0.94644 | -0.049089 |  | 0.95 | 1.05 | 0.03235 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2024-076 | 0.99553 | 0.94644 | -0.049089 |  | 0.95 | 1.05 | 0.031498 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2024-076 | 0.99553 | 0.94644 | -0.049089 |  | 0.95 | 1.05 | 0.033388 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2024-076 | 0.99553 | 0.94644 | -0.049089 |  | 0.95 | 1.05 | 0.034867 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2024-076 | 0.989 | 0.89509 | -0.093908 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2024-076 | 0.989 | 0.89509 | -0.093908 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2024-076 | 0.989 | 0.89509 | -0.093908 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2024-076 | 0.989 | 0.89509 | -0.093908 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2024-076 | 0.989 | 0.89509 | -0.093908 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2024-076 | 0.989 | 0.89509 | -0.093908 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2024-076 | 0.989 | 0.89509 | -0.093908 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2024-076 | 0.989 | 0.89509 | -0.093908 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2024-076 | 0.989 | 0.89509 | -0.093908 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2024-076 | 0.989 | 0.89509 | -0.093908 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2024-076 | 0.989 | 0.89509 | -0.093908 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2024-076 | 0.989 | 0.89509 | -0.093908 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2024-076 | 0.989 | 0.89509 | -0.093908 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2024-076 | 0.989 | 0.89509 | -0.093908 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2024-076 | 0.989 | 0.89509 | -0.093908 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2024-076 | 0.989 | 0.89509 | -0.093908 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2024-076 | 0.989 | 0.89509 | -0.093908 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2024-076 | 0.989 | 0.89509 | -0.093908 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2024-076 | 0.989 | 0.89509 | -0.093908 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2024-076 | 0.989 | 0.89509 | -0.093908 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2024-076 | 0.989 | 0.89509 | -0.093908 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2024-076 | 0.989 | 0.89509 | -0.093908 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2024-076 | 0.989 | 0.89509 | -0.093908 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2024-076 | 0.989 | 0.89509 | -0.093908 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2024-076 | 0.989 | 0.89509 | -0.093908 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2024-076 | 0.989 | 0.89509 | -0.093908 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2024-076 | 0.989 | 0.89509 | -0.093908 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2024-076 | 0.989 | 0.89509 | -0.093908 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2024-129 | 0.99908 | 0.94324 | -0.055841 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2024-129 | 0.99908 | 0.94324 | -0.055841 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2024-129 | 0.99908 | 0.94324 | -0.055841 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2024-129 | 0.99908 | 0.94324 | -0.055841 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2024-129 | 0.99908 | 0.94324 | -0.055841 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2024-129 | 0.99908 | 0.94324 | -0.055841 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2024-129 | 0.99908 | 0.94324 | -0.055841 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2024-129 | 0.99908 | 0.94324 | -0.055841 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2024-129 | 0.99908 | 0.94324 | -0.055841 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2024-129 | 0.99908 | 0.94324 | -0.055841 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2024-129 | 0.99908 | 0.94324 | -0.055841 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2024-129 | 0.99908 | 0.94324 | -0.055841 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2024-129 | 0.99908 | 0.94324 | -0.055841 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2024-129 | 0.99908 | 0.94324 | -0.055841 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2024-129 | 0.99908 | 0.94324 | -0.055841 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2024-129 | 0.99908 | 0.94324 | -0.055841 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2024-129 | 0.99908 | 0.94324 | -0.055841 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2024-129 | 0.99908 | 0.94324 | -0.055841 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2024-129 | 0.99908 | 0.94324 | -0.055841 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2024-129 | 0.99908 | 0.94324 | -0.055841 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2024-129 | 0.99908 | 0.94324 | -0.055841 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2024-129 | 0.99908 | 0.94324 | -0.055841 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2024-129 | 0.99908 | 0.94324 | -0.055841 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2024-129 | 0.99908 | 0.94324 | -0.055841 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2024-129 | 0.99908 | 0.94324 | -0.055841 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2024-129 | 0.99908 | 0.94324 | -0.055841 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2024-129 | 0.99908 | 0.94324 | -0.055841 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2024-129 | 0.99908 | 0.94324 | -0.055841 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2024-170 | 0.97377 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2024-170 | 0.97377 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2024-170 | 0.97377 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2024-170 | 0.97377 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2024-170 | 0.97377 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2024-170 | 0.97377 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2024-170 | 0.97377 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2024-170 | 0.97377 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2024-170 | 0.97377 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2024-170 | 0.97377 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2024-170 | 0.97377 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2024-170 | 0.97377 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2024-170 | 0.97377 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2024-170 | 0.97377 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2024-170 | 0.97377 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2024-170 | 0.97377 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2024-170 | 0.97377 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2024-170 | 0.97377 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2024-170 | 0.97377 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2024-170 | 0.97377 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2024-170 | 0.96999 | 0.93511 | -0.034879 |  | 0.95 | 1.05 | 0.042938 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 0.13 MVAR switched shunt at PECULR 7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2024-170 | 0.96999 | 0.93511 | -0.034879 |  | 0.95 | 1.05 | 0.032864 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 0.13 MVAR switched shunt at PECULR 7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2024-170 | 0.96999 | 0.93511 | -0.034879 |  | 0.95 | 1.05 | 0.03396 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 0.13 MVAR switched shunt at PECULR 7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2024-170 | 0.96999 | 0.93511 | -0.034879 |  | 0.95 | 1.05 | 0.055483 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 0.13 MVAR switched shunt at PECULR 7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2024-170 | 0.96999 | 0.93511 | -0.034879 |  | 0.95 | 1.05 | 0.034689 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 0.13 MVAR switched shunt at PECULR 7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2024-170 | 0.96999 | 0.93511 | -0.034879 |  | 0.95 | 1.05 | 0.033481 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 0.13 MVAR switched shunt at PECULR 7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2024-170 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2024-170 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2024-170 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2024-170 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2024-170 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2024-170 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2024-170 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2024-170 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2024-170 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2024-170 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2024-170 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2024-170 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2024-170 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2024-170 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2024-170 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2024-170 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2024-170 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2024-170 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2024-170 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2024-170 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2024-170 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2024-170 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2024-170 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2024-170 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2024-170 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2024-170 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2024-170 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2024-170 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2024-170 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2024-170 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2024-170 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2024-170 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2024-170 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2024-170 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2024-170 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2024-170 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2024-170 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2024-170 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2024-170 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2024-170 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2024-170 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2024-170 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2024-170 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2024-170 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2024-170 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2024-170 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2024-170 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2024-170 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2024-170 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2024-170 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2024-170 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2024-170 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2024-170 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2024-170 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2024-170 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2024-170 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2024-170 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2024-170 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2024-170 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2024-170 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2024-170 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2024-170 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2024-170 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2024-170 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2024-170 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2024-170 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2024-170 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2024-170 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2024-249 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.03965 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2024-249 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.042938 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2024-249 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.032864 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2024-249 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.034629 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2024-249 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.036988 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2024-249 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.03396 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2024-249 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.030296 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2024-249 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.037836 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2024-249 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.036214 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2024-249 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.055483 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2024-249 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.036214 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2024-249 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.037031 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2024-249 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.03728 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2024-249 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.034689 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2024-249 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.033481 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2024-249 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.035246 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2024-249 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.03235 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2024-249 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.031498 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2024-249 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.033388 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2024-249 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.034867 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2024-249 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2024-249 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2024-249 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2024-249 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2024-249 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2024-249 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2024-249 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2024-249 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2024-249 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2024-249 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2024-249 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2024-249 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2024-249 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2024-249 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2024-249 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2024-249 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2024-249 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2024-249 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2024-249 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2024-249 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2024-249 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2024-249 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2024-249 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2024-249 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2024-249 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2024-249 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2024-249 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2024-249 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2024-249 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2024-249 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2024-249 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2024-249 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2024-249 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2024-249 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2024-249 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2024-249 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2024-249 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2024-249 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2024-249 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2024-249 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2024-249 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2024-249 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2024-249 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2024-249 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2024-249 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2024-249 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2024-249 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2024-249 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2024-249 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2024-249 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2024-249 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2024-249 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2024-249 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2024-249 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2024-249 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2024-249 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2024-249 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2024-249 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2024-249 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2024-249 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2024-249 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2024-249 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2024-249 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2024-249 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2024-249 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2024-249 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2024-249 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2024-249 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2024-249 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2024-249 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2024-249 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2024-249 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2024-249 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2024-249 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2024-249 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2024-249 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2024-249 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2024-249 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2024-249 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2024-249 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2024-249 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2024-249 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2024-249 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2024-249 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2024-249 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2024-249 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2024-249 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2024-249 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2024-253 | 0.99113 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2024-253 | 0.99113 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2024-253 | 0.99113 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2024-253 | 0.99113 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2024-253 | 0.99113 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2024-253 | 0.99113 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2024-253 | 0.99113 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2024-253 | 0.99113 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2024-253 | 0.99113 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2024-253 | 0.99113 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2024-253 | 0.99113 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2024-253 | 0.99113 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2024-253 | 0.99113 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2024-253 | 0.99113 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2024-253 | 0.99113 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2024-253 | 0.99113 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2024-253 | 0.99113 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2024-253 | 0.99113 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2024-253 | 0.99113 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2024-253 | 0.99113 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2024-253 | 0.99113 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2024-253 | 0.99113 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2024-253 | 0.99113 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2024-253 | 0.99113 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2024-253 | 0.99113 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2024-253 | 0.99113 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2024-253 | 0.99113 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2024-253 | 0.99113 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2024-253 | 0.98062 | 0.94906 | -0.031558 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2024-253 | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2024-253 | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2024-253 | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2024-253 | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2024-253 | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2024-253 | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2024-253 | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2024-253 | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2024-253 | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2024-253 | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2024-253 | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2024-253 | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2024-253 | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2024-253 | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2024-253 | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2024-253 | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2024-253 | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2024-253 | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2024-253 | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2024-253 | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2024-253 | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2024-253 | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2024-253 | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2024-253 | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2024-253 | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2024-253 | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2024-253 | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2024-253 | 0.99112 | 0.9446 | -0.046526 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2024-276 | 0.95953 | 0.92502 | -0.034512 |  | 0.95 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2024-276 | 0.95953 | 0.92502 | -0.034512 |  | 0.95 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2024-276 | 0.95953 | 0.92502 | -0.034512 |  | 0.95 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2024-276 | 0.95953 | 0.92502 | -0.034512 |  | 0.95 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2024-276 | 0.95953 | 0.92502 | -0.034512 |  | 0.95 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2024-276 | 0.95953 | 0.92502 | -0.034512 |  | 0.95 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2024-276 | 0.95953 | 0.92502 | -0.034512 |  | 0.95 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2024-276 | 0.95953 | 0.92502 | -0.034512 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2024-276 | 0.95953 | 0.92502 | -0.034512 |  | 0.95 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2024-276 | 0.95953 | 0.92502 | -0.034512 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2024-276 | 0.95953 | 0.92502 | -0.034512 |  | 0.95 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2024-276 | 0.95953 | 0.92502 | -0.034512 |  | 0.95 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2024-276 | 0.95953 | 0.92502 | -0.034512 |  | 0.95 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2024-276 | 0.95953 | 0.92502 | -0.034512 |  | 0.95 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2024-276 | 0.95953 | 0.92502 | -0.034512 |  | 0.95 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2024-276 | 0.95953 | 0.92502 | -0.034512 |  | 0.95 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2024-276 | 0.95953 | 0.92502 | -0.034512 |  | 0.95 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2024-276 | 0.95953 | 0.92502 | -0.034512 |  | 0.95 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2024-276 | 0.95953 | 0.92502 | -0.034512 |  | 0.95 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2024-276 | 0.95953 | 0.92502 | -0.034512 |  | 0.95 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2024-276 | 0.95637 | 0.91721 | -0.039159 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2024-276 | 0.95637 | 0.91721 | -0.039159 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2024-276 | 0.95637 | 0.91721 | -0.039159 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2024-276 | 0.95637 | 0.91721 | -0.039159 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2024-276 | 0.95637 | 0.91721 | -0.039159 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2024-276 | 0.95637 | 0.91721 | -0.039159 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2024-276 | 0.95637 | 0.91721 | -0.039159 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2024-276 | 0.95637 | 0.91721 | -0.039159 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2024-276 | 0.95637 | 0.91721 | -0.039159 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2024-276 | 0.95637 | 0.91721 | -0.039159 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2024-276 | 0.95637 | 0.91721 | -0.039159 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2024-276 | 0.95637 | 0.91721 | -0.039159 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2024-276 | 0.95637 | 0.91721 | -0.039159 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2024-276 | 0.95637 | 0.91721 | -0.039159 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2024-276 | 0.95637 | 0.91721 | -0.039159 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2024-276 | 0.95637 | 0.91721 | -0.039159 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2024-276 | 0.95637 | 0.91721 | -0.039159 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2024-276 | 0.95637 | 0.91721 | -0.039159 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2024-276 | 0.95637 | 0.91721 | -0.039159 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2024-276 | 0.95637 | 0.91721 | -0.039159 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2024-276 | 0.9622 | 0.91848 | -0.043718 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2024-276 | 0.9622 | 0.91848 | -0.043718 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2024-276 | 0.9622 | 0.91848 | -0.043718 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2024-276 | 0.9622 | 0.91848 | -0.043718 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2024-276 | 0.9622 | 0.91848 | -0.043718 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2024-276 | 0.9622 | 0.91848 | -0.043718 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2024-276 | 0.9622 | 0.91848 | -0.043718 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2024-276 | 0.9622 | 0.91848 | -0.043718 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2024-276 | 0.9622 | 0.91848 | -0.043718 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2024-276 | 0.9622 | 0.91848 | -0.043718 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2024-276 | 0.9622 | 0.91848 | -0.043718 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2024-276 | 0.9622 | 0.91848 | -0.043718 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2024-276 | 0.9622 | 0.91848 | -0.043718 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2024-276 | 0.9622 | 0.91848 | -0.043718 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2024-276 | 0.9622 | 0.91848 | -0.043718 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2024-276 | 0.9622 | 0.91848 | -0.043718 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2024-276 | 0.9622 | 0.91848 | -0.043718 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2024-276 | 0.9622 | 0.91848 | -0.043718 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2024-276 | 0.9622 | 0.91848 | -0.043718 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2024-276 | 0.9622 | 0.91848 | -0.043718 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2024-276 | 0.96642 | 0.91785 | -0.048563 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2024-276 | 0.96642 | 0.91785 | -0.048563 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2024-276 | 0.96642 | 0.91785 | -0.048563 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2024-276 | 0.96642 | 0.91785 | -0.048563 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2024-276 | 0.96642 | 0.91785 | -0.048563 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2024-276 | 0.96642 | 0.91785 | -0.048563 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2024-276 | 0.96642 | 0.91785 | -0.048563 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2024-276 | 0.96642 | 0.91785 | -0.048563 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2024-276 | 0.96642 | 0.91785 | -0.048563 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2024-276 | 0.96642 | 0.91785 | -0.048563 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2024-276 | 0.96642 | 0.91785 | -0.048563 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2024-276 | 0.96642 | 0.91785 | -0.048563 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2024-276 | 0.96642 | 0.91785 | -0.048563 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2024-276 | 0.96642 | 0.91785 | -0.048563 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2024-276 | 0.96642 | 0.91785 | -0.048563 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2024-276 | 0.96642 | 0.91785 | -0.048563 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2024-276 | 0.96642 | 0.91785 | -0.048563 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2024-276 | 0.96642 | 0.91785 | -0.048563 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2024-276 | 0.96642 | 0.91785 | -0.048563 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2024-276 | 0.96642 | 0.91785 | -0.048563 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2024-276 | 0.96642 | 0.91785 | -0.048563 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2024-276 | 0.96642 | 0.91785 | -0.048563 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2024-276 | 0.96642 | 0.91785 | -0.048563 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2024-276 | 0.96642 | 0.91785 | -0.048563 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2024-276 | 0.96642 | 0.91785 | -0.048563 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2024-276 | 0.96642 | 0.91785 | -0.048563 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2024-276 | 0.96642 | 0.91785 | -0.048563 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2024-276 | 0.96642 | 0.91785 | -0.048563 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2024-276 | 0.95913 | 0.9237 | -0.035429 |  | 0.95 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2024-276 | 0.95913 | 0.9237 | -0.035429 |  | 0.95 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2024-276 | 0.95913 | 0.9237 | -0.035429 |  | 0.95 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2024-276 | 0.95913 | 0.9237 | -0.035429 |  | 0.95 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2024-276 | 0.95913 | 0.9237 | -0.035429 |  | 0.95 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2024-276 | 0.95913 | 0.9237 | -0.035429 |  | 0.95 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2024-276 | 0.95913 | 0.9237 | -0.035429 |  | 0.95 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2024-276 | 0.95913 | 0.9237 | -0.035429 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2024-276 | 0.95913 | 0.9237 | -0.035429 |  | 0.95 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2024-276 | 0.95913 | 0.9237 | -0.035429 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2024-276 | 0.95913 | 0.9237 | -0.035429 |  | 0.95 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2024-276 | 0.95913 | 0.9237 | -0.035429 |  | 0.95 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2024-276 | 0.95913 | 0.9237 | -0.035429 |  | 0.95 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2024-276 | 0.95913 | 0.9237 | -0.035429 |  | 0.95 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2024-276 | 0.95913 | 0.9237 | -0.035429 |  | 0.95 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2024-276 | 0.95913 | 0.9237 | -0.035429 |  | 0.95 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2024-276 | 0.95913 | 0.9237 | -0.035429 |  | 0.95 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2024-276 | 0.95913 | 0.9237 | -0.035429 |  | 0.95 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2024-276 | 0.95913 | 0.9237 | -0.035429 |  | 0.95 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2024-276 | 0.95913 | 0.9237 | -0.035429 |  | 0.95 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GEN-2024-352 | 0.98439 | 0.93034 | -0.054055 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GEN-2024-352 | 0.98439 | 0.93034 | -0.054055 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GEN-2024-352 | 0.98439 | 0.93034 | -0.054055 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GEN-2024-352 | 0.98439 | 0.93034 | -0.054055 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GEN-2024-352 | 0.98439 | 0.93034 | -0.054055 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GEN-2024-352 | 0.98439 | 0.93034 | -0.054055 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GEN-2024-352 | 0.98439 | 0.93034 | -0.054055 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GEN-2024-352 | 0.98439 | 0.93034 | -0.054055 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GEN-2024-352 | 0.98439 | 0.93034 | -0.054055 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GEN-2024-352 | 0.98439 | 0.93034 | -0.054055 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GEN-2024-352 | 0.98439 | 0.93034 | -0.054055 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GEN-2024-352 | 0.98439 | 0.93034 | -0.054055 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GEN-2024-352 | 0.98439 | 0.93034 | -0.054055 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2024-352 | 0.98439 | 0.93034 | -0.054055 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2024-352 | 0.98439 | 0.93034 | -0.054055 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2024-352 | 0.98439 | 0.93034 | -0.054055 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GEN-2024-352 | 0.98439 | 0.93034 | -0.054055 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GEN-2024-352 | 0.98439 | 0.93034 | -0.054055 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GEN-2024-352 | 0.98439 | 0.93034 | -0.054055 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GEN-2024-352 | 0.98439 | 0.93034 | -0.054055 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GEN-2024-352 | 0.98439 | 0.93034 | -0.054055 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GEN-2024-352 | 0.98439 | 0.93034 | -0.054055 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GEN-2024-352 | 0.98439 | 0.93034 | -0.054055 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GEN-2024-352 | 0.98439 | 0.93034 | -0.054055 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GEN-2024-352 | 0.98439 | 0.93034 | -0.054055 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GEN-2024-352 | 0.98439 | 0.93034 | -0.054055 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GEN-2024-352 | 0.98439 | 0.93034 | -0.054055 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GEN-2024-352 | 0.98439 | 0.93034 | -0.054055 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GODLNDT3 | 0.96504 | 0.89253 | -0.072507 |  | 0.9 | 1.05 | 0.041569 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GODLNDT3 | 0.96504 | 0.89253 | -0.072507 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GODLNDT3 | 0.96504 | 0.89253 | -0.072507 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GODLNDT3 | 0.96504 | 0.89253 | -0.072507 |  | 0.9 | 1.05 | 0.03222 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GODLNDT3 | 0.96504 | 0.89253 | -0.072507 |  | 0.9 | 1.05 | 0.030633 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GODLNDT3 | 0.96504 | 0.89253 | -0.072507 |  | 0.9 | 1.05 | 0.030061 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GODLNDT3 | 0.96504 | 0.89253 | -0.072507 |  | 0.9 | 1.05 | 0.031207 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GODLNDT3 | 0.95439 | 0.88166 | -0.072732 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GODLNDT3 | 0.95439 | 0.88166 | -0.072732 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GODLNDT3 | 0.95385 | 0.87288 | -0.080969 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GODLNDT3 | 0.95385 | 0.87288 | -0.080969 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GODLNDT3 | 0.95385 | 0.87288 | -0.080969 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GODLNDT3 | 0.95385 | 0.87288 | -0.080969 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GODLNDT3 | 0.95385 | 0.87288 | -0.08097 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GODLNDT3 | 0.95385 | 0.87288 | -0.08097 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GOODCTY3 | 0.96128 | 0.88845 | -0.072835 |  | 0.9 | 1.05 | 0.041569 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GOODCTY3 | 0.96128 | 0.88845 | -0.072835 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GOODCTY3 | 0.96128 | 0.88845 | -0.072835 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GOODCTY3 | 0.96128 | 0.88845 | -0.072835 |  | 0.9 | 1.05 | 0.03222 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GOODCTY3 | 0.96128 | 0.88845 | -0.072835 |  | 0.9 | 1.05 | 0.030633 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GOODCTY3 | 0.96128 | 0.88845 | -0.072835 |  | 0.9 | 1.05 | 0.030061 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GOODCTY3 | 0.96128 | 0.88845 | -0.072835 |  | 0.9 | 1.05 | 0.031207 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GOODCTY3 | 0.95059 | 0.87752 | -0.073069 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GOODCTY3 | 0.95059 | 0.87752 | -0.073069 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GOODCTY3 | 0.95004 | 0.86869 | -0.081348 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GOODCTY3 | 0.95004 | 0.86869 | -0.081348 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GOODCTY3 | 0.95004 | 0.86869 | -0.081348 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GOODCTY3 | 0.95004 | 0.86869 | -0.081348 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GOODCTY3 | 0.95004 | 0.86869 | -0.08135 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GOODCTY3 | 0.95004 | 0.86869 | -0.08135 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GOODLND3 | 0.96527 | 0.89268 | -0.072597 |  | 0.9 | 1.05 | 0.041569 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GOODLND3 | 0.96527 | 0.89268 | -0.072597 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GOODLND3 | 0.96527 | 0.89268 | -0.072597 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GOODLND3 | 0.96527 | 0.89268 | -0.072597 |  | 0.9 | 1.05 | 0.03222 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GOODLND3 | 0.96527 | 0.89268 | -0.072597 |  | 0.9 | 1.05 | 0.030633 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GOODLND3 | 0.96527 | 0.89268 | -0.072597 |  | 0.9 | 1.05 | 0.030061 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GOODLND3 | 0.96527 | 0.89268 | -0.072597 |  | 0.9 | 1.05 | 0.031207 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GOODLND3 | 0.95537 | 0.883 | -0.072371 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GOODLND3 | 0.95537 | 0.883 | -0.072371 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GOODLND3 | 0.9548 | 0.87425 | -0.080552 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GOODLND3 | 0.9548 | 0.87425 | -0.080552 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GOODLND3 | 0.9548 | 0.87425 | -0.080552 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GOODLND3 | 0.9548 | 0.87425 | -0.080552 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GOODLND3 | 0.9548 | 0.87425 | -0.080553 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GOODLND3 | 0.9548 | 0.87425 | -0.080553 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GOVE 3 | 0.9482 | 0.87722 | -0.070978 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GOVE 3 | 0.9482 | 0.87722 | -0.070978 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GOVE 3 | 0.94916 | 0.87194 | -0.077214 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GOVE 3 | 0.94916 | 0.87194 | -0.077214 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GOVE 3 | 0.94916 | 0.87194 | -0.077215 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GOVE 3 | 0.94916 | 0.87194 | -0.077215 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GOVE 3 | 0.94916 | 0.87194 | -0.077215 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GOVE 3 | 0.94916 | 0.87194 | -0.077215 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GRDVWE 5 | 0.98859 | 0.91549 | -0.073102 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GRDVWE 5 | 0.98859 | 0.91549 | -0.073102 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GRDVWE 5 | 0.98859 | 0.91549 | -0.073102 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GRDVWE 5 | 0.98859 | 0.91549 | -0.073102 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | GRDVWE 5 | 0.98859 | 0.91549 | -0.073102 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GRDVWE 5 | 0.98859 | 0.91549 | -0.073102 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GRDVWE 5 | 0.98859 | 0.91549 | -0.073102 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | GRDVWE 5 | 0.98859 | 0.91549 | -0.073102 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | GRDVWE 5 | 0.98859 | 0.91549 | -0.073102 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GRDVWE 5 | 0.98859 | 0.91549 | -0.073102 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GRDVWE 5 | 0.98859 | 0.91549 | -0.073102 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | GRDVWE 5 | 0.98859 | 0.91549 | -0.073102 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GRDVWE 5 | 0.98859 | 0.91549 | -0.073102 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | GRDVWE 5 | 0.98859 | 0.91549 | -0.073102 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | GRDVWE 5 | 0.98859 | 0.91549 | -0.073102 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | GRDVWE 5 | 0.98859 | 0.91549 | -0.073102 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GRDVWE 5 | 0.98859 | 0.91549 | -0.073102 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GRDVWE 5 | 0.98859 | 0.91549 | -0.073102 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GRDVWE 5 | 0.98859 | 0.91549 | -0.073102 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GRDVWE 5 | 0.98859 | 0.91549 | -0.073102 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GRDVWE 5 | 0.98859 | 0.91549 | -0.073102 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | GRDVWE 5 | 0.98859 | 0.91549 | -0.073102 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | GRDVWE 5 | 0.98859 | 0.91549 | -0.073102 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GRDVWE 5 | 0.98859 | 0.91549 | -0.073102 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | GRDVWE 5 | 0.98859 | 0.91549 | -0.073102 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GRDVWE 5 | 0.98859 | 0.91549 | -0.073102 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GRDVWE 5 | 0.98859 | 0.91549 | -0.073102 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | GRDVWE 5 | 0.98859 | 0.91549 | -0.073102 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GREENHOUSE 5 | 0.98892 | 0.91978 | -0.069142 |  | 0.92 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GREENHOUSE 5 | 0.98892 | 0.91978 | -0.069142 |  | 0.92 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GREENHOUSE 5 | 0.98892 | 0.91978 | -0.069142 |  | 0.92 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GREENHOUSE 5 | 0.98892 | 0.91978 | -0.069142 |  | 0.92 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GREENHOUSE 5 | 0.98892 | 0.91978 | -0.069142 |  | 0.92 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GREENHOUSE 5 | 0.98892 | 0.91978 | -0.069142 |  | 0.92 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GREENHOUSE 5 | 0.98892 | 0.91978 | -0.069142 |  | 0.92 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GREENHOUSE 5 | 0.98892 | 0.91978 | -0.069142 |  | 0.92 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GREENHOUSE 5 | 0.98892 | 0.91978 | -0.069142 |  | 0.92 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GREENHOUSE 5 | 0.98892 | 0.91978 | -0.069142 |  | 0.92 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GREENHOUSE 5 | 0.98892 | 0.91978 | -0.069142 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GREENHOUSE 5 | 0.98892 | 0.91978 | -0.069142 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GREENHOUSE 5 | 0.98892 | 0.91978 | -0.069142 |  | 0.92 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GREENHOUSE 5 | 0.98892 | 0.91978 | -0.069142 |  | 0.92 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GREENHOUSE 5 | 0.98892 | 0.91978 | -0.069142 |  | 0.92 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GRINNEL3 | 0.96473 | 0.89826 | -0.066478 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GRINNEL3 | 0.96473 | 0.89826 | -0.066478 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GRINNEL3 | 0.96488 | 0.89269 | -0.072189 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GRINNEL3 | 0.96488 | 0.89269 | -0.072189 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GRINNEL3 | 0.96488 | 0.89269 | -0.072189 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GRINNEL3 | 0.96488 | 0.89269 | -0.072189 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | GRINNEL3 | 0.96488 | 0.89269 | -0.07219 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | GRINNEL3 | 0.96488 | 0.89269 | -0.07219 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GROVE 4 | 0.95977 | 0.90076 | -0.059017 |  | 0.92 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GROVE 4 | 0.95977 | 0.90076 | -0.059017 |  | 0.92 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GROVE 4 | 0.95977 | 0.90076 | -0.059017 |  | 0.92 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GROVE 4 | 0.95977 | 0.90076 | -0.059017 |  | 0.92 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GROVE 4 | 0.95977 | 0.90076 | -0.059017 |  | 0.92 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GROVE 4 | 0.95977 | 0.90076 | -0.059017 |  | 0.92 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GROVE 4 | 0.95977 | 0.90076 | -0.059017 |  | 0.92 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GROVE 4 | 0.95977 | 0.90076 | -0.059017 |  | 0.92 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GROVE 4 | 0.95977 | 0.90076 | -0.059017 |  | 0.92 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GROVE 4 | 0.95977 | 0.90076 | -0.059017 |  | 0.92 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GROVE 4 | 0.95977 | 0.90076 | -0.059017 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GROVE 4 | 0.95977 | 0.90076 | -0.059017 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GROVE 4 | 0.95977 | 0.90076 | -0.059017 |  | 0.92 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GROVE 4 | 0.95977 | 0.90076 | -0.059017 |  | 0.92 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GROVE 4 | 0.95977 | 0.90076 | -0.059017 |  | 0.92 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GROVE 4 | 0.96012 | 0.90151 | -0.058616 |  | 0.92 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GROVE 4 | 0.96012 | 0.90151 | -0.058616 |  | 0.92 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GROVE 4 | 0.96012 | 0.90151 | -0.058616 |  | 0.92 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GROVE 4 | 0.96012 | 0.90151 | -0.058616 |  | 0.92 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GROVE 4 | 0.96012 | 0.90151 | -0.058616 |  | 0.92 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GROVE 4 | 0.96012 | 0.90151 | -0.058616 |  | 0.92 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GROVE 4 | 0.96012 | 0.90151 | -0.058616 |  | 0.92 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GROVE 4 | 0.96012 | 0.90151 | -0.058616 |  | 0.92 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GROVE 4 | 0.96012 | 0.90151 | -0.058616 |  | 0.92 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GROVE 4 | 0.96012 | 0.90151 | -0.058616 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GROVE 4 | 0.96012 | 0.90151 | -0.058616 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GROVE 4 | 0.96012 | 0.90151 | -0.058616 |  | 0.92 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GROVE 4 | 0.96012 | 0.90151 | -0.058616 |  | 0.92 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GROVE 4 | 0.96012 | 0.90151 | -0.058616 |  | 0.92 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GROVE 4 | 0.96033 | 0.90478 | -0.055554 |  | 0.92 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GROVE 4 | 0.96033 | 0.90478 | -0.055554 |  | 0.92 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GROVE 4 | 0.96033 | 0.90478 | -0.055554 |  | 0.92 | 1.05 | 0.055405 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GROVE 4 | 0.96033 | 0.90478 | -0.055554 |  | 0.92 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GROVE 4 | 0.96033 | 0.90478 | -0.055554 |  | 0.92 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GROVE 4 | 0.96033 | 0.90478 | -0.055554 |  | 0.92 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GROVE 4 | 0.96033 | 0.90478 | -0.055554 |  | 0.92 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GROVE 4 | 0.96033 | 0.90478 | -0.055554 |  | 0.92 | 1.05 | 0.082012 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GROVE 4 | 0.96033 | 0.90478 | -0.055554 |  | 0.92 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GROVE 4 | 0.96033 | 0.90478 | -0.055554 |  | 0.92 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GROVE 4 | 0.96033 | 0.90478 | -0.055554 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GROVE 4 | 0.96033 | 0.90478 | -0.055554 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GROVE 4 | 0.96033 | 0.90478 | -0.055554 |  | 0.92 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GROVE 4 | 0.96033 | 0.90478 | -0.055554 |  | 0.92 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GROVE 4 | 0.96033 | 0.90478 | -0.055554 |  | 0.92 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GROVE 4 | 0.95721 | 0.9061 | -0.05111 |  | 0.92 | 1.05 | 0.030712 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GROVE 4 | 0.95721 | 0.9061 | -0.05111 |  | 0.92 | 1.05 | 0.038311 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GROVE 4 | 0.95721 | 0.9061 | -0.05111 |  | 0.92 | 1.05 | 0.061498 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GROVE 4 | 0.95721 | 0.9061 | -0.05111 |  | 0.92 | 1.05 | 0.070613 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GROVE 4 | 0.95721 | 0.9061 | -0.05111 |  | 0.92 | 1.05 | 0.037457 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GROVE 4 | 0.95721 | 0.9061 | -0.05111 |  | 0.92 | 1.05 | 0.15352 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GROVE 4 | 0.95721 | 0.9061 | -0.05111 |  | 0.92 | 1.05 | 0.062033 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GROVE 4 | 0.95837 | 0.90884 | -0.049533 |  | 0.92 | 1.05 | 0.038311 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GROVE 4 | 0.95837 | 0.90884 | -0.049533 |  | 0.92 | 1.05 | 0.058472 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GROVE 4 | 0.95837 | 0.90884 | -0.049533 |  | 0.92 | 1.05 | 0.070613 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GROVE 4 | 0.95837 | 0.90884 | -0.049533 |  | 0.92 | 1.05 | 0.036297 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GROVE 4 | 0.95837 | 0.90884 | -0.049533 |  | 0.92 | 1.05 | 0.15352 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GROVE 4 | 0.95837 | 0.90884 | -0.049533 |  | 0.92 | 1.05 | 0.060874 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GROVE 5 | 0.96794 | 0.90693 | -0.061013 |  | 0.92 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GROVE 5 | 0.96794 | 0.90693 | -0.061013 |  | 0.92 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GROVE 5 | 0.96794 | 0.90693 | -0.061013 |  | 0.92 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GROVE 5 | 0.96794 | 0.90693 | -0.061013 |  | 0.92 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GROVE 5 | 0.96794 | 0.90693 | -0.061013 |  | 0.92 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GROVE 5 | 0.96794 | 0.90693 | -0.061013 |  | 0.92 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GROVE 5 | 0.96794 | 0.90693 | -0.061013 |  | 0.92 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GROVE 5 | 0.96794 | 0.90693 | -0.061013 |  | 0.92 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GROVE 5 | 0.96794 | 0.90693 | -0.061013 |  | 0.92 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GROVE 5 | 0.96794 | 0.90693 | -0.061013 |  | 0.92 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GROVE 5 | 0.96794 | 0.90693 | -0.061013 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GROVE 5 | 0.96794 | 0.90693 | -0.061013 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GROVE 5 | 0.96794 | 0.90693 | -0.061013 |  | 0.92 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GROVE 5 | 0.96794 | 0.90693 | -0.061013 |  | 0.92 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GROVE 5 | 0.96794 | 0.90693 | -0.061013 |  | 0.92 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GROVE 5 | 0.96836 | 0.90778 | -0.060574 |  | 0.92 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GROVE 5 | 0.96836 | 0.90778 | -0.060574 |  | 0.92 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GROVE 5 | 0.96836 | 0.90778 | -0.060574 |  | 0.92 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GROVE 5 | 0.96836 | 0.90778 | -0.060574 |  | 0.92 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GROVE 5 | 0.96836 | 0.90778 | -0.060574 |  | 0.92 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GROVE 5 | 0.96836 | 0.90778 | -0.060574 |  | 0.92 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GROVE 5 | 0.96836 | 0.90778 | -0.060574 |  | 0.92 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GROVE 5 | 0.96836 | 0.90778 | -0.060574 |  | 0.92 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GROVE 5 | 0.96836 | 0.90778 | -0.060574 |  | 0.92 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GROVE 5 | 0.96836 | 0.90778 | -0.060574 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GROVE 5 | 0.96836 | 0.90778 | -0.060574 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GROVE 5 | 0.96836 | 0.90778 | -0.060574 |  | 0.92 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GROVE 5 | 0.96836 | 0.90778 | -0.060574 |  | 0.92 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GROVE 5 | 0.96836 | 0.90778 | -0.060574 |  | 0.92 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | GROVE 5 | 0.96857 | 0.9115 | -0.057078 |  | 0.92 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | GROVE 5 | 0.96857 | 0.9115 | -0.057078 |  | 0.92 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | GROVE 5 | 0.96857 | 0.9115 | -0.057078 |  | 0.92 | 1.05 | 0.055405 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | GROVE 5 | 0.96857 | 0.9115 | -0.057078 |  | 0.92 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | GROVE 5 | 0.96857 | 0.9115 | -0.057078 |  | 0.92 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | GROVE 5 | 0.96857 | 0.9115 | -0.057078 |  | 0.92 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | GROVE 5 | 0.96857 | 0.9115 | -0.057078 |  | 0.92 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | GROVE 5 | 0.96857 | 0.9115 | -0.057078 |  | 0.92 | 1.05 | 0.082012 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | GROVE 5 | 0.96857 | 0.9115 | -0.057078 |  | 0.92 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | GROVE 5 | 0.96857 | 0.9115 | -0.057078 |  | 0.92 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | GROVE 5 | 0.96857 | 0.9115 | -0.057078 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | GROVE 5 | 0.96857 | 0.9115 | -0.057078 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | GROVE 5 | 0.96857 | 0.9115 | -0.057078 |  | 0.92 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | GROVE 5 | 0.96857 | 0.9115 | -0.057078 |  | 0.92 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | GROVE 5 | 0.96857 | 0.9115 | -0.057078 |  | 0.92 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | HALSTD 4 | 0.94846 | 0.91128 | -0.037185 |  | 0.93 | 1.05 | 0.055416 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | HALSTD 4 | 0.94846 | 0.91128 | -0.037185 |  | 0.93 | 1.05 | 0.031006 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | HALSTD 4 | 0.94846 | 0.91128 | -0.037185 |  | 0.93 | 1.05 | 0.065094 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | HALSTD 4 | 0.94846 | 0.91128 | -0.037185 |  | 0.93 | 1.05 | 0.044621 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | HALSTD 4 | 0.94846 | 0.91128 | -0.037185 |  | 0.93 | 1.05 | 0.048914 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | HALSTD 4 | 0.94846 | 0.91128 | -0.037185 |  | 0.93 | 1.05 | 0.048508 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | HALSTD 4 | 0.94846 | 0.91128 | -0.037185 |  | 0.93 | 1.05 | 0.047017 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | HALSTD 4 | 0.94846 | 0.91128 | -0.037185 |  | 0.93 | 1.05 | 0.040068 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | HALSTD 4 | 0.94846 | 0.91128 | -0.037185 |  | 0.93 | 1.05 | 0.043101 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | HALSTD 4 | 0.94846 | 0.91128 | -0.037185 |  | 0.93 | 1.05 | 0.051186 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | HALSTD 4 | 0.94846 | 0.91128 | -0.037185 |  | 0.93 | 1.05 | 0.041545 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | HALSTD 4 | 0.94846 | 0.91128 | -0.037185 |  | 0.93 | 1.05 | 0.050897 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | HALSTD 4 | 0.94846 | 0.91128 | -0.037185 |  | 0.93 | 1.05 | 0.07159 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | HALSTD 4 | 0.94846 | 0.91128 | -0.037185 |  | 0.93 | 1.05 | 0.050897 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | HALSTD 4 | 0.94846 | 0.91128 | -0.037185 |  | 0.93 | 1.05 | 0.052178 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | HALSTD 4 | 0.94846 | 0.91128 | -0.037185 |  | 0.93 | 1.05 | 0.0519 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | HALSTD 4 | 0.94846 | 0.91128 | -0.037185 |  | 0.93 | 1.05 | 0.034974 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | HALSTD 4 | 0.94846 | 0.91128 | -0.037185 |  | 0.93 | 1.05 | 0.050152 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | HALSTD 4 | 0.94846 | 0.91128 | -0.037185 |  | 0.93 | 1.05 | 0.037496 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | HALSTD 4 | 0.94846 | 0.91128 | -0.037185 |  | 0.93 | 1.05 | 0.037496 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | HALSTD 4 | 0.94846 | 0.91128 | -0.037185 |  | 0.93 | 1.05 | 0.045947 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | HALSTD 4 | 0.94846 | 0.91128 | -0.037185 |  | 0.93 | 1.05 | 0.049649 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | HALSTD 4 | 0.94846 | 0.91128 | -0.037185 |  | 0.93 | 1.05 | 0.040149 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | HALSTD 4 | 0.94846 | 0.91128 | -0.037185 |  | 0.93 | 1.05 | 0.046162 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | HALSTD 4 | 0.94846 | 0.91128 | -0.037185 |  | 0.93 | 1.05 | 0.044763 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | HALSTD 4 | 0.94846 | 0.91128 | -0.037185 |  | 0.93 | 1.05 | 0.047325 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | HALSTD 4 | 0.94846 | 0.91128 | -0.037185 |  | 0.93 | 1.05 | 0.048761 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | HALSTD 4 | 0.94846 | 0.91128 | -0.037185 |  | 0.93 | 1.05 | 0.035454 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | HALSTD 4 | 0.9489 | 0.91151 | -0.037385 |  | 0.93 | 1.05 | 0.055416 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | HALSTD 4 | 0.9489 | 0.91151 | -0.037385 |  | 0.93 | 1.05 | 0.031006 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | HALSTD 4 | 0.9489 | 0.91151 | -0.037385 |  | 0.93 | 1.05 | 0.036106 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | HALSTD 4 | 0.9489 | 0.91151 | -0.037385 |  | 0.93 | 1.05 | 0.037647 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | HALSTD 4 | 0.9489 | 0.91151 | -0.037385 |  | 0.93 | 1.05 | 0.048914 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | HALSTD 4 | 0.9489 | 0.91151 | -0.037385 |  | 0.93 | 1.05 | 0.048508 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | HALSTD 4 | 0.9489 | 0.91151 | -0.037385 |  | 0.93 | 1.05 | 0.040159 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | HALSTD 4 | 0.9489 | 0.91151 | -0.037385 |  | 0.93 | 1.05 | 0.040068 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | HALSTD 4 | 0.9489 | 0.91151 | -0.037385 |  | 0.93 | 1.05 | 0.043101 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | HALSTD 4 | 0.9489 | 0.91151 | -0.037385 |  | 0.93 | 1.05 | 0.051186 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | HALSTD 4 | 0.9489 | 0.91151 | -0.037385 |  | 0.93 | 1.05 | 0.041545 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | HALSTD 4 | 0.9489 | 0.91151 | -0.037385 |  | 0.93 | 1.05 | 0.050897 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | HALSTD 4 | 0.9489 | 0.91151 | -0.037385 |  | 0.93 | 1.05 | 0.032959 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | HALSTD 4 | 0.9489 | 0.91151 | -0.037385 |  | 0.93 | 1.05 | 0.050897 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | HALSTD 4 | 0.9489 | 0.91151 | -0.037385 |  | 0.93 | 1.05 | 0.052178 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | HALSTD 4 | 0.9489 | 0.91151 | -0.037385 |  | 0.93 | 1.05 | 0.0519 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | HALSTD 4 | 0.9489 | 0.91151 | -0.037385 |  | 0.93 | 1.05 | 0.034974 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | HALSTD 4 | 0.9489 | 0.91151 | -0.037385 |  | 0.93 | 1.05 | 0.035428 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | HALSTD 4 | 0.9489 | 0.91151 | -0.037385 |  | 0.93 | 1.05 | 0.037496 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | HALSTD 4 | 0.9489 | 0.91151 | -0.037385 |  | 0.93 | 1.05 | 0.037496 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | HALSTD 4 | 0.9489 | 0.91151 | -0.037385 |  | 0.93 | 1.05 | 0.039177 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | HALSTD 4 | 0.9489 | 0.91151 | -0.037385 |  | 0.93 | 1.05 | 0.049649 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | HALSTD 4 | 0.9489 | 0.91151 | -0.037385 |  | 0.93 | 1.05 | 0.040149 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | HALSTD 4 | 0.9489 | 0.91151 | -0.037385 |  | 0.93 | 1.05 | 0.046162 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | HALSTD 4 | 0.9489 | 0.91151 | -0.037385 |  | 0.93 | 1.05 | 0.044763 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | HALSTD 4 | 0.9489 | 0.91151 | -0.037385 |  | 0.93 | 1.05 | 0.047325 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | HALSTD 4 | 0.9489 | 0.91151 | -0.037385 |  | 0.93 | 1.05 | 0.048761 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | HALSTD 4 | 0.9489 | 0.91151 | -0.037385 |  | 0.93 | 1.05 | 0.035454 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | HALSTD 4 | 0.97513 | 0.907 | -0.068134 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | HALSTD 4 | 0.97513 | 0.907 | -0.068134 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | HALSTD 4 | 0.97513 | 0.907 | -0.068134 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | HALSTD 4 | 0.97513 | 0.907 | -0.068134 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | HALSTD 4 | 0.97513 | 0.907 | -0.068134 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | HALSTD 4 | 0.97513 | 0.907 | -0.068134 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | HALSTD 4 | 0.97513 | 0.907 | -0.068134 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | HALSTD 4 | 0.97513 | 0.907 | -0.068134 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | HALSTD 4 | 0.97513 | 0.907 | -0.068134 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | HALSTD 4 | 0.97513 | 0.907 | -0.068134 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | HALSTD 4 | 0.97513 | 0.907 | -0.068134 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | HALSTD 4 | 0.97513 | 0.907 | -0.068134 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | HALSTD 4 | 0.97513 | 0.907 | -0.068134 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | HALSTD 4 | 0.97513 | 0.907 | -0.068134 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | HALSTD 4 | 0.97513 | 0.907 | -0.068134 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | HALSTD 4 | 0.97513 | 0.907 | -0.068134 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | HALSTD 4 | 0.97513 | 0.907 | -0.068134 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | HALSTD 4 | 0.97513 | 0.907 | -0.068134 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | HALSTD 4 | 0.97513 | 0.907 | -0.068134 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | HALSTD 4 | 0.97513 | 0.907 | -0.068134 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | HALSTD 4 | 0.97513 | 0.907 | -0.068134 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | HALSTD 4 | 0.97513 | 0.907 | -0.068134 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | HALSTD 4 | 0.97513 | 0.907 | -0.068134 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | HALSTD 4 | 0.97513 | 0.907 | -0.068134 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | HALSTD 4 | 0.97513 | 0.907 | -0.068134 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | HALSTD 4 | 0.97513 | 0.907 | -0.068134 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | HALSTD 4 | 0.97513 | 0.907 | -0.068134 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | HALSTD 4 | 0.97513 | 0.907 | -0.068134 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | HAWTH 7 | 0.98552 | 0.93837 | -0.047153 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | HAWTH 7 | 0.98552 | 0.93837 | -0.047153 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | HAWTH 7 | 0.98552 | 0.93837 | -0.047153 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | HAWTH 7 | 0.98552 | 0.93837 | -0.047153 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | HAWTH 7 | 0.98552 | 0.93837 | -0.047153 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | HAWTH 7 | 0.98552 | 0.93837 | -0.047153 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | HAWTH 7 | 0.98552 | 0.93837 | -0.047153 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | HAWTH 7 | 0.98552 | 0.93837 | -0.047153 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | HAWTH 7 | 0.98552 | 0.93837 | -0.047153 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | HAWTH 7 | 0.98552 | 0.93837 | -0.047153 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | HAWTH 7 | 0.98552 | 0.93837 | -0.047153 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | HAWTH 7 | 0.98552 | 0.93837 | -0.047153 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | HAWTH 7 | 0.98552 | 0.93837 | -0.047153 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | HAWTH 7 | 0.98552 | 0.93837 | -0.047153 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | HAWTH 7 | 0.98552 | 0.93837 | -0.047153 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | HAWTH 7 | 0.98552 | 0.93837 | -0.047153 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | HAWTH 7 | 0.98552 | 0.93837 | -0.047153 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | HAWTH 7 | 0.98552 | 0.93837 | -0.047153 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | HAWTH 7 | 0.98552 | 0.93837 | -0.047153 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | HAWTH 7 | 0.98552 | 0.93837 | -0.047153 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | HAWTH 7 | 0.98552 | 0.93837 | -0.047153 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | HAWTH 7 | 0.98552 | 0.93837 | -0.047153 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | HAWTH 7 | 0.98552 | 0.93837 | -0.047153 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | HAWTH 7 | 0.98552 | 0.93837 | -0.047153 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | HAWTH 7 | 0.98552 | 0.93837 | -0.047153 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | HAWTH 7 | 0.98552 | 0.93837 | -0.047153 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | HAWTH 7 | 0.98552 | 0.93837 | -0.047153 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | HAWTH 7 | 0.98552 | 0.93837 | -0.047153 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | HERNDON3 | 0.95793 | 0.89697 | -0.060957 |  | 0.9 | 1.05 | 0.041569 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | HERNDON3 | 0.95793 | 0.89697 | -0.060957 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | HERNDON3 | 0.95793 | 0.89697 | -0.060957 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | HERNDON3 | 0.95793 | 0.89697 | -0.060957 |  | 0.9 | 1.05 | 0.03222 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | HERNDON3 | 0.95793 | 0.89697 | -0.060957 |  | 0.9 | 1.05 | 0.030633 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | HERNDON3 | 0.95793 | 0.89697 | -0.060957 |  | 0.9 | 1.05 | 0.030061 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | HERNDON3 | 0.95793 | 0.89697 | -0.060957 |  | 0.9 | 1.05 | 0.031207 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | HERNDON3 | 0.95911 | 0.89434 | -0.064775 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | HERNDON3 | 0.95911 | 0.89434 | -0.064775 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | HERNDON3 | 0.95998 | 0.89131 | -0.068675 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | HERNDON3 | 0.95998 | 0.89131 | -0.068675 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | HERNDON3 | 0.95998 | 0.89131 | -0.068675 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | HERNDON3 | 0.95998 | 0.89131 | -0.068675 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | HERNDON3 | 0.95998 | 0.89131 | -0.068676 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | HERNDON3 | 0.95998 | 0.89131 | -0.068676 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | HICKMAN5 | 0.98239 | 0.90926 | -0.073125 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | HICKMAN5 | 0.98239 | 0.90926 | -0.073125 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | HICKMAN5 | 0.98239 | 0.90926 | -0.073125 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | HICKMAN5 | 0.98239 | 0.90926 | -0.073125 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | HICKMAN5 | 0.98239 | 0.90926 | -0.073125 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | HICKMAN5 | 0.98239 | 0.90926 | -0.073125 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | HICKMAN5 | 0.98239 | 0.90926 | -0.073125 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | HICKMAN5 | 0.98239 | 0.90926 | -0.073125 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | HICKMAN5 | 0.98239 | 0.90926 | -0.073125 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | HICKMAN5 | 0.98239 | 0.90926 | -0.073125 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | HICKMAN5 | 0.98239 | 0.90926 | -0.073125 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | HICKMAN5 | 0.98239 | 0.90926 | -0.073125 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | HICKMAN5 | 0.98239 | 0.90926 | -0.073125 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | HICKMAN5 | 0.98239 | 0.90926 | -0.073125 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | HICKMAN5 | 0.98239 | 0.90926 | -0.073125 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | HICKMAN5 | 0.98239 | 0.90926 | -0.073125 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | HICKMAN5 | 0.98239 | 0.90926 | -0.073125 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | HICKMAN5 | 0.98239 | 0.90926 | -0.073125 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | HICKMAN5 | 0.98239 | 0.90926 | -0.073125 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | HICKMAN5 | 0.98239 | 0.90926 | -0.073125 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | HICKMAN5 | 0.98239 | 0.90926 | -0.073125 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | HICKMAN5 | 0.98239 | 0.90926 | -0.073125 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | HICKMAN5 | 0.98239 | 0.90926 | -0.073125 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | HICKMAN5 | 0.98239 | 0.90926 | -0.073125 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | HICKMAN5 | 0.98239 | 0.90926 | -0.073125 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | HICKMAN5 | 0.98239 | 0.90926 | -0.073125 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | HICKMAN5 | 0.98239 | 0.90926 | -0.073125 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | HICKMAN5 | 0.98239 | 0.90926 | -0.073125 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | HIGHPT 3 | 0.92844 | 0.85402 | -0.07442 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | HIGHPT 3 | 0.92844 | 0.85402 | -0.07442 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | HIGHPT 3 | 0.93537 | 0.85298 | -0.082389 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | HIGHPT 3 | 0.93537 | 0.85298 | -0.082389 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | HIGHPT 3 | 0.93537 | 0.85298 | -0.082389 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | HIGHPT 3 | 0.93537 | 0.85298 | -0.082389 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | HIGHPT 3 | 0.93537 | 0.85298 | -0.08239 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | HIGHPT 3 | 0.93537 | 0.85298 | -0.08239 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | HONEYWL5 | 0.98524 | 0.90886 | -0.076378 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | HONEYWL5 | 0.98524 | 0.90886 | -0.076378 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | HONEYWL5 | 0.98524 | 0.90886 | -0.076378 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | HONEYWL5 | 0.98524 | 0.90886 | -0.076378 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | HONEYWL5 | 0.98524 | 0.90886 | -0.076378 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | HONEYWL5 | 0.98524 | 0.90886 | -0.076378 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | HONEYWL5 | 0.98524 | 0.90886 | -0.076378 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | HONEYWL5 | 0.98524 | 0.90886 | -0.076378 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | HONEYWL5 | 0.98524 | 0.90886 | -0.076378 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | HONEYWL5 | 0.98524 | 0.90886 | -0.076378 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | HONEYWL5 | 0.98524 | 0.90886 | -0.076378 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | HONEYWL5 | 0.98524 | 0.90886 | -0.076378 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | HONEYWL5 | 0.98524 | 0.90886 | -0.076378 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | HONEYWL5 | 0.98524 | 0.90886 | -0.076378 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | HONEYWL5 | 0.98524 | 0.90886 | -0.076378 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | HONEYWL5 | 0.98524 | 0.90886 | -0.076378 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | HONEYWL5 | 0.98524 | 0.90886 | -0.076378 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | HONEYWL5 | 0.98524 | 0.90886 | -0.076378 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | HONEYWL5 | 0.98524 | 0.90886 | -0.076378 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | HONEYWL5 | 0.98524 | 0.90886 | -0.076378 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | HONEYWL5 | 0.98524 | 0.90886 | -0.076378 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | HONEYWL5 | 0.98524 | 0.90886 | -0.076378 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | HONEYWL5 | 0.98524 | 0.90886 | -0.076378 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | HONEYWL5 | 0.98524 | 0.90886 | -0.076378 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | HONEYWL5 | 0.98524 | 0.90886 | -0.076378 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | HONEYWL5 | 0.98524 | 0.90886 | -0.076378 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | HONEYWL5 | 0.98524 | 0.90886 | -0.076378 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | HONEYWL5 | 0.98524 | 0.90886 | -0.076378 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | HOYT 7 | 0.97097 | 0.9354 | -0.035576 |  | 0.95 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | HOYT 7 | 0.97097 | 0.9354 | -0.035576 |  | 0.95 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | HOYT 7 | 0.97097 | 0.9354 | -0.035576 |  | 0.95 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | HOYT 7 | 0.97097 | 0.9354 | -0.035576 |  | 0.95 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | HOYT 7 | 0.97097 | 0.9354 | -0.035576 |  | 0.95 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | HOYT 7 | 0.97097 | 0.9354 | -0.035576 |  | 0.95 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | HOYT 7 | 0.97097 | 0.9354 | -0.035576 |  | 0.95 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | HOYT 7 | 0.97097 | 0.9354 | -0.035576 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | HOYT 7 | 0.97097 | 0.9354 | -0.035576 |  | 0.95 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | HOYT 7 | 0.97097 | 0.9354 | -0.035576 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | HOYT 7 | 0.97097 | 0.9354 | -0.035576 |  | 0.95 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | HOYT 7 | 0.97097 | 0.9354 | -0.035576 |  | 0.95 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | HOYT 7 | 0.97097 | 0.9354 | -0.035576 |  | 0.95 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | HOYT 7 | 0.97097 | 0.9354 | -0.035576 |  | 0.95 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | HOYT 7 | 0.97097 | 0.9354 | -0.035576 |  | 0.95 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | HOYT 7 | 0.97097 | 0.9354 | -0.035576 |  | 0.95 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | HOYT 7 | 0.97097 | 0.9354 | -0.035576 |  | 0.95 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | HOYT 7 | 0.97097 | 0.9354 | -0.035576 |  | 0.95 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | HOYT 7 | 0.97097 | 0.9354 | -0.035576 |  | 0.95 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | HOYT 7 | 0.97097 | 0.9354 | -0.035576 |  | 0.95 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | HOYT 7 | 0.96715 | 0.92935 | -0.037797 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | HOYT 7 | 0.96715 | 0.92935 | -0.037797 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | HOYT 7 | 0.96715 | 0.92935 | -0.037797 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | HOYT 7 | 0.96715 | 0.92935 | -0.037797 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | HOYT 7 | 0.96715 | 0.92935 | -0.037797 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | HOYT 7 | 0.96715 | 0.92935 | -0.037797 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | HOYT 7 | 0.96715 | 0.92935 | -0.037797 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | HOYT 7 | 0.96715 | 0.92935 | -0.037797 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | HOYT 7 | 0.96715 | 0.92935 | -0.037797 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | HOYT 7 | 0.96715 | 0.92935 | -0.037797 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | HOYT 7 | 0.96715 | 0.92935 | -0.037797 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | HOYT 7 | 0.96715 | 0.92935 | -0.037797 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | HOYT 7 | 0.96715 | 0.92935 | -0.037797 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | HOYT 7 | 0.96715 | 0.92935 | -0.037797 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | HOYT 7 | 0.96715 | 0.92935 | -0.037797 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | HOYT 7 | 0.96715 | 0.92935 | -0.037797 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | HOYT 7 | 0.96715 | 0.92935 | -0.037797 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | HOYT 7 | 0.96715 | 0.92935 | -0.037797 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | HOYT 7 | 0.96715 | 0.92935 | -0.037797 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | HOYT 7 | 0.96715 | 0.92935 | -0.037797 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | HOYT 7 | 0.97425 | 0.93079 | -0.04346 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | HOYT 7 | 0.97425 | 0.93079 | -0.04346 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | HOYT 7 | 0.97425 | 0.93079 | -0.04346 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | HOYT 7 | 0.97425 | 0.93079 | -0.04346 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | HOYT 7 | 0.97425 | 0.93079 | -0.04346 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | HOYT 7 | 0.97425 | 0.93079 | -0.04346 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | HOYT 7 | 0.97425 | 0.93079 | -0.04346 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | HOYT 7 | 0.97425 | 0.93079 | -0.04346 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | HOYT 7 | 0.97425 | 0.93079 | -0.04346 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | HOYT 7 | 0.97425 | 0.93079 | -0.04346 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | HOYT 7 | 0.97425 | 0.93079 | -0.04346 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | HOYT 7 | 0.97425 | 0.93079 | -0.04346 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | HOYT 7 | 0.97425 | 0.93079 | -0.04346 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | HOYT 7 | 0.97425 | 0.93079 | -0.04346 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | HOYT 7 | 0.97425 | 0.93079 | -0.04346 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | HOYT 7 | 0.97425 | 0.93079 | -0.04346 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | HOYT 7 | 0.97425 | 0.93079 | -0.04346 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | HOYT 7 | 0.97425 | 0.93079 | -0.04346 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | HOYT 7 | 0.97425 | 0.93079 | -0.04346 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | HOYT 7 | 0.97425 | 0.93079 | -0.04346 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | HOYT 7 | 0.98354 | 0.93411 | -0.049432 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | HOYT 7 | 0.98354 | 0.93411 | -0.049432 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | HOYT 7 | 0.98354 | 0.93411 | -0.049432 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | HOYT 7 | 0.98354 | 0.93411 | -0.049432 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | HOYT 7 | 0.98354 | 0.93411 | -0.049432 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | HOYT 7 | 0.98354 | 0.93411 | -0.049432 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | HOYT 7 | 0.98354 | 0.93411 | -0.049432 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | HOYT 7 | 0.98354 | 0.93411 | -0.049432 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | HOYT 7 | 0.98354 | 0.93411 | -0.049432 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | HOYT 7 | 0.98354 | 0.93411 | -0.049432 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | HOYT 7 | 0.98354 | 0.93411 | -0.049432 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | HOYT 7 | 0.98354 | 0.93411 | -0.049432 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | HOYT 7 | 0.98354 | 0.93411 | -0.049432 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | HOYT 7 | 0.98354 | 0.93411 | -0.049432 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | HOYT 7 | 0.98354 | 0.93411 | -0.049432 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | HOYT 7 | 0.98354 | 0.93411 | -0.049432 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | HOYT 7 | 0.98354 | 0.93411 | -0.049432 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | HOYT 7 | 0.98354 | 0.93411 | -0.049432 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | HOYT 7 | 0.98354 | 0.93411 | -0.049432 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | HOYT 7 | 0.98354 | 0.93411 | -0.049432 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | HOYT 7 | 0.98354 | 0.93411 | -0.049432 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | HOYT 7 | 0.98354 | 0.93411 | -0.049432 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | HOYT 7 | 0.98354 | 0.93411 | -0.049432 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | HOYT 7 | 0.98354 | 0.93411 | -0.049432 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | HOYT 7 | 0.98354 | 0.93411 | -0.049432 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | HOYT 7 | 0.98354 | 0.93411 | -0.049432 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | HOYT 7 | 0.98354 | 0.93411 | -0.049432 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | HOYT 7 | 0.98354 | 0.93411 | -0.049432 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | HOYT 7 | 0.97073 | 0.93431 | -0.036419 |  | 0.95 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | HOYT 7 | 0.97073 | 0.93431 | -0.036419 |  | 0.95 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | HOYT 7 | 0.97073 | 0.93431 | -0.036419 |  | 0.95 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | HOYT 7 | 0.97073 | 0.93431 | -0.036419 |  | 0.95 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | HOYT 7 | 0.97073 | 0.93431 | -0.036419 |  | 0.95 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | HOYT 7 | 0.97073 | 0.93431 | -0.036419 |  | 0.95 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | HOYT 7 | 0.97073 | 0.93431 | -0.036419 |  | 0.95 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | HOYT 7 | 0.97073 | 0.93431 | -0.036419 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | HOYT 7 | 0.97073 | 0.93431 | -0.036419 |  | 0.95 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | HOYT 7 | 0.97073 | 0.93431 | -0.036419 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | HOYT 7 | 0.97073 | 0.93431 | -0.036419 |  | 0.95 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | HOYT 7 | 0.97073 | 0.93431 | -0.036419 |  | 0.95 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | HOYT 7 | 0.97073 | 0.93431 | -0.036419 |  | 0.95 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | HOYT 7 | 0.97073 | 0.93431 | -0.036419 |  | 0.95 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | HOYT 7 | 0.97073 | 0.93431 | -0.036419 |  | 0.95 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | HOYT 7 | 0.97073 | 0.93431 | -0.036419 |  | 0.95 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | HOYT 7 | 0.97073 | 0.93431 | -0.036419 |  | 0.95 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | HOYT 7 | 0.97073 | 0.93431 | -0.036419 |  | 0.95 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | HOYT 7 | 0.97073 | 0.93431 | -0.036419 |  | 0.95 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | HOYT 7 | 0.97073 | 0.93431 | -0.036419 |  | 0.95 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | HSNVL 5 | 0.99358 | 0.92685 | -0.066739 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | HSNVL 5 | 0.99358 | 0.92685 | -0.066739 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | HSNVL 5 | 0.99358 | 0.92685 | -0.066739 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | HSNVL 5 | 0.99358 | 0.92685 | -0.066739 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | HSNVL 5 | 0.99358 | 0.92685 | -0.066739 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | HSNVL 5 | 0.99358 | 0.92685 | -0.066739 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | HSNVL 5 | 0.99358 | 0.92685 | -0.066739 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | HSNVL 5 | 0.99358 | 0.92685 | -0.066739 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | HSNVL 5 | 0.99358 | 0.92685 | -0.066739 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | HSNVL 5 | 0.99358 | 0.92685 | -0.066739 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | HSNVL 5 | 0.99358 | 0.92685 | -0.066739 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | HSNVL 5 | 0.99358 | 0.92685 | -0.066739 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | HSNVL 5 | 0.99358 | 0.92685 | -0.066739 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | HSNVL 5 | 0.99358 | 0.92685 | -0.066739 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | HSNVL 5 | 0.99358 | 0.92685 | -0.066739 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | HSNVL 5 | 0.99358 | 0.92685 | -0.066739 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | HSNVL 5 | 0.99358 | 0.92685 | -0.066739 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | HSNVL 5 | 0.99358 | 0.92685 | -0.066739 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | HSNVL 5 | 0.99358 | 0.92685 | -0.066739 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | HSNVL 5 | 0.99358 | 0.92685 | -0.066739 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | HSNVL 5 | 0.99358 | 0.92685 | -0.066739 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | HSNVL 5 | 0.99358 | 0.92685 | -0.066739 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | HSNVL 5 | 0.99358 | 0.92685 | -0.066739 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | HSNVL 5 | 0.99358 | 0.92685 | -0.066739 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | HSNVL 5 | 0.99358 | 0.92685 | -0.066739 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | HSNVL 5 | 0.99358 | 0.92685 | -0.066739 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | HSNVL 5 | 0.99358 | 0.92685 | -0.066739 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | HSNVL 5 | 0.99358 | 0.92685 | -0.066739 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | INDIAN_CK_5 | 0.9657 | 0.92789 | -0.037811 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | INDIAN_CK_5 | 0.9657 | 0.92789 | -0.037811 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | INDIAN_CK_5 | 0.9657 | 0.92789 | -0.037811 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | INDIAN_CK_5 | 0.9657 | 0.92789 | -0.037811 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | INDIAN_CK_5 | 0.9657 | 0.92789 | -0.037811 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | INDIAN_CK_5 | 0.9657 | 0.92789 | -0.037811 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | INDIAN_CK_5 | 0.9657 | 0.92789 | -0.037811 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | INDIAN_CK_5 | 0.9657 | 0.92789 | -0.037811 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | INDIAN_CK_5 | 0.9657 | 0.92789 | -0.037811 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | INDIAN_CK_5 | 0.9657 | 0.92789 | -0.037811 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | INDIAN_CK_5 | 0.9657 | 0.92789 | -0.037811 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | INDIAN_CK_5 | 0.9657 | 0.92789 | -0.037811 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | INDIAN_CK_5 | 0.9657 | 0.92789 | -0.037811 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | INDIAN_CK_5 | 0.9657 | 0.92789 | -0.037811 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | INDIAN_CK_5 | 0.9657 | 0.92789 | -0.037811 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | INDIAN_CK_5 | 0.9657 | 0.92789 | -0.037811 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | INDIAN_CK_5 | 0.9657 | 0.92789 | -0.037811 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | INDIAN_CK_5 | 0.9657 | 0.92789 | -0.037811 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | INDIAN_CK_5 | 0.9657 | 0.92789 | -0.037811 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | INDIAN_CK_5 | 0.9657 | 0.92789 | -0.037811 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | INDIAN_CK_5 | 0.97538 | 0.90733 | -0.068048 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | INDIAN_CK_5 | 0.97538 | 0.90733 | -0.068048 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | INDIAN_CK_5 | 0.97538 | 0.90733 | -0.068048 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | INDIAN_CK_5 | 0.97538 | 0.90733 | -0.068048 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | INDIAN_CK_5 | 0.97538 | 0.90733 | -0.068048 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | INDIAN_CK_5 | 0.97538 | 0.90733 | -0.068048 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | INDIAN_CK_5 | 0.97538 | 0.90733 | -0.068048 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | INDIAN_CK_5 | 0.97538 | 0.90733 | -0.068048 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | INDIAN_CK_5 | 0.97538 | 0.90733 | -0.068048 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | INDIAN_CK_5 | 0.97538 | 0.90733 | -0.068048 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | INDIAN_CK_5 | 0.97538 | 0.90733 | -0.068048 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | INDIAN_CK_5 | 0.97538 | 0.90733 | -0.068048 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | INDIAN_CK_5 | 0.97538 | 0.90733 | -0.068048 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | INDIAN_CK_5 | 0.97538 | 0.90733 | -0.068048 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | INDIAN_CK_5 | 0.97538 | 0.90733 | -0.068048 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | INDIAN_CK_5 | 0.97538 | 0.90733 | -0.068048 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | INDIAN_CK_5 | 0.97538 | 0.90733 | -0.068048 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | INDIAN_CK_5 | 0.97538 | 0.90733 | -0.068048 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | INDIAN_CK_5 | 0.97538 | 0.90733 | -0.068048 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | INDIAN_CK_5 | 0.97538 | 0.90733 | -0.068048 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | INDIAN_CK_5 | 0.97538 | 0.90733 | -0.068048 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | INDIAN_CK_5 | 0.97538 | 0.90733 | -0.068048 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | INDIAN_CK_5 | 0.97538 | 0.90733 | -0.068048 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | INDIAN_CK_5 | 0.97538 | 0.90733 | -0.068048 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | INDIAN_CK_5 | 0.97538 | 0.90733 | -0.068048 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | INDIAN_CK_5 | 0.97538 | 0.90733 | -0.068048 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | INDIAN_CK_5 | 0.97538 | 0.90733 | -0.068048 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | INDIAN_CK_5 | 0.97538 | 0.90733 | -0.068048 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | JADE 3 | 0.9615 | 0.90122 | -0.060286 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | JADE 3 | 0.9615 | 0.90122 | -0.060286 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | JADE 3 | 0.9615 | 0.90122 | -0.060286 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | JADE 3 | 0.9615 | 0.90122 | -0.060286 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | JADE 3 | 0.9615 | 0.90122 | -0.060286 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | JADE 3 | 0.9615 | 0.90122 | -0.060286 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | JADE 3 | 0.9615 | 0.90122 | -0.060286 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | JADE 3 | 0.9615 | 0.90122 | -0.060286 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | JADE 3 | 0.9615 | 0.90122 | -0.060286 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | JADE 3 | 0.9615 | 0.90122 | -0.060286 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | JADE 3 | 0.9615 | 0.90122 | -0.060286 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | JADE 3 | 0.9615 | 0.90122 | -0.060286 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | JADE 3 | 0.9615 | 0.90122 | -0.060286 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | JADE 3 | 0.9615 | 0.90122 | -0.060286 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | JADE 3 | 0.9615 | 0.90122 | -0.060286 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | JADE 3 | 0.9615 | 0.90122 | -0.060286 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | JADE 3 | 0.9615 | 0.90122 | -0.060286 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | JADE 3 | 0.9615 | 0.90122 | -0.060286 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | JADE 3 | 0.9615 | 0.90122 | -0.060286 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | JADE 3 | 0.9615 | 0.90122 | -0.060286 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | JADE 3 | 0.9615 | 0.90122 | -0.060286 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | JADE 3 | 0.9615 | 0.90122 | -0.060286 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | JADE 3 | 0.9615 | 0.90122 | -0.060286 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | JADE 3 | 0.9615 | 0.90122 | -0.060286 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | JADE 3 | 0.9615 | 0.90122 | -0.060286 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | JADE 3 | 0.9615 | 0.90122 | -0.060286 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | JADE 3 | 0.9615 | 0.90122 | -0.060286 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | JADE 3 | 0.9615 | 0.90122 | -0.060286 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | JAGGER 3 | 0.96216 | 0.89662 | -0.065542 |  | 0.9 | 1.05 | 0.045977 | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | Add 1 MVAR switched shunt at DIGHTON3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | JAGGER 3 | 0.96216 | 0.89662 | -0.065542 |  | 0.9 | 1.05 | 0.045977 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Add 1 MVAR switched shunt at DIGHTON3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | JAY 4 | 0.9639 | 0.91033 | -0.053568 |  | 0.92 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | JAY 4 | 0.9639 | 0.91033 | -0.053568 |  | 0.92 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | JAY 4 | 0.9639 | 0.91033 | -0.053568 |  | 0.92 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | JAY 4 | 0.9639 | 0.91033 | -0.053568 |  | 0.92 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | JAY 4 | 0.9639 | 0.91033 | -0.053568 |  | 0.92 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | JAY 4 | 0.9639 | 0.91033 | -0.053568 |  | 0.92 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | JAY 4 | 0.9639 | 0.91033 | -0.053568 |  | 0.92 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | JAY 4 | 0.9639 | 0.91033 | -0.053568 |  | 0.92 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | JAY 4 | 0.9639 | 0.91033 | -0.053568 |  | 0.92 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | JAY 4 | 0.9639 | 0.91033 | -0.053568 |  | 0.92 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | JAY 4 | 0.9639 | 0.91033 | -0.053568 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | JAY 4 | 0.9639 | 0.91033 | -0.053568 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | JAY 4 | 0.9639 | 0.91033 | -0.053568 |  | 0.92 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | JAY 4 | 0.9639 | 0.91033 | -0.053568 |  | 0.92 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | JAY 4 | 0.9639 | 0.91033 | -0.053568 |  | 0.92 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | JAY 4 | 0.96418 | 0.91097 | -0.053216 |  | 0.92 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | JAY 4 | 0.96418 | 0.91097 | -0.053216 |  | 0.92 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | JAY 4 | 0.96418 | 0.91097 | -0.053216 |  | 0.92 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | JAY 4 | 0.96418 | 0.91097 | -0.053216 |  | 0.92 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | JAY 4 | 0.96418 | 0.91097 | -0.053216 |  | 0.92 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | JAY 4 | 0.96418 | 0.91097 | -0.053216 |  | 0.92 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | JAY 4 | 0.96418 | 0.91097 | -0.053216 |  | 0.92 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | JAY 4 | 0.96418 | 0.91097 | -0.053216 |  | 0.92 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | JAY 4 | 0.96418 | 0.91097 | -0.053216 |  | 0.92 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | JAY 4 | 0.96418 | 0.91097 | -0.053216 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | JAY 4 | 0.96418 | 0.91097 | -0.053216 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | JAY 4 | 0.96418 | 0.91097 | -0.053216 |  | 0.92 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | JAY 4 | 0.96418 | 0.91097 | -0.053216 |  | 0.92 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | JAY 4 | 0.96418 | 0.91097 | -0.053216 |  | 0.92 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | JAY 4 | 0.95987 | 0.91146 | -0.048418 |  | 0.92 | 1.05 | 0.030712 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | JAY 4 | 0.95987 | 0.91146 | -0.048418 |  | 0.92 | 1.05 | 0.038311 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | JAY 4 | 0.95987 | 0.91146 | -0.048418 |  | 0.92 | 1.05 | 0.061498 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | JAY 4 | 0.95987 | 0.91146 | -0.048418 |  | 0.92 | 1.05 | 0.070613 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | JAY 4 | 0.95987 | 0.91146 | -0.048418 |  | 0.92 | 1.05 | 0.037457 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | JAY 4 | 0.95987 | 0.91146 | -0.048418 |  | 0.92 | 1.05 | 0.15352 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | JAY 4 | 0.95987 | 0.91146 | -0.048418 |  | 0.92 | 1.05 | 0.062033 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | JAY 4 | 0.96437 | 0.91375 | -0.050624 |  | 0.92 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | JAY 4 | 0.96437 | 0.91375 | -0.050624 |  | 0.92 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | JAY 4 | 0.96437 | 0.91375 | -0.050624 |  | 0.92 | 1.05 | 0.055405 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | JAY 4 | 0.96437 | 0.91375 | -0.050624 |  | 0.92 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | JAY 4 | 0.96437 | 0.91375 | -0.050624 |  | 0.92 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | JAY 4 | 0.96437 | 0.91375 | -0.050624 |  | 0.92 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | JAY 4 | 0.96437 | 0.91375 | -0.050624 |  | 0.92 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | JAY 4 | 0.96437 | 0.91375 | -0.050624 |  | 0.92 | 1.05 | 0.082012 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | JAY 4 | 0.96437 | 0.91375 | -0.050624 |  | 0.92 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | JAY 4 | 0.96437 | 0.91375 | -0.050624 |  | 0.92 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | JAY 4 | 0.96437 | 0.91375 | -0.050624 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | JAY 4 | 0.96437 | 0.91375 | -0.050624 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | JAY 4 | 0.96437 | 0.91375 | -0.050624 |  | 0.92 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | JAY 4 | 0.96437 | 0.91375 | -0.050624 |  | 0.92 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | JAY 4 | 0.96437 | 0.91375 | -0.050624 |  | 0.92 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | JAY 4 | 0.96088 | 0.91384 | -0.047046 |  | 0.92 | 1.05 | 0.038311 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | JAY 4 | 0.96088 | 0.91384 | -0.047046 |  | 0.92 | 1.05 | 0.058472 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | JAY 4 | 0.96088 | 0.91384 | -0.047046 |  | 0.92 | 1.05 | 0.070613 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | JAY 4 | 0.96088 | 0.91384 | -0.047046 |  | 0.92 | 1.05 | 0.036297 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | JAY 4 | 0.96088 | 0.91384 | -0.047046 |  | 0.92 | 1.05 | 0.15352 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | JAY 4 | 0.96088 | 0.91384 | -0.047046 |  | 0.92 | 1.05 | 0.060874 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | JEC 6 | 0.97747 | 0.9468 | -0.030667 |  | 0.95 | 1.05 | 0.03965 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | JEC 6 | 0.97747 | 0.9468 | -0.030667 |  | 0.95 | 1.05 | 0.042938 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | JEC 6 | 0.97747 | 0.9468 | -0.030667 |  | 0.95 | 1.05 | 0.032864 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | JEC 6 | 0.97747 | 0.9468 | -0.030667 |  | 0.95 | 1.05 | 0.034629 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | JEC 6 | 0.97747 | 0.9468 | -0.030667 |  | 0.95 | 1.05 | 0.036988 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | JEC 6 | 0.97747 | 0.9468 | -0.030667 |  | 0.95 | 1.05 | 0.03396 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | JEC 6 | 0.97747 | 0.9468 | -0.030667 |  | 0.95 | 1.05 | 0.030296 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | JEC 6 | 0.97747 | 0.9468 | -0.030667 |  | 0.95 | 1.05 | 0.037836 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | JEC 6 | 0.97747 | 0.9468 | -0.030667 |  | 0.95 | 1.05 | 0.036214 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | JEC 6 | 0.97747 | 0.9468 | -0.030667 |  | 0.95 | 1.05 | 0.055483 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | JEC 6 | 0.97747 | 0.9468 | -0.030667 |  | 0.95 | 1.05 | 0.036214 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | JEC 6 | 0.97747 | 0.9468 | -0.030667 |  | 0.95 | 1.05 | 0.037031 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | JEC 6 | 0.97747 | 0.9468 | -0.030667 |  | 0.95 | 1.05 | 0.03728 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | JEC 6 | 0.97747 | 0.9468 | -0.030667 |  | 0.95 | 1.05 | 0.034689 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | JEC 6 | 0.97747 | 0.9468 | -0.030667 |  | 0.95 | 1.05 | 0.033481 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | JEC 6 | 0.97747 | 0.9468 | -0.030667 |  | 0.95 | 1.05 | 0.035246 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | JEC 6 | 0.97747 | 0.9468 | -0.030667 |  | 0.95 | 1.05 | 0.03235 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | JEC 6 | 0.97747 | 0.9468 | -0.030667 |  | 0.95 | 1.05 | 0.031498 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | JEC 6 | 0.97747 | 0.9468 | -0.030667 |  | 0.95 | 1.05 | 0.033388 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | JEC 6 | 0.97747 | 0.9468 | -0.030667 |  | 0.95 | 1.05 | 0.034867 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | JEC 6 | 0.97535 | 0.94089 | -0.034462 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | JEC 6 | 0.97535 | 0.94089 | -0.034462 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | JEC 6 | 0.97535 | 0.94089 | -0.034462 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | JEC 6 | 0.97535 | 0.94089 | -0.034462 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | JEC 6 | 0.97535 | 0.94089 | -0.034462 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | JEC 6 | 0.97535 | 0.94089 | -0.034462 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | JEC 6 | 0.97535 | 0.94089 | -0.034462 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | JEC 6 | 0.97535 | 0.94089 | -0.034462 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | JEC 6 | 0.97535 | 0.94089 | -0.034462 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | JEC 6 | 0.97535 | 0.94089 | -0.034462 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | JEC 6 | 0.97535 | 0.94089 | -0.034462 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | JEC 6 | 0.97535 | 0.94089 | -0.034462 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | JEC 6 | 0.97535 | 0.94089 | -0.034462 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | JEC 6 | 0.97535 | 0.94089 | -0.034462 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | JEC 6 | 0.97535 | 0.94089 | -0.034462 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | JEC 6 | 0.97535 | 0.94089 | -0.034462 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | JEC 6 | 0.97535 | 0.94089 | -0.034462 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | JEC 6 | 0.97535 | 0.94089 | -0.034462 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | JEC 6 | 0.97535 | 0.94089 | -0.034462 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | JEC 6 | 0.97535 | 0.94089 | -0.034462 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | JEC 6 | 0.98177 | 0.94172 | -0.040045 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | JEC 6 | 0.98177 | 0.94172 | -0.040045 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | JEC 6 | 0.98177 | 0.94172 | -0.040045 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | JEC 6 | 0.98177 | 0.94172 | -0.040045 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | JEC 6 | 0.98177 | 0.94172 | -0.040045 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | JEC 6 | 0.98177 | 0.94172 | -0.040045 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | JEC 6 | 0.98177 | 0.94172 | -0.040045 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | JEC 6 | 0.98177 | 0.94172 | -0.040045 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | JEC 6 | 0.98177 | 0.94172 | -0.040045 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | JEC 6 | 0.98177 | 0.94172 | -0.040045 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | JEC 6 | 0.98177 | 0.94172 | -0.040045 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | JEC 6 | 0.98177 | 0.94172 | -0.040045 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | JEC 6 | 0.98177 | 0.94172 | -0.040045 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | JEC 6 | 0.98177 | 0.94172 | -0.040045 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | JEC 6 | 0.98177 | 0.94172 | -0.040045 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | JEC 6 | 0.98177 | 0.94172 | -0.040045 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | JEC 6 | 0.98177 | 0.94172 | -0.040045 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | JEC 6 | 0.98177 | 0.94172 | -0.040045 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | JEC 6 | 0.98177 | 0.94172 | -0.040045 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | JEC 6 | 0.98177 | 0.94172 | -0.040045 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | JEC 6 | 0.98676 | 0.94095 | -0.045805 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | JEC 6 | 0.98676 | 0.94095 | -0.045805 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | JEC 6 | 0.98676 | 0.94095 | -0.045805 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | JEC 6 | 0.98676 | 0.94095 | -0.045805 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | JEC 6 | 0.98676 | 0.94095 | -0.045805 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | JEC 6 | 0.98676 | 0.94095 | -0.045805 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | JEC 6 | 0.98676 | 0.94095 | -0.045805 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | JEC 6 | 0.98676 | 0.94095 | -0.045805 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | JEC 6 | 0.98676 | 0.94095 | -0.045805 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | JEC 6 | 0.98676 | 0.94095 | -0.045805 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | JEC 6 | 0.98676 | 0.94095 | -0.045805 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | JEC 6 | 0.98676 | 0.94095 | -0.045805 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | JEC 6 | 0.98676 | 0.94095 | -0.045805 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | JEC 6 | 0.98676 | 0.94095 | -0.045805 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | JEC 6 | 0.98676 | 0.94095 | -0.045805 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | JEC 6 | 0.98676 | 0.94095 | -0.045805 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | JEC 6 | 0.98676 | 0.94095 | -0.045805 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | JEC 6 | 0.98676 | 0.94095 | -0.045805 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | JEC 6 | 0.98676 | 0.94095 | -0.045805 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | JEC 6 | 0.98676 | 0.94095 | -0.045805 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | JEC 6 | 0.98676 | 0.94095 | -0.045805 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | JEC 6 | 0.98676 | 0.94095 | -0.045805 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | JEC 6 | 0.98676 | 0.94095 | -0.045805 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | JEC 6 | 0.98676 | 0.94095 | -0.045805 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | JEC 6 | 0.98676 | 0.94095 | -0.045805 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | JEC 6 | 0.98676 | 0.94095 | -0.045805 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | JEC 6 | 0.98676 | 0.94095 | -0.045805 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | JEC 6 | 0.98676 | 0.94095 | -0.045805 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | JEC 6 | 0.97839 | 0.94583 | -0.032562 |  | 0.95 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | JEC 6 | 0.97839 | 0.94583 | -0.032562 |  | 0.95 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | JEC 6 | 0.97839 | 0.94583 | -0.032562 |  | 0.95 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | JEC 6 | 0.97839 | 0.94583 | -0.032562 |  | 0.95 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | JEC 6 | 0.97839 | 0.94583 | -0.032562 |  | 0.95 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | JEC 6 | 0.97839 | 0.94583 | -0.032562 |  | 0.95 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | JEC 6 | 0.97839 | 0.94583 | -0.032562 |  | 0.95 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | JEC 6 | 0.97839 | 0.94583 | -0.032562 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | JEC 6 | 0.97839 | 0.94583 | -0.032562 |  | 0.95 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | JEC 6 | 0.97839 | 0.94583 | -0.032562 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | JEC 6 | 0.97839 | 0.94583 | -0.032562 |  | 0.95 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | JEC 6 | 0.97839 | 0.94583 | -0.032562 |  | 0.95 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | JEC 6 | 0.97839 | 0.94583 | -0.032562 |  | 0.95 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | JEC 6 | 0.97839 | 0.94583 | -0.032562 |  | 0.95 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | JEC 6 | 0.97839 | 0.94583 | -0.032562 |  | 0.95 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | JEC 6 | 0.97839 | 0.94583 | -0.032562 |  | 0.95 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | JEC 6 | 0.97839 | 0.94583 | -0.032562 |  | 0.95 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | JEC 6 | 0.97839 | 0.94583 | -0.032562 |  | 0.95 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | JEC 6 | 0.97839 | 0.94583 | -0.032562 |  | 0.95 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | JEC 6 | 0.97839 | 0.94583 | -0.032562 |  | 0.95 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | JEC N 7 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.03965 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | JEC N 7 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.042938 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | JEC N 7 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.032864 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | JEC N 7 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.034629 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | JEC N 7 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.036988 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | JEC N 7 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.03396 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | JEC N 7 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.030296 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | JEC N 7 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.037836 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | JEC N 7 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.036214 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | JEC N 7 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.055483 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | JEC N 7 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.036214 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | JEC N 7 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.037031 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | JEC N 7 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.03728 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | JEC N 7 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.034689 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | JEC N 7 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.033481 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | JEC N 7 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.035246 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | JEC N 7 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.03235 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | JEC N 7 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.031498 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | JEC N 7 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.033388 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | JEC N 7 | 0.97817 | 0.94333 | -0.034846 |  | 0.95 | 1.05 | 0.034867 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | JEC N 7 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | JEC N 7 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | JEC N 7 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | JEC N 7 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | JEC N 7 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | JEC N 7 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | JEC N 7 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | JEC N 7 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | JEC N 7 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | JEC N 7 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | JEC N 7 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | JEC N 7 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | JEC N 7 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | JEC N 7 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | JEC N 7 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | JEC N 7 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | JEC N 7 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | JEC N 7 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | JEC N 7 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | JEC N 7 | 0.97621 | 0.93769 | -0.038524 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | JEC N 7 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | JEC N 7 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | JEC N 7 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | JEC N 7 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | JEC N 7 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | JEC N 7 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | JEC N 7 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | JEC N 7 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | JEC N 7 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | JEC N 7 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | JEC N 7 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | JEC N 7 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | JEC N 7 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | JEC N 7 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | JEC N 7 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | JEC N 7 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | JEC N 7 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | JEC N 7 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | JEC N 7 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | JEC N 7 | 0.98302 | 0.93838 | -0.044645 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | JEC N 7 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | JEC N 7 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | JEC N 7 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | JEC N 7 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | JEC N 7 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | JEC N 7 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | JEC N 7 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | JEC N 7 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | JEC N 7 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | JEC N 7 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | JEC N 7 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | JEC N 7 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | JEC N 7 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | JEC N 7 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | JEC N 7 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | JEC N 7 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | JEC N 7 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | JEC N 7 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | JEC N 7 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | JEC N 7 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | JEC N 7 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | JEC N 7 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | JEC N 7 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | JEC N 7 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | JEC N 7 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | JEC N 7 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | JEC N 7 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | JEC N 7 | 0.98858 | 0.93868 | -0.049895 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | JEC N 7 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | JEC N 7 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | JEC N 7 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | JEC N 7 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | JEC N 7 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | JEC N 7 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | JEC N 7 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | JEC N 7 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | JEC N 7 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | JEC N 7 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | JEC N 7 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | JEC N 7 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | JEC N 7 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | JEC N 7 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | JEC N 7 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | JEC N 7 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | JEC N 7 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | JEC N 7 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | JEC N 7 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | JEC N 7 | 0.9795 | 0.9427 | -0.036794 |  | 0.95 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | JOHNSON3 | 0.95843 | 0.89453 | -0.063897 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | JOHNSON3 | 0.95843 | 0.89453 | -0.063897 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | JOHNSON3 | 0.95962 | 0.89247 | -0.067147 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | JOHNSON3 | 0.95962 | 0.89247 | -0.067147 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | JOHNSON3 | 0.95962 | 0.89247 | -0.067147 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | JOHNSON3 | 0.95962 | 0.89247 | -0.067147 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | JOHNSON3 | 0.95962 | 0.89247 | -0.067148 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | JOHNSON3 | 0.95962 | 0.89247 | -0.067148 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | JOP391 5 | 0.97398 | 0.92324 | -0.050747 |  | 0.925 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | JOP391 5 | 0.97398 | 0.92324 | -0.050747 |  | 0.925 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | JOP391 5 | 0.97398 | 0.92324 | -0.050747 |  | 0.925 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | JOP391 5 | 0.97398 | 0.92324 | -0.050747 |  | 0.925 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | JOP391 5 | 0.97398 | 0.92324 | -0.050747 |  | 0.925 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | JOP391 5 | 0.97398 | 0.92324 | -0.050747 |  | 0.925 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | JOP391 5 | 0.97398 | 0.92324 | -0.050747 |  | 0.925 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | JOP391 5 | 0.97398 | 0.92324 | -0.050747 |  | 0.925 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | JOP391 5 | 0.97398 | 0.92324 | -0.050747 |  | 0.925 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | JOP391 5 | 0.97398 | 0.92324 | -0.050747 |  | 0.925 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | JOP391 5 | 0.97398 | 0.92324 | -0.050747 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | JOP391 5 | 0.97398 | 0.92324 | -0.050747 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | JOP391 5 | 0.97398 | 0.92324 | -0.050747 |  | 0.925 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | JOP391 5 | 0.97398 | 0.92324 | -0.050747 |  | 0.925 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | JOP391 5 | 0.97398 | 0.92324 | -0.050747 |  | 0.925 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | JOP391 5 | 0.97463 | 0.92425 | -0.05038 |  | 0.925 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | JOP391 5 | 0.97463 | 0.92425 | -0.05038 |  | 0.925 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | JOP391 5 | 0.97463 | 0.92425 | -0.05038 |  | 0.925 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | JOP391 5 | 0.97463 | 0.92425 | -0.05038 |  | 0.925 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | JOP391 5 | 0.97463 | 0.92425 | -0.05038 |  | 0.925 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | JOP391 5 | 0.97463 | 0.92425 | -0.05038 |  | 0.925 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | JOP391 5 | 0.97463 | 0.92425 | -0.05038 |  | 0.925 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | JOP391 5 | 0.97463 | 0.92425 | -0.05038 |  | 0.925 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | JOP391 5 | 0.97463 | 0.92425 | -0.05038 |  | 0.925 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | JOP391 5 | 0.97463 | 0.92425 | -0.05038 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | JOP391 5 | 0.97463 | 0.92425 | -0.05038 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | JOP391 5 | 0.97463 | 0.92425 | -0.05038 |  | 0.925 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | JOP391 5 | 0.97463 | 0.92425 | -0.05038 |  | 0.925 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | JOP391 5 | 0.97463 | 0.92425 | -0.05038 |  | 0.925 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | KANARAD3 | 0.96429 | 0.89796 | -0.066328 |  | 0.9 | 1.05 | 0.041569 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | KANARAD3 | 0.96429 | 0.89796 | -0.066328 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | KANARAD3 | 0.96429 | 0.89796 | -0.066328 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | KANARAD3 | 0.96429 | 0.89796 | -0.066328 |  | 0.9 | 1.05 | 0.03222 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | KANARAD3 | 0.96429 | 0.89796 | -0.066328 |  | 0.9 | 1.05 | 0.030633 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | KANARAD3 | 0.96429 | 0.89796 | -0.066328 |  | 0.9 | 1.05 | 0.030061 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | KANARAD3 | 0.96429 | 0.89796 | -0.066328 |  | 0.9 | 1.05 | 0.031207 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | KANARAD3 | 0.93452 | 0.8571 | -0.077422 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | KANARAD3 | 0.93452 | 0.8571 | -0.077422 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | KANARAD3 | 0.93734 | 0.85097 | -0.086374 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | KANARAD3 | 0.93734 | 0.85097 | -0.086374 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | KANARAD3 | 0.93734 | 0.85097 | -0.086374 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | KANARAD3 | 0.93734 | 0.85097 | -0.086374 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | KANARAD3 | 0.93735 | 0.85097 | -0.086375 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | KANARAD3 | 0.93735 | 0.85097 | -0.086375 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | KNLWRTH5 | 0.96311 | 0.92475 | -0.038356 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | KNLWRTH5 | 0.96311 | 0.92475 | -0.038356 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | KNLWRTH5 | 0.96311 | 0.92475 | -0.038356 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | KNLWRTH5 | 0.96311 | 0.92475 | -0.038356 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | KNLWRTH5 | 0.96311 | 0.92475 | -0.038356 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | KNLWRTH5 | 0.96311 | 0.92475 | -0.038356 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | KNLWRTH5 | 0.96311 | 0.92475 | -0.038356 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | KNLWRTH5 | 0.96311 | 0.92475 | -0.038356 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | KNLWRTH5 | 0.96311 | 0.92475 | -0.038356 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | KNLWRTH5 | 0.96311 | 0.92475 | -0.038356 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | KNLWRTH5 | 0.96311 | 0.92475 | -0.038356 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | KNLWRTH5 | 0.96311 | 0.92475 | -0.038356 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | KNLWRTH5 | 0.96311 | 0.92475 | -0.038356 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | KNLWRTH5 | 0.96311 | 0.92475 | -0.038356 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | KNLWRTH5 | 0.96311 | 0.92475 | -0.038356 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | KNLWRTH5 | 0.96311 | 0.92475 | -0.038356 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | KNLWRTH5 | 0.96311 | 0.92475 | -0.038356 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | KNLWRTH5 | 0.96311 | 0.92475 | -0.038356 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | KNLWRTH5 | 0.96311 | 0.92475 | -0.038356 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | KNLWRTH5 | 0.96311 | 0.92475 | -0.038356 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | KNLWRTH5 | 0.97122 | 0.92828 | -0.042946 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | KNLWRTH5 | 0.97122 | 0.92828 | -0.042946 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | KNLWRTH5 | 0.97122 | 0.92828 | -0.042946 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | KNLWRTH5 | 0.97122 | 0.92828 | -0.042946 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | KNLWRTH5 | 0.97122 | 0.92828 | -0.042946 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | KNLWRTH5 | 0.97122 | 0.92828 | -0.042946 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | KNLWRTH5 | 0.97122 | 0.92828 | -0.042946 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | KNLWRTH5 | 0.97122 | 0.92828 | -0.042946 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | KNLWRTH5 | 0.97122 | 0.92828 | -0.042946 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | KNLWRTH5 | 0.97122 | 0.92828 | -0.042946 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | KNLWRTH5 | 0.97122 | 0.92828 | -0.042946 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | KNLWRTH5 | 0.97122 | 0.92828 | -0.042946 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | KNLWRTH5 | 0.97122 | 0.92828 | -0.042946 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | KNLWRTH5 | 0.97122 | 0.92828 | -0.042946 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | KNLWRTH5 | 0.97122 | 0.92828 | -0.042946 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | KNLWRTH5 | 0.97122 | 0.92828 | -0.042946 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | KNLWRTH5 | 0.97122 | 0.92828 | -0.042946 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | KNLWRTH5 | 0.97122 | 0.92828 | -0.042946 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | KNLWRTH5 | 0.97122 | 0.92828 | -0.042946 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | KNLWRTH5 | 0.97122 | 0.92828 | -0.042946 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | KNLWRTH5 | 0.9735 | 0.90609 | -0.067413 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | KNLWRTH5 | 0.9735 | 0.90609 | -0.067413 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | KNLWRTH5 | 0.9735 | 0.90609 | -0.067413 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | KNLWRTH5 | 0.9735 | 0.90609 | -0.067413 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | KNLWRTH5 | 0.9735 | 0.90609 | -0.067413 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | KNLWRTH5 | 0.9735 | 0.90609 | -0.067413 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | KNLWRTH5 | 0.9735 | 0.90609 | -0.067413 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | KNLWRTH5 | 0.9735 | 0.90609 | -0.067413 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | KNLWRTH5 | 0.9735 | 0.90609 | -0.067413 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | KNLWRTH5 | 0.9735 | 0.90609 | -0.067413 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | KNLWRTH5 | 0.9735 | 0.90609 | -0.067413 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | KNLWRTH5 | 0.9735 | 0.90609 | -0.067413 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | KNLWRTH5 | 0.9735 | 0.90609 | -0.067413 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | KNLWRTH5 | 0.9735 | 0.90609 | -0.067413 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | KNLWRTH5 | 0.9735 | 0.90609 | -0.067413 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | KNLWRTH5 | 0.9735 | 0.90609 | -0.067413 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | KNLWRTH5 | 0.9735 | 0.90609 | -0.067413 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | KNLWRTH5 | 0.9735 | 0.90609 | -0.067413 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | KNLWRTH5 | 0.9735 | 0.90609 | -0.067413 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | KNLWRTH5 | 0.9735 | 0.90609 | -0.067413 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | KNLWRTH5 | 0.9735 | 0.90609 | -0.067413 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | KNLWRTH5 | 0.9735 | 0.90609 | -0.067413 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | KNLWRTH5 | 0.9735 | 0.90609 | -0.067413 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | KNLWRTH5 | 0.9735 | 0.90609 | -0.067413 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | KNLWRTH5 | 0.9735 | 0.90609 | -0.067413 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | KNLWRTH5 | 0.9735 | 0.90609 | -0.067413 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | KNLWRTH5 | 0.9735 | 0.90609 | -0.067413 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | KNLWRTH5 | 0.9735 | 0.90609 | -0.067413 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | KNOLL N 6 | 0.97117 | 0.89975 | -0.071422 |  | 0.9 | 1.05 | 0.064516 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | KNOLL S 6 | 0.97117 | 0.89975 | -0.071422 |  | 0.9 | 1.05 | 0.064516 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | LABETTE2 | 0.95416 | 0.91154 | -0.042622 |  | 0.93 | 1.05 | 0.077629 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | LABETTE2 | 0.95416 | 0.91154 | -0.042622 |  | 0.93 | 1.05 | 0.06446 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | LABETTE2 | 0.95416 | 0.91154 | -0.042622 |  | 0.93 | 1.05 | 0.066434 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | LABETTE2 | 0.95416 | 0.91154 | -0.042622 |  | 0.93 | 1.05 | 0.073293 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | LABETTE2 | 0.95416 | 0.91154 | -0.042622 |  | 0.93 | 1.05 | 0.053415 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-122 | LABETTE2 | 0.95416 | 0.91154 | -0.042622 |  | 0.93 | 1.05 | 0.08103 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-177 | LABETTE2 | 0.95416 | 0.91154 | -0.042622 |  | 0.93 | 1.05 | 0.08268 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-178 | LABETTE2 | 0.95416 | 0.91154 | -0.042622 |  | 0.93 | 1.05 | 0.077122 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | LABETTE2 | 0.95416 | 0.91154 | -0.042622 |  | 0.93 | 1.05 | 0.032185 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | LABETTE2 | 0.95416 | 0.91154 | -0.042622 |  | 0.93 | 1.05 | 0.073922 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-232 | LABETTE2 | 0.95416 | 0.91154 | -0.042622 |  | 0.93 | 1.05 | 0.076776 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | LABETTE2 | 0.95416 | 0.91154 | -0.042622 |  | 0.93 | 1.05 | 0.06446 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LABETTE2 | 0.95416 | 0.91154 | -0.042622 |  | 0.93 | 1.05 | 0.038841 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | LABETTE2 | 0.95416 | 0.91154 | -0.042622 |  | 0.93 | 1.05 | 0.034687 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | LABETTE2 | 0.95416 | 0.91154 | -0.042622 |  | 0.93 | 1.05 | 0.034687 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | LABETTE2 | 0.95416 | 0.91154 | -0.042622 |  | 0.93 | 1.05 | 0.031574 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | LABETTE2 | 0.95416 | 0.91154 | -0.042622 |  | 0.93 | 1.05 | 0.042889 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-376 | LABETTE2 | 0.95416 | 0.91154 | -0.042622 |  | 0.93 | 1.05 | 0.079908 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | LABETTE2 | 0.95122 | 0.91254 | -0.038679 |  | 0.93 | 1.05 | 0.040299 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LABETTE2 | 0.95122 | 0.91254 | -0.038679 |  | 0.93 | 1.05 | 0.048812 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LABETTE2 | 0.95122 | 0.91254 | -0.038679 |  | 0.93 | 1.05 | 0.076211 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LABETTE2 | 0.95122 | 0.91254 | -0.038679 |  | 0.93 | 1.05 | 0.069331 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LABETTE2 | 0.95122 | 0.91254 | -0.038679 |  | 0.93 | 1.05 | 0.035943 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LABETTE2 | 0.95122 | 0.91254 | -0.038679 |  | 0.93 | 1.05 | 0.034061 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LABETTE2 | 0.95122 | 0.91254 | -0.038679 |  | 0.93 | 1.05 | 0.064216 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LABETTE2 | 0.95122 | 0.91254 | -0.038679 |  | 0.93 | 1.05 | 0.045005 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LABETTE2 | 0.95122 | 0.91254 | -0.038679 |  | 0.93 | 1.05 | 0.13572 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | LABETTE2 | 0.95122 | 0.91254 | -0.038679 |  | 0.93 | 1.05 | 0.037472 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | LABETTE2 | 0.95122 | 0.91254 | -0.038679 |  | 0.93 | 1.05 | 0.037472 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LABETTE2 | 0.95122 | 0.91254 | -0.038679 |  | 0.93 | 1.05 | 0.06894 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LABETTE2 | 0.95122 | 0.91254 | -0.038679 |  | 0.93 | 1.05 | 0.034713 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LABETTE2 | 0.95122 | 0.91254 | -0.038679 |  | 0.93 | 1.05 | 0.035229 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LABETTE2 | 0.95122 | 0.91275 | -0.038468 |  | 0.93 | 1.05 | 0.094783 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | LABETTE2 | 0.95122 | 0.91275 | -0.038468 |  | 0.93 | 1.05 | 0.03645 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LABETTE2 | 0.95122 | 0.91275 | -0.038468 |  | 0.93 | 1.05 | 0.04755 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LABETTE2 | 0.95122 | 0.91275 | -0.038468 |  | 0.93 | 1.05 | 0.06097 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LABETTE2 | 0.95122 | 0.91275 | -0.038468 |  | 0.93 | 1.05 | 0.061051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | LABETTE2 | 0.95122 | 0.91275 | -0.038468 |  | 0.93 | 1.05 | 0.04456 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | LABETTE2 | 0.95122 | 0.91275 | -0.038468 |  | 0.93 | 1.05 | 0.048811 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LABETTE2 | 0.95122 | 0.91275 | -0.038468 |  | 0.93 | 1.05 | 0.13004 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LABETTE2 | 0.95122 | 0.91275 | -0.038468 |  | 0.93 | 1.05 | 0.049018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LABETTE2 | 0.95122 | 0.91275 | -0.038468 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LABETTE2 | 0.95122 | 0.91275 | -0.038468 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LABETTE2 | 0.95122 | 0.91275 | -0.038468 |  | 0.93 | 1.05 | 0.05974 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LABETTE2 | 0.95122 | 0.91275 | -0.038468 |  | 0.93 | 1.05 | 0.076949 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LABETTE2 | 0.95122 | 0.91275 | -0.038468 |  | 0.93 | 1.05 | 0.042157 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LABETTE2 | 0.95122 | 0.91275 | -0.038468 |  | 0.93 | 1.05 | 0.040957 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | LABETTE2 | 0.95122 | 0.91275 | -0.038468 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | LABETTE2 | 0.95122 | 0.91275 | -0.038468 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LABETTE2 | 0.95122 | 0.91275 | -0.038468 |  | 0.93 | 1.05 | 0.054637 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LABETTE2 | 0.95122 | 0.91275 | -0.038468 |  | 0.93 | 1.05 | 0.060597 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | LABETTE2 | 0.95122 | 0.91275 | -0.038468 |  | 0.93 | 1.05 | 0.044286 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LABETTE2 | 0.95122 | 0.91275 | -0.038468 |  | 0.93 | 1.05 | 0.059107 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LABETTE2 | 0.95122 | 0.91275 | -0.038468 |  | 0.93 | 1.05 | 0.052698 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LABETTE2 | 0.95122 | 0.91275 | -0.038468 |  | 0.93 | 1.05 | 0.067422 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LABETTE2 | 0.95122 | 0.91275 | -0.038468 |  | 0.93 | 1.05 | 0.053768 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | LABETTE2 | 0.95122 | 0.91275 | -0.038468 |  | 0.93 | 1.05 | 0.03909 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LABETTE2 | 0.9501 | 0.90872 | -0.041385 |  | 0.93 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | LABETTE2 | 0.9501 | 0.90872 | -0.041385 |  | 0.93 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LABETTE2 | 0.9501 | 0.90872 | -0.041385 |  | 0.93 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LABETTE2 | 0.9501 | 0.90872 | -0.041385 |  | 0.93 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LABETTE2 | 0.9501 | 0.90872 | -0.041385 |  | 0.93 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LABETTE2 | 0.9501 | 0.90872 | -0.041385 |  | 0.93 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LABETTE2 | 0.9501 | 0.90872 | -0.041385 |  | 0.93 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | LABETTE2 | 0.9501 | 0.90872 | -0.041385 |  | 0.93 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LABETTE2 | 0.9501 | 0.90872 | -0.041385 |  | 0.93 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LABETTE2 | 0.9501 | 0.90872 | -0.041385 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LABETTE2 | 0.9501 | 0.90872 | -0.041385 |  | 0.93 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LABETTE2 | 0.9501 | 0.90872 | -0.041385 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LABETTE2 | 0.9501 | 0.90872 | -0.041385 |  | 0.93 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LABETTE2 | 0.9501 | 0.90872 | -0.041385 |  | 0.93 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LABETTE2 | 0.9501 | 0.90872 | -0.041385 |  | 0.93 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LABETTE2 | 0.9501 | 0.90872 | -0.041385 |  | 0.93 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LABETTE2 | 0.9501 | 0.90872 | -0.041385 |  | 0.93 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LABETTE2 | 0.9501 | 0.90872 | -0.041385 |  | 0.93 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LABETTE2 | 0.9501 | 0.90872 | -0.041385 |  | 0.93 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LABETTE2 | 0.9501 | 0.90872 | -0.041385 |  | 0.93 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LABETTE2 | 0.9501 | 0.90872 | -0.041385 |  | 0.93 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LABETTE2 | 0.9501 | 0.90872 | -0.041385 |  | 0.93 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LABETTE2 | 0.95044 | 0.89412 | -0.056317 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | LABETTE2 | 0.95044 | 0.89412 | -0.056317 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LABETTE2 | 0.95044 | 0.89412 | -0.056317 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LABETTE2 | 0.95044 | 0.89412 | -0.056317 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LABETTE2 | 0.95044 | 0.89412 | -0.056317 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LABETTE2 | 0.95044 | 0.89412 | -0.056317 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LABETTE2 | 0.95044 | 0.89412 | -0.056317 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | LABETTE2 | 0.95044 | 0.89412 | -0.056317 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | LABETTE2 | 0.95044 | 0.89412 | -0.056317 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LABETTE2 | 0.95044 | 0.89412 | -0.056317 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LABETTE2 | 0.95044 | 0.89412 | -0.056317 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LABETTE2 | 0.95044 | 0.89412 | -0.056317 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LABETTE2 | 0.95044 | 0.89412 | -0.056317 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LABETTE2 | 0.95044 | 0.89412 | -0.056317 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LABETTE2 | 0.95044 | 0.89412 | -0.056317 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LABETTE2 | 0.95044 | 0.89412 | -0.056317 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LABETTE2 | 0.95044 | 0.89412 | -0.056317 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LABETTE2 | 0.95044 | 0.89412 | -0.056317 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | LABETTE2 | 0.95044 | 0.89412 | -0.056317 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | LABETTE2 | 0.95044 | 0.89412 | -0.056317 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LABETTE2 | 0.95044 | 0.89412 | -0.056317 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LABETTE2 | 0.95044 | 0.89412 | -0.056317 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | LABETTE2 | 0.95044 | 0.89412 | -0.056317 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LABETTE2 | 0.95044 | 0.89412 | -0.056317 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LABETTE2 | 0.95044 | 0.89412 | -0.056317 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LABETTE2 | 0.95044 | 0.89412 | -0.056317 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LABETTE2 | 0.95044 | 0.89412 | -0.056317 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | LABETTE2 | 0.95044 | 0.89412 | -0.056317 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | LABETTS2 | 0.9561 | 0.91357 | -0.042527 |  | 0.93 | 1.05 | 0.077629 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | LABETTS2 | 0.9561 | 0.91357 | -0.042527 |  | 0.93 | 1.05 | 0.06446 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | LABETTS2 | 0.9561 | 0.91357 | -0.042527 |  | 0.93 | 1.05 | 0.066434 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | LABETTS2 | 0.9561 | 0.91357 | -0.042527 |  | 0.93 | 1.05 | 0.073293 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | LABETTS2 | 0.9561 | 0.91357 | -0.042527 |  | 0.93 | 1.05 | 0.053415 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-122 | LABETTS2 | 0.9561 | 0.91357 | -0.042527 |  | 0.93 | 1.05 | 0.08103 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-177 | LABETTS2 | 0.9561 | 0.91357 | -0.042527 |  | 0.93 | 1.05 | 0.08268 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-178 | LABETTS2 | 0.9561 | 0.91357 | -0.042527 |  | 0.93 | 1.05 | 0.077122 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | LABETTS2 | 0.9561 | 0.91357 | -0.042527 |  | 0.93 | 1.05 | 0.032185 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | LABETTS2 | 0.9561 | 0.91357 | -0.042527 |  | 0.93 | 1.05 | 0.073922 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-232 | LABETTS2 | 0.9561 | 0.91357 | -0.042527 |  | 0.93 | 1.05 | 0.076776 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | LABETTS2 | 0.9561 | 0.91357 | -0.042527 |  | 0.93 | 1.05 | 0.06446 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LABETTS2 | 0.9561 | 0.91357 | -0.042527 |  | 0.93 | 1.05 | 0.038841 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | LABETTS2 | 0.9561 | 0.91357 | -0.042527 |  | 0.93 | 1.05 | 0.034687 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | LABETTS2 | 0.9561 | 0.91357 | -0.042527 |  | 0.93 | 1.05 | 0.034687 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | LABETTS2 | 0.9561 | 0.91357 | -0.042527 |  | 0.93 | 1.05 | 0.031574 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | LABETTS2 | 0.9561 | 0.91357 | -0.042527 |  | 0.93 | 1.05 | 0.042889 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-376 | LABETTS2 | 0.9561 | 0.91357 | -0.042527 |  | 0.93 | 1.05 | 0.079908 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | LABETTS2 | 0.95316 | 0.91457 | -0.038593 |  | 0.93 | 1.05 | 0.040299 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LABETTS2 | 0.95316 | 0.91457 | -0.038593 |  | 0.93 | 1.05 | 0.048812 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LABETTS2 | 0.95316 | 0.91457 | -0.038593 |  | 0.93 | 1.05 | 0.076211 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LABETTS2 | 0.95316 | 0.91457 | -0.038593 |  | 0.93 | 1.05 | 0.069331 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LABETTS2 | 0.95316 | 0.91457 | -0.038593 |  | 0.93 | 1.05 | 0.035943 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LABETTS2 | 0.95316 | 0.91457 | -0.038593 |  | 0.93 | 1.05 | 0.034061 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LABETTS2 | 0.95316 | 0.91457 | -0.038593 |  | 0.93 | 1.05 | 0.064216 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LABETTS2 | 0.95316 | 0.91457 | -0.038593 |  | 0.93 | 1.05 | 0.045005 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LABETTS2 | 0.95316 | 0.91457 | -0.038593 |  | 0.93 | 1.05 | 0.13572 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | LABETTS2 | 0.95316 | 0.91457 | -0.038593 |  | 0.93 | 1.05 | 0.037472 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | LABETTS2 | 0.95316 | 0.91457 | -0.038593 |  | 0.93 | 1.05 | 0.037472 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LABETTS2 | 0.95316 | 0.91457 | -0.038593 |  | 0.93 | 1.05 | 0.06894 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LABETTS2 | 0.95316 | 0.91457 | -0.038593 |  | 0.93 | 1.05 | 0.034713 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LABETTS2 | 0.95316 | 0.91457 | -0.038593 |  | 0.93 | 1.05 | 0.035229 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LABETTS2 | 0.95316 | 0.91478 | -0.038383 |  | 0.93 | 1.05 | 0.094783 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | LABETTS2 | 0.95316 | 0.91478 | -0.038383 |  | 0.93 | 1.05 | 0.03645 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LABETTS2 | 0.95316 | 0.91478 | -0.038383 |  | 0.93 | 1.05 | 0.04755 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LABETTS2 | 0.95316 | 0.91478 | -0.038383 |  | 0.93 | 1.05 | 0.06097 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LABETTS2 | 0.95316 | 0.91478 | -0.038383 |  | 0.93 | 1.05 | 0.061051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | LABETTS2 | 0.95316 | 0.91478 | -0.038383 |  | 0.93 | 1.05 | 0.04456 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | LABETTS2 | 0.95316 | 0.91478 | -0.038383 |  | 0.93 | 1.05 | 0.048811 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LABETTS2 | 0.95316 | 0.91478 | -0.038383 |  | 0.93 | 1.05 | 0.13004 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LABETTS2 | 0.95316 | 0.91478 | -0.038383 |  | 0.93 | 1.05 | 0.049018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LABETTS2 | 0.95316 | 0.91478 | -0.038383 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LABETTS2 | 0.95316 | 0.91478 | -0.038383 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LABETTS2 | 0.95316 | 0.91478 | -0.038383 |  | 0.93 | 1.05 | 0.05974 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LABETTS2 | 0.95316 | 0.91478 | -0.038383 |  | 0.93 | 1.05 | 0.076949 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LABETTS2 | 0.95316 | 0.91478 | -0.038383 |  | 0.93 | 1.05 | 0.042157 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LABETTS2 | 0.95316 | 0.91478 | -0.038383 |  | 0.93 | 1.05 | 0.040957 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | LABETTS2 | 0.95316 | 0.91478 | -0.038383 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | LABETTS2 | 0.95316 | 0.91478 | -0.038383 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LABETTS2 | 0.95316 | 0.91478 | -0.038383 |  | 0.93 | 1.05 | 0.054637 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LABETTS2 | 0.95316 | 0.91478 | -0.038383 |  | 0.93 | 1.05 | 0.060597 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | LABETTS2 | 0.95316 | 0.91478 | -0.038383 |  | 0.93 | 1.05 | 0.044286 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LABETTS2 | 0.95316 | 0.91478 | -0.038383 |  | 0.93 | 1.05 | 0.059107 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LABETTS2 | 0.95316 | 0.91478 | -0.038383 |  | 0.93 | 1.05 | 0.052698 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LABETTS2 | 0.95316 | 0.91478 | -0.038383 |  | 0.93 | 1.05 | 0.067422 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LABETTS2 | 0.95316 | 0.91478 | -0.038383 |  | 0.93 | 1.05 | 0.053768 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | LABETTS2 | 0.95316 | 0.91478 | -0.038383 |  | 0.93 | 1.05 | 0.03909 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LABETTS2 | 0.95205 | 0.91076 | -0.041292 |  | 0.93 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | LABETTS2 | 0.95205 | 0.91076 | -0.041292 |  | 0.93 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LABETTS2 | 0.95205 | 0.91076 | -0.041292 |  | 0.93 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LABETTS2 | 0.95205 | 0.91076 | -0.041292 |  | 0.93 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LABETTS2 | 0.95205 | 0.91076 | -0.041292 |  | 0.93 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LABETTS2 | 0.95205 | 0.91076 | -0.041292 |  | 0.93 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LABETTS2 | 0.95205 | 0.91076 | -0.041292 |  | 0.93 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | LABETTS2 | 0.95205 | 0.91076 | -0.041292 |  | 0.93 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LABETTS2 | 0.95205 | 0.91076 | -0.041292 |  | 0.93 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LABETTS2 | 0.95205 | 0.91076 | -0.041292 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LABETTS2 | 0.95205 | 0.91076 | -0.041292 |  | 0.93 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LABETTS2 | 0.95205 | 0.91076 | -0.041292 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LABETTS2 | 0.95205 | 0.91076 | -0.041292 |  | 0.93 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LABETTS2 | 0.95205 | 0.91076 | -0.041292 |  | 0.93 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LABETTS2 | 0.95205 | 0.91076 | -0.041292 |  | 0.93 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LABETTS2 | 0.95205 | 0.91076 | -0.041292 |  | 0.93 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LABETTS2 | 0.95205 | 0.91076 | -0.041292 |  | 0.93 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LABETTS2 | 0.95205 | 0.91076 | -0.041292 |  | 0.93 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LABETTS2 | 0.95205 | 0.91076 | -0.041292 |  | 0.93 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LABETTS2 | 0.95205 | 0.91076 | -0.041292 |  | 0.93 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LABETTS2 | 0.95205 | 0.91076 | -0.041292 |  | 0.93 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LABETTS2 | 0.95205 | 0.91076 | -0.041292 |  | 0.93 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LABETTS2 | 0.95238 | 0.89619 | -0.056189 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | LABETTS2 | 0.95238 | 0.89619 | -0.056189 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LABETTS2 | 0.95238 | 0.89619 | -0.056189 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LABETTS2 | 0.95238 | 0.89619 | -0.056189 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LABETTS2 | 0.95238 | 0.89619 | -0.056189 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LABETTS2 | 0.95238 | 0.89619 | -0.056189 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LABETTS2 | 0.95238 | 0.89619 | -0.056189 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | LABETTS2 | 0.95238 | 0.89619 | -0.056189 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | LABETTS2 | 0.95238 | 0.89619 | -0.056189 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LABETTS2 | 0.95238 | 0.89619 | -0.056189 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LABETTS2 | 0.95238 | 0.89619 | -0.056189 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LABETTS2 | 0.95238 | 0.89619 | -0.056189 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LABETTS2 | 0.95238 | 0.89619 | -0.056189 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LABETTS2 | 0.95238 | 0.89619 | -0.056189 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LABETTS2 | 0.95238 | 0.89619 | -0.056189 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LABETTS2 | 0.95238 | 0.89619 | -0.056189 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LABETTS2 | 0.95238 | 0.89619 | -0.056189 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LABETTS2 | 0.95238 | 0.89619 | -0.056189 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | LABETTS2 | 0.95238 | 0.89619 | -0.056189 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | LABETTS2 | 0.95238 | 0.89619 | -0.056189 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LABETTS2 | 0.95238 | 0.89619 | -0.056189 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LABETTS2 | 0.95238 | 0.89619 | -0.056189 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | LABETTS2 | 0.95238 | 0.89619 | -0.056189 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LABETTS2 | 0.95238 | 0.89619 | -0.056189 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LABETTS2 | 0.95238 | 0.89619 | -0.056189 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LABETTS2 | 0.95238 | 0.89619 | -0.056189 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LABETTS2 | 0.95238 | 0.89619 | -0.056189 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | LABETTS2 | 0.95238 | 0.89619 | -0.056189 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LACKMAN5 | 0.97053 | 0.92556 | -0.044971 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LACKMAN5 | 0.97053 | 0.92556 | -0.044971 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LACKMAN5 | 0.97053 | 0.92556 | -0.044971 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LACKMAN5 | 0.97053 | 0.92556 | -0.044971 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LACKMAN5 | 0.97053 | 0.92556 | -0.044971 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LACKMAN5 | 0.97053 | 0.92556 | -0.044971 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LACKMAN5 | 0.97053 | 0.92556 | -0.044971 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LACKMAN5 | 0.97053 | 0.92556 | -0.044971 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LACKMAN5 | 0.97053 | 0.92556 | -0.044971 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LACKMAN5 | 0.97053 | 0.92556 | -0.044971 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LACKMAN5 | 0.97053 | 0.92556 | -0.044971 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LACKMAN5 | 0.97053 | 0.92556 | -0.044971 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LACKMAN5 | 0.97053 | 0.92556 | -0.044971 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LACKMAN5 | 0.97053 | 0.92556 | -0.044971 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LACKMAN5 | 0.97053 | 0.92556 | -0.044971 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LACKMAN5 | 0.97053 | 0.92556 | -0.044971 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LACKMAN5 | 0.97053 | 0.92556 | -0.044971 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LACKMAN5 | 0.97053 | 0.92556 | -0.044971 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LACKMAN5 | 0.97053 | 0.92556 | -0.044971 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LACKMAN5 | 0.97053 | 0.92556 | -0.044971 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LACKMAN5 | 0.98352 | 0.90168 | -0.081837 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | LACKMAN5 | 0.98352 | 0.90168 | -0.081837 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LACKMAN5 | 0.98352 | 0.90168 | -0.081837 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LACKMAN5 | 0.98352 | 0.90168 | -0.081837 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LACKMAN5 | 0.98352 | 0.90168 | -0.081837 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LACKMAN5 | 0.98352 | 0.90168 | -0.081837 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LACKMAN5 | 0.98352 | 0.90168 | -0.081837 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | LACKMAN5 | 0.98352 | 0.90168 | -0.081837 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | LACKMAN5 | 0.98352 | 0.90168 | -0.081837 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LACKMAN5 | 0.98352 | 0.90168 | -0.081837 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LACKMAN5 | 0.98352 | 0.90168 | -0.081837 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LACKMAN5 | 0.98352 | 0.90168 | -0.081837 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LACKMAN5 | 0.98352 | 0.90168 | -0.081837 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LACKMAN5 | 0.98352 | 0.90168 | -0.081837 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LACKMAN5 | 0.98352 | 0.90168 | -0.081837 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LACKMAN5 | 0.98352 | 0.90168 | -0.081837 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LACKMAN5 | 0.98352 | 0.90168 | -0.081837 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LACKMAN5 | 0.98352 | 0.90168 | -0.081837 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | LACKMAN5 | 0.98352 | 0.90168 | -0.081837 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | LACKMAN5 | 0.98352 | 0.90168 | -0.081837 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LACKMAN5 | 0.98352 | 0.90168 | -0.081837 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LACKMAN5 | 0.98352 | 0.90168 | -0.081837 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | LACKMAN5 | 0.98352 | 0.90168 | -0.081837 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LACKMAN5 | 0.98352 | 0.90168 | -0.081837 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LACKMAN5 | 0.98352 | 0.90168 | -0.081837 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LACKMAN5 | 0.98352 | 0.90168 | -0.081837 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LACKMAN5 | 0.98352 | 0.90168 | -0.081837 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | LACKMAN5 | 0.98352 | 0.90168 | -0.081837 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | LACYGNE11_7 | 0.9891 | 0.93437 | -0.054726 |  | 0.95 | 1.05 | 0.030773 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | LACYGNE11_7 | 0.9891 | 0.93437 | -0.054726 |  | 0.95 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LACYGNE11_7 | 0.9891 | 0.93437 | -0.054726 |  | 0.95 | 1.05 | 0.046711 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | LACYGNE11_7 | 0.9891 | 0.93437 | -0.054726 |  | 0.95 | 1.05 | 0.032369 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | LACYGNE11_7 | 0.9891 | 0.93437 | -0.054726 |  | 0.95 | 1.05 | 0.030466 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | LACYGNE11_7 | 0.9891 | 0.93437 | -0.054726 |  | 0.95 | 1.05 | 0.04987 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LACYGNE11_7 | 0.9891 | 0.93437 | -0.054726 |  | 0.95 | 1.05 | 0.099365 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LACYGNE11_7 | 0.9891 | 0.93437 | -0.054726 |  | 0.95 | 1.05 | 0.071132 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LACYGNE11_7 | 0.9891 | 0.93437 | -0.054726 |  | 0.95 | 1.05 | 0.043927 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LACYGNE11_7 | 0.9891 | 0.93437 | -0.054726 |  | 0.95 | 1.05 | 0.030565 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LACYGNE11_7 | 0.9891 | 0.93437 | -0.054726 |  | 0.95 | 1.05 | 0.072847 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | LACYGNE11_7 | 0.9891 | 0.93437 | -0.054726 |  | 0.95 | 1.05 | 0.041148 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | LACYGNE11_7 | 0.9891 | 0.93437 | -0.054726 |  | 0.95 | 1.05 | 0.042015 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | LACYGNE11_7 | 0.9891 | 0.93437 | -0.054726 |  | 0.95 | 1.05 | 0.030318 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LACYGNE11_7 | 0.9891 | 0.93437 | -0.054726 |  | 0.95 | 1.05 | 0.054104 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LACYGNE11_7 | 0.9891 | 0.93437 | -0.054726 |  | 0.95 | 1.05 | 0.047089 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LACYGNE11_7 | 0.9891 | 0.93437 | -0.054726 |  | 0.95 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LACYGNE11_7 | 0.9891 | 0.93437 | -0.054726 |  | 0.95 | 1.05 | 0.13688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | LACYGNE11_7 | 0.9891 | 0.93437 | -0.054726 |  | 0.95 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LACYGNE11_7 | 0.9891 | 0.93437 | -0.054726 |  | 0.95 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LACYGNE11_7 | 0.9891 | 0.93437 | -0.054726 |  | 0.95 | 1.05 | 0.039752 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LACYGNE11_7 | 0.9891 | 0.93437 | -0.054726 |  | 0.95 | 1.05 | 0.041972 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LACYGNE11_7 | 0.9891 | 0.93437 | -0.054726 |  | 0.95 | 1.05 | 0.054397 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LACYGNE11_7 | 0.9891 | 0.93437 | -0.054726 |  | 0.95 | 1.05 | 0.073688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | LACYGNE11_7 | 0.9891 | 0.93437 | -0.054726 |  | 0.95 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | LACYGNE11_7 | 0.9891 | 0.93437 | -0.054726 |  | 0.95 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LACYGNE11_7 | 0.9891 | 0.93437 | -0.054726 |  | 0.95 | 1.05 | 0.072188 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LACYGNE11_7 | 0.9891 | 0.93437 | -0.054726 |  | 0.95 | 1.05 | 0.042186 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | LACYGNE11_7 | 0.9891 | 0.93437 | -0.054726 |  | 0.95 | 1.05 | 0.041423 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LACYGNE11_7 | 0.9891 | 0.93437 | -0.054726 |  | 0.95 | 1.05 | 0.050171 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LACYGNE11_7 | 0.9891 | 0.93437 | -0.054726 |  | 0.95 | 1.05 | 0.04386 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LACYGNE11_7 | 0.9891 | 0.93437 | -0.054726 |  | 0.95 | 1.05 | 0.050218 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LACYGNE11_7 | 0.9891 | 0.93437 | -0.054726 |  | 0.95 | 1.05 | 0.040041 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | LACYGNE11_7 | 0.9891 | 0.93437 | -0.054726 |  | 0.95 | 1.05 | 0.038784 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LACYGNE11_7 | 0.99764 | 0.93195 | -0.065691 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LACYGNE11_7 | 0.99764 | 0.93195 | -0.065691 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LACYGNE11_7 | 0.99764 | 0.93195 | -0.065691 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LACYGNE11_7 | 0.99764 | 0.93195 | -0.065691 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LACYGNE11_7 | 0.99764 | 0.93195 | -0.065691 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LACYGNE11_7 | 0.99764 | 0.93195 | -0.065691 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LACYGNE11_7 | 0.99764 | 0.93195 | -0.065691 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LACYGNE11_7 | 0.99764 | 0.93195 | -0.065691 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LACYGNE11_7 | 0.99764 | 0.93195 | -0.065691 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LACYGNE11_7 | 0.99764 | 0.93195 | -0.065691 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LACYGNE11_7 | 0.99764 | 0.93195 | -0.065691 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LACYGNE11_7 | 0.99764 | 0.93195 | -0.065691 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LACYGNE11_7 | 0.99764 | 0.93195 | -0.065691 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LACYGNE11_7 | 0.99764 | 0.93195 | -0.065691 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LACYGNE11_7 | 0.99764 | 0.93195 | -0.065691 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LACYGNE11_7 | 0.99764 | 0.93195 | -0.065691 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LACYGNE11_7 | 0.99764 | 0.93195 | -0.065691 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LACYGNE11_7 | 0.99764 | 0.93195 | -0.065691 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LACYGNE11_7 | 0.99764 | 0.93195 | -0.065691 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LACYGNE11_7 | 0.99764 | 0.93195 | -0.065691 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LACYGNE11_7 | 0.98884 | 0.87974 | -0.1091 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | LACYGNE11_7 | 0.98884 | 0.87974 | -0.1091 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LACYGNE11_7 | 0.98884 | 0.87974 | -0.1091 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LACYGNE11_7 | 0.98884 | 0.87974 | -0.1091 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LACYGNE11_7 | 0.98884 | 0.87974 | -0.1091 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LACYGNE11_7 | 0.98884 | 0.87974 | -0.1091 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LACYGNE11_7 | 0.98884 | 0.87974 | -0.1091 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | LACYGNE11_7 | 0.98884 | 0.87974 | -0.1091 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | LACYGNE11_7 | 0.98884 | 0.87974 | -0.1091 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LACYGNE11_7 | 0.98884 | 0.87974 | -0.1091 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LACYGNE11_7 | 0.98884 | 0.87974 | -0.1091 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LACYGNE11_7 | 0.98884 | 0.87974 | -0.1091 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LACYGNE11_7 | 0.98884 | 0.87974 | -0.1091 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LACYGNE11_7 | 0.98884 | 0.87974 | -0.1091 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LACYGNE11_7 | 0.98884 | 0.87974 | -0.1091 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LACYGNE11_7 | 0.98884 | 0.87974 | -0.1091 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LACYGNE11_7 | 0.98884 | 0.87974 | -0.1091 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LACYGNE11_7 | 0.98884 | 0.87974 | -0.1091 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | LACYGNE11_7 | 0.98884 | 0.87974 | -0.1091 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | LACYGNE11_7 | 0.98884 | 0.87974 | -0.1091 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LACYGNE11_7 | 0.98884 | 0.87974 | -0.1091 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LACYGNE11_7 | 0.98884 | 0.87974 | -0.1091 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | LACYGNE11_7 | 0.98884 | 0.87974 | -0.1091 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LACYGNE11_7 | 0.98884 | 0.87974 | -0.1091 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LACYGNE11_7 | 0.98884 | 0.87974 | -0.1091 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LACYGNE11_7 | 0.98884 | 0.87974 | -0.1091 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LACYGNE11_7 | 0.98884 | 0.87974 | -0.1091 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | LACYGNE11_7 | 0.98884 | 0.87974 | -0.1091 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | LACYGNE2 | 0.97822 | 0.92271 | -0.055504 |  | 0.93 | 1.05 | 0.030773 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | LACYGNE2 | 0.97822 | 0.92271 | -0.055504 |  | 0.93 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LACYGNE2 | 0.97822 | 0.92271 | -0.055504 |  | 0.93 | 1.05 | 0.046711 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | LACYGNE2 | 0.97822 | 0.92271 | -0.055504 |  | 0.93 | 1.05 | 0.032369 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | LACYGNE2 | 0.97822 | 0.92271 | -0.055504 |  | 0.93 | 1.05 | 0.030466 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | LACYGNE2 | 0.97822 | 0.92271 | -0.055504 |  | 0.93 | 1.05 | 0.04987 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LACYGNE2 | 0.97822 | 0.92271 | -0.055504 |  | 0.93 | 1.05 | 0.099365 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LACYGNE2 | 0.97822 | 0.92271 | -0.055504 |  | 0.93 | 1.05 | 0.071132 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LACYGNE2 | 0.97822 | 0.92271 | -0.055504 |  | 0.93 | 1.05 | 0.043927 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LACYGNE2 | 0.97822 | 0.92271 | -0.055504 |  | 0.93 | 1.05 | 0.030565 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LACYGNE2 | 0.97822 | 0.92271 | -0.055504 |  | 0.93 | 1.05 | 0.072847 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | LACYGNE2 | 0.97822 | 0.92271 | -0.055504 |  | 0.93 | 1.05 | 0.041148 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | LACYGNE2 | 0.97822 | 0.92271 | -0.055504 |  | 0.93 | 1.05 | 0.042015 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | LACYGNE2 | 0.97822 | 0.92271 | -0.055504 |  | 0.93 | 1.05 | 0.030318 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LACYGNE2 | 0.97822 | 0.92271 | -0.055504 |  | 0.93 | 1.05 | 0.054104 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LACYGNE2 | 0.97822 | 0.92271 | -0.055504 |  | 0.93 | 1.05 | 0.047089 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LACYGNE2 | 0.97822 | 0.92271 | -0.055504 |  | 0.93 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LACYGNE2 | 0.97822 | 0.92271 | -0.055504 |  | 0.93 | 1.05 | 0.13688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | LACYGNE2 | 0.97822 | 0.92271 | -0.055504 |  | 0.93 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LACYGNE2 | 0.97822 | 0.92271 | -0.055504 |  | 0.93 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LACYGNE2 | 0.97822 | 0.92271 | -0.055504 |  | 0.93 | 1.05 | 0.039752 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LACYGNE2 | 0.97822 | 0.92271 | -0.055504 |  | 0.93 | 1.05 | 0.041972 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LACYGNE2 | 0.97822 | 0.92271 | -0.055504 |  | 0.93 | 1.05 | 0.054397 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LACYGNE2 | 0.97822 | 0.92271 | -0.055504 |  | 0.93 | 1.05 | 0.073688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | LACYGNE2 | 0.97822 | 0.92271 | -0.055504 |  | 0.93 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | LACYGNE2 | 0.97822 | 0.92271 | -0.055504 |  | 0.93 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LACYGNE2 | 0.97822 | 0.92271 | -0.055504 |  | 0.93 | 1.05 | 0.072188 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LACYGNE2 | 0.97822 | 0.92271 | -0.055504 |  | 0.93 | 1.05 | 0.042186 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | LACYGNE2 | 0.97822 | 0.92271 | -0.055504 |  | 0.93 | 1.05 | 0.041423 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LACYGNE2 | 0.97822 | 0.92271 | -0.055504 |  | 0.93 | 1.05 | 0.050171 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LACYGNE2 | 0.97822 | 0.92271 | -0.055504 |  | 0.93 | 1.05 | 0.04386 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LACYGNE2 | 0.97822 | 0.92271 | -0.055504 |  | 0.93 | 1.05 | 0.050218 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LACYGNE2 | 0.97822 | 0.92271 | -0.055504 |  | 0.93 | 1.05 | 0.040041 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | LACYGNE2 | 0.97822 | 0.92271 | -0.055504 |  | 0.93 | 1.05 | 0.038784 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LACYGNE2 | 0.98687 | 0.92025 | -0.066618 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LACYGNE2 | 0.98687 | 0.92025 | -0.066618 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LACYGNE2 | 0.98687 | 0.92025 | -0.066618 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LACYGNE2 | 0.98687 | 0.92025 | -0.066618 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LACYGNE2 | 0.98687 | 0.92025 | -0.066618 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LACYGNE2 | 0.98687 | 0.92025 | -0.066618 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LACYGNE2 | 0.98687 | 0.92025 | -0.066618 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LACYGNE2 | 0.98687 | 0.92025 | -0.066618 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LACYGNE2 | 0.98687 | 0.92025 | -0.066618 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LACYGNE2 | 0.98687 | 0.92025 | -0.066618 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LACYGNE2 | 0.98687 | 0.92025 | -0.066618 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LACYGNE2 | 0.98687 | 0.92025 | -0.066618 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LACYGNE2 | 0.98687 | 0.92025 | -0.066618 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LACYGNE2 | 0.98687 | 0.92025 | -0.066618 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LACYGNE2 | 0.98687 | 0.92025 | -0.066618 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LACYGNE2 | 0.98687 | 0.92025 | -0.066618 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LACYGNE2 | 0.98687 | 0.92025 | -0.066618 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LACYGNE2 | 0.98687 | 0.92025 | -0.066618 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LACYGNE2 | 0.98687 | 0.92025 | -0.066618 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LACYGNE2 | 0.98687 | 0.92025 | -0.066618 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LACYGNE2 | 0.97795 | 0.86718 | -0.11078 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | LACYGNE2 | 0.97795 | 0.86718 | -0.11078 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LACYGNE2 | 0.97795 | 0.86718 | -0.11078 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LACYGNE2 | 0.97795 | 0.86718 | -0.11078 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LACYGNE2 | 0.97795 | 0.86718 | -0.11078 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LACYGNE2 | 0.97795 | 0.86718 | -0.11078 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LACYGNE2 | 0.97795 | 0.86718 | -0.11078 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | LACYGNE2 | 0.97795 | 0.86718 | -0.11078 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | LACYGNE2 | 0.97795 | 0.86718 | -0.11078 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LACYGNE2 | 0.97795 | 0.86718 | -0.11078 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LACYGNE2 | 0.97795 | 0.86718 | -0.11078 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LACYGNE2 | 0.97795 | 0.86718 | -0.11078 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LACYGNE2 | 0.97795 | 0.86718 | -0.11078 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LACYGNE2 | 0.97795 | 0.86718 | -0.11078 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LACYGNE2 | 0.97795 | 0.86718 | -0.11078 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LACYGNE2 | 0.97795 | 0.86718 | -0.11078 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LACYGNE2 | 0.97795 | 0.86718 | -0.11078 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LACYGNE2 | 0.97795 | 0.86718 | -0.11078 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | LACYGNE2 | 0.97795 | 0.86718 | -0.11078 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | LACYGNE2 | 0.97795 | 0.86718 | -0.11078 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LACYGNE2 | 0.97795 | 0.86718 | -0.11078 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LACYGNE2 | 0.97795 | 0.86718 | -0.11078 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | LACYGNE2 | 0.97795 | 0.86718 | -0.11078 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LACYGNE2 | 0.97795 | 0.86718 | -0.11078 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LACYGNE2 | 0.97795 | 0.86718 | -0.11078 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LACYGNE2 | 0.97795 | 0.86718 | -0.11078 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LACYGNE2 | 0.97795 | 0.86718 | -0.11078 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | LACYGNE2 | 0.97795 | 0.86718 | -0.11078 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | LACYGNE22_7 | 0.98911 | 0.93438 | -0.054725 |  | 0.95 | 1.05 | 0.030773 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | LACYGNE22_7 | 0.98911 | 0.93438 | -0.054725 |  | 0.95 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LACYGNE22_7 | 0.98911 | 0.93438 | -0.054725 |  | 0.95 | 1.05 | 0.046711 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | LACYGNE22_7 | 0.98911 | 0.93438 | -0.054725 |  | 0.95 | 1.05 | 0.032369 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | LACYGNE22_7 | 0.98911 | 0.93438 | -0.054725 |  | 0.95 | 1.05 | 0.030466 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | LACYGNE22_7 | 0.98911 | 0.93438 | -0.054725 |  | 0.95 | 1.05 | 0.04987 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LACYGNE22_7 | 0.98911 | 0.93438 | -0.054725 |  | 0.95 | 1.05 | 0.099365 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LACYGNE22_7 | 0.98911 | 0.93438 | -0.054725 |  | 0.95 | 1.05 | 0.071132 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LACYGNE22_7 | 0.98911 | 0.93438 | -0.054725 |  | 0.95 | 1.05 | 0.043927 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LACYGNE22_7 | 0.98911 | 0.93438 | -0.054725 |  | 0.95 | 1.05 | 0.030565 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LACYGNE22_7 | 0.98911 | 0.93438 | -0.054725 |  | 0.95 | 1.05 | 0.072847 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | LACYGNE22_7 | 0.98911 | 0.93438 | -0.054725 |  | 0.95 | 1.05 | 0.041148 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | LACYGNE22_7 | 0.98911 | 0.93438 | -0.054725 |  | 0.95 | 1.05 | 0.042015 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | LACYGNE22_7 | 0.98911 | 0.93438 | -0.054725 |  | 0.95 | 1.05 | 0.030318 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LACYGNE22_7 | 0.98911 | 0.93438 | -0.054725 |  | 0.95 | 1.05 | 0.054104 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LACYGNE22_7 | 0.98911 | 0.93438 | -0.054725 |  | 0.95 | 1.05 | 0.047089 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LACYGNE22_7 | 0.98911 | 0.93438 | -0.054725 |  | 0.95 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LACYGNE22_7 | 0.98911 | 0.93438 | -0.054725 |  | 0.95 | 1.05 | 0.13688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | LACYGNE22_7 | 0.98911 | 0.93438 | -0.054725 |  | 0.95 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LACYGNE22_7 | 0.98911 | 0.93438 | -0.054725 |  | 0.95 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LACYGNE22_7 | 0.98911 | 0.93438 | -0.054725 |  | 0.95 | 1.05 | 0.039752 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LACYGNE22_7 | 0.98911 | 0.93438 | -0.054725 |  | 0.95 | 1.05 | 0.041972 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LACYGNE22_7 | 0.98911 | 0.93438 | -0.054725 |  | 0.95 | 1.05 | 0.054397 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LACYGNE22_7 | 0.98911 | 0.93438 | -0.054725 |  | 0.95 | 1.05 | 0.073688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | LACYGNE22_7 | 0.98911 | 0.93438 | -0.054725 |  | 0.95 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | LACYGNE22_7 | 0.98911 | 0.93438 | -0.054725 |  | 0.95 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LACYGNE22_7 | 0.98911 | 0.93438 | -0.054725 |  | 0.95 | 1.05 | 0.072188 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LACYGNE22_7 | 0.98911 | 0.93438 | -0.054725 |  | 0.95 | 1.05 | 0.042186 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | LACYGNE22_7 | 0.98911 | 0.93438 | -0.054725 |  | 0.95 | 1.05 | 0.041423 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LACYGNE22_7 | 0.98911 | 0.93438 | -0.054725 |  | 0.95 | 1.05 | 0.050171 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LACYGNE22_7 | 0.98911 | 0.93438 | -0.054725 |  | 0.95 | 1.05 | 0.04386 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LACYGNE22_7 | 0.98911 | 0.93438 | -0.054725 |  | 0.95 | 1.05 | 0.050218 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LACYGNE22_7 | 0.98911 | 0.93438 | -0.054725 |  | 0.95 | 1.05 | 0.040041 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | LACYGNE22_7 | 0.98911 | 0.93438 | -0.054725 |  | 0.95 | 1.05 | 0.038784 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LACYGNE22_7 | 0.99765 | 0.93196 | -0.06569 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LACYGNE22_7 | 0.99765 | 0.93196 | -0.06569 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LACYGNE22_7 | 0.99765 | 0.93196 | -0.06569 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LACYGNE22_7 | 0.99765 | 0.93196 | -0.06569 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LACYGNE22_7 | 0.99765 | 0.93196 | -0.06569 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LACYGNE22_7 | 0.99765 | 0.93196 | -0.06569 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LACYGNE22_7 | 0.99765 | 0.93196 | -0.06569 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LACYGNE22_7 | 0.99765 | 0.93196 | -0.06569 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LACYGNE22_7 | 0.99765 | 0.93196 | -0.06569 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LACYGNE22_7 | 0.99765 | 0.93196 | -0.06569 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LACYGNE22_7 | 0.99765 | 0.93196 | -0.06569 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LACYGNE22_7 | 0.99765 | 0.93196 | -0.06569 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LACYGNE22_7 | 0.99765 | 0.93196 | -0.06569 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LACYGNE22_7 | 0.99765 | 0.93196 | -0.06569 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LACYGNE22_7 | 0.99765 | 0.93196 | -0.06569 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LACYGNE22_7 | 0.99765 | 0.93196 | -0.06569 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LACYGNE22_7 | 0.99765 | 0.93196 | -0.06569 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LACYGNE22_7 | 0.99765 | 0.93196 | -0.06569 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LACYGNE22_7 | 0.99765 | 0.93196 | -0.06569 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LACYGNE22_7 | 0.99765 | 0.93196 | -0.06569 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LACYGNE22_7 | 0.98885 | 0.87975 | -0.1091 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | LACYGNE22_7 | 0.98885 | 0.87975 | -0.1091 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LACYGNE22_7 | 0.98885 | 0.87975 | -0.1091 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LACYGNE22_7 | 0.98885 | 0.87975 | -0.1091 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LACYGNE22_7 | 0.98885 | 0.87975 | -0.1091 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LACYGNE22_7 | 0.98885 | 0.87975 | -0.1091 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LACYGNE22_7 | 0.98885 | 0.87975 | -0.1091 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | LACYGNE22_7 | 0.98885 | 0.87975 | -0.1091 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | LACYGNE22_7 | 0.98885 | 0.87975 | -0.1091 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LACYGNE22_7 | 0.98885 | 0.87975 | -0.1091 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LACYGNE22_7 | 0.98885 | 0.87975 | -0.1091 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LACYGNE22_7 | 0.98885 | 0.87975 | -0.1091 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LACYGNE22_7 | 0.98885 | 0.87975 | -0.1091 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LACYGNE22_7 | 0.98885 | 0.87975 | -0.1091 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LACYGNE22_7 | 0.98885 | 0.87975 | -0.1091 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LACYGNE22_7 | 0.98885 | 0.87975 | -0.1091 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LACYGNE22_7 | 0.98885 | 0.87975 | -0.1091 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LACYGNE22_7 | 0.98885 | 0.87975 | -0.1091 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | LACYGNE22_7 | 0.98885 | 0.87975 | -0.1091 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | LACYGNE22_7 | 0.98885 | 0.87975 | -0.1091 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LACYGNE22_7 | 0.98885 | 0.87975 | -0.1091 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LACYGNE22_7 | 0.98885 | 0.87975 | -0.1091 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | LACYGNE22_7 | 0.98885 | 0.87975 | -0.1091 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LACYGNE22_7 | 0.98885 | 0.87975 | -0.1091 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LACYGNE22_7 | 0.98885 | 0.87975 | -0.1091 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LACYGNE22_7 | 0.98885 | 0.87975 | -0.1091 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LACYGNE22_7 | 0.98885 | 0.87975 | -0.1091 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | LACYGNE22_7 | 0.98885 | 0.87975 | -0.1091 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | LACYGNE_LK2 | 0.97704 | 0.92146 | -0.055576 |  | 0.93 | 1.05 | 0.030773 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | LACYGNE_LK2 | 0.97704 | 0.92146 | -0.055576 |  | 0.93 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LACYGNE_LK2 | 0.97704 | 0.92146 | -0.055576 |  | 0.93 | 1.05 | 0.046711 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | LACYGNE_LK2 | 0.97704 | 0.92146 | -0.055576 |  | 0.93 | 1.05 | 0.032369 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | LACYGNE_LK2 | 0.97704 | 0.92146 | -0.055576 |  | 0.93 | 1.05 | 0.030466 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | LACYGNE_LK2 | 0.97704 | 0.92146 | -0.055576 |  | 0.93 | 1.05 | 0.04987 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LACYGNE_LK2 | 0.97704 | 0.92146 | -0.055576 |  | 0.93 | 1.05 | 0.099365 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LACYGNE_LK2 | 0.97704 | 0.92146 | -0.055576 |  | 0.93 | 1.05 | 0.071132 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LACYGNE_LK2 | 0.97704 | 0.92146 | -0.055576 |  | 0.93 | 1.05 | 0.043927 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LACYGNE_LK2 | 0.97704 | 0.92146 | -0.055576 |  | 0.93 | 1.05 | 0.030565 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LACYGNE_LK2 | 0.97704 | 0.92146 | -0.055576 |  | 0.93 | 1.05 | 0.072847 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | LACYGNE_LK2 | 0.97704 | 0.92146 | -0.055576 |  | 0.93 | 1.05 | 0.041148 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | LACYGNE_LK2 | 0.97704 | 0.92146 | -0.055576 |  | 0.93 | 1.05 | 0.042015 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | LACYGNE_LK2 | 0.97704 | 0.92146 | -0.055576 |  | 0.93 | 1.05 | 0.030318 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LACYGNE_LK2 | 0.97704 | 0.92146 | -0.055576 |  | 0.93 | 1.05 | 0.054104 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LACYGNE_LK2 | 0.97704 | 0.92146 | -0.055576 |  | 0.93 | 1.05 | 0.047089 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LACYGNE_LK2 | 0.97704 | 0.92146 | -0.055576 |  | 0.93 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LACYGNE_LK2 | 0.97704 | 0.92146 | -0.055576 |  | 0.93 | 1.05 | 0.13688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | LACYGNE_LK2 | 0.97704 | 0.92146 | -0.055576 |  | 0.93 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LACYGNE_LK2 | 0.97704 | 0.92146 | -0.055576 |  | 0.93 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LACYGNE_LK2 | 0.97704 | 0.92146 | -0.055576 |  | 0.93 | 1.05 | 0.039752 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LACYGNE_LK2 | 0.97704 | 0.92146 | -0.055576 |  | 0.93 | 1.05 | 0.041972 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LACYGNE_LK2 | 0.97704 | 0.92146 | -0.055576 |  | 0.93 | 1.05 | 0.054397 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LACYGNE_LK2 | 0.97704 | 0.92146 | -0.055576 |  | 0.93 | 1.05 | 0.073688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | LACYGNE_LK2 | 0.97704 | 0.92146 | -0.055576 |  | 0.93 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | LACYGNE_LK2 | 0.97704 | 0.92146 | -0.055576 |  | 0.93 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LACYGNE_LK2 | 0.97704 | 0.92146 | -0.055576 |  | 0.93 | 1.05 | 0.072188 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LACYGNE_LK2 | 0.97704 | 0.92146 | -0.055576 |  | 0.93 | 1.05 | 0.042186 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | LACYGNE_LK2 | 0.97704 | 0.92146 | -0.055576 |  | 0.93 | 1.05 | 0.041423 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LACYGNE_LK2 | 0.97704 | 0.92146 | -0.055576 |  | 0.93 | 1.05 | 0.050171 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LACYGNE_LK2 | 0.97704 | 0.92146 | -0.055576 |  | 0.93 | 1.05 | 0.04386 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LACYGNE_LK2 | 0.97704 | 0.92146 | -0.055576 |  | 0.93 | 1.05 | 0.050218 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LACYGNE_LK2 | 0.97704 | 0.92146 | -0.055576 |  | 0.93 | 1.05 | 0.040041 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | LACYGNE_LK2 | 0.97704 | 0.92146 | -0.055576 |  | 0.93 | 1.05 | 0.038784 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LACYGNE_LK2 | 0.98571 | 0.919 | -0.066704 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LACYGNE_LK2 | 0.98571 | 0.919 | -0.066704 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LACYGNE_LK2 | 0.98571 | 0.919 | -0.066704 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LACYGNE_LK2 | 0.98571 | 0.919 | -0.066704 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LACYGNE_LK2 | 0.98571 | 0.919 | -0.066704 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LACYGNE_LK2 | 0.98571 | 0.919 | -0.066704 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LACYGNE_LK2 | 0.98571 | 0.919 | -0.066704 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LACYGNE_LK2 | 0.98571 | 0.919 | -0.066704 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LACYGNE_LK2 | 0.98571 | 0.919 | -0.066704 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LACYGNE_LK2 | 0.98571 | 0.919 | -0.066704 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LACYGNE_LK2 | 0.98571 | 0.919 | -0.066704 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LACYGNE_LK2 | 0.98571 | 0.919 | -0.066704 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LACYGNE_LK2 | 0.98571 | 0.919 | -0.066704 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LACYGNE_LK2 | 0.98571 | 0.919 | -0.066704 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LACYGNE_LK2 | 0.98571 | 0.919 | -0.066704 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LACYGNE_LK2 | 0.98571 | 0.919 | -0.066704 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LACYGNE_LK2 | 0.98571 | 0.919 | -0.066704 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LACYGNE_LK2 | 0.98571 | 0.919 | -0.066704 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LACYGNE_LK2 | 0.98571 | 0.919 | -0.066704 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LACYGNE_LK2 | 0.98571 | 0.919 | -0.066704 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LACYGNE_LK2 | 0.97678 | 0.86585 | -0.11093 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | LACYGNE_LK2 | 0.97678 | 0.86585 | -0.11093 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LACYGNE_LK2 | 0.97678 | 0.86585 | -0.11093 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LACYGNE_LK2 | 0.97678 | 0.86585 | -0.11093 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LACYGNE_LK2 | 0.97678 | 0.86585 | -0.11093 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LACYGNE_LK2 | 0.97678 | 0.86585 | -0.11093 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LACYGNE_LK2 | 0.97678 | 0.86585 | -0.11093 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | LACYGNE_LK2 | 0.97678 | 0.86585 | -0.11093 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | LACYGNE_LK2 | 0.97678 | 0.86585 | -0.11093 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LACYGNE_LK2 | 0.97678 | 0.86585 | -0.11093 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LACYGNE_LK2 | 0.97678 | 0.86585 | -0.11093 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LACYGNE_LK2 | 0.97678 | 0.86585 | -0.11093 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LACYGNE_LK2 | 0.97678 | 0.86585 | -0.11093 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LACYGNE_LK2 | 0.97678 | 0.86585 | -0.11093 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LACYGNE_LK2 | 0.97678 | 0.86585 | -0.11093 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LACYGNE_LK2 | 0.97678 | 0.86585 | -0.11093 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LACYGNE_LK2 | 0.97678 | 0.86585 | -0.11093 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LACYGNE_LK2 | 0.97678 | 0.86585 | -0.11093 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | LACYGNE_LK2 | 0.97678 | 0.86585 | -0.11093 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | LACYGNE_LK2 | 0.97678 | 0.86585 | -0.11093 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LACYGNE_LK2 | 0.97678 | 0.86585 | -0.11093 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LACYGNE_LK2 | 0.97678 | 0.86585 | -0.11093 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | LACYGNE_LK2 | 0.97678 | 0.86585 | -0.11093 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LACYGNE_LK2 | 0.97678 | 0.86585 | -0.11093 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LACYGNE_LK2 | 0.97678 | 0.86585 | -0.11093 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LACYGNE_LK2 | 0.97678 | 0.86585 | -0.11093 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LACYGNE_LK2 | 0.97678 | 0.86585 | -0.11093 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | LACYGNE_LK2 | 0.97678 | 0.86585 | -0.11093 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LANG 3 | 0.9459 | 0.85844 | -0.087454 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | LANG 3 | 0.9459 | 0.85844 | -0.087454 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LANG 3 | 0.9459 | 0.85844 | -0.087454 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LANG 3 | 0.9459 | 0.85844 | -0.087454 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LANG 3 | 0.9459 | 0.85844 | -0.087454 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LANG 3 | 0.9459 | 0.85844 | -0.087454 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LANG 3 | 0.9459 | 0.85844 | -0.087454 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | LANG 3 | 0.9459 | 0.85844 | -0.087454 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | LANG 3 | 0.9459 | 0.85844 | -0.087454 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LANG 3 | 0.9459 | 0.85844 | -0.087454 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LANG 3 | 0.9459 | 0.85844 | -0.087454 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LANG 3 | 0.9459 | 0.85844 | -0.087454 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LANG 3 | 0.9459 | 0.85844 | -0.087454 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LANG 3 | 0.9459 | 0.85844 | -0.087454 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LANG 3 | 0.9459 | 0.85844 | -0.087454 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LANG 3 | 0.9459 | 0.85844 | -0.087454 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LANG 3 | 0.9459 | 0.85844 | -0.087454 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LANG 3 | 0.9459 | 0.85844 | -0.087454 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | LANG 3 | 0.9459 | 0.85844 | -0.087454 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | LANG 3 | 0.9459 | 0.85844 | -0.087454 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LANG 3 | 0.9459 | 0.85844 | -0.087454 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LANG 3 | 0.9459 | 0.85844 | -0.087454 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | LANG 3 | 0.9459 | 0.85844 | -0.087454 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LANG 3 | 0.9459 | 0.85844 | -0.087454 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LANG 3 | 0.9459 | 0.85844 | -0.087454 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LANG 3 | 0.9459 | 0.85844 | -0.087454 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LANG 3 | 0.9459 | 0.85844 | -0.087454 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | LANG 3 | 0.9459 | 0.85844 | -0.087454 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LANG 7 | 0.99438 | 0.94415 | -0.050228 |  | 0.95 | 1.05 | 0.03965 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LANG 7 | 0.99438 | 0.94415 | -0.050228 |  | 0.95 | 1.05 | 0.042938 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LANG 7 | 0.99438 | 0.94415 | -0.050228 |  | 0.95 | 1.05 | 0.032864 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LANG 7 | 0.99438 | 0.94415 | -0.050228 |  | 0.95 | 1.05 | 0.034629 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LANG 7 | 0.99438 | 0.94415 | -0.050228 |  | 0.95 | 1.05 | 0.036988 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LANG 7 | 0.99438 | 0.94415 | -0.050228 |  | 0.95 | 1.05 | 0.03396 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | LANG 7 | 0.99438 | 0.94415 | -0.050228 |  | 0.95 | 1.05 | 0.030296 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LANG 7 | 0.99438 | 0.94415 | -0.050228 |  | 0.95 | 1.05 | 0.037836 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LANG 7 | 0.99438 | 0.94415 | -0.050228 |  | 0.95 | 1.05 | 0.036214 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LANG 7 | 0.99438 | 0.94415 | -0.050228 |  | 0.95 | 1.05 | 0.055483 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LANG 7 | 0.99438 | 0.94415 | -0.050228 |  | 0.95 | 1.05 | 0.036214 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LANG 7 | 0.99438 | 0.94415 | -0.050228 |  | 0.95 | 1.05 | 0.037031 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LANG 7 | 0.99438 | 0.94415 | -0.050228 |  | 0.95 | 1.05 | 0.03728 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LANG 7 | 0.99438 | 0.94415 | -0.050228 |  | 0.95 | 1.05 | 0.034689 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LANG 7 | 0.99438 | 0.94415 | -0.050228 |  | 0.95 | 1.05 | 0.033481 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LANG 7 | 0.99438 | 0.94415 | -0.050228 |  | 0.95 | 1.05 | 0.035246 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LANG 7 | 0.99438 | 0.94415 | -0.050228 |  | 0.95 | 1.05 | 0.03235 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LANG 7 | 0.99438 | 0.94415 | -0.050228 |  | 0.95 | 1.05 | 0.031498 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LANG 7 | 0.99438 | 0.94415 | -0.050228 |  | 0.95 | 1.05 | 0.033388 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LANG 7 | 0.99438 | 0.94415 | -0.050228 |  | 0.95 | 1.05 | 0.034867 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | LANG 7 | 1.005 | 0.94681 | -0.058145 |  | 0.95 | 1.05 | 0.030773 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | LANG 7 | 1.005 | 0.94681 | -0.058145 |  | 0.95 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LANG 7 | 1.005 | 0.94681 | -0.058145 |  | 0.95 | 1.05 | 0.046711 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | LANG 7 | 1.005 | 0.94681 | -0.058145 |  | 0.95 | 1.05 | 0.032369 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | LANG 7 | 1.005 | 0.94681 | -0.058145 |  | 0.95 | 1.05 | 0.030466 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | LANG 7 | 1.005 | 0.94681 | -0.058145 |  | 0.95 | 1.05 | 0.04987 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LANG 7 | 1.005 | 0.94681 | -0.058145 |  | 0.95 | 1.05 | 0.099365 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LANG 7 | 1.005 | 0.94681 | -0.058145 |  | 0.95 | 1.05 | 0.071132 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LANG 7 | 1.005 | 0.94681 | -0.058145 |  | 0.95 | 1.05 | 0.043927 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LANG 7 | 1.005 | 0.94681 | -0.058145 |  | 0.95 | 1.05 | 0.030565 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LANG 7 | 1.005 | 0.94681 | -0.058145 |  | 0.95 | 1.05 | 0.072847 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | LANG 7 | 1.005 | 0.94681 | -0.058145 |  | 0.95 | 1.05 | 0.041148 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | LANG 7 | 1.005 | 0.94681 | -0.058145 |  | 0.95 | 1.05 | 0.042015 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | LANG 7 | 1.005 | 0.94681 | -0.058145 |  | 0.95 | 1.05 | 0.030318 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LANG 7 | 1.005 | 0.94681 | -0.058145 |  | 0.95 | 1.05 | 0.054104 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LANG 7 | 1.005 | 0.94681 | -0.058145 |  | 0.95 | 1.05 | 0.047089 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LANG 7 | 1.005 | 0.94681 | -0.058145 |  | 0.95 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LANG 7 | 1.005 | 0.94681 | -0.058145 |  | 0.95 | 1.05 | 0.13688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | LANG 7 | 1.005 | 0.94681 | -0.058145 |  | 0.95 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LANG 7 | 1.005 | 0.94681 | -0.058145 |  | 0.95 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LANG 7 | 1.005 | 0.94681 | -0.058145 |  | 0.95 | 1.05 | 0.039752 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LANG 7 | 1.005 | 0.94681 | -0.058145 |  | 0.95 | 1.05 | 0.041972 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LANG 7 | 1.005 | 0.94681 | -0.058145 |  | 0.95 | 1.05 | 0.054397 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LANG 7 | 1.005 | 0.94681 | -0.058145 |  | 0.95 | 1.05 | 0.073688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | LANG 7 | 1.005 | 0.94681 | -0.058145 |  | 0.95 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | LANG 7 | 1.005 | 0.94681 | -0.058145 |  | 0.95 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LANG 7 | 1.005 | 0.94681 | -0.058145 |  | 0.95 | 1.05 | 0.072188 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LANG 7 | 1.005 | 0.94681 | -0.058145 |  | 0.95 | 1.05 | 0.042186 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | LANG 7 | 1.005 | 0.94681 | -0.058145 |  | 0.95 | 1.05 | 0.041423 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LANG 7 | 1.005 | 0.94681 | -0.058145 |  | 0.95 | 1.05 | 0.050171 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LANG 7 | 1.005 | 0.94681 | -0.058145 |  | 0.95 | 1.05 | 0.04386 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LANG 7 | 1.005 | 0.94681 | -0.058145 |  | 0.95 | 1.05 | 0.050218 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LANG 7 | 1.005 | 0.94681 | -0.058145 |  | 0.95 | 1.05 | 0.040041 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | LANG 7 | 1.005 | 0.94681 | -0.058145 |  | 0.95 | 1.05 | 0.038784 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LANG 7 | 0.9974 | 0.94686 | -0.050541 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LANG 7 | 0.9974 | 0.94686 | -0.050541 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LANG 7 | 0.9974 | 0.94686 | -0.050541 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LANG 7 | 0.9974 | 0.94686 | -0.050541 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LANG 7 | 0.9974 | 0.94686 | -0.050541 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LANG 7 | 0.9974 | 0.94686 | -0.050541 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LANG 7 | 0.9974 | 0.94686 | -0.050541 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LANG 7 | 0.9974 | 0.94686 | -0.050541 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LANG 7 | 0.9974 | 0.94686 | -0.050541 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LANG 7 | 0.9974 | 0.94686 | -0.050541 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LANG 7 | 0.9974 | 0.94686 | -0.050541 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LANG 7 | 0.9974 | 0.94686 | -0.050541 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LANG 7 | 0.9974 | 0.94686 | -0.050541 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LANG 7 | 0.9974 | 0.94686 | -0.050541 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LANG 7 | 0.9974 | 0.94686 | -0.050541 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LANG 7 | 0.9974 | 0.94686 | -0.050541 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LANG 7 | 0.9974 | 0.94686 | -0.050541 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LANG 7 | 0.9974 | 0.94686 | -0.050541 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LANG 7 | 0.9974 | 0.94686 | -0.050541 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LANG 7 | 0.9974 | 0.94686 | -0.050541 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LANG 7 | 1.001 | 0.94098 | -0.060012 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LANG 7 | 1.001 | 0.94098 | -0.060012 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LANG 7 | 1.001 | 0.94098 | -0.060012 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LANG 7 | 1.001 | 0.94098 | -0.060012 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LANG 7 | 1.001 | 0.94098 | -0.060012 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LANG 7 | 1.001 | 0.94098 | -0.060012 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LANG 7 | 1.001 | 0.94098 | -0.060012 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LANG 7 | 1.001 | 0.94098 | -0.060012 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LANG 7 | 1.001 | 0.94098 | -0.060012 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LANG 7 | 1.001 | 0.94098 | -0.060012 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LANG 7 | 1.001 | 0.94098 | -0.060012 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LANG 7 | 1.001 | 0.94098 | -0.060012 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LANG 7 | 1.001 | 0.94098 | -0.060012 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LANG 7 | 1.001 | 0.94098 | -0.060012 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LANG 7 | 1.001 | 0.94098 | -0.060012 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LANG 7 | 1.001 | 0.94098 | -0.060012 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LANG 7 | 1.001 | 0.94098 | -0.060012 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LANG 7 | 1.001 | 0.94098 | -0.060012 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LANG 7 | 1.001 | 0.94098 | -0.060012 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LANG 7 | 1.001 | 0.94098 | -0.060012 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LANG 7 | 0.85988 | 0.78038 | -0.079501 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | LANG 7 | 0.85988 | 0.78038 | -0.079501 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LANG 7 | 0.85988 | 0.78038 | -0.079501 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LANG 7 | 0.85988 | 0.78038 | -0.079501 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LANG 7 | 0.85988 | 0.78038 | -0.079501 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LANG 7 | 0.85988 | 0.78038 | -0.079501 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LANG 7 | 0.85988 | 0.78038 | -0.079501 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | LANG 7 | 0.85988 | 0.78038 | -0.079501 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | LANG 7 | 0.85988 | 0.78038 | -0.079501 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LANG 7 | 0.85988 | 0.78038 | -0.079501 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LANG 7 | 0.85988 | 0.78038 | -0.079501 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LANG 7 | 0.85988 | 0.78038 | -0.079501 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LANG 7 | 0.85988 | 0.78038 | -0.079501 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LANG 7 | 0.85988 | 0.78038 | -0.079501 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LANG 7 | 0.85988 | 0.78038 | -0.079501 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LANG 7 | 0.85988 | 0.78038 | -0.079501 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LANG 7 | 0.85988 | 0.78038 | -0.079501 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LANG 7 | 0.85988 | 0.78038 | -0.079501 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | LANG 7 | 0.85988 | 0.78038 | -0.079501 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | LANG 7 | 0.85988 | 0.78038 | -0.079501 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LANG 7 | 0.85988 | 0.78038 | -0.079501 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LANG 7 | 0.85988 | 0.78038 | -0.079501 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | LANG 7 | 0.85988 | 0.78038 | -0.079501 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LANG 7 | 0.85988 | 0.78038 | -0.079501 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LANG 7 | 0.85988 | 0.78038 | -0.079501 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LANG 7 | 0.85988 | 0.78038 | -0.079501 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LANG 7 | 0.85988 | 0.78038 | -0.079501 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | LANG 7 | 0.85988 | 0.78038 | -0.079501 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LAWHILL6 | 0.98209 | 0.94666 | -0.035438 |  | 0.95 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LAWHILL6 | 0.98209 | 0.94666 | -0.035438 |  | 0.95 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LAWHILL6 | 0.98209 | 0.94666 | -0.035438 |  | 0.95 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LAWHILL6 | 0.98209 | 0.94666 | -0.035438 |  | 0.95 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LAWHILL6 | 0.98209 | 0.94666 | -0.035438 |  | 0.95 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LAWHILL6 | 0.98209 | 0.94666 | -0.035438 |  | 0.95 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LAWHILL6 | 0.98209 | 0.94666 | -0.035438 |  | 0.95 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LAWHILL6 | 0.98209 | 0.94666 | -0.035438 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LAWHILL6 | 0.98209 | 0.94666 | -0.035438 |  | 0.95 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LAWHILL6 | 0.98209 | 0.94666 | -0.035438 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LAWHILL6 | 0.98209 | 0.94666 | -0.035438 |  | 0.95 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LAWHILL6 | 0.98209 | 0.94666 | -0.035438 |  | 0.95 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LAWHILL6 | 0.98209 | 0.94666 | -0.035438 |  | 0.95 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LAWHILL6 | 0.98209 | 0.94666 | -0.035438 |  | 0.95 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LAWHILL6 | 0.98209 | 0.94666 | -0.035438 |  | 0.95 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LAWHILL6 | 0.98209 | 0.94666 | -0.035438 |  | 0.95 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LAWHILL6 | 0.98209 | 0.94666 | -0.035438 |  | 0.95 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LAWHILL6 | 0.98209 | 0.94666 | -0.035438 |  | 0.95 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LAWHILL6 | 0.98209 | 0.94666 | -0.035438 |  | 0.95 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LAWHILL6 | 0.98209 | 0.94666 | -0.035438 |  | 0.95 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LAWHILL6 | 0.97946 | 0.93781 | -0.04165 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LAWHILL6 | 0.97946 | 0.93781 | -0.04165 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LAWHILL6 | 0.97946 | 0.93781 | -0.04165 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LAWHILL6 | 0.97946 | 0.93781 | -0.04165 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LAWHILL6 | 0.97946 | 0.93781 | -0.04165 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LAWHILL6 | 0.97946 | 0.93781 | -0.04165 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LAWHILL6 | 0.97946 | 0.93781 | -0.04165 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LAWHILL6 | 0.97946 | 0.93781 | -0.04165 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LAWHILL6 | 0.97946 | 0.93781 | -0.04165 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LAWHILL6 | 0.97946 | 0.93781 | -0.04165 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LAWHILL6 | 0.97946 | 0.93781 | -0.04165 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LAWHILL6 | 0.97946 | 0.93781 | -0.04165 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LAWHILL6 | 0.97946 | 0.93781 | -0.04165 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LAWHILL6 | 0.97946 | 0.93781 | -0.04165 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LAWHILL6 | 0.97946 | 0.93781 | -0.04165 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LAWHILL6 | 0.97946 | 0.93781 | -0.04165 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LAWHILL6 | 0.97946 | 0.93781 | -0.04165 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LAWHILL6 | 0.97946 | 0.93781 | -0.04165 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LAWHILL6 | 0.97946 | 0.93781 | -0.04165 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LAWHILL6 | 0.97946 | 0.93781 | -0.04165 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LAWHILL6 | 0.98399 | 0.94023 | -0.043766 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LAWHILL6 | 0.98399 | 0.94023 | -0.043766 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LAWHILL6 | 0.98399 | 0.94023 | -0.043766 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LAWHILL6 | 0.98399 | 0.94023 | -0.043766 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LAWHILL6 | 0.98399 | 0.94023 | -0.043766 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LAWHILL6 | 0.98399 | 0.94023 | -0.043766 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LAWHILL6 | 0.98399 | 0.94023 | -0.043766 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LAWHILL6 | 0.98399 | 0.94023 | -0.043766 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LAWHILL6 | 0.98399 | 0.94023 | -0.043766 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LAWHILL6 | 0.98399 | 0.94023 | -0.043766 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LAWHILL6 | 0.98399 | 0.94023 | -0.043766 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LAWHILL6 | 0.98399 | 0.94023 | -0.043766 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LAWHILL6 | 0.98399 | 0.94023 | -0.043766 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LAWHILL6 | 0.98399 | 0.94023 | -0.043766 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LAWHILL6 | 0.98399 | 0.94023 | -0.043766 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LAWHILL6 | 0.98399 | 0.94023 | -0.043766 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LAWHILL6 | 0.98399 | 0.94023 | -0.043766 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LAWHILL6 | 0.98399 | 0.94023 | -0.043766 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LAWHILL6 | 0.98399 | 0.94023 | -0.043766 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LAWHILL6 | 0.98399 | 0.94023 | -0.043766 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LAWHILL6 | 0.98992 | 0.94256 | -0.04736 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | LAWHILL6 | 0.98992 | 0.94256 | -0.04736 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LAWHILL6 | 0.98992 | 0.94256 | -0.04736 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LAWHILL6 | 0.98992 | 0.94256 | -0.04736 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LAWHILL6 | 0.98992 | 0.94256 | -0.04736 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LAWHILL6 | 0.98992 | 0.94256 | -0.04736 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LAWHILL6 | 0.98992 | 0.94256 | -0.04736 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | LAWHILL6 | 0.98992 | 0.94256 | -0.04736 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | LAWHILL6 | 0.98992 | 0.94256 | -0.04736 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LAWHILL6 | 0.98992 | 0.94256 | -0.04736 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LAWHILL6 | 0.98992 | 0.94256 | -0.04736 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LAWHILL6 | 0.98992 | 0.94256 | -0.04736 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LAWHILL6 | 0.98992 | 0.94256 | -0.04736 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LAWHILL6 | 0.98992 | 0.94256 | -0.04736 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LAWHILL6 | 0.98992 | 0.94256 | -0.04736 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LAWHILL6 | 0.98992 | 0.94256 | -0.04736 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LAWHILL6 | 0.98992 | 0.94256 | -0.04736 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LAWHILL6 | 0.98992 | 0.94256 | -0.04736 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | LAWHILL6 | 0.98992 | 0.94256 | -0.04736 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | LAWHILL6 | 0.98992 | 0.94256 | -0.04736 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LAWHILL6 | 0.98992 | 0.94256 | -0.04736 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LAWHILL6 | 0.98992 | 0.94256 | -0.04736 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | LAWHILL6 | 0.98992 | 0.94256 | -0.04736 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LAWHILL6 | 0.98992 | 0.94256 | -0.04736 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LAWHILL6 | 0.98992 | 0.94256 | -0.04736 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LAWHILL6 | 0.98992 | 0.94256 | -0.04736 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LAWHILL6 | 0.98992 | 0.94256 | -0.04736 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | LAWHILL6 | 0.98992 | 0.94256 | -0.04736 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LAWHILL6 | 0.9818 | 0.94526 | -0.036536 |  | 0.95 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LAWHILL6 | 0.9818 | 0.94526 | -0.036536 |  | 0.95 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LAWHILL6 | 0.9818 | 0.94526 | -0.036536 |  | 0.95 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LAWHILL6 | 0.9818 | 0.94526 | -0.036536 |  | 0.95 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LAWHILL6 | 0.9818 | 0.94526 | -0.036536 |  | 0.95 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LAWHILL6 | 0.9818 | 0.94526 | -0.036536 |  | 0.95 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LAWHILL6 | 0.9818 | 0.94526 | -0.036536 |  | 0.95 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LAWHILL6 | 0.9818 | 0.94526 | -0.036536 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LAWHILL6 | 0.9818 | 0.94526 | -0.036536 |  | 0.95 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LAWHILL6 | 0.9818 | 0.94526 | -0.036536 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LAWHILL6 | 0.9818 | 0.94526 | -0.036536 |  | 0.95 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LAWHILL6 | 0.9818 | 0.94526 | -0.036536 |  | 0.95 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LAWHILL6 | 0.9818 | 0.94526 | -0.036536 |  | 0.95 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LAWHILL6 | 0.9818 | 0.94526 | -0.036536 |  | 0.95 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LAWHILL6 | 0.9818 | 0.94526 | -0.036536 |  | 0.95 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LAWHILL6 | 0.9818 | 0.94526 | -0.036536 |  | 0.95 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LAWHILL6 | 0.9818 | 0.94526 | -0.036536 |  | 0.95 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LAWHILL6 | 0.9818 | 0.94526 | -0.036536 |  | 0.95 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LAWHILL6 | 0.9818 | 0.94526 | -0.036536 |  | 0.95 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LAWHILL6 | 0.9818 | 0.94526 | -0.036536 |  | 0.95 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LAWNRID3 | 0.96186 | 0.8921 | -0.069753 |  | 0.9 | 1.05 | 0.041569 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LAWNRID3 | 0.96186 | 0.8921 | -0.069753 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LAWNRID3 | 0.96186 | 0.8921 | -0.069753 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LAWNRID3 | 0.96186 | 0.8921 | -0.069753 |  | 0.9 | 1.05 | 0.03222 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LAWNRID3 | 0.96186 | 0.8921 | -0.069753 |  | 0.9 | 1.05 | 0.030633 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LAWNRID3 | 0.96186 | 0.8921 | -0.069753 |  | 0.9 | 1.05 | 0.030061 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LAWNRID3 | 0.96186 | 0.8921 | -0.069753 |  | 0.9 | 1.05 | 0.031207 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LAWNRID3 | 0.94525 | 0.87032 | -0.074926 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LAWNRID3 | 0.94525 | 0.87032 | -0.074926 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LAWNRID3 | 0.94491 | 0.86176 | -0.083147 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LAWNRID3 | 0.94491 | 0.86176 | -0.083147 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LAWNRID3 | 0.94491 | 0.86176 | -0.083148 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LAWNRID3 | 0.94491 | 0.86176 | -0.083148 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LAWNRID3 | 0.94491 | 0.86176 | -0.083149 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LAWNRID3 | 0.94491 | 0.86176 | -0.083149 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LEC U5 6 | 0.98269 | 0.94727 | -0.035418 |  | 0.95 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LEC U5 6 | 0.98269 | 0.94727 | -0.035418 |  | 0.95 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LEC U5 6 | 0.98269 | 0.94727 | -0.035418 |  | 0.95 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LEC U5 6 | 0.98269 | 0.94727 | -0.035418 |  | 0.95 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LEC U5 6 | 0.98269 | 0.94727 | -0.035418 |  | 0.95 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LEC U5 6 | 0.98269 | 0.94727 | -0.035418 |  | 0.95 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LEC U5 6 | 0.98269 | 0.94727 | -0.035418 |  | 0.95 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LEC U5 6 | 0.98269 | 0.94727 | -0.035418 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LEC U5 6 | 0.98269 | 0.94727 | -0.035418 |  | 0.95 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LEC U5 6 | 0.98269 | 0.94727 | -0.035418 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LEC U5 6 | 0.98269 | 0.94727 | -0.035418 |  | 0.95 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LEC U5 6 | 0.98269 | 0.94727 | -0.035418 |  | 0.95 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LEC U5 6 | 0.98269 | 0.94727 | -0.035418 |  | 0.95 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LEC U5 6 | 0.98269 | 0.94727 | -0.035418 |  | 0.95 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LEC U5 6 | 0.98269 | 0.94727 | -0.035418 |  | 0.95 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LEC U5 6 | 0.98269 | 0.94727 | -0.035418 |  | 0.95 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LEC U5 6 | 0.98269 | 0.94727 | -0.035418 |  | 0.95 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LEC U5 6 | 0.98269 | 0.94727 | -0.035418 |  | 0.95 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LEC U5 6 | 0.98269 | 0.94727 | -0.035418 |  | 0.95 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LEC U5 6 | 0.98269 | 0.94727 | -0.035418 |  | 0.95 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LEC U5 6 | 0.98008 | 0.93843 | -0.04165 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LEC U5 6 | 0.98008 | 0.93843 | -0.04165 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LEC U5 6 | 0.98008 | 0.93843 | -0.04165 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LEC U5 6 | 0.98008 | 0.93843 | -0.04165 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LEC U5 6 | 0.98008 | 0.93843 | -0.04165 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LEC U5 6 | 0.98008 | 0.93843 | -0.04165 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LEC U5 6 | 0.98008 | 0.93843 | -0.04165 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LEC U5 6 | 0.98008 | 0.93843 | -0.04165 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LEC U5 6 | 0.98008 | 0.93843 | -0.04165 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LEC U5 6 | 0.98008 | 0.93843 | -0.04165 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LEC U5 6 | 0.98008 | 0.93843 | -0.04165 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LEC U5 6 | 0.98008 | 0.93843 | -0.04165 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LEC U5 6 | 0.98008 | 0.93843 | -0.04165 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LEC U5 6 | 0.98008 | 0.93843 | -0.04165 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LEC U5 6 | 0.98008 | 0.93843 | -0.04165 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LEC U5 6 | 0.98008 | 0.93843 | -0.04165 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LEC U5 6 | 0.98008 | 0.93843 | -0.04165 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LEC U5 6 | 0.98008 | 0.93843 | -0.04165 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LEC U5 6 | 0.98008 | 0.93843 | -0.04165 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LEC U5 6 | 0.98008 | 0.93843 | -0.04165 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LEC U5 6 | 0.98457 | 0.94084 | -0.043724 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LEC U5 6 | 0.98457 | 0.94084 | -0.043724 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LEC U5 6 | 0.98457 | 0.94084 | -0.043724 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LEC U5 6 | 0.98457 | 0.94084 | -0.043724 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LEC U5 6 | 0.98457 | 0.94084 | -0.043724 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LEC U5 6 | 0.98457 | 0.94084 | -0.043724 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LEC U5 6 | 0.98457 | 0.94084 | -0.043724 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LEC U5 6 | 0.98457 | 0.94084 | -0.043724 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LEC U5 6 | 0.98457 | 0.94084 | -0.043724 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LEC U5 6 | 0.98457 | 0.94084 | -0.043724 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LEC U5 6 | 0.98457 | 0.94084 | -0.043724 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LEC U5 6 | 0.98457 | 0.94084 | -0.043724 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LEC U5 6 | 0.98457 | 0.94084 | -0.043724 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LEC U5 6 | 0.98457 | 0.94084 | -0.043724 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LEC U5 6 | 0.98457 | 0.94084 | -0.043724 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LEC U5 6 | 0.98457 | 0.94084 | -0.043724 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LEC U5 6 | 0.98457 | 0.94084 | -0.043724 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LEC U5 6 | 0.98457 | 0.94084 | -0.043724 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LEC U5 6 | 0.98457 | 0.94084 | -0.043724 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LEC U5 6 | 0.98457 | 0.94084 | -0.043724 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LEC U5 6 | 0.99044 | 0.94318 | -0.047263 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | LEC U5 6 | 0.99044 | 0.94318 | -0.047263 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LEC U5 6 | 0.99044 | 0.94318 | -0.047263 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LEC U5 6 | 0.99044 | 0.94318 | -0.047263 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LEC U5 6 | 0.99044 | 0.94318 | -0.047263 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LEC U5 6 | 0.99044 | 0.94318 | -0.047263 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LEC U5 6 | 0.99044 | 0.94318 | -0.047263 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | LEC U5 6 | 0.99044 | 0.94318 | -0.047263 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | LEC U5 6 | 0.99044 | 0.94318 | -0.047263 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LEC U5 6 | 0.99044 | 0.94318 | -0.047263 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LEC U5 6 | 0.99044 | 0.94318 | -0.047263 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LEC U5 6 | 0.99044 | 0.94318 | -0.047263 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LEC U5 6 | 0.99044 | 0.94318 | -0.047263 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LEC U5 6 | 0.99044 | 0.94318 | -0.047263 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LEC U5 6 | 0.99044 | 0.94318 | -0.047263 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LEC U5 6 | 0.99044 | 0.94318 | -0.047263 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LEC U5 6 | 0.99044 | 0.94318 | -0.047263 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LEC U5 6 | 0.99044 | 0.94318 | -0.047263 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | LEC U5 6 | 0.99044 | 0.94318 | -0.047263 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | LEC U5 6 | 0.99044 | 0.94318 | -0.047263 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LEC U5 6 | 0.99044 | 0.94318 | -0.047263 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LEC U5 6 | 0.99044 | 0.94318 | -0.047263 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | LEC U5 6 | 0.99044 | 0.94318 | -0.047263 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LEC U5 6 | 0.99044 | 0.94318 | -0.047263 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LEC U5 6 | 0.99044 | 0.94318 | -0.047263 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LEC U5 6 | 0.99044 | 0.94318 | -0.047263 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LEC U5 6 | 0.99044 | 0.94318 | -0.047263 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | LEC U5 6 | 0.99044 | 0.94318 | -0.047263 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LEC U5 6 | 0.98239 | 0.94587 | -0.036518 |  | 0.95 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LEC U5 6 | 0.98239 | 0.94587 | -0.036518 |  | 0.95 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LEC U5 6 | 0.98239 | 0.94587 | -0.036518 |  | 0.95 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LEC U5 6 | 0.98239 | 0.94587 | -0.036518 |  | 0.95 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LEC U5 6 | 0.98239 | 0.94587 | -0.036518 |  | 0.95 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LEC U5 6 | 0.98239 | 0.94587 | -0.036518 |  | 0.95 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LEC U5 6 | 0.98239 | 0.94587 | -0.036518 |  | 0.95 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LEC U5 6 | 0.98239 | 0.94587 | -0.036518 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LEC U5 6 | 0.98239 | 0.94587 | -0.036518 |  | 0.95 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LEC U5 6 | 0.98239 | 0.94587 | -0.036518 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LEC U5 6 | 0.98239 | 0.94587 | -0.036518 |  | 0.95 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LEC U5 6 | 0.98239 | 0.94587 | -0.036518 |  | 0.95 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LEC U5 6 | 0.98239 | 0.94587 | -0.036518 |  | 0.95 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LEC U5 6 | 0.98239 | 0.94587 | -0.036518 |  | 0.95 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LEC U5 6 | 0.98239 | 0.94587 | -0.036518 |  | 0.95 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LEC U5 6 | 0.98239 | 0.94587 | -0.036518 |  | 0.95 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LEC U5 6 | 0.98239 | 0.94587 | -0.036518 |  | 0.95 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LEC U5 6 | 0.98239 | 0.94587 | -0.036518 |  | 0.95 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LEC U5 6 | 0.98239 | 0.94587 | -0.036518 |  | 0.95 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LEC U5 6 | 0.98239 | 0.94587 | -0.036518 |  | 0.95 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LENEXA 5 | 0.96748 | 0.92853 | -0.038951 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LENEXA 5 | 0.96748 | 0.92853 | -0.038951 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LENEXA 5 | 0.96748 | 0.92853 | -0.038951 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LENEXA 5 | 0.96748 | 0.92853 | -0.038951 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LENEXA 5 | 0.96748 | 0.92853 | -0.038951 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LENEXA 5 | 0.96748 | 0.92853 | -0.038951 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LENEXA 5 | 0.96748 | 0.92853 | -0.038951 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LENEXA 5 | 0.96748 | 0.92853 | -0.038951 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LENEXA 5 | 0.96748 | 0.92853 | -0.038951 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LENEXA 5 | 0.96748 | 0.92853 | -0.038951 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LENEXA 5 | 0.96748 | 0.92853 | -0.038951 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LENEXA 5 | 0.96748 | 0.92853 | -0.038951 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LENEXA 5 | 0.96748 | 0.92853 | -0.038951 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LENEXA 5 | 0.96748 | 0.92853 | -0.038951 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LENEXA 5 | 0.96748 | 0.92853 | -0.038951 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LENEXA 5 | 0.96748 | 0.92853 | -0.038951 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LENEXA 5 | 0.96748 | 0.92853 | -0.038951 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LENEXA 5 | 0.96748 | 0.92853 | -0.038951 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LENEXA 5 | 0.96748 | 0.92853 | -0.038951 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LENEXA 5 | 0.96748 | 0.92853 | -0.038951 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LENEXA 5 | 0.97969 | 0.91419 | -0.065496 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | LENEXA 5 | 0.97969 | 0.91419 | -0.065496 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LENEXA 5 | 0.97969 | 0.91419 | -0.065496 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LENEXA 5 | 0.97969 | 0.91419 | -0.065496 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LENEXA 5 | 0.97969 | 0.91419 | -0.065496 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LENEXA 5 | 0.97969 | 0.91419 | -0.065496 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LENEXA 5 | 0.97969 | 0.91419 | -0.065496 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | LENEXA 5 | 0.97969 | 0.91419 | -0.065496 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | LENEXA 5 | 0.97969 | 0.91419 | -0.065496 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LENEXA 5 | 0.97969 | 0.91419 | -0.065496 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LENEXA 5 | 0.97969 | 0.91419 | -0.065496 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LENEXA 5 | 0.97969 | 0.91419 | -0.065496 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LENEXA 5 | 0.97969 | 0.91419 | -0.065496 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LENEXA 5 | 0.97969 | 0.91419 | -0.065496 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LENEXA 5 | 0.97969 | 0.91419 | -0.065496 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LENEXA 5 | 0.97969 | 0.91419 | -0.065496 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LENEXA 5 | 0.97969 | 0.91419 | -0.065496 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LENEXA 5 | 0.97969 | 0.91419 | -0.065496 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | LENEXA 5 | 0.97969 | 0.91419 | -0.065496 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | LENEXA 5 | 0.97969 | 0.91419 | -0.065496 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LENEXA 5 | 0.97969 | 0.91419 | -0.065496 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LENEXA 5 | 0.97969 | 0.91419 | -0.065496 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | LENEXA 5 | 0.97969 | 0.91419 | -0.065496 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LENEXA 5 | 0.97969 | 0.91419 | -0.065496 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LENEXA 5 | 0.97969 | 0.91419 | -0.065496 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LENEXA 5 | 0.97969 | 0.91419 | -0.065496 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LENEXA 5 | 0.97969 | 0.91419 | -0.065496 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | LENEXA 5 | 0.97969 | 0.91419 | -0.065496 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LEX161 5 | 0.98904 | 0.92961 | -0.05943 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | LEX161 5 | 0.98904 | 0.92961 | -0.05943 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LEX161 5 | 0.98904 | 0.92961 | -0.05943 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LEX161 5 | 0.98904 | 0.92961 | -0.05943 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LEX161 5 | 0.98904 | 0.92961 | -0.05943 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LEX161 5 | 0.98904 | 0.92961 | -0.05943 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LEX161 5 | 0.98904 | 0.92961 | -0.05943 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | LEX161 5 | 0.98904 | 0.92961 | -0.05943 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | LEX161 5 | 0.98904 | 0.92961 | -0.05943 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LEX161 5 | 0.98904 | 0.92961 | -0.05943 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LEX161 5 | 0.98904 | 0.92961 | -0.05943 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LEX161 5 | 0.98904 | 0.92961 | -0.05943 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LEX161 5 | 0.98904 | 0.92961 | -0.05943 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LEX161 5 | 0.98904 | 0.92961 | -0.05943 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LEX161 5 | 0.98904 | 0.92961 | -0.05943 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LEX161 5 | 0.98904 | 0.92961 | -0.05943 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LEX161 5 | 0.98904 | 0.92961 | -0.05943 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LEX161 5 | 0.98904 | 0.92961 | -0.05943 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | LEX161 5 | 0.98904 | 0.92961 | -0.05943 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | LEX161 5 | 0.98904 | 0.92961 | -0.05943 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LEX161 5 | 0.98904 | 0.92961 | -0.05943 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LEX161 5 | 0.98904 | 0.92961 | -0.05943 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | LEX161 5 | 0.98904 | 0.92961 | -0.05943 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LEX161 5 | 0.98904 | 0.92961 | -0.05943 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LEX161 5 | 0.98904 | 0.92961 | -0.05943 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LEX161 5 | 0.98904 | 0.92961 | -0.05943 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LEX161 5 | 0.98904 | 0.92961 | -0.05943 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | LEX161 5 | 0.98904 | 0.92961 | -0.05943 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | LIBERTY4 | 0.95933 | 0.92187 | -0.03745 |  | 0.93 | 1.05 | 0.030148 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LIBERTY4 | 0.95933 | 0.92187 | -0.03745 |  | 0.93 | 1.05 | 0.049467 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | LIBERTY4 | 0.95933 | 0.92187 | -0.03745 |  | 0.93 | 1.05 | 0.058621 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LIBERTY4 | 0.95933 | 0.92187 | -0.03745 |  | 0.93 | 1.05 | 0.082177 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LIBERTY4 | 0.95933 | 0.92187 | -0.03745 |  | 0.93 | 1.05 | 0.087314 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LIBERTY4 | 0.95933 | 0.92187 | -0.03745 |  | 0.93 | 1.05 | 0.048683 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LIBERTY4 | 0.95933 | 0.92187 | -0.03745 |  | 0.93 | 1.05 | 0.11232 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | LIBERTY4 | 0.95933 | 0.92187 | -0.03745 |  | 0.93 | 1.05 | 0.044109 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | LIBERTY4 | 0.95933 | 0.92187 | -0.03745 |  | 0.93 | 1.05 | 0.045565 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LIBERTY4 | 0.95933 | 0.92187 | -0.03745 |  | 0.93 | 1.05 | 0.066779 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LIBERTY4 | 0.95933 | 0.92187 | -0.03745 |  | 0.93 | 1.05 | 0.05473 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LIBERTY4 | 0.95933 | 0.92187 | -0.03745 |  | 0.93 | 1.05 | 0.041831 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LIBERTY4 | 0.95933 | 0.92187 | -0.03745 |  | 0.93 | 1.05 | 0.46658 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | LIBERTY4 | 0.95933 | 0.92187 | -0.03745 |  | 0.93 | 1.05 | 0.030148 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LIBERTY4 | 0.95933 | 0.92187 | -0.03745 |  | 0.93 | 1.05 | 0.041831 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LIBERTY4 | 0.95933 | 0.92187 | -0.03745 |  | 0.93 | 1.05 | 0.040658 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LIBERTY4 | 0.95933 | 0.92187 | -0.03745 |  | 0.93 | 1.05 | 0.043997 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LIBERTY4 | 0.95933 | 0.92187 | -0.03745 |  | 0.93 | 1.05 | 0.068133 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LIBERTY4 | 0.95933 | 0.92187 | -0.03745 |  | 0.93 | 1.05 | 0.068393 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | LIBERTY4 | 0.95933 | 0.92187 | -0.03745 |  | 0.93 | 1.05 | 0.05813 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | LIBERTY4 | 0.95933 | 0.92187 | -0.03745 |  | 0.93 | 1.05 | 0.05813 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LIBERTY4 | 0.95933 | 0.92187 | -0.03745 |  | 0.93 | 1.05 | 0.098736 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LIBERTY4 | 0.95933 | 0.92187 | -0.03745 |  | 0.93 | 1.05 | 0.045332 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | LIBERTY4 | 0.95933 | 0.92187 | -0.03745 |  | 0.93 | 1.05 | 0.044706 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LIBERTY4 | 0.95933 | 0.92187 | -0.03745 |  | 0.93 | 1.05 | 0.063507 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LIBERTY4 | 0.95933 | 0.92187 | -0.03745 |  | 0.93 | 1.05 | 0.048755 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LIBERTY4 | 0.95933 | 0.92187 | -0.03745 |  | 0.93 | 1.05 | 0.060242 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LIBERTY4 | 0.95933 | 0.92187 | -0.03745 |  | 0.93 | 1.05 | 0.041736 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | LIBERTY4 | 0.95933 | 0.92187 | -0.03745 |  | 0.93 | 1.05 | 0.040069 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LIBERTY4 | 0.96168 | 0.92576 | -0.035924 |  | 0.93 | 1.05 | 0.040027 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LIBERTY4 | 0.96168 | 0.92576 | -0.035924 |  | 0.93 | 1.05 | 0.090773 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | LIBERTY4 | 0.96168 | 0.92576 | -0.035924 |  | 0.93 | 1.05 | 0.034521 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | LIBERTY4 | 0.96168 | 0.92576 | -0.035924 |  | 0.93 | 1.05 | 0.038035 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LIBERTY4 | 0.96168 | 0.92576 | -0.035924 |  | 0.93 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LIBERTY4 | 0.96168 | 0.92576 | -0.035924 |  | 0.93 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LIBERTY4 | 0.96168 | 0.92576 | -0.035924 |  | 0.93 | 1.05 | 0.050618 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LIBERTY4 | 0.96168 | 0.92576 | -0.035924 |  | 0.93 | 1.05 | 0.04163 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LIBERTY4 | 0.96168 | 0.92576 | -0.035924 |  | 0.93 | 1.05 | 0.043776 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | LIBERTY4 | 0.96168 | 0.92576 | -0.035924 |  | 0.93 | 1.05 | 0.034868 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LIBERTY4 | 0.96168 | 0.92576 | -0.035924 |  | 0.93 | 1.05 | 0.031975 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LIBERTY4 | 0.96168 | 0.92576 | -0.035924 |  | 0.93 | 1.05 | 0.037422 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LIBERTY4 | 0.96168 | 0.92576 | -0.035924 |  | 0.93 | 1.05 | 0.050095 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LIBERTY4 | 0.95804 | 0.91689 | -0.041151 |  | 0.93 | 1.05 | 0.094783 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | LIBERTY4 | 0.95804 | 0.91689 | -0.041151 |  | 0.93 | 1.05 | 0.03645 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LIBERTY4 | 0.95804 | 0.91689 | -0.041151 |  | 0.93 | 1.05 | 0.04755 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LIBERTY4 | 0.95804 | 0.91689 | -0.041151 |  | 0.93 | 1.05 | 0.06097 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LIBERTY4 | 0.95804 | 0.91689 | -0.041151 |  | 0.93 | 1.05 | 0.061051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | LIBERTY4 | 0.95804 | 0.91689 | -0.041151 |  | 0.93 | 1.05 | 0.04456 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | LIBERTY4 | 0.95804 | 0.91689 | -0.041151 |  | 0.93 | 1.05 | 0.048811 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LIBERTY4 | 0.95804 | 0.91689 | -0.041151 |  | 0.93 | 1.05 | 0.13004 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LIBERTY4 | 0.95804 | 0.91689 | -0.041151 |  | 0.93 | 1.05 | 0.049018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LIBERTY4 | 0.95804 | 0.91689 | -0.041151 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LIBERTY4 | 0.95804 | 0.91689 | -0.041151 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LIBERTY4 | 0.95804 | 0.91689 | -0.041151 |  | 0.93 | 1.05 | 0.05974 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LIBERTY4 | 0.95804 | 0.91689 | -0.041151 |  | 0.93 | 1.05 | 0.076949 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LIBERTY4 | 0.95804 | 0.91689 | -0.041151 |  | 0.93 | 1.05 | 0.042157 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LIBERTY4 | 0.95804 | 0.91689 | -0.041151 |  | 0.93 | 1.05 | 0.040957 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | LIBERTY4 | 0.95804 | 0.91689 | -0.041151 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | LIBERTY4 | 0.95804 | 0.91689 | -0.041151 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LIBERTY4 | 0.95804 | 0.91689 | -0.041151 |  | 0.93 | 1.05 | 0.054637 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LIBERTY4 | 0.95804 | 0.91689 | -0.041151 |  | 0.93 | 1.05 | 0.060597 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | LIBERTY4 | 0.95804 | 0.91689 | -0.041151 |  | 0.93 | 1.05 | 0.044286 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LIBERTY4 | 0.95804 | 0.91689 | -0.041151 |  | 0.93 | 1.05 | 0.059107 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LIBERTY4 | 0.95804 | 0.91689 | -0.041151 |  | 0.93 | 1.05 | 0.052698 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LIBERTY4 | 0.95804 | 0.91689 | -0.041151 |  | 0.93 | 1.05 | 0.067422 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LIBERTY4 | 0.95804 | 0.91689 | -0.041151 |  | 0.93 | 1.05 | 0.053768 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | LIBERTY4 | 0.95804 | 0.91689 | -0.041151 |  | 0.93 | 1.05 | 0.03909 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LIBERTY4 | 0.97046 | 0.94976 | -0.020697 |  | 0.95 | 1.05 | 0.14254 | System Intact | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LIBERTY4 | 0.95854 | 0.92329 | -0.035245 |  | 0.93 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | LIBERTY4 | 0.95854 | 0.92329 | -0.035245 |  | 0.93 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LIBERTY4 | 0.95854 | 0.92329 | -0.035245 |  | 0.93 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LIBERTY4 | 0.95854 | 0.92329 | -0.035245 |  | 0.93 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LIBERTY4 | 0.95854 | 0.92329 | -0.035245 |  | 0.93 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LIBERTY4 | 0.95854 | 0.92329 | -0.035245 |  | 0.93 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LIBERTY4 | 0.95854 | 0.92329 | -0.035245 |  | 0.93 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | LIBERTY4 | 0.95854 | 0.92329 | -0.035245 |  | 0.93 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LIBERTY4 | 0.95854 | 0.92329 | -0.035245 |  | 0.93 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LIBERTY4 | 0.95854 | 0.92329 | -0.035245 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LIBERTY4 | 0.95854 | 0.92329 | -0.035245 |  | 0.93 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LIBERTY4 | 0.95854 | 0.92329 | -0.035245 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LIBERTY4 | 0.95854 | 0.92329 | -0.035245 |  | 0.93 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LIBERTY4 | 0.95854 | 0.92329 | -0.035245 |  | 0.93 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LIBERTY4 | 0.95854 | 0.92329 | -0.035245 |  | 0.93 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LIBERTY4 | 0.95854 | 0.92329 | -0.035245 |  | 0.93 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LIBERTY4 | 0.95854 | 0.92329 | -0.035245 |  | 0.93 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LIBERTY4 | 0.95854 | 0.92329 | -0.035245 |  | 0.93 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LIBERTY4 | 0.95854 | 0.92329 | -0.035245 |  | 0.93 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LIBERTY4 | 0.95854 | 0.92329 | -0.035245 |  | 0.93 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LIBERTY4 | 0.95854 | 0.92329 | -0.035245 |  | 0.93 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LIBERTY4 | 0.95854 | 0.92329 | -0.035245 |  | 0.93 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LIBERTY4 | 0.96104 | 0.91494 | -0.046104 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | LIBERTY4 | 0.96104 | 0.91494 | -0.046104 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LIBERTY4 | 0.96104 | 0.91494 | -0.046104 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LIBERTY4 | 0.96104 | 0.91494 | -0.046104 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LIBERTY4 | 0.96104 | 0.91494 | -0.046104 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LIBERTY4 | 0.96104 | 0.91494 | -0.046104 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LIBERTY4 | 0.96104 | 0.91494 | -0.046104 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | LIBERTY4 | 0.96104 | 0.91494 | -0.046104 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | LIBERTY4 | 0.96104 | 0.91494 | -0.046104 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LIBERTY4 | 0.96104 | 0.91494 | -0.046104 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LIBERTY4 | 0.96104 | 0.91494 | -0.046104 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LIBERTY4 | 0.96104 | 0.91494 | -0.046104 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LIBERTY4 | 0.96104 | 0.91494 | -0.046104 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LIBERTY4 | 0.96104 | 0.91494 | -0.046104 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LIBERTY4 | 0.96104 | 0.91494 | -0.046104 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LIBERTY4 | 0.96104 | 0.91494 | -0.046104 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LIBERTY4 | 0.96104 | 0.91494 | -0.046104 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LIBERTY4 | 0.96104 | 0.91494 | -0.046104 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | LIBERTY4 | 0.96104 | 0.91494 | -0.046104 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | LIBERTY4 | 0.96104 | 0.91494 | -0.046104 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LIBERTY4 | 0.96104 | 0.91494 | -0.046104 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LIBERTY4 | 0.96104 | 0.91494 | -0.046104 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | LIBERTY4 | 0.96104 | 0.91494 | -0.046104 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LIBERTY4 | 0.96104 | 0.91494 | -0.046104 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LIBERTY4 | 0.96104 | 0.91494 | -0.046104 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LIBERTY4 | 0.96104 | 0.91494 | -0.046104 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LIBERTY4 | 0.96104 | 0.91494 | -0.046104 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | LIBERTY4 | 0.96104 | 0.91494 | -0.046104 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LITTLEBLUEW3 | 0.9694 | 0.89748 | -0.07192 |  | 0.9 | 1.05 | 0.0326 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LITTLEBLUEW3 | 0.9694 | 0.89748 | -0.07192 |  | 0.9 | 1.05 | 0.030348 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LITTLEBLUEW3 | 0.9694 | 0.89748 | -0.07192 |  | 0.9 | 1.05 | 0.031036 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LITTLEBLUEW3 | 0.9694 | 0.89748 | -0.07192 |  | 0.9 | 1.05 | 0.030059 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LITTLEBLUEW3 | 0.9694 | 0.89748 | -0.07192 |  | 0.9 | 1.05 | 0.030059 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LITTLEBLUEW3 | 0.9694 | 0.89748 | -0.07192 |  | 0.9 | 1.05 | 0.030771 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LITTLEBLUEW3 | 0.9694 | 0.89748 | -0.07192 |  | 0.9 | 1.05 | 0.030685 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LKWOOD 5 | 0.9915 | 0.92868 | -0.062827 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | LKWOOD 5 | 0.9915 | 0.92868 | -0.062827 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LKWOOD 5 | 0.9915 | 0.92868 | -0.062827 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LKWOOD 5 | 0.9915 | 0.92868 | -0.062827 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LKWOOD 5 | 0.9915 | 0.92868 | -0.062827 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LKWOOD 5 | 0.9915 | 0.92868 | -0.062827 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LKWOOD 5 | 0.9915 | 0.92868 | -0.062827 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | LKWOOD 5 | 0.9915 | 0.92868 | -0.062827 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | LKWOOD 5 | 0.9915 | 0.92868 | -0.062827 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LKWOOD 5 | 0.9915 | 0.92868 | -0.062827 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LKWOOD 5 | 0.9915 | 0.92868 | -0.062827 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LKWOOD 5 | 0.9915 | 0.92868 | -0.062827 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LKWOOD 5 | 0.9915 | 0.92868 | -0.062827 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LKWOOD 5 | 0.9915 | 0.92868 | -0.062827 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LKWOOD 5 | 0.9915 | 0.92868 | -0.062827 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LKWOOD 5 | 0.9915 | 0.92868 | -0.062827 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LKWOOD 5 | 0.9915 | 0.92868 | -0.062827 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LKWOOD 5 | 0.9915 | 0.92868 | -0.062827 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | LKWOOD 5 | 0.9915 | 0.92868 | -0.062827 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | LKWOOD 5 | 0.9915 | 0.92868 | -0.062827 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LKWOOD 5 | 0.9915 | 0.92868 | -0.062827 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LKWOOD 5 | 0.9915 | 0.92868 | -0.062827 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | LKWOOD 5 | 0.9915 | 0.92868 | -0.062827 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LKWOOD 5 | 0.9915 | 0.92868 | -0.062827 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LKWOOD 5 | 0.9915 | 0.92868 | -0.062827 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LKWOOD 5 | 0.9915 | 0.92868 | -0.062827 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LKWOOD 5 | 0.9915 | 0.92868 | -0.062827 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | LKWOOD 5 | 0.9915 | 0.92868 | -0.062827 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LNGVW 5 | 0.99687 | 0.92783 | -0.069035 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | LNGVW 5 | 0.99687 | 0.92783 | -0.069035 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LNGVW 5 | 0.99687 | 0.92783 | -0.069035 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LNGVW 5 | 0.99687 | 0.92783 | -0.069035 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LNGVW 5 | 0.99687 | 0.92783 | -0.069035 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LNGVW 5 | 0.99687 | 0.92783 | -0.069035 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LNGVW 5 | 0.99687 | 0.92783 | -0.069035 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | LNGVW 5 | 0.99687 | 0.92783 | -0.069035 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | LNGVW 5 | 0.99687 | 0.92783 | -0.069035 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LNGVW 5 | 0.99687 | 0.92783 | -0.069035 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LNGVW 5 | 0.99687 | 0.92783 | -0.069035 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LNGVW 5 | 0.99687 | 0.92783 | -0.069035 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LNGVW 5 | 0.99687 | 0.92783 | -0.069035 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LNGVW 5 | 0.99687 | 0.92783 | -0.069035 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LNGVW 5 | 0.99687 | 0.92783 | -0.069035 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LNGVW 5 | 0.99687 | 0.92783 | -0.069035 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LNGVW 5 | 0.99687 | 0.92783 | -0.069035 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LNGVW 5 | 0.99687 | 0.92783 | -0.069035 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | LNGVW 5 | 0.99687 | 0.92783 | -0.069035 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | LNGVW 5 | 0.99687 | 0.92783 | -0.069035 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LNGVW 5 | 0.99687 | 0.92783 | -0.069035 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LNGVW 5 | 0.99687 | 0.92783 | -0.069035 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | LNGVW 5 | 0.99687 | 0.92783 | -0.069035 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LNGVW 5 | 0.99687 | 0.92783 | -0.069035 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LNGVW 5 | 0.99687 | 0.92783 | -0.069035 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LNGVW 5 | 0.99687 | 0.92783 | -0.069035 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LNGVW 5 | 0.99687 | 0.92783 | -0.069035 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | LNGVW 5 | 0.99687 | 0.92783 | -0.069035 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LUDELL 3 | 0.95722 | 0.89362 | -0.063601 |  | 0.9 | 1.05 | 0.041569 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LUDELL 3 | 0.95722 | 0.89362 | -0.063601 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LUDELL 3 | 0.95722 | 0.89362 | -0.063601 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LUDELL 3 | 0.95722 | 0.89362 | -0.063601 |  | 0.9 | 1.05 | 0.03222 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LUDELL 3 | 0.95722 | 0.89362 | -0.063601 |  | 0.9 | 1.05 | 0.030633 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LUDELL 3 | 0.95722 | 0.89362 | -0.063601 |  | 0.9 | 1.05 | 0.030061 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LUDELL 3 | 0.95722 | 0.89362 | -0.063601 |  | 0.9 | 1.05 | 0.031207 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LUDELL 3 | 0.95948 | 0.89428 | -0.065201 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LUDELL 3 | 0.95948 | 0.89428 | -0.065201 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LUDELL 3 | 0.96008 | 0.89046 | -0.069625 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LUDELL 3 | 0.96008 | 0.89046 | -0.069625 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LUDELL 3 | 0.96008 | 0.89046 | -0.069625 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LUDELL 3 | 0.96008 | 0.89046 | -0.069625 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LUDELL 3 | 0.96009 | 0.89046 | -0.069626 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LUDELL 3 | 0.96009 | 0.89046 | -0.069626 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LUDELLT3 | 0.95723 | 0.89363 | -0.063601 |  | 0.9 | 1.05 | 0.041569 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LUDELLT3 | 0.95723 | 0.89363 | -0.063601 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LUDELLT3 | 0.95723 | 0.89363 | -0.063601 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LUDELLT3 | 0.95723 | 0.89363 | -0.063601 |  | 0.9 | 1.05 | 0.03222 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LUDELLT3 | 0.95723 | 0.89363 | -0.063601 |  | 0.9 | 1.05 | 0.030633 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LUDELLT3 | 0.95723 | 0.89363 | -0.063601 |  | 0.9 | 1.05 | 0.030061 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LUDELLT3 | 0.95723 | 0.89363 | -0.063601 |  | 0.9 | 1.05 | 0.031207 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LUDELLT3 | 0.95948 | 0.89428 | -0.065201 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LUDELLT3 | 0.95948 | 0.89428 | -0.065201 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LUDELLT3 | 0.96009 | 0.89047 | -0.069625 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LUDELLT3 | 0.96009 | 0.89047 | -0.069625 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LUDELLT3 | 0.96009 | 0.89047 | -0.069625 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LUDELLT3 | 0.96009 | 0.89047 | -0.069625 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LUDELLT3 | 0.96009 | 0.89047 | -0.069626 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LUDELLT3 | 0.96009 | 0.89047 | -0.069626 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | LVISTA 5 | 0.99025 | 0.92575 | -0.064506 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | LVISTA 5 | 0.99025 | 0.92575 | -0.064506 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | LVISTA 5 | 0.99025 | 0.92575 | -0.064506 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | LVISTA 5 | 0.99025 | 0.92575 | -0.064506 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | LVISTA 5 | 0.99025 | 0.92575 | -0.064506 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | LVISTA 5 | 0.99025 | 0.92575 | -0.064506 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | LVISTA 5 | 0.99025 | 0.92575 | -0.064506 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | LVISTA 5 | 0.99025 | 0.92575 | -0.064506 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | LVISTA 5 | 0.99025 | 0.92575 | -0.064506 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | LVISTA 5 | 0.99025 | 0.92575 | -0.064506 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | LVISTA 5 | 0.99025 | 0.92575 | -0.064506 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | LVISTA 5 | 0.99025 | 0.92575 | -0.064506 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | LVISTA 5 | 0.99025 | 0.92575 | -0.064506 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | LVISTA 5 | 0.99025 | 0.92575 | -0.064506 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | LVISTA 5 | 0.99025 | 0.92575 | -0.064506 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | LVISTA 5 | 0.99025 | 0.92575 | -0.064506 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | LVISTA 5 | 0.99025 | 0.92575 | -0.064506 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | LVISTA 5 | 0.99025 | 0.92575 | -0.064506 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | LVISTA 5 | 0.99025 | 0.92575 | -0.064506 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | LVISTA 5 | 0.99025 | 0.92575 | -0.064506 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | LVISTA 5 | 0.99025 | 0.92575 | -0.064506 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | LVISTA 5 | 0.99025 | 0.92575 | -0.064506 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | LVISTA 5 | 0.99025 | 0.92575 | -0.064506 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | LVISTA 5 | 0.99025 | 0.92575 | -0.064506 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | LVISTA 5 | 0.99025 | 0.92575 | -0.064506 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | LVISTA 5 | 0.99025 | 0.92575 | -0.064506 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | LVISTA 5 | 0.99025 | 0.92575 | -0.064506 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | LVISTA 5 | 0.99025 | 0.92575 | -0.064506 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | MACON 3 | 0.98094 | 0.93254 | -0.048401 |  | 0.95 | 1.05 | 0.041569 | System Intact | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MACON 3 | 0.98094 | 0.93254 | -0.048401 |  | 0.95 | 1.05 | 0.031515 | System Intact | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MACON 3 | 0.98094 | 0.93254 | -0.048401 |  | 0.95 | 1.05 | 0.031515 | System Intact | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MACON 3 | 0.98094 | 0.93254 | -0.048401 |  | 0.95 | 1.05 | 0.03222 | System Intact | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MACON 3 | 0.98094 | 0.93254 | -0.048401 |  | 0.95 | 1.05 | 0.030633 | System Intact | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MACON 3 | 0.98094 | 0.93254 | -0.048401 |  | 0.95 | 1.05 | 0.030061 | System Intact | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MACON 3 | 0.98094 | 0.93254 | -0.048401 |  | 0.95 | 1.05 | 0.031207 | System Intact | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MACON 3 | 0.96554 | 0.89048 | -0.075061 |  | 0.9 | 1.05 | 0.0326 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | MACON 3 | 0.96554 | 0.89048 | -0.075061 |  | 0.9 | 1.05 | 0.030348 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MACON 3 | 0.96554 | 0.89048 | -0.075061 |  | 0.9 | 1.05 | 0.031036 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MACON 3 | 0.96554 | 0.89048 | -0.075061 |  | 0.9 | 1.05 | 0.030059 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MACON 3 | 0.96554 | 0.89048 | -0.075061 |  | 0.9 | 1.05 | 0.030059 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MACON 3 | 0.96554 | 0.89048 | -0.075061 |  | 0.9 | 1.05 | 0.030771 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MACON 3 | 0.96554 | 0.89048 | -0.075061 |  | 0.9 | 1.05 | 0.030685 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | MACON 3 | 0.97101 | 0.89905 | -0.07196 |  | 0.9 | 1.05 | 0.064516 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | MANNING3 | 0.96482 | 0.89937 | -0.065449 |  | 0.9 | 1.05 | 0.045977 | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | Add 1 MVAR switched shunt at DIGHTON3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | MANNING3 | 0.96482 | 0.89937 | -0.065449 |  | 0.9 | 1.05 | 0.045977 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Add 1 MVAR switched shunt at DIGHTON3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MARTCIT5 | 0.98407 | 0.90631 | -0.077757 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | MARTCIT5 | 0.98407 | 0.90631 | -0.077757 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MARTCIT5 | 0.98407 | 0.90631 | -0.077757 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MARTCIT5 | 0.98407 | 0.90631 | -0.077757 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MARTCIT5 | 0.98407 | 0.90631 | -0.077757 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | MARTCIT5 | 0.98407 | 0.90631 | -0.077757 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MARTCIT5 | 0.98407 | 0.90631 | -0.077757 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | MARTCIT5 | 0.98407 | 0.90631 | -0.077757 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | MARTCIT5 | 0.98407 | 0.90631 | -0.077757 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MARTCIT5 | 0.98407 | 0.90631 | -0.077757 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MARTCIT5 | 0.98407 | 0.90631 | -0.077757 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MARTCIT5 | 0.98407 | 0.90631 | -0.077757 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MARTCIT5 | 0.98407 | 0.90631 | -0.077757 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MARTCIT5 | 0.98407 | 0.90631 | -0.077757 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MARTCIT5 | 0.98407 | 0.90631 | -0.077757 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MARTCIT5 | 0.98407 | 0.90631 | -0.077757 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MARTCIT5 | 0.98407 | 0.90631 | -0.077757 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MARTCIT5 | 0.98407 | 0.90631 | -0.077757 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | MARTCIT5 | 0.98407 | 0.90631 | -0.077757 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | MARTCIT5 | 0.98407 | 0.90631 | -0.077757 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MARTCIT5 | 0.98407 | 0.90631 | -0.077757 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MARTCIT5 | 0.98407 | 0.90631 | -0.077757 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | MARTCIT5 | 0.98407 | 0.90631 | -0.077757 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MARTCIT5 | 0.98407 | 0.90631 | -0.077757 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MARTCIT5 | 0.98407 | 0.90631 | -0.077757 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MARTCIT5 | 0.98407 | 0.90631 | -0.077757 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MARTCIT5 | 0.98407 | 0.90631 | -0.077757 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | MARTCIT5 | 0.98407 | 0.90631 | -0.077757 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MARTCTY5 | 0.98486 | 0.90907 | -0.075792 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | MARTCTY5 | 0.98486 | 0.90907 | -0.075792 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MARTCTY5 | 0.98486 | 0.90907 | -0.075792 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MARTCTY5 | 0.98486 | 0.90907 | -0.075792 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MARTCTY5 | 0.98486 | 0.90907 | -0.075792 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | MARTCTY5 | 0.98486 | 0.90907 | -0.075792 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MARTCTY5 | 0.98486 | 0.90907 | -0.075792 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | MARTCTY5 | 0.98486 | 0.90907 | -0.075792 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | MARTCTY5 | 0.98486 | 0.90907 | -0.075792 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MARTCTY5 | 0.98486 | 0.90907 | -0.075792 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MARTCTY5 | 0.98486 | 0.90907 | -0.075792 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MARTCTY5 | 0.98486 | 0.90907 | -0.075792 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MARTCTY5 | 0.98486 | 0.90907 | -0.075792 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MARTCTY5 | 0.98486 | 0.90907 | -0.075792 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MARTCTY5 | 0.98486 | 0.90907 | -0.075792 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MARTCTY5 | 0.98486 | 0.90907 | -0.075792 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MARTCTY5 | 0.98486 | 0.90907 | -0.075792 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MARTCTY5 | 0.98486 | 0.90907 | -0.075792 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | MARTCTY5 | 0.98486 | 0.90907 | -0.075792 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | MARTCTY5 | 0.98486 | 0.90907 | -0.075792 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MARTCTY5 | 0.98486 | 0.90907 | -0.075792 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MARTCTY5 | 0.98486 | 0.90907 | -0.075792 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | MARTCTY5 | 0.98486 | 0.90907 | -0.075792 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MARTCTY5 | 0.98486 | 0.90907 | -0.075792 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MARTCTY5 | 0.98486 | 0.90907 | -0.075792 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MARTCTY5 | 0.98486 | 0.90907 | -0.075792 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MARTCTY5 | 0.98486 | 0.90907 | -0.075792 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | MARTCTY5 | 0.98486 | 0.90907 | -0.075792 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | MCDONLD3 | 0.95766 | 0.88991 | -0.067755 |  | 0.9 | 1.05 | 0.041569 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MCDONLD3 | 0.95766 | 0.88991 | -0.067755 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MCDONLD3 | 0.95766 | 0.88991 | -0.067755 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MCDONLD3 | 0.95766 | 0.88991 | -0.067755 |  | 0.9 | 1.05 | 0.03222 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MCDONLD3 | 0.95766 | 0.88991 | -0.067755 |  | 0.9 | 1.05 | 0.030633 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MCDONLD3 | 0.95766 | 0.88991 | -0.067755 |  | 0.9 | 1.05 | 0.030061 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MCDONLD3 | 0.95766 | 0.88991 | -0.067755 |  | 0.9 | 1.05 | 0.031207 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | MCDONLD3 | 0.95477 | 0.88604 | -0.06873 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MCDONLD3 | 0.95477 | 0.88604 | -0.06873 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | MCDONLD3 | 0.95478 | 0.87996 | -0.074822 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MCDONLD3 | 0.95478 | 0.87996 | -0.074822 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | MCDONLD3 | 0.95478 | 0.87996 | -0.074822 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MCDONLD3 | 0.95478 | 0.87996 | -0.074822 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | MCDONLD3 | 0.95479 | 0.87996 | -0.074823 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MCDONLD3 | 0.95479 | 0.87996 | -0.074823 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MERRIAM5 | 0.97993 | 0.9156 | -0.064331 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | MERRIAM5 | 0.97993 | 0.9156 | -0.064331 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MERRIAM5 | 0.97993 | 0.9156 | -0.064331 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MERRIAM5 | 0.97993 | 0.9156 | -0.064331 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MERRIAM5 | 0.97993 | 0.9156 | -0.064331 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | MERRIAM5 | 0.97993 | 0.9156 | -0.064331 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MERRIAM5 | 0.97993 | 0.9156 | -0.064331 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | MERRIAM5 | 0.97993 | 0.9156 | -0.064331 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | MERRIAM5 | 0.97993 | 0.9156 | -0.064331 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MERRIAM5 | 0.97993 | 0.9156 | -0.064331 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MERRIAM5 | 0.97993 | 0.9156 | -0.064331 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MERRIAM5 | 0.97993 | 0.9156 | -0.064331 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MERRIAM5 | 0.97993 | 0.9156 | -0.064331 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MERRIAM5 | 0.97993 | 0.9156 | -0.064331 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MERRIAM5 | 0.97993 | 0.9156 | -0.064331 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MERRIAM5 | 0.97993 | 0.9156 | -0.064331 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MERRIAM5 | 0.97993 | 0.9156 | -0.064331 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MERRIAM5 | 0.97993 | 0.9156 | -0.064331 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | MERRIAM5 | 0.97993 | 0.9156 | -0.064331 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | MERRIAM5 | 0.97993 | 0.9156 | -0.064331 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MERRIAM5 | 0.97993 | 0.9156 | -0.064331 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MERRIAM5 | 0.97993 | 0.9156 | -0.064331 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | MERRIAM5 | 0.97993 | 0.9156 | -0.064331 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MERRIAM5 | 0.97993 | 0.9156 | -0.064331 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MERRIAM5 | 0.97993 | 0.9156 | -0.064331 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MERRIAM5 | 0.97993 | 0.9156 | -0.064331 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MERRIAM5 | 0.97993 | 0.9156 | -0.064331 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | MERRIAM5 | 0.97993 | 0.9156 | -0.064331 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MERRIAM_CAP5 | 0.98101 | 0.9166 | -0.064401 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | MERRIAM_CAP5 | 0.98101 | 0.9166 | -0.064401 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MERRIAM_CAP5 | 0.98101 | 0.9166 | -0.064401 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MERRIAM_CAP5 | 0.98101 | 0.9166 | -0.064401 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MERRIAM_CAP5 | 0.98101 | 0.9166 | -0.064401 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | MERRIAM_CAP5 | 0.98101 | 0.9166 | -0.064401 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MERRIAM_CAP5 | 0.98101 | 0.9166 | -0.064401 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | MERRIAM_CAP5 | 0.98101 | 0.9166 | -0.064401 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | MERRIAM_CAP5 | 0.98101 | 0.9166 | -0.064401 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MERRIAM_CAP5 | 0.98101 | 0.9166 | -0.064401 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MERRIAM_CAP5 | 0.98101 | 0.9166 | -0.064401 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MERRIAM_CAP5 | 0.98101 | 0.9166 | -0.064401 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MERRIAM_CAP5 | 0.98101 | 0.9166 | -0.064401 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MERRIAM_CAP5 | 0.98101 | 0.9166 | -0.064401 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MERRIAM_CAP5 | 0.98101 | 0.9166 | -0.064401 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MERRIAM_CAP5 | 0.98101 | 0.9166 | -0.064401 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MERRIAM_CAP5 | 0.98101 | 0.9166 | -0.064401 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MERRIAM_CAP5 | 0.98101 | 0.9166 | -0.064401 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | MERRIAM_CAP5 | 0.98101 | 0.9166 | -0.064401 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | MERRIAM_CAP5 | 0.98101 | 0.9166 | -0.064401 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MERRIAM_CAP5 | 0.98101 | 0.9166 | -0.064401 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MERRIAM_CAP5 | 0.98101 | 0.9166 | -0.064401 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | MERRIAM_CAP5 | 0.98101 | 0.9166 | -0.064401 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MERRIAM_CAP5 | 0.98101 | 0.9166 | -0.064401 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MERRIAM_CAP5 | 0.98101 | 0.9166 | -0.064401 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MERRIAM_CAP5 | 0.98101 | 0.9166 | -0.064401 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MERRIAM_CAP5 | 0.98101 | 0.9166 | -0.064401 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | MERRIAM_CAP5 | 0.98101 | 0.9166 | -0.064401 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MIDLAND6 | 0.9807 | 0.94538 | -0.035321 |  | 0.95 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MIDLAND6 | 0.9807 | 0.94538 | -0.035321 |  | 0.95 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MIDLAND6 | 0.9807 | 0.94538 | -0.035321 |  | 0.95 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MIDLAND6 | 0.9807 | 0.94538 | -0.035321 |  | 0.95 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MIDLAND6 | 0.9807 | 0.94538 | -0.035321 |  | 0.95 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MIDLAND6 | 0.9807 | 0.94538 | -0.035321 |  | 0.95 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MIDLAND6 | 0.9807 | 0.94538 | -0.035321 |  | 0.95 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MIDLAND6 | 0.9807 | 0.94538 | -0.035321 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MIDLAND6 | 0.9807 | 0.94538 | -0.035321 |  | 0.95 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MIDLAND6 | 0.9807 | 0.94538 | -0.035321 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MIDLAND6 | 0.9807 | 0.94538 | -0.035321 |  | 0.95 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MIDLAND6 | 0.9807 | 0.94538 | -0.035321 |  | 0.95 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MIDLAND6 | 0.9807 | 0.94538 | -0.035321 |  | 0.95 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MIDLAND6 | 0.9807 | 0.94538 | -0.035321 |  | 0.95 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MIDLAND6 | 0.9807 | 0.94538 | -0.035321 |  | 0.95 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MIDLAND6 | 0.9807 | 0.94538 | -0.035321 |  | 0.95 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MIDLAND6 | 0.9807 | 0.94538 | -0.035321 |  | 0.95 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MIDLAND6 | 0.9807 | 0.94538 | -0.035321 |  | 0.95 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MIDLAND6 | 0.9807 | 0.94538 | -0.035321 |  | 0.95 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MIDLAND6 | 0.9807 | 0.94538 | -0.035321 |  | 0.95 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MIDLAND6 | 0.97799 | 0.93651 | -0.041476 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MIDLAND6 | 0.97799 | 0.93651 | -0.041476 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MIDLAND6 | 0.97799 | 0.93651 | -0.041476 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MIDLAND6 | 0.97799 | 0.93651 | -0.041476 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MIDLAND6 | 0.97799 | 0.93651 | -0.041476 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MIDLAND6 | 0.97799 | 0.93651 | -0.041476 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MIDLAND6 | 0.97799 | 0.93651 | -0.041476 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MIDLAND6 | 0.97799 | 0.93651 | -0.041476 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MIDLAND6 | 0.97799 | 0.93651 | -0.041476 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MIDLAND6 | 0.97799 | 0.93651 | -0.041476 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MIDLAND6 | 0.97799 | 0.93651 | -0.041476 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MIDLAND6 | 0.97799 | 0.93651 | -0.041476 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MIDLAND6 | 0.97799 | 0.93651 | -0.041476 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MIDLAND6 | 0.97799 | 0.93651 | -0.041476 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MIDLAND6 | 0.97799 | 0.93651 | -0.041476 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MIDLAND6 | 0.97799 | 0.93651 | -0.041476 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MIDLAND6 | 0.97799 | 0.93651 | -0.041476 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MIDLAND6 | 0.97799 | 0.93651 | -0.041476 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MIDLAND6 | 0.97799 | 0.93651 | -0.041476 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MIDLAND6 | 0.97799 | 0.93651 | -0.041476 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MIDLAND6 | 0.98266 | 0.93901 | -0.043647 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MIDLAND6 | 0.98266 | 0.93901 | -0.043647 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MIDLAND6 | 0.98266 | 0.93901 | -0.043647 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MIDLAND6 | 0.98266 | 0.93901 | -0.043647 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MIDLAND6 | 0.98266 | 0.93901 | -0.043647 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MIDLAND6 | 0.98266 | 0.93901 | -0.043647 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MIDLAND6 | 0.98266 | 0.93901 | -0.043647 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MIDLAND6 | 0.98266 | 0.93901 | -0.043647 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MIDLAND6 | 0.98266 | 0.93901 | -0.043647 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MIDLAND6 | 0.98266 | 0.93901 | -0.043647 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MIDLAND6 | 0.98266 | 0.93901 | -0.043647 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MIDLAND6 | 0.98266 | 0.93901 | -0.043647 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MIDLAND6 | 0.98266 | 0.93901 | -0.043647 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MIDLAND6 | 0.98266 | 0.93901 | -0.043647 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MIDLAND6 | 0.98266 | 0.93901 | -0.043647 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MIDLAND6 | 0.98266 | 0.93901 | -0.043647 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MIDLAND6 | 0.98266 | 0.93901 | -0.043647 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MIDLAND6 | 0.98266 | 0.93901 | -0.043647 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MIDLAND6 | 0.98266 | 0.93901 | -0.043647 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MIDLAND6 | 0.98266 | 0.93901 | -0.043647 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MIDLAND6 | 0.98891 | 0.94141 | -0.047505 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | MIDLAND6 | 0.98891 | 0.94141 | -0.047505 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MIDLAND6 | 0.98891 | 0.94141 | -0.047505 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MIDLAND6 | 0.98891 | 0.94141 | -0.047505 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MIDLAND6 | 0.98891 | 0.94141 | -0.047505 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | MIDLAND6 | 0.98891 | 0.94141 | -0.047505 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MIDLAND6 | 0.98891 | 0.94141 | -0.047505 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | MIDLAND6 | 0.98891 | 0.94141 | -0.047505 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | MIDLAND6 | 0.98891 | 0.94141 | -0.047505 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MIDLAND6 | 0.98891 | 0.94141 | -0.047505 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MIDLAND6 | 0.98891 | 0.94141 | -0.047505 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MIDLAND6 | 0.98891 | 0.94141 | -0.047505 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MIDLAND6 | 0.98891 | 0.94141 | -0.047505 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MIDLAND6 | 0.98891 | 0.94141 | -0.047505 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MIDLAND6 | 0.98891 | 0.94141 | -0.047505 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MIDLAND6 | 0.98891 | 0.94141 | -0.047505 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MIDLAND6 | 0.98891 | 0.94141 | -0.047505 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MIDLAND6 | 0.98891 | 0.94141 | -0.047505 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | MIDLAND6 | 0.98891 | 0.94141 | -0.047505 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | MIDLAND6 | 0.98891 | 0.94141 | -0.047505 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MIDLAND6 | 0.98891 | 0.94141 | -0.047505 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MIDLAND6 | 0.98891 | 0.94141 | -0.047505 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | MIDLAND6 | 0.98891 | 0.94141 | -0.047505 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MIDLAND6 | 0.98891 | 0.94141 | -0.047505 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MIDLAND6 | 0.98891 | 0.94141 | -0.047505 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MIDLAND6 | 0.98891 | 0.94141 | -0.047505 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MIDLAND6 | 0.98891 | 0.94141 | -0.047505 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | MIDLAND6 | 0.98891 | 0.94141 | -0.047505 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MIDLAND6 | 0.9804 | 0.94398 | -0.036416 |  | 0.95 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MIDLAND6 | 0.9804 | 0.94398 | -0.036416 |  | 0.95 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MIDLAND6 | 0.9804 | 0.94398 | -0.036416 |  | 0.95 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MIDLAND6 | 0.9804 | 0.94398 | -0.036416 |  | 0.95 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MIDLAND6 | 0.9804 | 0.94398 | -0.036416 |  | 0.95 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MIDLAND6 | 0.9804 | 0.94398 | -0.036416 |  | 0.95 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MIDLAND6 | 0.9804 | 0.94398 | -0.036416 |  | 0.95 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MIDLAND6 | 0.9804 | 0.94398 | -0.036416 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MIDLAND6 | 0.9804 | 0.94398 | -0.036416 |  | 0.95 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MIDLAND6 | 0.9804 | 0.94398 | -0.036416 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MIDLAND6 | 0.9804 | 0.94398 | -0.036416 |  | 0.95 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MIDLAND6 | 0.9804 | 0.94398 | -0.036416 |  | 0.95 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MIDLAND6 | 0.9804 | 0.94398 | -0.036416 |  | 0.95 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MIDLAND6 | 0.9804 | 0.94398 | -0.036416 |  | 0.95 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MIDLAND6 | 0.9804 | 0.94398 | -0.036416 |  | 0.95 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MIDLAND6 | 0.9804 | 0.94398 | -0.036416 |  | 0.95 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MIDLAND6 | 0.9804 | 0.94398 | -0.036416 |  | 0.95 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MIDLAND6 | 0.9804 | 0.94398 | -0.036416 |  | 0.95 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MIDLAND6 | 0.9804 | 0.94398 | -0.036416 |  | 0.95 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MIDLAND6 | 0.9804 | 0.94398 | -0.036416 |  | 0.95 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MIDTOWN5 | 0.98717 | 0.9253 | -0.061869 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | MIDTOWN5 | 0.98717 | 0.9253 | -0.061869 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MIDTOWN5 | 0.98717 | 0.9253 | -0.061869 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MIDTOWN5 | 0.98717 | 0.9253 | -0.061869 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MIDTOWN5 | 0.98717 | 0.9253 | -0.061869 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | MIDTOWN5 | 0.98717 | 0.9253 | -0.061869 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MIDTOWN5 | 0.98717 | 0.9253 | -0.061869 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | MIDTOWN5 | 0.98717 | 0.9253 | -0.061869 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | MIDTOWN5 | 0.98717 | 0.9253 | -0.061869 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MIDTOWN5 | 0.98717 | 0.9253 | -0.061869 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MIDTOWN5 | 0.98717 | 0.9253 | -0.061869 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MIDTOWN5 | 0.98717 | 0.9253 | -0.061869 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MIDTOWN5 | 0.98717 | 0.9253 | -0.061869 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MIDTOWN5 | 0.98717 | 0.9253 | -0.061869 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MIDTOWN5 | 0.98717 | 0.9253 | -0.061869 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MIDTOWN5 | 0.98717 | 0.9253 | -0.061869 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MIDTOWN5 | 0.98717 | 0.9253 | -0.061869 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MIDTOWN5 | 0.98717 | 0.9253 | -0.061869 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | MIDTOWN5 | 0.98717 | 0.9253 | -0.061869 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | MIDTOWN5 | 0.98717 | 0.9253 | -0.061869 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MIDTOWN5 | 0.98717 | 0.9253 | -0.061869 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MIDTOWN5 | 0.98717 | 0.9253 | -0.061869 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | MIDTOWN5 | 0.98717 | 0.9253 | -0.061869 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MIDTOWN5 | 0.98717 | 0.9253 | -0.061869 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MIDTOWN5 | 0.98717 | 0.9253 | -0.061869 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MIDTOWN5 | 0.98717 | 0.9253 | -0.061869 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MIDTOWN5 | 0.98717 | 0.9253 | -0.061869 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | MIDTOWN5 | 0.98717 | 0.9253 | -0.061869 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MISNJCT5 | 0.96447 | 0.92638 | -0.038092 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MISNJCT5 | 0.96447 | 0.92638 | -0.038092 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MISNJCT5 | 0.96447 | 0.92638 | -0.038092 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MISNJCT5 | 0.96447 | 0.92638 | -0.038092 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MISNJCT5 | 0.96447 | 0.92638 | -0.038092 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MISNJCT5 | 0.96447 | 0.92638 | -0.038092 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MISNJCT5 | 0.96447 | 0.92638 | -0.038092 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MISNJCT5 | 0.96447 | 0.92638 | -0.038092 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MISNJCT5 | 0.96447 | 0.92638 | -0.038092 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MISNJCT5 | 0.96447 | 0.92638 | -0.038092 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MISNJCT5 | 0.96447 | 0.92638 | -0.038092 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MISNJCT5 | 0.96447 | 0.92638 | -0.038092 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MISNJCT5 | 0.96447 | 0.92638 | -0.038092 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MISNJCT5 | 0.96447 | 0.92638 | -0.038092 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MISNJCT5 | 0.96447 | 0.92638 | -0.038092 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MISNJCT5 | 0.96447 | 0.92638 | -0.038092 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MISNJCT5 | 0.96447 | 0.92638 | -0.038092 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MISNJCT5 | 0.96447 | 0.92638 | -0.038092 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MISNJCT5 | 0.96447 | 0.92638 | -0.038092 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MISNJCT5 | 0.96447 | 0.92638 | -0.038092 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MISNJCT5 | 0.97246 | 0.92962 | -0.042832 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MISNJCT5 | 0.97246 | 0.92962 | -0.042832 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MISNJCT5 | 0.97246 | 0.92962 | -0.042832 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MISNJCT5 | 0.97246 | 0.92962 | -0.042832 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MISNJCT5 | 0.97246 | 0.92962 | -0.042832 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MISNJCT5 | 0.97246 | 0.92962 | -0.042832 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MISNJCT5 | 0.97246 | 0.92962 | -0.042832 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MISNJCT5 | 0.97246 | 0.92962 | -0.042832 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MISNJCT5 | 0.97246 | 0.92962 | -0.042832 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MISNJCT5 | 0.97246 | 0.92962 | -0.042832 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MISNJCT5 | 0.97246 | 0.92962 | -0.042832 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MISNJCT5 | 0.97246 | 0.92962 | -0.042832 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MISNJCT5 | 0.97246 | 0.92962 | -0.042832 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MISNJCT5 | 0.97246 | 0.92962 | -0.042832 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MISNJCT5 | 0.97246 | 0.92962 | -0.042832 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MISNJCT5 | 0.97246 | 0.92962 | -0.042832 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MISNJCT5 | 0.97246 | 0.92962 | -0.042832 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MISNJCT5 | 0.97246 | 0.92962 | -0.042832 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MISNJCT5 | 0.97246 | 0.92962 | -0.042832 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MISNJCT5 | 0.97246 | 0.92962 | -0.042832 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MISNJCT5 | 0.97453 | 0.90647 | -0.068058 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | MISNJCT5 | 0.97453 | 0.90647 | -0.068058 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MISNJCT5 | 0.97453 | 0.90647 | -0.068058 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MISNJCT5 | 0.97453 | 0.90647 | -0.068058 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MISNJCT5 | 0.97453 | 0.90647 | -0.068058 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | MISNJCT5 | 0.97453 | 0.90647 | -0.068058 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MISNJCT5 | 0.97453 | 0.90647 | -0.068058 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | MISNJCT5 | 0.97453 | 0.90647 | -0.068058 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | MISNJCT5 | 0.97453 | 0.90647 | -0.068058 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MISNJCT5 | 0.97453 | 0.90647 | -0.068058 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MISNJCT5 | 0.97453 | 0.90647 | -0.068058 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MISNJCT5 | 0.97453 | 0.90647 | -0.068058 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MISNJCT5 | 0.97453 | 0.90647 | -0.068058 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MISNJCT5 | 0.97453 | 0.90647 | -0.068058 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MISNJCT5 | 0.97453 | 0.90647 | -0.068058 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MISNJCT5 | 0.97453 | 0.90647 | -0.068058 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MISNJCT5 | 0.97453 | 0.90647 | -0.068058 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MISNJCT5 | 0.97453 | 0.90647 | -0.068058 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | MISNJCT5 | 0.97453 | 0.90647 | -0.068058 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | MISNJCT5 | 0.97453 | 0.90647 | -0.068058 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MISNJCT5 | 0.97453 | 0.90647 | -0.068058 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MISNJCT5 | 0.97453 | 0.90647 | -0.068058 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | MISNJCT5 | 0.97453 | 0.90647 | -0.068058 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MISNJCT5 | 0.97453 | 0.90647 | -0.068058 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MISNJCT5 | 0.97453 | 0.90647 | -0.068058 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MISNJCT5 | 0.97453 | 0.90647 | -0.068058 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MISNJCT5 | 0.97453 | 0.90647 | -0.068058 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | MISNJCT5 | 0.97453 | 0.90647 | -0.068058 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MNTCLLO3 | 0.96919 | 0.92967 | -0.039521 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MNTCLLO3 | 0.96919 | 0.92967 | -0.039521 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MNTCLLO3 | 0.96919 | 0.92967 | -0.039521 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MNTCLLO3 | 0.96919 | 0.92967 | -0.039521 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MNTCLLO3 | 0.96919 | 0.92967 | -0.039521 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MNTCLLO3 | 0.96919 | 0.92967 | -0.039521 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MNTCLLO3 | 0.96919 | 0.92967 | -0.039521 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MNTCLLO3 | 0.96919 | 0.92967 | -0.039521 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MNTCLLO3 | 0.96919 | 0.92967 | -0.039521 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MNTCLLO3 | 0.96919 | 0.92967 | -0.039521 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MNTCLLO3 | 0.96919 | 0.92967 | -0.039521 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MNTCLLO3 | 0.96919 | 0.92967 | -0.039521 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MNTCLLO3 | 0.96919 | 0.92967 | -0.039521 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MNTCLLO3 | 0.96919 | 0.92967 | -0.039521 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MNTCLLO3 | 0.96919 | 0.92967 | -0.039521 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MNTCLLO3 | 0.96919 | 0.92967 | -0.039521 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MNTCLLO3 | 0.96919 | 0.92967 | -0.039521 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MNTCLLO3 | 0.96919 | 0.92967 | -0.039521 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MNTCLLO3 | 0.96919 | 0.92967 | -0.039521 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MNTCLLO3 | 0.96919 | 0.92967 | -0.039521 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MNTCLLO3 | 0.98361 | 0.92317 | -0.060438 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | MNTCLLO3 | 0.98361 | 0.92317 | -0.060438 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MNTCLLO3 | 0.98361 | 0.92317 | -0.060438 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MNTCLLO3 | 0.98361 | 0.92317 | -0.060438 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MNTCLLO3 | 0.98361 | 0.92317 | -0.060438 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | MNTCLLO3 | 0.98361 | 0.92317 | -0.060438 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MNTCLLO3 | 0.98361 | 0.92317 | -0.060438 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | MNTCLLO3 | 0.98361 | 0.92317 | -0.060438 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | MNTCLLO3 | 0.98361 | 0.92317 | -0.060438 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MNTCLLO3 | 0.98361 | 0.92317 | -0.060438 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MNTCLLO3 | 0.98361 | 0.92317 | -0.060438 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MNTCLLO3 | 0.98361 | 0.92317 | -0.060438 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MNTCLLO3 | 0.98361 | 0.92317 | -0.060438 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MNTCLLO3 | 0.98361 | 0.92317 | -0.060438 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MNTCLLO3 | 0.98361 | 0.92317 | -0.060438 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MNTCLLO3 | 0.98361 | 0.92317 | -0.060438 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MNTCLLO3 | 0.98361 | 0.92317 | -0.060438 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MNTCLLO3 | 0.98361 | 0.92317 | -0.060438 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | MNTCLLO3 | 0.98361 | 0.92317 | -0.060438 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | MNTCLLO3 | 0.98361 | 0.92317 | -0.060438 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MNTCLLO3 | 0.98361 | 0.92317 | -0.060438 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MNTCLLO3 | 0.98361 | 0.92317 | -0.060438 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | MNTCLLO3 | 0.98361 | 0.92317 | -0.060438 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MNTCLLO3 | 0.98361 | 0.92317 | -0.060438 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MNTCLLO3 | 0.98361 | 0.92317 | -0.060438 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MNTCLLO3 | 0.98361 | 0.92317 | -0.060438 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MNTCLLO3 | 0.98361 | 0.92317 | -0.060438 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | MNTCLLO3 | 0.98361 | 0.92317 | -0.060438 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MOCKBRD3 | 0.96866 | 0.92867 | -0.039982 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MOCKBRD3 | 0.96866 | 0.92867 | -0.039982 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MOCKBRD3 | 0.96866 | 0.92867 | -0.039982 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MOCKBRD3 | 0.96866 | 0.92867 | -0.039982 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MOCKBRD3 | 0.96866 | 0.92867 | -0.039982 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MOCKBRD3 | 0.96866 | 0.92867 | -0.039982 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MOCKBRD3 | 0.96866 | 0.92867 | -0.039982 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MOCKBRD3 | 0.96866 | 0.92867 | -0.039982 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MOCKBRD3 | 0.96866 | 0.92867 | -0.039982 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MOCKBRD3 | 0.96866 | 0.92867 | -0.039982 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MOCKBRD3 | 0.96866 | 0.92867 | -0.039982 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MOCKBRD3 | 0.96866 | 0.92867 | -0.039982 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MOCKBRD3 | 0.96866 | 0.92867 | -0.039982 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MOCKBRD3 | 0.96866 | 0.92867 | -0.039982 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MOCKBRD3 | 0.96866 | 0.92867 | -0.039982 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MOCKBRD3 | 0.96866 | 0.92867 | -0.039982 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MOCKBRD3 | 0.96866 | 0.92867 | -0.039982 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MOCKBRD3 | 0.96866 | 0.92867 | -0.039982 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MOCKBRD3 | 0.96866 | 0.92867 | -0.039982 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MOCKBRD3 | 0.96866 | 0.92867 | -0.039982 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MOCKBRD3 | 0.97968 | 0.92959 | -0.050093 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | MOCKBRD3 | 0.97968 | 0.92959 | -0.050093 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MOCKBRD3 | 0.97968 | 0.92959 | -0.050093 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MOCKBRD3 | 0.97968 | 0.92959 | -0.050093 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MOCKBRD3 | 0.97968 | 0.92959 | -0.050093 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | MOCKBRD3 | 0.97968 | 0.92959 | -0.050093 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MOCKBRD3 | 0.97968 | 0.92959 | -0.050093 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | MOCKBRD3 | 0.97968 | 0.92959 | -0.050093 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | MOCKBRD3 | 0.97968 | 0.92959 | -0.050093 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MOCKBRD3 | 0.97968 | 0.92959 | -0.050093 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MOCKBRD3 | 0.97968 | 0.92959 | -0.050093 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MOCKBRD3 | 0.97968 | 0.92959 | -0.050093 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MOCKBRD3 | 0.97968 | 0.92959 | -0.050093 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MOCKBRD3 | 0.97968 | 0.92959 | -0.050093 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MOCKBRD3 | 0.97968 | 0.92959 | -0.050093 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MOCKBRD3 | 0.97968 | 0.92959 | -0.050093 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MOCKBRD3 | 0.97968 | 0.92959 | -0.050093 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MOCKBRD3 | 0.97968 | 0.92959 | -0.050093 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | MOCKBRD3 | 0.97968 | 0.92959 | -0.050093 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | MOCKBRD3 | 0.97968 | 0.92959 | -0.050093 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MOCKBRD3 | 0.97968 | 0.92959 | -0.050093 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MOCKBRD3 | 0.97968 | 0.92959 | -0.050093 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | MOCKBRD3 | 0.97968 | 0.92959 | -0.050093 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MOCKBRD3 | 0.97968 | 0.92959 | -0.050093 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MOCKBRD3 | 0.97968 | 0.92959 | -0.050093 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MOCKBRD3 | 0.97968 | 0.92959 | -0.050093 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MOCKBRD3 | 0.97968 | 0.92959 | -0.050093 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | MOCKBRD3 | 0.97968 | 0.92959 | -0.050093 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MON383 5 | 0.9646 | 0.91886 | -0.04574 |  | 0.925 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | MON383 5 | 0.9646 | 0.91886 | -0.04574 |  | 0.925 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MON383 5 | 0.9646 | 0.91886 | -0.04574 |  | 0.925 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MON383 5 | 0.9646 | 0.91886 | -0.04574 |  | 0.925 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MON383 5 | 0.9646 | 0.91886 | -0.04574 |  | 0.925 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MON383 5 | 0.9646 | 0.91886 | -0.04574 |  | 0.925 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MON383 5 | 0.9646 | 0.91886 | -0.04574 |  | 0.925 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MON383 5 | 0.9646 | 0.91886 | -0.04574 |  | 0.925 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MON383 5 | 0.9646 | 0.91886 | -0.04574 |  | 0.925 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MON383 5 | 0.9646 | 0.91886 | -0.04574 |  | 0.925 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | MON383 5 | 0.9646 | 0.91886 | -0.04574 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | MON383 5 | 0.9646 | 0.91886 | -0.04574 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MON383 5 | 0.9646 | 0.91886 | -0.04574 |  | 0.925 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MON383 5 | 0.9646 | 0.91886 | -0.04574 |  | 0.925 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MON383 5 | 0.9646 | 0.91886 | -0.04574 |  | 0.925 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | MON383 5 | 0.96576 | 0.92057 | -0.045192 |  | 0.925 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MON383 5 | 0.96576 | 0.92057 | -0.045192 |  | 0.925 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MON383 5 | 0.96576 | 0.92057 | -0.045192 |  | 0.925 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MON383 5 | 0.96576 | 0.92057 | -0.045192 |  | 0.925 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MON383 5 | 0.96576 | 0.92057 | -0.045192 |  | 0.925 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MON383 5 | 0.96576 | 0.92057 | -0.045192 |  | 0.925 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MON383 5 | 0.96576 | 0.92057 | -0.045192 |  | 0.925 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MON383 5 | 0.96576 | 0.92057 | -0.045192 |  | 0.925 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MON383 5 | 0.96576 | 0.92057 | -0.045192 |  | 0.925 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | MON383 5 | 0.96576 | 0.92057 | -0.045192 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | MON383 5 | 0.96576 | 0.92057 | -0.045192 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MON383 5 | 0.96576 | 0.92057 | -0.045192 |  | 0.925 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MON383 5 | 0.96576 | 0.92057 | -0.045192 |  | 0.925 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MON383 5 | 0.96576 | 0.92057 | -0.045192 |  | 0.925 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MON383 5 | 0.96552 | 0.92487 | -0.040648 |  | 0.925 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | MON383 5 | 0.96552 | 0.92487 | -0.040648 |  | 0.925 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MON383 5 | 0.96552 | 0.92487 | -0.040648 |  | 0.925 | 1.05 | 0.055405 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MON383 5 | 0.96552 | 0.92487 | -0.040648 |  | 0.925 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MON383 5 | 0.96552 | 0.92487 | -0.040648 |  | 0.925 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MON383 5 | 0.96552 | 0.92487 | -0.040648 |  | 0.925 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MON383 5 | 0.96552 | 0.92487 | -0.040648 |  | 0.925 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MON383 5 | 0.96552 | 0.92487 | -0.040648 |  | 0.925 | 1.05 | 0.082012 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MON383 5 | 0.96552 | 0.92487 | -0.040648 |  | 0.925 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MON383 5 | 0.96552 | 0.92487 | -0.040648 |  | 0.925 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | MON383 5 | 0.96552 | 0.92487 | -0.040648 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | MON383 5 | 0.96552 | 0.92487 | -0.040648 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MON383 5 | 0.96552 | 0.92487 | -0.040648 |  | 0.925 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MON383 5 | 0.96552 | 0.92487 | -0.040648 |  | 0.925 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MON383 5 | 0.96552 | 0.92487 | -0.040648 |  | 0.925 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MONTGOM4 | 0.96198 | 0.92247 | -0.039516 |  | 0.93 | 1.05 | 0.094783 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | MONTGOM4 | 0.96198 | 0.92247 | -0.039516 |  | 0.93 | 1.05 | 0.03645 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MONTGOM4 | 0.96198 | 0.92247 | -0.039516 |  | 0.93 | 1.05 | 0.04755 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MONTGOM4 | 0.96198 | 0.92247 | -0.039516 |  | 0.93 | 1.05 | 0.06097 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MONTGOM4 | 0.96198 | 0.92247 | -0.039516 |  | 0.93 | 1.05 | 0.061051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | MONTGOM4 | 0.96198 | 0.92247 | -0.039516 |  | 0.93 | 1.05 | 0.04456 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | MONTGOM4 | 0.96198 | 0.92247 | -0.039516 |  | 0.93 | 1.05 | 0.048811 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MONTGOM4 | 0.96198 | 0.92247 | -0.039516 |  | 0.93 | 1.05 | 0.13004 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MONTGOM4 | 0.96198 | 0.92247 | -0.039516 |  | 0.93 | 1.05 | 0.049018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MONTGOM4 | 0.96198 | 0.92247 | -0.039516 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MONTGOM4 | 0.96198 | 0.92247 | -0.039516 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MONTGOM4 | 0.96198 | 0.92247 | -0.039516 |  | 0.93 | 1.05 | 0.05974 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MONTGOM4 | 0.96198 | 0.92247 | -0.039516 |  | 0.93 | 1.05 | 0.076949 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MONTGOM4 | 0.96198 | 0.92247 | -0.039516 |  | 0.93 | 1.05 | 0.042157 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MONTGOM4 | 0.96198 | 0.92247 | -0.039516 |  | 0.93 | 1.05 | 0.040957 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | MONTGOM4 | 0.96198 | 0.92247 | -0.039516 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | MONTGOM4 | 0.96198 | 0.92247 | -0.039516 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MONTGOM4 | 0.96198 | 0.92247 | -0.039516 |  | 0.93 | 1.05 | 0.054637 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MONTGOM4 | 0.96198 | 0.92247 | -0.039516 |  | 0.93 | 1.05 | 0.060597 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | MONTGOM4 | 0.96198 | 0.92247 | -0.039516 |  | 0.93 | 1.05 | 0.044286 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MONTGOM4 | 0.96198 | 0.92247 | -0.039516 |  | 0.93 | 1.05 | 0.059107 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MONTGOM4 | 0.96198 | 0.92247 | -0.039516 |  | 0.93 | 1.05 | 0.052698 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MONTGOM4 | 0.96198 | 0.92247 | -0.039516 |  | 0.93 | 1.05 | 0.067422 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MONTGOM4 | 0.96198 | 0.92247 | -0.039516 |  | 0.93 | 1.05 | 0.053768 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | MONTGOM4 | 0.96198 | 0.92247 | -0.039516 |  | 0.93 | 1.05 | 0.03909 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MONTGOM4 | 0.96146 | 0.92681 | -0.034652 |  | 0.93 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | MONTGOM4 | 0.96146 | 0.92681 | -0.034652 |  | 0.93 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MONTGOM4 | 0.96146 | 0.92681 | -0.034652 |  | 0.93 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MONTGOM4 | 0.96146 | 0.92681 | -0.034652 |  | 0.93 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MONTGOM4 | 0.96146 | 0.92681 | -0.034652 |  | 0.93 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | MONTGOM4 | 0.96146 | 0.92681 | -0.034652 |  | 0.93 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MONTGOM4 | 0.96146 | 0.92681 | -0.034652 |  | 0.93 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | MONTGOM4 | 0.96146 | 0.92681 | -0.034652 |  | 0.93 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MONTGOM4 | 0.96146 | 0.92681 | -0.034652 |  | 0.93 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MONTGOM4 | 0.96146 | 0.92681 | -0.034652 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MONTGOM4 | 0.96146 | 0.92681 | -0.034652 |  | 0.93 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MONTGOM4 | 0.96146 | 0.92681 | -0.034652 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MONTGOM4 | 0.96146 | 0.92681 | -0.034652 |  | 0.93 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MONTGOM4 | 0.96146 | 0.92681 | -0.034652 |  | 0.93 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MONTGOM4 | 0.96146 | 0.92681 | -0.034652 |  | 0.93 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MONTGOM4 | 0.96146 | 0.92681 | -0.034652 |  | 0.93 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MONTGOM4 | 0.96146 | 0.92681 | -0.034652 |  | 0.93 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MONTGOM4 | 0.96146 | 0.92681 | -0.034652 |  | 0.93 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MONTGOM4 | 0.96146 | 0.92681 | -0.034652 |  | 0.93 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MONTGOM4 | 0.96146 | 0.92681 | -0.034652 |  | 0.93 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MONTGOM4 | 0.96146 | 0.92681 | -0.034652 |  | 0.93 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MONTGOM4 | 0.96146 | 0.92681 | -0.034652 |  | 0.93 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MONTGOM4 | 0.96428 | 0.91847 | -0.04581 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | MONTGOM4 | 0.96428 | 0.91847 | -0.04581 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MONTGOM4 | 0.96428 | 0.91847 | -0.04581 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MONTGOM4 | 0.96428 | 0.91847 | -0.04581 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MONTGOM4 | 0.96428 | 0.91847 | -0.04581 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | MONTGOM4 | 0.96428 | 0.91847 | -0.04581 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MONTGOM4 | 0.96428 | 0.91847 | -0.04581 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | MONTGOM4 | 0.96428 | 0.91847 | -0.04581 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | MONTGOM4 | 0.96428 | 0.91847 | -0.04581 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MONTGOM4 | 0.96428 | 0.91847 | -0.04581 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MONTGOM4 | 0.96428 | 0.91847 | -0.04581 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MONTGOM4 | 0.96428 | 0.91847 | -0.04581 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MONTGOM4 | 0.96428 | 0.91847 | -0.04581 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MONTGOM4 | 0.96428 | 0.91847 | -0.04581 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MONTGOM4 | 0.96428 | 0.91847 | -0.04581 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MONTGOM4 | 0.96428 | 0.91847 | -0.04581 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MONTGOM4 | 0.96428 | 0.91847 | -0.04581 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MONTGOM4 | 0.96428 | 0.91847 | -0.04581 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | MONTGOM4 | 0.96428 | 0.91847 | -0.04581 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | MONTGOM4 | 0.96428 | 0.91847 | -0.04581 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MONTGOM4 | 0.96428 | 0.91847 | -0.04581 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MONTGOM4 | 0.96428 | 0.91847 | -0.04581 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | MONTGOM4 | 0.96428 | 0.91847 | -0.04581 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MONTGOM4 | 0.96428 | 0.91847 | -0.04581 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MONTGOM4 | 0.96428 | 0.91847 | -0.04581 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MONTGOM4 | 0.96428 | 0.91847 | -0.04581 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MONTGOM4 | 0.96428 | 0.91847 | -0.04581 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | MONTGOM4 | 0.96428 | 0.91847 | -0.04581 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MOONLIT3 | 0.96758 | 0.92919 | -0.038399 |  | 0.93 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MOONLIT3 | 0.96758 | 0.92919 | -0.038399 |  | 0.93 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MOONLIT3 | 0.96758 | 0.92919 | -0.038399 |  | 0.93 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MOONLIT3 | 0.96758 | 0.92919 | -0.038399 |  | 0.93 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MOONLIT3 | 0.96758 | 0.92919 | -0.038399 |  | 0.93 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MOONLIT3 | 0.96758 | 0.92919 | -0.038399 |  | 0.93 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MOONLIT3 | 0.96758 | 0.92919 | -0.038399 |  | 0.93 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MOONLIT3 | 0.96758 | 0.92919 | -0.038399 |  | 0.93 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MOONLIT3 | 0.96758 | 0.92919 | -0.038399 |  | 0.93 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MOONLIT3 | 0.96758 | 0.92919 | -0.038399 |  | 0.93 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MOONLIT3 | 0.96758 | 0.92919 | -0.038399 |  | 0.93 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MOONLIT3 | 0.96758 | 0.92919 | -0.038399 |  | 0.93 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MOONLIT3 | 0.96758 | 0.92919 | -0.038399 |  | 0.93 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MOONLIT3 | 0.96758 | 0.92919 | -0.038399 |  | 0.93 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MOONLIT3 | 0.96758 | 0.92919 | -0.038399 |  | 0.93 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MOONLIT3 | 0.96758 | 0.92919 | -0.038399 |  | 0.93 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MOONLIT3 | 0.96758 | 0.92919 | -0.038399 |  | 0.93 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MOONLIT3 | 0.96758 | 0.92919 | -0.038399 |  | 0.93 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MOONLIT3 | 0.96758 | 0.92919 | -0.038399 |  | 0.93 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MOONLIT3 | 0.96758 | 0.92919 | -0.038399 |  | 0.93 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MOONLIT3 | 0.96099 | 0.91752 | -0.043467 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MOONLIT3 | 0.96099 | 0.91752 | -0.043467 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MOONLIT3 | 0.96099 | 0.91752 | -0.043467 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MOONLIT3 | 0.96099 | 0.91752 | -0.043467 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MOONLIT3 | 0.96099 | 0.91752 | -0.043467 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MOONLIT3 | 0.96099 | 0.91752 | -0.043467 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MOONLIT3 | 0.96099 | 0.91752 | -0.043467 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MOONLIT3 | 0.96099 | 0.91752 | -0.043467 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MOONLIT3 | 0.96099 | 0.91752 | -0.043467 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MOONLIT3 | 0.96099 | 0.91752 | -0.043467 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MOONLIT3 | 0.96099 | 0.91752 | -0.043467 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MOONLIT3 | 0.96099 | 0.91752 | -0.043467 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MOONLIT3 | 0.96099 | 0.91752 | -0.043467 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MOONLIT3 | 0.96099 | 0.91752 | -0.043467 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MOONLIT3 | 0.96099 | 0.91752 | -0.043467 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MOONLIT3 | 0.96099 | 0.91752 | -0.043467 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MOONLIT3 | 0.96099 | 0.91752 | -0.043467 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MOONLIT3 | 0.96099 | 0.91752 | -0.043467 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MOONLIT3 | 0.96099 | 0.91752 | -0.043467 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MOONLIT3 | 0.96099 | 0.91752 | -0.043467 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MOONLIT3 | 0.97141 | 0.92371 | -0.047699 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MOONLIT3 | 0.97141 | 0.92371 | -0.047699 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MOONLIT3 | 0.97141 | 0.92371 | -0.047699 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MOONLIT3 | 0.97141 | 0.92371 | -0.047699 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MOONLIT3 | 0.97141 | 0.92371 | -0.047699 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MOONLIT3 | 0.97141 | 0.92371 | -0.047699 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MOONLIT3 | 0.97141 | 0.92371 | -0.047699 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MOONLIT3 | 0.97141 | 0.92371 | -0.047699 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MOONLIT3 | 0.97141 | 0.92371 | -0.047699 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MOONLIT3 | 0.97141 | 0.92371 | -0.047699 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MOONLIT3 | 0.97141 | 0.92371 | -0.047699 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MOONLIT3 | 0.97141 | 0.92371 | -0.047699 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MOONLIT3 | 0.97141 | 0.92371 | -0.047699 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MOONLIT3 | 0.97141 | 0.92371 | -0.047699 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MOONLIT3 | 0.97141 | 0.92371 | -0.047699 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MOONLIT3 | 0.97141 | 0.92371 | -0.047699 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MOONLIT3 | 0.97141 | 0.92371 | -0.047699 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MOONLIT3 | 0.97141 | 0.92371 | -0.047699 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MOONLIT3 | 0.97141 | 0.92371 | -0.047699 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MOONLIT3 | 0.97141 | 0.92371 | -0.047699 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MOONLIT3 | 0.97701 | 0.90793 | -0.069076 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | MOONLIT3 | 0.97701 | 0.90793 | -0.069076 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MOONLIT3 | 0.97701 | 0.90793 | -0.069076 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MOONLIT3 | 0.97701 | 0.90793 | -0.069076 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MOONLIT3 | 0.97701 | 0.90793 | -0.069076 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | MOONLIT3 | 0.97701 | 0.90793 | -0.069076 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MOONLIT3 | 0.97701 | 0.90793 | -0.069076 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | MOONLIT3 | 0.97701 | 0.90793 | -0.069076 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | MOONLIT3 | 0.97701 | 0.90793 | -0.069076 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MOONLIT3 | 0.97701 | 0.90793 | -0.069076 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MOONLIT3 | 0.97701 | 0.90793 | -0.069076 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MOONLIT3 | 0.97701 | 0.90793 | -0.069076 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MOONLIT3 | 0.97701 | 0.90793 | -0.069076 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MOONLIT3 | 0.97701 | 0.90793 | -0.069076 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MOONLIT3 | 0.97701 | 0.90793 | -0.069076 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MOONLIT3 | 0.97701 | 0.90793 | -0.069076 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MOONLIT3 | 0.97701 | 0.90793 | -0.069076 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MOONLIT3 | 0.97701 | 0.90793 | -0.069076 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | MOONLIT3 | 0.97701 | 0.90793 | -0.069076 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | MOONLIT3 | 0.97701 | 0.90793 | -0.069076 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MOONLIT3 | 0.97701 | 0.90793 | -0.069076 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MOONLIT3 | 0.97701 | 0.90793 | -0.069076 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | MOONLIT3 | 0.97701 | 0.90793 | -0.069076 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MOONLIT3 | 0.97701 | 0.90793 | -0.069076 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MOONLIT3 | 0.97701 | 0.90793 | -0.069076 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MOONLIT3 | 0.97701 | 0.90793 | -0.069076 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MOONLIT3 | 0.97701 | 0.90793 | -0.069076 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | MOONLIT3 | 0.97701 | 0.90793 | -0.069076 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MOONLIT3 | 0.96685 | 0.92747 | -0.039379 |  | 0.93 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MOONLIT3 | 0.96685 | 0.92747 | -0.039379 |  | 0.93 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MOONLIT3 | 0.96685 | 0.92747 | -0.039379 |  | 0.93 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MOONLIT3 | 0.96685 | 0.92747 | -0.039379 |  | 0.93 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MOONLIT3 | 0.96685 | 0.92747 | -0.039379 |  | 0.93 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MOONLIT3 | 0.96685 | 0.92747 | -0.039379 |  | 0.93 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MOONLIT3 | 0.96685 | 0.92747 | -0.039379 |  | 0.93 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MOONLIT3 | 0.96685 | 0.92747 | -0.039379 |  | 0.93 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MOONLIT3 | 0.96685 | 0.92747 | -0.039379 |  | 0.93 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MOONLIT3 | 0.96685 | 0.92747 | -0.039379 |  | 0.93 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MOONLIT3 | 0.96685 | 0.92747 | -0.039379 |  | 0.93 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MOONLIT3 | 0.96685 | 0.92747 | -0.039379 |  | 0.93 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MOONLIT3 | 0.96685 | 0.92747 | -0.039379 |  | 0.93 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MOONLIT3 | 0.96685 | 0.92747 | -0.039379 |  | 0.93 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MOONLIT3 | 0.96685 | 0.92747 | -0.039379 |  | 0.93 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MOONLIT3 | 0.96685 | 0.92747 | -0.039379 |  | 0.93 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MOONLIT3 | 0.96685 | 0.92747 | -0.039379 |  | 0.93 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MOONLIT3 | 0.96685 | 0.92747 | -0.039379 |  | 0.93 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MOONLIT3 | 0.96685 | 0.92747 | -0.039379 |  | 0.93 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MOONLIT3 | 0.96685 | 0.92747 | -0.039379 |  | 0.93 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MOONLT 5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MOONLT 5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MOONLT 5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MOONLT 5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MOONLT 5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MOONLT 5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MOONLT 5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MOONLT 5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MOONLT 5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MOONLT 5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MOONLT 5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MOONLT 5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MOONLT 5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MOONLT 5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MOONLT 5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MOONLT 5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MOONLT 5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MOONLT 5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MOONLT 5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MOONLT 5 | 0.97425 | 0.9261 | -0.048149 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MOONLT 5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | MOONLT 5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MOONLT 5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MOONLT 5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MOONLT 5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | MOONLT 5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MOONLT 5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | MOONLT 5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | MOONLT 5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MOONLT 5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MOONLT 5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MOONLT 5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MOONLT 5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MOONLT 5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MOONLT 5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MOONLT 5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MOONLT 5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MOONLT 5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | MOONLT 5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | MOONLT 5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MOONLT 5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MOONLT 5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | MOONLT 5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MOONLT 5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MOONLT 5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MOONLT 5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MOONLT 5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | MOONLT 5 | 0.99148 | 0.91199 | -0.07949 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MORRIS 3 | 0.98232 | 0.92692 | -0.055405 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | MORRIS 3 | 0.98232 | 0.92692 | -0.055405 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MORRIS 3 | 0.98232 | 0.92692 | -0.055405 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MORRIS 3 | 0.98232 | 0.92692 | -0.055405 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MORRIS 3 | 0.98232 | 0.92692 | -0.055405 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | MORRIS 3 | 0.98232 | 0.92692 | -0.055405 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MORRIS 3 | 0.98232 | 0.92692 | -0.055405 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | MORRIS 3 | 0.98232 | 0.92692 | -0.055405 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | MORRIS 3 | 0.98232 | 0.92692 | -0.055405 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MORRIS 3 | 0.98232 | 0.92692 | -0.055405 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MORRIS 3 | 0.98232 | 0.92692 | -0.055405 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MORRIS 3 | 0.98232 | 0.92692 | -0.055405 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MORRIS 3 | 0.98232 | 0.92692 | -0.055405 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MORRIS 3 | 0.98232 | 0.92692 | -0.055405 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MORRIS 3 | 0.98232 | 0.92692 | -0.055405 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MORRIS 3 | 0.98232 | 0.92692 | -0.055405 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MORRIS 3 | 0.98232 | 0.92692 | -0.055405 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MORRIS 3 | 0.98232 | 0.92692 | -0.055405 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | MORRIS 3 | 0.98232 | 0.92692 | -0.055405 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | MORRIS 3 | 0.98232 | 0.92692 | -0.055405 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MORRIS 3 | 0.98232 | 0.92692 | -0.055405 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MORRIS 3 | 0.98232 | 0.92692 | -0.055405 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | MORRIS 3 | 0.98232 | 0.92692 | -0.055405 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MORRIS 3 | 0.98232 | 0.92692 | -0.055405 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MORRIS 3 | 0.98232 | 0.92692 | -0.055405 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MORRIS 3 | 0.98232 | 0.92692 | -0.055405 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MORRIS 3 | 0.98232 | 0.92692 | -0.055405 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | MORRIS 3 | 0.98232 | 0.92692 | -0.055405 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MORRIS 6 | 0.9874 | 0.93875 | -0.048651 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | MORRIS 6 | 0.9874 | 0.93875 | -0.048651 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MORRIS 6 | 0.9874 | 0.93875 | -0.048651 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MORRIS 6 | 0.9874 | 0.93875 | -0.048651 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MORRIS 6 | 0.9874 | 0.93875 | -0.048651 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | MORRIS 6 | 0.9874 | 0.93875 | -0.048651 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MORRIS 6 | 0.9874 | 0.93875 | -0.048651 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | MORRIS 6 | 0.9874 | 0.93875 | -0.048651 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | MORRIS 6 | 0.9874 | 0.93875 | -0.048651 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MORRIS 6 | 0.9874 | 0.93875 | -0.048651 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MORRIS 6 | 0.9874 | 0.93875 | -0.048651 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MORRIS 6 | 0.9874 | 0.93875 | -0.048651 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MORRIS 6 | 0.9874 | 0.93875 | -0.048651 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MORRIS 6 | 0.9874 | 0.93875 | -0.048651 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MORRIS 6 | 0.9874 | 0.93875 | -0.048651 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MORRIS 6 | 0.9874 | 0.93875 | -0.048651 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MORRIS 6 | 0.9874 | 0.93875 | -0.048651 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MORRIS 6 | 0.9874 | 0.93875 | -0.048651 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | MORRIS 6 | 0.9874 | 0.93875 | -0.048651 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | MORRIS 6 | 0.9874 | 0.93875 | -0.048651 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MORRIS 6 | 0.9874 | 0.93875 | -0.048651 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MORRIS 6 | 0.9874 | 0.93875 | -0.048651 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | MORRIS 6 | 0.9874 | 0.93875 | -0.048651 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MORRIS 6 | 0.9874 | 0.93875 | -0.048651 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MORRIS 6 | 0.9874 | 0.93875 | -0.048651 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MORRIS 6 | 0.9874 | 0.93875 | -0.048651 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MORRIS 6 | 0.9874 | 0.93875 | -0.048651 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | MORRIS 6 | 0.9874 | 0.93875 | -0.048651 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MORRIS 7 | 0.98761 | 0.94246 | -0.045151 |  | 0.95 | 1.05 | 0.03965 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MORRIS 7 | 0.98761 | 0.94246 | -0.045151 |  | 0.95 | 1.05 | 0.042938 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MORRIS 7 | 0.98761 | 0.94246 | -0.045151 |  | 0.95 | 1.05 | 0.032864 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MORRIS 7 | 0.98761 | 0.94246 | -0.045151 |  | 0.95 | 1.05 | 0.034629 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | MORRIS 7 | 0.98761 | 0.94246 | -0.045151 |  | 0.95 | 1.05 | 0.036988 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MORRIS 7 | 0.98761 | 0.94246 | -0.045151 |  | 0.95 | 1.05 | 0.03396 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | MORRIS 7 | 0.98761 | 0.94246 | -0.045151 |  | 0.95 | 1.05 | 0.030296 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MORRIS 7 | 0.98761 | 0.94246 | -0.045151 |  | 0.95 | 1.05 | 0.037836 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MORRIS 7 | 0.98761 | 0.94246 | -0.045151 |  | 0.95 | 1.05 | 0.036214 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MORRIS 7 | 0.98761 | 0.94246 | -0.045151 |  | 0.95 | 1.05 | 0.055483 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MORRIS 7 | 0.98761 | 0.94246 | -0.045151 |  | 0.95 | 1.05 | 0.036214 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MORRIS 7 | 0.98761 | 0.94246 | -0.045151 |  | 0.95 | 1.05 | 0.037031 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MORRIS 7 | 0.98761 | 0.94246 | -0.045151 |  | 0.95 | 1.05 | 0.03728 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MORRIS 7 | 0.98761 | 0.94246 | -0.045151 |  | 0.95 | 1.05 | 0.034689 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MORRIS 7 | 0.98761 | 0.94246 | -0.045151 |  | 0.95 | 1.05 | 0.033481 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MORRIS 7 | 0.98761 | 0.94246 | -0.045151 |  | 0.95 | 1.05 | 0.035246 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MORRIS 7 | 0.98761 | 0.94246 | -0.045151 |  | 0.95 | 1.05 | 0.03235 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MORRIS 7 | 0.98761 | 0.94246 | -0.045151 |  | 0.95 | 1.05 | 0.031498 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MORRIS 7 | 0.98761 | 0.94246 | -0.045151 |  | 0.95 | 1.05 | 0.033388 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MORRIS 7 | 0.98761 | 0.94246 | -0.045151 |  | 0.95 | 1.05 | 0.034867 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MORRIS 7 | 0.98882 | 0.94286 | -0.04596 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MORRIS 7 | 0.98882 | 0.94286 | -0.04596 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MORRIS 7 | 0.98882 | 0.94286 | -0.04596 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MORRIS 7 | 0.98882 | 0.94286 | -0.04596 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MORRIS 7 | 0.98882 | 0.94286 | -0.04596 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MORRIS 7 | 0.98882 | 0.94286 | -0.04596 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MORRIS 7 | 0.98882 | 0.94286 | -0.04596 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MORRIS 7 | 0.98882 | 0.94286 | -0.04596 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MORRIS 7 | 0.98882 | 0.94286 | -0.04596 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MORRIS 7 | 0.98882 | 0.94286 | -0.04596 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MORRIS 7 | 0.98882 | 0.94286 | -0.04596 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MORRIS 7 | 0.98882 | 0.94286 | -0.04596 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MORRIS 7 | 0.98882 | 0.94286 | -0.04596 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MORRIS 7 | 0.98882 | 0.94286 | -0.04596 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MORRIS 7 | 0.98882 | 0.94286 | -0.04596 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MORRIS 7 | 0.98882 | 0.94286 | -0.04596 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MORRIS 7 | 0.98882 | 0.94286 | -0.04596 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MORRIS 7 | 0.98882 | 0.94286 | -0.04596 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MORRIS 7 | 0.98882 | 0.94286 | -0.04596 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MORRIS 7 | 0.98882 | 0.94286 | -0.04596 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MORRIS 7 | 0.99373 | 0.94033 | -0.053403 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MORRIS 7 | 0.99373 | 0.94033 | -0.053403 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MORRIS 7 | 0.99373 | 0.94033 | -0.053403 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MORRIS 7 | 0.99373 | 0.94033 | -0.053403 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MORRIS 7 | 0.99373 | 0.94033 | -0.053403 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MORRIS 7 | 0.99373 | 0.94033 | -0.053403 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MORRIS 7 | 0.99373 | 0.94033 | -0.053403 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MORRIS 7 | 0.99373 | 0.94033 | -0.053403 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MORRIS 7 | 0.99373 | 0.94033 | -0.053403 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MORRIS 7 | 0.99373 | 0.94033 | -0.053403 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MORRIS 7 | 0.99373 | 0.94033 | -0.053403 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MORRIS 7 | 0.99373 | 0.94033 | -0.053403 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MORRIS 7 | 0.99373 | 0.94033 | -0.053403 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MORRIS 7 | 0.99373 | 0.94033 | -0.053403 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MORRIS 7 | 0.99373 | 0.94033 | -0.053403 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MORRIS 7 | 0.99373 | 0.94033 | -0.053403 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MORRIS 7 | 0.99373 | 0.94033 | -0.053403 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MORRIS 7 | 0.99373 | 0.94033 | -0.053403 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MORRIS 7 | 0.99373 | 0.94033 | -0.053403 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MORRIS 7 | 0.99373 | 0.94033 | -0.053403 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MORRIS 7 | 0.98895 | 0.94106 | -0.04789 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | MORRIS 7 | 0.98895 | 0.94106 | -0.04789 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MORRIS 7 | 0.98895 | 0.94106 | -0.04789 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MORRIS 7 | 0.98895 | 0.94106 | -0.04789 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MORRIS 7 | 0.98895 | 0.94106 | -0.04789 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | MORRIS 7 | 0.98895 | 0.94106 | -0.04789 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MORRIS 7 | 0.98895 | 0.94106 | -0.04789 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | MORRIS 7 | 0.98895 | 0.94106 | -0.04789 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | MORRIS 7 | 0.98895 | 0.94106 | -0.04789 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MORRIS 7 | 0.98895 | 0.94106 | -0.04789 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MORRIS 7 | 0.98895 | 0.94106 | -0.04789 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MORRIS 7 | 0.98895 | 0.94106 | -0.04789 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MORRIS 7 | 0.98895 | 0.94106 | -0.04789 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MORRIS 7 | 0.98895 | 0.94106 | -0.04789 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MORRIS 7 | 0.98895 | 0.94106 | -0.04789 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MORRIS 7 | 0.98895 | 0.94106 | -0.04789 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MORRIS 7 | 0.98895 | 0.94106 | -0.04789 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MORRIS 7 | 0.98895 | 0.94106 | -0.04789 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | MORRIS 7 | 0.98895 | 0.94106 | -0.04789 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | MORRIS 7 | 0.98895 | 0.94106 | -0.04789 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MORRIS 7 | 0.98895 | 0.94106 | -0.04789 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MORRIS 7 | 0.98895 | 0.94106 | -0.04789 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | MORRIS 7 | 0.98895 | 0.94106 | -0.04789 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MORRIS 7 | 0.98895 | 0.94106 | -0.04789 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MORRIS 7 | 0.98895 | 0.94106 | -0.04789 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MORRIS 7 | 0.98895 | 0.94106 | -0.04789 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MORRIS 7 | 0.98895 | 0.94106 | -0.04789 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | MORRIS 7 | 0.98895 | 0.94106 | -0.04789 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MORRIS 7 | 0.99103 | 0.94728 | -0.043748 |  | 0.95 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MORRIS 7 | 0.99103 | 0.94728 | -0.043748 |  | 0.95 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MORRIS 7 | 0.99103 | 0.94728 | -0.043748 |  | 0.95 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MORRIS 7 | 0.99103 | 0.94728 | -0.043748 |  | 0.95 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MORRIS 7 | 0.99103 | 0.94728 | -0.043748 |  | 0.95 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MORRIS 7 | 0.99103 | 0.94728 | -0.043748 |  | 0.95 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MORRIS 7 | 0.99103 | 0.94728 | -0.043748 |  | 0.95 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MORRIS 7 | 0.99103 | 0.94728 | -0.043748 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MORRIS 7 | 0.99103 | 0.94728 | -0.043748 |  | 0.95 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MORRIS 7 | 0.99103 | 0.94728 | -0.043748 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MORRIS 7 | 0.99103 | 0.94728 | -0.043748 |  | 0.95 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MORRIS 7 | 0.99103 | 0.94728 | -0.043748 |  | 0.95 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MORRIS 7 | 0.99103 | 0.94728 | -0.043748 |  | 0.95 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MORRIS 7 | 0.99103 | 0.94728 | -0.043748 |  | 0.95 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MORRIS 7 | 0.99103 | 0.94728 | -0.043748 |  | 0.95 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MORRIS 7 | 0.99103 | 0.94728 | -0.043748 |  | 0.95 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MORRIS 7 | 0.99103 | 0.94728 | -0.043748 |  | 0.95 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MORRIS 7 | 0.99103 | 0.94728 | -0.043748 |  | 0.95 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MORRIS 7 | 0.99103 | 0.94728 | -0.043748 |  | 0.95 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MORRIS 7 | 0.99103 | 0.94728 | -0.043748 |  | 0.95 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MOUND 4 | 0.94059 | 0.90212 | -0.03847 |  | 0.93 | 1.05 | 0.055416 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | MOUND 4 | 0.94059 | 0.90212 | -0.03847 |  | 0.93 | 1.05 | 0.031006 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MOUND 4 | 0.94059 | 0.90212 | -0.03847 |  | 0.93 | 1.05 | 0.065094 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MOUND 4 | 0.94059 | 0.90212 | -0.03847 |  | 0.93 | 1.05 | 0.044621 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MOUND 4 | 0.94059 | 0.90212 | -0.03847 |  | 0.93 | 1.05 | 0.048914 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | MOUND 4 | 0.94059 | 0.90212 | -0.03847 |  | 0.93 | 1.05 | 0.048508 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MOUND 4 | 0.94059 | 0.90212 | -0.03847 |  | 0.93 | 1.05 | 0.047017 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | MOUND 4 | 0.94059 | 0.90212 | -0.03847 |  | 0.93 | 1.05 | 0.040068 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | MOUND 4 | 0.94059 | 0.90212 | -0.03847 |  | 0.93 | 1.05 | 0.043101 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MOUND 4 | 0.94059 | 0.90212 | -0.03847 |  | 0.93 | 1.05 | 0.051186 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MOUND 4 | 0.94059 | 0.90212 | -0.03847 |  | 0.93 | 1.05 | 0.041545 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MOUND 4 | 0.94059 | 0.90212 | -0.03847 |  | 0.93 | 1.05 | 0.050897 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MOUND 4 | 0.94059 | 0.90212 | -0.03847 |  | 0.93 | 1.05 | 0.07159 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MOUND 4 | 0.94059 | 0.90212 | -0.03847 |  | 0.93 | 1.05 | 0.050897 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MOUND 4 | 0.94059 | 0.90212 | -0.03847 |  | 0.93 | 1.05 | 0.052178 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MOUND 4 | 0.94059 | 0.90212 | -0.03847 |  | 0.93 | 1.05 | 0.0519 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MOUND 4 | 0.94059 | 0.90212 | -0.03847 |  | 0.93 | 1.05 | 0.034974 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MOUND 4 | 0.94059 | 0.90212 | -0.03847 |  | 0.93 | 1.05 | 0.050152 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | MOUND 4 | 0.94059 | 0.90212 | -0.03847 |  | 0.93 | 1.05 | 0.037496 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | MOUND 4 | 0.94059 | 0.90212 | -0.03847 |  | 0.93 | 1.05 | 0.037496 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MOUND 4 | 0.94059 | 0.90212 | -0.03847 |  | 0.93 | 1.05 | 0.045947 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MOUND 4 | 0.94059 | 0.90212 | -0.03847 |  | 0.93 | 1.05 | 0.049649 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | MOUND 4 | 0.94059 | 0.90212 | -0.03847 |  | 0.93 | 1.05 | 0.040149 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MOUND 4 | 0.94059 | 0.90212 | -0.03847 |  | 0.93 | 1.05 | 0.046162 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MOUND 4 | 0.94059 | 0.90212 | -0.03847 |  | 0.93 | 1.05 | 0.044763 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MOUND 4 | 0.94059 | 0.90212 | -0.03847 |  | 0.93 | 1.05 | 0.047325 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MOUND 4 | 0.94059 | 0.90212 | -0.03847 |  | 0.93 | 1.05 | 0.048761 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | MOUND 4 | 0.94059 | 0.90212 | -0.03847 |  | 0.93 | 1.05 | 0.035454 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MOUND 4 | 0.94102 | 0.90242 | -0.038608 |  | 0.93 | 1.05 | 0.055416 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | MOUND 4 | 0.94102 | 0.90242 | -0.038608 |  | 0.93 | 1.05 | 0.031006 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MOUND 4 | 0.94102 | 0.90242 | -0.038608 |  | 0.93 | 1.05 | 0.036106 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MOUND 4 | 0.94102 | 0.90242 | -0.038608 |  | 0.93 | 1.05 | 0.037647 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MOUND 4 | 0.94102 | 0.90242 | -0.038608 |  | 0.93 | 1.05 | 0.048914 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | MOUND 4 | 0.94102 | 0.90242 | -0.038608 |  | 0.93 | 1.05 | 0.048508 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MOUND 4 | 0.94102 | 0.90242 | -0.038608 |  | 0.93 | 1.05 | 0.040159 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | MOUND 4 | 0.94102 | 0.90242 | -0.038608 |  | 0.93 | 1.05 | 0.040068 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | MOUND 4 | 0.94102 | 0.90242 | -0.038608 |  | 0.93 | 1.05 | 0.043101 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MOUND 4 | 0.94102 | 0.90242 | -0.038608 |  | 0.93 | 1.05 | 0.051186 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MOUND 4 | 0.94102 | 0.90242 | -0.038608 |  | 0.93 | 1.05 | 0.041545 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MOUND 4 | 0.94102 | 0.90242 | -0.038608 |  | 0.93 | 1.05 | 0.050897 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MOUND 4 | 0.94102 | 0.90242 | -0.038608 |  | 0.93 | 1.05 | 0.032959 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MOUND 4 | 0.94102 | 0.90242 | -0.038608 |  | 0.93 | 1.05 | 0.050897 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MOUND 4 | 0.94102 | 0.90242 | -0.038608 |  | 0.93 | 1.05 | 0.052178 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MOUND 4 | 0.94102 | 0.90242 | -0.038608 |  | 0.93 | 1.05 | 0.0519 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MOUND 4 | 0.94102 | 0.90242 | -0.038608 |  | 0.93 | 1.05 | 0.034974 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MOUND 4 | 0.94102 | 0.90242 | -0.038608 |  | 0.93 | 1.05 | 0.035428 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | MOUND 4 | 0.94102 | 0.90242 | -0.038608 |  | 0.93 | 1.05 | 0.037496 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | MOUND 4 | 0.94102 | 0.90242 | -0.038608 |  | 0.93 | 1.05 | 0.037496 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MOUND 4 | 0.94102 | 0.90242 | -0.038608 |  | 0.93 | 1.05 | 0.039177 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MOUND 4 | 0.94102 | 0.90242 | -0.038608 |  | 0.93 | 1.05 | 0.049649 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | MOUND 4 | 0.94102 | 0.90242 | -0.038608 |  | 0.93 | 1.05 | 0.040149 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MOUND 4 | 0.94102 | 0.90242 | -0.038608 |  | 0.93 | 1.05 | 0.046162 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MOUND 4 | 0.94102 | 0.90242 | -0.038608 |  | 0.93 | 1.05 | 0.044763 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MOUND 4 | 0.94102 | 0.90242 | -0.038608 |  | 0.93 | 1.05 | 0.047325 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MOUND 4 | 0.94102 | 0.90242 | -0.038608 |  | 0.93 | 1.05 | 0.048761 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | MOUND 4 | 0.94102 | 0.90242 | -0.038608 |  | 0.93 | 1.05 | 0.035454 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MOUND 4 | 0.96949 | 0.89164 | -0.077851 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | MOUND 4 | 0.96949 | 0.89164 | -0.077851 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MOUND 4 | 0.96949 | 0.89164 | -0.077851 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MOUND 4 | 0.96949 | 0.89164 | -0.077851 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MOUND 4 | 0.96949 | 0.89164 | -0.077851 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | MOUND 4 | 0.96949 | 0.89164 | -0.077851 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MOUND 4 | 0.96949 | 0.89164 | -0.077851 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | MOUND 4 | 0.96949 | 0.89164 | -0.077851 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | MOUND 4 | 0.96949 | 0.89164 | -0.077851 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MOUND 4 | 0.96949 | 0.89164 | -0.077851 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MOUND 4 | 0.96949 | 0.89164 | -0.077851 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MOUND 4 | 0.96949 | 0.89164 | -0.077851 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MOUND 4 | 0.96949 | 0.89164 | -0.077851 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MOUND 4 | 0.96949 | 0.89164 | -0.077851 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MOUND 4 | 0.96949 | 0.89164 | -0.077851 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MOUND 4 | 0.96949 | 0.89164 | -0.077851 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MOUND 4 | 0.96949 | 0.89164 | -0.077851 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MOUND 4 | 0.96949 | 0.89164 | -0.077851 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | MOUND 4 | 0.96949 | 0.89164 | -0.077851 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | MOUND 4 | 0.96949 | 0.89164 | -0.077851 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MOUND 4 | 0.96949 | 0.89164 | -0.077851 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MOUND 4 | 0.96949 | 0.89164 | -0.077851 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | MOUND 4 | 0.96949 | 0.89164 | -0.077851 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MOUND 4 | 0.96949 | 0.89164 | -0.077851 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MOUND 4 | 0.96949 | 0.89164 | -0.077851 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MOUND 4 | 0.96949 | 0.89164 | -0.077851 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MOUND 4 | 0.96949 | 0.89164 | -0.077851 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | MOUND 4 | 0.96949 | 0.89164 | -0.077851 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MURLEN 5 | 0.96764 | 0.92735 | -0.040281 |  | 0.93 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MURLEN 5 | 0.96764 | 0.92735 | -0.040281 |  | 0.93 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MURLEN 5 | 0.96764 | 0.92735 | -0.040281 |  | 0.93 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MURLEN 5 | 0.96764 | 0.92735 | -0.040281 |  | 0.93 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MURLEN 5 | 0.96764 | 0.92735 | -0.040281 |  | 0.93 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MURLEN 5 | 0.96764 | 0.92735 | -0.040281 |  | 0.93 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MURLEN 5 | 0.96764 | 0.92735 | -0.040281 |  | 0.93 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MURLEN 5 | 0.96764 | 0.92735 | -0.040281 |  | 0.93 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MURLEN 5 | 0.96764 | 0.92735 | -0.040281 |  | 0.93 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MURLEN 5 | 0.96764 | 0.92735 | -0.040281 |  | 0.93 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MURLEN 5 | 0.96764 | 0.92735 | -0.040281 |  | 0.93 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MURLEN 5 | 0.96764 | 0.92735 | -0.040281 |  | 0.93 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MURLEN 5 | 0.96764 | 0.92735 | -0.040281 |  | 0.93 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MURLEN 5 | 0.96764 | 0.92735 | -0.040281 |  | 0.93 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MURLEN 5 | 0.96764 | 0.92735 | -0.040281 |  | 0.93 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MURLEN 5 | 0.96764 | 0.92735 | -0.040281 |  | 0.93 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MURLEN 5 | 0.96764 | 0.92735 | -0.040281 |  | 0.93 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MURLEN 5 | 0.96764 | 0.92735 | -0.040281 |  | 0.93 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MURLEN 5 | 0.96764 | 0.92735 | -0.040281 |  | 0.93 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MURLEN 5 | 0.96764 | 0.92735 | -0.040281 |  | 0.93 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MURLEN 5 | 0.96037 | 0.91577 | -0.044593 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MURLEN 5 | 0.96037 | 0.91577 | -0.044593 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MURLEN 5 | 0.96037 | 0.91577 | -0.044593 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MURLEN 5 | 0.96037 | 0.91577 | -0.044593 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MURLEN 5 | 0.96037 | 0.91577 | -0.044593 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MURLEN 5 | 0.96037 | 0.91577 | -0.044593 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MURLEN 5 | 0.96037 | 0.91577 | -0.044593 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MURLEN 5 | 0.96037 | 0.91577 | -0.044593 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MURLEN 5 | 0.96037 | 0.91577 | -0.044593 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MURLEN 5 | 0.96037 | 0.91577 | -0.044593 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MURLEN 5 | 0.96037 | 0.91577 | -0.044593 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MURLEN 5 | 0.96037 | 0.91577 | -0.044593 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MURLEN 5 | 0.96037 | 0.91577 | -0.044593 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MURLEN 5 | 0.96037 | 0.91577 | -0.044593 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MURLEN 5 | 0.96037 | 0.91577 | -0.044593 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MURLEN 5 | 0.96037 | 0.91577 | -0.044593 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MURLEN 5 | 0.96037 | 0.91577 | -0.044593 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MURLEN 5 | 0.96037 | 0.91577 | -0.044593 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MURLEN 5 | 0.96037 | 0.91577 | -0.044593 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MURLEN 5 | 0.96037 | 0.91577 | -0.044593 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MURLEN 5 | 0.97167 | 0.92214 | -0.049528 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MURLEN 5 | 0.97167 | 0.92214 | -0.049528 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MURLEN 5 | 0.97167 | 0.92214 | -0.049528 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MURLEN 5 | 0.97167 | 0.92214 | -0.049528 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MURLEN 5 | 0.97167 | 0.92214 | -0.049528 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MURLEN 5 | 0.97167 | 0.92214 | -0.049528 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MURLEN 5 | 0.97167 | 0.92214 | -0.049528 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MURLEN 5 | 0.97167 | 0.92214 | -0.049528 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MURLEN 5 | 0.97167 | 0.92214 | -0.049528 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MURLEN 5 | 0.97167 | 0.92214 | -0.049528 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MURLEN 5 | 0.97167 | 0.92214 | -0.049528 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MURLEN 5 | 0.97167 | 0.92214 | -0.049528 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MURLEN 5 | 0.97167 | 0.92214 | -0.049528 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MURLEN 5 | 0.97167 | 0.92214 | -0.049528 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MURLEN 5 | 0.97167 | 0.92214 | -0.049528 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MURLEN 5 | 0.97167 | 0.92214 | -0.049528 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MURLEN 5 | 0.97167 | 0.92214 | -0.049528 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MURLEN 5 | 0.97167 | 0.92214 | -0.049528 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MURLEN 5 | 0.97167 | 0.92214 | -0.049528 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MURLEN 5 | 0.97167 | 0.92214 | -0.049528 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MURLEN 5 | 0.97512 | 0.89955 | -0.075571 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | MURLEN 5 | 0.97512 | 0.89955 | -0.075571 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MURLEN 5 | 0.97512 | 0.89955 | -0.075571 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MURLEN 5 | 0.97512 | 0.89955 | -0.075571 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MURLEN 5 | 0.97512 | 0.89955 | -0.075571 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | MURLEN 5 | 0.97512 | 0.89955 | -0.075571 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MURLEN 5 | 0.97512 | 0.89955 | -0.075571 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | MURLEN 5 | 0.97512 | 0.89955 | -0.075571 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | MURLEN 5 | 0.97512 | 0.89955 | -0.075571 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MURLEN 5 | 0.97512 | 0.89955 | -0.075571 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MURLEN 5 | 0.97512 | 0.89955 | -0.075571 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MURLEN 5 | 0.97512 | 0.89955 | -0.075571 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MURLEN 5 | 0.97512 | 0.89955 | -0.075571 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MURLEN 5 | 0.97512 | 0.89955 | -0.075571 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MURLEN 5 | 0.97512 | 0.89955 | -0.075571 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MURLEN 5 | 0.97512 | 0.89955 | -0.075571 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MURLEN 5 | 0.97512 | 0.89955 | -0.075571 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MURLEN 5 | 0.97512 | 0.89955 | -0.075571 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | MURLEN 5 | 0.97512 | 0.89955 | -0.075571 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | MURLEN 5 | 0.97512 | 0.89955 | -0.075571 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MURLEN 5 | 0.97512 | 0.89955 | -0.075571 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MURLEN 5 | 0.97512 | 0.89955 | -0.075571 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | MURLEN 5 | 0.97512 | 0.89955 | -0.075571 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MURLEN 5 | 0.97512 | 0.89955 | -0.075571 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MURLEN 5 | 0.97512 | 0.89955 | -0.075571 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MURLEN 5 | 0.97512 | 0.89955 | -0.075571 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MURLEN 5 | 0.97512 | 0.89955 | -0.075571 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | MURLEN 5 | 0.97512 | 0.89955 | -0.075571 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MURLEN 5 | 0.9668 | 0.92555 | -0.041252 |  | 0.93 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MURLEN 5 | 0.9668 | 0.92555 | -0.041252 |  | 0.93 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MURLEN 5 | 0.9668 | 0.92555 | -0.041252 |  | 0.93 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MURLEN 5 | 0.9668 | 0.92555 | -0.041252 |  | 0.93 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MURLEN 5 | 0.9668 | 0.92555 | -0.041252 |  | 0.93 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MURLEN 5 | 0.9668 | 0.92555 | -0.041252 |  | 0.93 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MURLEN 5 | 0.9668 | 0.92555 | -0.041252 |  | 0.93 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MURLEN 5 | 0.9668 | 0.92555 | -0.041252 |  | 0.93 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MURLEN 5 | 0.9668 | 0.92555 | -0.041252 |  | 0.93 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MURLEN 5 | 0.9668 | 0.92555 | -0.041252 |  | 0.93 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MURLEN 5 | 0.9668 | 0.92555 | -0.041252 |  | 0.93 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MURLEN 5 | 0.9668 | 0.92555 | -0.041252 |  | 0.93 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MURLEN 5 | 0.9668 | 0.92555 | -0.041252 |  | 0.93 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MURLEN 5 | 0.9668 | 0.92555 | -0.041252 |  | 0.93 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MURLEN 5 | 0.9668 | 0.92555 | -0.041252 |  | 0.93 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MURLEN 5 | 0.9668 | 0.92555 | -0.041252 |  | 0.93 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MURLEN 5 | 0.9668 | 0.92555 | -0.041252 |  | 0.93 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MURLEN 5 | 0.9668 | 0.92555 | -0.041252 |  | 0.93 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MURLEN 5 | 0.9668 | 0.92555 | -0.041252 |  | 0.93 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MURLEN 5 | 0.9668 | 0.92555 | -0.041252 |  | 0.93 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | MUSTNG5 | 0.9864 | 0.91876 | -0.067642 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | MUSTNG5 | 0.9864 | 0.91876 | -0.067642 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | MUSTNG5 | 0.9864 | 0.91876 | -0.067642 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | MUSTNG5 | 0.9864 | 0.91876 | -0.067642 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | MUSTNG5 | 0.9864 | 0.91876 | -0.067642 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | MUSTNG5 | 0.9864 | 0.91876 | -0.067642 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | MUSTNG5 | 0.9864 | 0.91876 | -0.067642 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | MUSTNG5 | 0.9864 | 0.91876 | -0.067642 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | MUSTNG5 | 0.9864 | 0.91876 | -0.067642 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | MUSTNG5 | 0.9864 | 0.91876 | -0.067642 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | MUSTNG5 | 0.9864 | 0.91876 | -0.067642 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | MUSTNG5 | 0.9864 | 0.91876 | -0.067642 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | MUSTNG5 | 0.9864 | 0.91876 | -0.067642 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | MUSTNG5 | 0.9864 | 0.91876 | -0.067642 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | MUSTNG5 | 0.9864 | 0.91876 | -0.067642 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | MUSTNG5 | 0.9864 | 0.91876 | -0.067642 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | MUSTNG5 | 0.9864 | 0.91876 | -0.067642 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | MUSTNG5 | 0.9864 | 0.91876 | -0.067642 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | MUSTNG5 | 0.9864 | 0.91876 | -0.067642 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | MUSTNG5 | 0.9864 | 0.91876 | -0.067642 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | MUSTNG5 | 0.9864 | 0.91876 | -0.067642 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | MUSTNG5 | 0.9864 | 0.91876 | -0.067642 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | MUSTNG5 | 0.9864 | 0.91876 | -0.067642 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | MUSTNG5 | 0.9864 | 0.91876 | -0.067642 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | MUSTNG5 | 0.9864 | 0.91876 | -0.067642 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | MUSTNG5 | 0.9864 | 0.91876 | -0.067642 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | MUSTNG5 | 0.9864 | 0.91876 | -0.067642 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | MUSTNG5 | 0.9864 | 0.91876 | -0.067642 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NATWOOD3 | 0.95711 | 0.89273 | -0.064381 |  | 0.9 | 1.05 | 0.041569 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NATWOOD3 | 0.95711 | 0.89273 | -0.064381 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NATWOOD3 | 0.95711 | 0.89273 | -0.064381 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NATWOOD3 | 0.95711 | 0.89273 | -0.064381 |  | 0.9 | 1.05 | 0.03222 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NATWOOD3 | 0.95711 | 0.89273 | -0.064381 |  | 0.9 | 1.05 | 0.030633 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NATWOOD3 | 0.95711 | 0.89273 | -0.064381 |  | 0.9 | 1.05 | 0.030061 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NATWOOD3 | 0.95711 | 0.89273 | -0.064381 |  | 0.9 | 1.05 | 0.031207 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NATWOOD3 | 0.95971 | 0.89443 | -0.065278 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NATWOOD3 | 0.95971 | 0.89443 | -0.065278 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NATWOOD3 | 0.96023 | 0.89036 | -0.069864 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NATWOOD3 | 0.96023 | 0.89036 | -0.069864 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NATWOOD3 | 0.96023 | 0.89037 | -0.069864 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NATWOOD3 | 0.96023 | 0.89037 | -0.069864 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NATWOOD3 | 0.96023 | 0.89037 | -0.069865 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NATWOOD3 | 0.96023 | 0.89037 | -0.069865 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NEASTOTTW5 | 1.0102 | 0.92071 | -0.08947 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEASTOTTW5 | 1.0102 | 0.92071 | -0.08947 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NEASTOTTW5 | 1.0102 | 0.92071 | -0.08947 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEASTOTTW5 | 1.0102 | 0.92071 | -0.08947 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NEASTOTTW5 | 1.0102 | 0.92071 | -0.08947 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NEASTOTTW5 | 1.0102 | 0.92071 | -0.08947 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEASTOTTW5 | 1.0102 | 0.92071 | -0.08947 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NEASTOTTW5 | 1.0102 | 0.92071 | -0.08947 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NEASTOTTW5 | 1.0102 | 0.92071 | -0.08947 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEASTOTTW5 | 1.0102 | 0.92071 | -0.08947 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NEASTOTTW5 | 1.0102 | 0.92071 | -0.08947 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NEASTOTTW5 | 1.0102 | 0.92071 | -0.08947 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NEASTOTTW5 | 1.0102 | 0.92071 | -0.08947 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NEASTOTTW5 | 1.0102 | 0.92071 | -0.08947 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NEASTOTTW5 | 1.0102 | 0.92071 | -0.08947 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NEASTOTTW5 | 1.0102 | 0.92071 | -0.08947 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEASTOTTW5 | 1.0102 | 0.92071 | -0.08947 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEASTOTTW5 | 1.0102 | 0.92071 | -0.08947 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NEASTOTTW5 | 1.0102 | 0.92071 | -0.08947 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NEASTOTTW5 | 1.0102 | 0.92071 | -0.08947 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEASTOTTW5 | 1.0102 | 0.92071 | -0.08947 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NEASTOTTW5 | 1.0102 | 0.92071 | -0.08947 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NEASTOTTW5 | 1.0102 | 0.92071 | -0.08947 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEASTOTTW5 | 1.0102 | 0.92071 | -0.08947 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NEASTOTTW5 | 1.0102 | 0.92071 | -0.08947 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEASTOTTW5 | 1.0102 | 0.92071 | -0.08947 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NEASTOTTW5 | 1.0102 | 0.92071 | -0.08947 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | NEASTOTTW5 | 1.0102 | 0.92071 | -0.08947 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NEO SPA5 | 0.97174 | 0.91793 | -0.053811 |  | 0.92 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEO SPA5 | 0.97174 | 0.91793 | -0.053811 |  | 0.92 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NEO SPA5 | 0.97174 | 0.91793 | -0.053811 |  | 0.92 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEO SPA5 | 0.97174 | 0.91793 | -0.053811 |  | 0.92 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEO SPA5 | 0.97174 | 0.91793 | -0.053811 |  | 0.92 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEO SPA5 | 0.97174 | 0.91793 | -0.053811 |  | 0.92 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NEO SPA5 | 0.97174 | 0.91793 | -0.053811 |  | 0.92 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NEO SPA5 | 0.97174 | 0.91793 | -0.053811 |  | 0.92 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEO SPA5 | 0.97174 | 0.91793 | -0.053811 |  | 0.92 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEO SPA5 | 0.97174 | 0.91793 | -0.053811 |  | 0.92 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NEO SPA5 | 0.97174 | 0.91793 | -0.053811 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NEO SPA5 | 0.97174 | 0.91793 | -0.053811 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEO SPA5 | 0.97174 | 0.91793 | -0.053811 |  | 0.92 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEO SPA5 | 0.97174 | 0.91793 | -0.053811 |  | 0.92 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEO SPA5 | 0.97174 | 0.91793 | -0.053811 |  | 0.92 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEO SPA5 | 0.97233 | 0.91905 | -0.053282 |  | 0.92 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NEO SPA5 | 0.97233 | 0.91905 | -0.053282 |  | 0.92 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEO SPA5 | 0.97233 | 0.91905 | -0.053282 |  | 0.92 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEO SPA5 | 0.97233 | 0.91905 | -0.053282 |  | 0.92 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEO SPA5 | 0.97233 | 0.91905 | -0.053282 |  | 0.92 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NEO SPA5 | 0.97233 | 0.91905 | -0.053282 |  | 0.92 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NEO SPA5 | 0.97233 | 0.91905 | -0.053282 |  | 0.92 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEO SPA5 | 0.97233 | 0.91905 | -0.053282 |  | 0.92 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEO SPA5 | 0.97233 | 0.91905 | -0.053282 |  | 0.92 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NEO SPA5 | 0.97233 | 0.91905 | -0.053282 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NEO SPA5 | 0.97233 | 0.91905 | -0.053282 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEO SPA5 | 0.97233 | 0.91905 | -0.053282 |  | 0.92 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEO SPA5 | 0.97233 | 0.91905 | -0.053282 |  | 0.92 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEO SPA5 | 0.97233 | 0.91905 | -0.053282 |  | 0.92 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NEO184 5 | 0.97042 | 0.9157 | -0.054717 |  | 0.925 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEO184 5 | 0.97042 | 0.9157 | -0.054717 |  | 0.925 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NEO184 5 | 0.97042 | 0.9157 | -0.054717 |  | 0.925 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEO184 5 | 0.97042 | 0.9157 | -0.054717 |  | 0.925 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEO184 5 | 0.97042 | 0.9157 | -0.054717 |  | 0.925 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEO184 5 | 0.97042 | 0.9157 | -0.054717 |  | 0.925 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NEO184 5 | 0.97042 | 0.9157 | -0.054717 |  | 0.925 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NEO184 5 | 0.97042 | 0.9157 | -0.054717 |  | 0.925 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEO184 5 | 0.97042 | 0.9157 | -0.054717 |  | 0.925 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEO184 5 | 0.97042 | 0.9157 | -0.054717 |  | 0.925 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NEO184 5 | 0.97042 | 0.9157 | -0.054717 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NEO184 5 | 0.97042 | 0.9157 | -0.054717 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEO184 5 | 0.97042 | 0.9157 | -0.054717 |  | 0.925 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEO184 5 | 0.97042 | 0.9157 | -0.054717 |  | 0.925 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEO184 5 | 0.97042 | 0.9157 | -0.054717 |  | 0.925 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEO184 5 | 0.97097 | 0.9168 | -0.054171 |  | 0.925 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NEO184 5 | 0.97097 | 0.9168 | -0.054171 |  | 0.925 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEO184 5 | 0.97097 | 0.9168 | -0.054171 |  | 0.925 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEO184 5 | 0.97097 | 0.9168 | -0.054171 |  | 0.925 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEO184 5 | 0.97097 | 0.9168 | -0.054171 |  | 0.925 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NEO184 5 | 0.97097 | 0.9168 | -0.054171 |  | 0.925 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NEO184 5 | 0.97097 | 0.9168 | -0.054171 |  | 0.925 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEO184 5 | 0.97097 | 0.9168 | -0.054171 |  | 0.925 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEO184 5 | 0.97097 | 0.9168 | -0.054171 |  | 0.925 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NEO184 5 | 0.97097 | 0.9168 | -0.054171 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NEO184 5 | 0.97097 | 0.9168 | -0.054171 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEO184 5 | 0.97097 | 0.9168 | -0.054171 |  | 0.925 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEO184 5 | 0.97097 | 0.9168 | -0.054171 |  | 0.925 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEO184 5 | 0.97097 | 0.9168 | -0.054171 |  | 0.925 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NEO184 5 | 0.97152 | 0.92241 | -0.049111 |  | 0.925 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEO184 5 | 0.97152 | 0.92241 | -0.049111 |  | 0.925 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NEO184 5 | 0.97152 | 0.92241 | -0.049111 |  | 0.925 | 1.05 | 0.055405 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEO184 5 | 0.97152 | 0.92241 | -0.049111 |  | 0.925 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEO184 5 | 0.97152 | 0.92241 | -0.049111 |  | 0.925 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEO184 5 | 0.97152 | 0.92241 | -0.049111 |  | 0.925 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NEO184 5 | 0.97152 | 0.92241 | -0.049111 |  | 0.925 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NEO184 5 | 0.97152 | 0.92241 | -0.049111 |  | 0.925 | 1.05 | 0.082012 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEO184 5 | 0.97152 | 0.92241 | -0.049111 |  | 0.925 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEO184 5 | 0.97152 | 0.92241 | -0.049111 |  | 0.925 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NEO184 5 | 0.97152 | 0.92241 | -0.049111 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NEO184 5 | 0.97152 | 0.92241 | -0.049111 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEO184 5 | 0.97152 | 0.92241 | -0.049111 |  | 0.925 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEO184 5 | 0.97152 | 0.92241 | -0.049111 |  | 0.925 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEO184 5 | 0.97152 | 0.92241 | -0.049111 |  | 0.925 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | NEOSHO 4 | 0.94947 | 0.90381 | -0.045657 |  | 0.93 | 1.05 | 0.077629 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | NEOSHO 4 | 0.94947 | 0.90381 | -0.045657 |  | 0.93 | 1.05 | 0.06446 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | NEOSHO 4 | 0.94947 | 0.90381 | -0.045657 |  | 0.93 | 1.05 | 0.066434 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | NEOSHO 4 | 0.94947 | 0.90381 | -0.045657 |  | 0.93 | 1.05 | 0.073293 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEOSHO 4 | 0.94947 | 0.90381 | -0.045657 |  | 0.93 | 1.05 | 0.053415 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-122 | NEOSHO 4 | 0.94947 | 0.90381 | -0.045657 |  | 0.93 | 1.05 | 0.08103 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-177 | NEOSHO 4 | 0.94947 | 0.90381 | -0.045657 |  | 0.93 | 1.05 | 0.08268 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-178 | NEOSHO 4 | 0.94947 | 0.90381 | -0.045657 |  | 0.93 | 1.05 | 0.077122 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NEOSHO 4 | 0.94947 | 0.90381 | -0.045657 |  | 0.93 | 1.05 | 0.032185 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | NEOSHO 4 | 0.94947 | 0.90381 | -0.045657 |  | 0.93 | 1.05 | 0.073922 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-232 | NEOSHO 4 | 0.94947 | 0.90381 | -0.045657 |  | 0.93 | 1.05 | 0.076776 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | NEOSHO 4 | 0.94947 | 0.90381 | -0.045657 |  | 0.93 | 1.05 | 0.06446 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEOSHO 4 | 0.94947 | 0.90381 | -0.045657 |  | 0.93 | 1.05 | 0.038841 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NEOSHO 4 | 0.94947 | 0.90381 | -0.045657 |  | 0.93 | 1.05 | 0.034687 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NEOSHO 4 | 0.94947 | 0.90381 | -0.045657 |  | 0.93 | 1.05 | 0.034687 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NEOSHO 4 | 0.94947 | 0.90381 | -0.045657 |  | 0.93 | 1.05 | 0.031574 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | NEOSHO 4 | 0.94947 | 0.90381 | -0.045657 |  | 0.93 | 1.05 | 0.042889 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-376 | NEOSHO 4 | 0.94947 | 0.90381 | -0.045657 |  | 0.93 | 1.05 | 0.079908 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEOSHO 4 | 0.94635 | 0.90473 | -0.041623 |  | 0.93 | 1.05 | 0.040299 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NEOSHO 4 | 0.94635 | 0.90473 | -0.041623 |  | 0.93 | 1.05 | 0.048812 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEOSHO 4 | 0.94635 | 0.90473 | -0.041623 |  | 0.93 | 1.05 | 0.076211 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEOSHO 4 | 0.94635 | 0.90473 | -0.041623 |  | 0.93 | 1.05 | 0.069331 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEOSHO 4 | 0.94635 | 0.90473 | -0.041623 |  | 0.93 | 1.05 | 0.035943 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NEOSHO 4 | 0.94635 | 0.90473 | -0.041623 |  | 0.93 | 1.05 | 0.034061 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NEOSHO 4 | 0.94635 | 0.90473 | -0.041623 |  | 0.93 | 1.05 | 0.064216 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEOSHO 4 | 0.94635 | 0.90473 | -0.041623 |  | 0.93 | 1.05 | 0.045005 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEOSHO 4 | 0.94635 | 0.90473 | -0.041623 |  | 0.93 | 1.05 | 0.13572 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NEOSHO 4 | 0.94635 | 0.90473 | -0.041623 |  | 0.93 | 1.05 | 0.037472 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NEOSHO 4 | 0.94635 | 0.90473 | -0.041623 |  | 0.93 | 1.05 | 0.037472 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEOSHO 4 | 0.94635 | 0.90473 | -0.041623 |  | 0.93 | 1.05 | 0.06894 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEOSHO 4 | 0.94635 | 0.90473 | -0.041623 |  | 0.93 | 1.05 | 0.034713 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEOSHO 4 | 0.94635 | 0.90473 | -0.041623 |  | 0.93 | 1.05 | 0.035229 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NEOSHO 4 | 0.94641 | 0.90505 | -0.041357 |  | 0.93 | 1.05 | 0.094783 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEOSHO 4 | 0.94641 | 0.90505 | -0.041357 |  | 0.93 | 1.05 | 0.03645 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEOSHO 4 | 0.94641 | 0.90505 | -0.041357 |  | 0.93 | 1.05 | 0.04755 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NEOSHO 4 | 0.94641 | 0.90505 | -0.041357 |  | 0.93 | 1.05 | 0.06097 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEOSHO 4 | 0.94641 | 0.90505 | -0.041357 |  | 0.93 | 1.05 | 0.061051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NEOSHO 4 | 0.94641 | 0.90505 | -0.041357 |  | 0.93 | 1.05 | 0.04456 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NEOSHO 4 | 0.94641 | 0.90505 | -0.041357 |  | 0.93 | 1.05 | 0.048811 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEOSHO 4 | 0.94641 | 0.90505 | -0.041357 |  | 0.93 | 1.05 | 0.13004 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NEOSHO 4 | 0.94641 | 0.90505 | -0.041357 |  | 0.93 | 1.05 | 0.049018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NEOSHO 4 | 0.94641 | 0.90505 | -0.041357 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NEOSHO 4 | 0.94641 | 0.90505 | -0.041357 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NEOSHO 4 | 0.94641 | 0.90505 | -0.041357 |  | 0.93 | 1.05 | 0.05974 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NEOSHO 4 | 0.94641 | 0.90505 | -0.041357 |  | 0.93 | 1.05 | 0.076949 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEOSHO 4 | 0.94641 | 0.90505 | -0.041357 |  | 0.93 | 1.05 | 0.042157 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEOSHO 4 | 0.94641 | 0.90505 | -0.041357 |  | 0.93 | 1.05 | 0.040957 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NEOSHO 4 | 0.94641 | 0.90505 | -0.041357 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NEOSHO 4 | 0.94641 | 0.90505 | -0.041357 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEOSHO 4 | 0.94641 | 0.90505 | -0.041357 |  | 0.93 | 1.05 | 0.054637 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NEOSHO 4 | 0.94641 | 0.90505 | -0.041357 |  | 0.93 | 1.05 | 0.060597 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NEOSHO 4 | 0.94641 | 0.90505 | -0.041357 |  | 0.93 | 1.05 | 0.044286 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEOSHO 4 | 0.94641 | 0.90505 | -0.041357 |  | 0.93 | 1.05 | 0.059107 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NEOSHO 4 | 0.94641 | 0.90505 | -0.041357 |  | 0.93 | 1.05 | 0.052698 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEOSHO 4 | 0.94641 | 0.90505 | -0.041357 |  | 0.93 | 1.05 | 0.067422 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NEOSHO 4 | 0.94641 | 0.90505 | -0.041357 |  | 0.93 | 1.05 | 0.053768 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | NEOSHO 4 | 0.94641 | 0.90505 | -0.041357 |  | 0.93 | 1.05 | 0.03909 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NEOSHO 4 | 0.94526 | 0.90058 | -0.04468 |  | 0.93 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEOSHO 4 | 0.94526 | 0.90058 | -0.04468 |  | 0.93 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NEOSHO 4 | 0.94526 | 0.90058 | -0.04468 |  | 0.93 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEOSHO 4 | 0.94526 | 0.90058 | -0.04468 |  | 0.93 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NEOSHO 4 | 0.94526 | 0.90058 | -0.04468 |  | 0.93 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NEOSHO 4 | 0.94526 | 0.90058 | -0.04468 |  | 0.93 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEOSHO 4 | 0.94526 | 0.90058 | -0.04468 |  | 0.93 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NEOSHO 4 | 0.94526 | 0.90058 | -0.04468 |  | 0.93 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEOSHO 4 | 0.94526 | 0.90058 | -0.04468 |  | 0.93 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NEOSHO 4 | 0.94526 | 0.90058 | -0.04468 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NEOSHO 4 | 0.94526 | 0.90058 | -0.04468 |  | 0.93 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NEOSHO 4 | 0.94526 | 0.90058 | -0.04468 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NEOSHO 4 | 0.94526 | 0.90058 | -0.04468 |  | 0.93 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NEOSHO 4 | 0.94526 | 0.90058 | -0.04468 |  | 0.93 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEOSHO 4 | 0.94526 | 0.90058 | -0.04468 |  | 0.93 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEOSHO 4 | 0.94526 | 0.90058 | -0.04468 |  | 0.93 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEOSHO 4 | 0.94526 | 0.90058 | -0.04468 |  | 0.93 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NEOSHO 4 | 0.94526 | 0.90058 | -0.04468 |  | 0.93 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEOSHO 4 | 0.94526 | 0.90058 | -0.04468 |  | 0.93 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NEOSHO 4 | 0.94526 | 0.90058 | -0.04468 |  | 0.93 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEOSHO 4 | 0.94526 | 0.90058 | -0.04468 |  | 0.93 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NEOSHO 4 | 0.94526 | 0.90058 | -0.04468 |  | 0.93 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NEOSHO 4 | 0.94558 | 0.88501 | -0.060575 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEOSHO 4 | 0.94558 | 0.88501 | -0.060575 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NEOSHO 4 | 0.94558 | 0.88501 | -0.060575 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEOSHO 4 | 0.94558 | 0.88501 | -0.060575 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NEOSHO 4 | 0.94558 | 0.88501 | -0.060575 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NEOSHO 4 | 0.94558 | 0.88501 | -0.060575 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEOSHO 4 | 0.94558 | 0.88501 | -0.060575 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NEOSHO 4 | 0.94558 | 0.88501 | -0.060575 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NEOSHO 4 | 0.94558 | 0.88501 | -0.060575 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEOSHO 4 | 0.94558 | 0.88501 | -0.060575 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NEOSHO 4 | 0.94558 | 0.88501 | -0.060575 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NEOSHO 4 | 0.94558 | 0.88501 | -0.060575 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NEOSHO 4 | 0.94558 | 0.88501 | -0.060575 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NEOSHO 4 | 0.94558 | 0.88501 | -0.060575 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NEOSHO 4 | 0.94558 | 0.88501 | -0.060575 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NEOSHO 4 | 0.94558 | 0.88501 | -0.060575 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEOSHO 4 | 0.94558 | 0.88501 | -0.060575 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEOSHO 4 | 0.94558 | 0.88501 | -0.060575 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NEOSHO 4 | 0.94558 | 0.88501 | -0.060575 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NEOSHO 4 | 0.94558 | 0.88501 | -0.060575 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEOSHO 4 | 0.94558 | 0.88501 | -0.060575 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NEOSHO 4 | 0.94558 | 0.88501 | -0.060575 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NEOSHO 4 | 0.94558 | 0.88501 | -0.060575 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEOSHO 4 | 0.94558 | 0.88501 | -0.060575 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NEOSHO 4 | 0.94558 | 0.88501 | -0.060575 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEOSHO 4 | 0.94558 | 0.88501 | -0.060575 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NEOSHO 4 | 0.94558 | 0.88501 | -0.060575 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | NEOSHO 4 | 0.94558 | 0.88501 | -0.060575 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NEOSHO 5 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEOSHO 5 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NEOSHO 5 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEOSHO 5 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NEOSHO 5 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NEOSHO 5 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEOSHO 5 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NEOSHO 5 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NEOSHO 5 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEOSHO 5 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NEOSHO 5 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NEOSHO 5 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NEOSHO 5 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NEOSHO 5 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NEOSHO 5 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NEOSHO 5 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEOSHO 5 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEOSHO 5 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NEOSHO 5 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NEOSHO 5 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEOSHO 5 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NEOSHO 5 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NEOSHO 5 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEOSHO 5 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NEOSHO 5 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEOSHO 5 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NEOSHO 5 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | NEOSHO 5 | 0.98808 | 0.92559 | -0.062487 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | NEOSHO 7 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.077629 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | NEOSHO 7 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.06446 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | NEOSHO 7 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.066434 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | NEOSHO 7 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.073293 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEOSHO 7 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.053415 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-122 | NEOSHO 7 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.08103 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-177 | NEOSHO 7 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.08268 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-178 | NEOSHO 7 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.077122 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NEOSHO 7 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.032185 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | NEOSHO 7 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.073922 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-232 | NEOSHO 7 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.076776 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | NEOSHO 7 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.06446 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEOSHO 7 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.038841 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NEOSHO 7 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.034687 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NEOSHO 7 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.034687 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NEOSHO 7 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.031574 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | NEOSHO 7 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.042889 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-376 | NEOSHO 7 | 0.99916 | 0.94696 | -0.052197 |  | 0.95 | 1.05 | 0.079908 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEOSHO 7 | 0.99592 | 0.9481 | -0.047817 |  | 0.95 | 1.05 | 0.040299 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NEOSHO 7 | 0.99592 | 0.9481 | -0.047817 |  | 0.95 | 1.05 | 0.048812 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEOSHO 7 | 0.99592 | 0.9481 | -0.047817 |  | 0.95 | 1.05 | 0.076211 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEOSHO 7 | 0.99592 | 0.9481 | -0.047817 |  | 0.95 | 1.05 | 0.069331 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEOSHO 7 | 0.99592 | 0.9481 | -0.047817 |  | 0.95 | 1.05 | 0.035943 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NEOSHO 7 | 0.99592 | 0.9481 | -0.047817 |  | 0.95 | 1.05 | 0.034061 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NEOSHO 7 | 0.99592 | 0.9481 | -0.047817 |  | 0.95 | 1.05 | 0.064216 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEOSHO 7 | 0.99592 | 0.9481 | -0.047817 |  | 0.95 | 1.05 | 0.045005 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEOSHO 7 | 0.99592 | 0.9481 | -0.047817 |  | 0.95 | 1.05 | 0.13572 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NEOSHO 7 | 0.99592 | 0.9481 | -0.047817 |  | 0.95 | 1.05 | 0.037472 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NEOSHO 7 | 0.99592 | 0.9481 | -0.047817 |  | 0.95 | 1.05 | 0.037472 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEOSHO 7 | 0.99592 | 0.9481 | -0.047817 |  | 0.95 | 1.05 | 0.06894 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEOSHO 7 | 0.99592 | 0.9481 | -0.047817 |  | 0.95 | 1.05 | 0.034713 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEOSHO 7 | 0.99592 | 0.9481 | -0.047817 |  | 0.95 | 1.05 | 0.035229 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NEOSHO 7 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.094783 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEOSHO 7 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.03645 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEOSHO 7 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.04755 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NEOSHO 7 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.06097 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEOSHO 7 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.061051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NEOSHO 7 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.04456 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NEOSHO 7 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.048811 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEOSHO 7 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.13004 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NEOSHO 7 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.049018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NEOSHO 7 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NEOSHO 7 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NEOSHO 7 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.05974 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NEOSHO 7 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.076949 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEOSHO 7 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.042157 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEOSHO 7 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.040957 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NEOSHO 7 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NEOSHO 7 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEOSHO 7 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.054637 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NEOSHO 7 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.060597 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NEOSHO 7 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.044286 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEOSHO 7 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.059107 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NEOSHO 7 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.052698 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEOSHO 7 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.067422 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NEOSHO 7 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.053768 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | NEOSHO 7 | 0.99619 | 0.94965 | -0.046544 |  | 0.95 | 1.05 | 0.03909 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NEOSHO 7 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEOSHO 7 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NEOSHO 7 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEOSHO 7 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NEOSHO 7 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NEOSHO 7 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEOSHO 7 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NEOSHO 7 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEOSHO 7 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NEOSHO 7 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NEOSHO 7 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NEOSHO 7 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NEOSHO 7 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NEOSHO 7 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEOSHO 7 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEOSHO 7 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEOSHO 7 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NEOSHO 7 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEOSHO 7 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NEOSHO 7 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEOSHO 7 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NEOSHO 7 | 0.99476 | 0.94256 | -0.052198 |  | 0.95 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NEOSHO 7 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEOSHO 7 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NEOSHO 7 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEOSHO 7 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NEOSHO 7 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NEOSHO 7 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEOSHO 7 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NEOSHO 7 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NEOSHO 7 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEOSHO 7 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NEOSHO 7 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NEOSHO 7 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NEOSHO 7 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NEOSHO 7 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NEOSHO 7 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NEOSHO 7 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEOSHO 7 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEOSHO 7 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NEOSHO 7 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NEOSHO 7 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEOSHO 7 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NEOSHO 7 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NEOSHO 7 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEOSHO 7 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NEOSHO 7 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEOSHO 7 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NEOSHO 7 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | NEOSHO 7 | 0.99483 | 0.92459 | -0.070241 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | NEOSHON2 | 0.95638 | 0.91413 | -0.042252 |  | 0.93 | 1.05 | 0.077629 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | NEOSHON2 | 0.95638 | 0.91413 | -0.042252 |  | 0.93 | 1.05 | 0.06446 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | NEOSHON2 | 0.95638 | 0.91413 | -0.042252 |  | 0.93 | 1.05 | 0.066434 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | NEOSHON2 | 0.95638 | 0.91413 | -0.042252 |  | 0.93 | 1.05 | 0.073293 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEOSHON2 | 0.95638 | 0.91413 | -0.042252 |  | 0.93 | 1.05 | 0.053415 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-122 | NEOSHON2 | 0.95638 | 0.91413 | -0.042252 |  | 0.93 | 1.05 | 0.08103 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-177 | NEOSHON2 | 0.95638 | 0.91413 | -0.042252 |  | 0.93 | 1.05 | 0.08268 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-178 | NEOSHON2 | 0.95638 | 0.91413 | -0.042252 |  | 0.93 | 1.05 | 0.077122 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NEOSHON2 | 0.95638 | 0.91413 | -0.042252 |  | 0.93 | 1.05 | 0.032185 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | NEOSHON2 | 0.95638 | 0.91413 | -0.042252 |  | 0.93 | 1.05 | 0.073922 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-232 | NEOSHON2 | 0.95638 | 0.91413 | -0.042252 |  | 0.93 | 1.05 | 0.076776 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | NEOSHON2 | 0.95638 | 0.91413 | -0.042252 |  | 0.93 | 1.05 | 0.06446 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEOSHON2 | 0.95638 | 0.91413 | -0.042252 |  | 0.93 | 1.05 | 0.038841 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NEOSHON2 | 0.95638 | 0.91413 | -0.042252 |  | 0.93 | 1.05 | 0.034687 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NEOSHON2 | 0.95638 | 0.91413 | -0.042252 |  | 0.93 | 1.05 | 0.034687 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NEOSHON2 | 0.95638 | 0.91413 | -0.042252 |  | 0.93 | 1.05 | 0.031574 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | NEOSHON2 | 0.95638 | 0.91413 | -0.042252 |  | 0.93 | 1.05 | 0.042889 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-376 | NEOSHON2 | 0.95638 | 0.91413 | -0.042252 |  | 0.93 | 1.05 | 0.079908 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEOSHON2 | 0.95346 | 0.91511 | -0.038342 |  | 0.93 | 1.05 | 0.040299 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NEOSHON2 | 0.95346 | 0.91511 | -0.038342 |  | 0.93 | 1.05 | 0.048812 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEOSHON2 | 0.95346 | 0.91511 | -0.038342 |  | 0.93 | 1.05 | 0.076211 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEOSHON2 | 0.95346 | 0.91511 | -0.038342 |  | 0.93 | 1.05 | 0.069331 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEOSHON2 | 0.95346 | 0.91511 | -0.038342 |  | 0.93 | 1.05 | 0.035943 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NEOSHON2 | 0.95346 | 0.91511 | -0.038342 |  | 0.93 | 1.05 | 0.034061 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NEOSHON2 | 0.95346 | 0.91511 | -0.038342 |  | 0.93 | 1.05 | 0.064216 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEOSHON2 | 0.95346 | 0.91511 | -0.038342 |  | 0.93 | 1.05 | 0.045005 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEOSHON2 | 0.95346 | 0.91511 | -0.038342 |  | 0.93 | 1.05 | 0.13572 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NEOSHON2 | 0.95346 | 0.91511 | -0.038342 |  | 0.93 | 1.05 | 0.037472 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NEOSHON2 | 0.95346 | 0.91511 | -0.038342 |  | 0.93 | 1.05 | 0.037472 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEOSHON2 | 0.95346 | 0.91511 | -0.038342 |  | 0.93 | 1.05 | 0.06894 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEOSHON2 | 0.95346 | 0.91511 | -0.038342 |  | 0.93 | 1.05 | 0.034713 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEOSHON2 | 0.95346 | 0.91511 | -0.038342 |  | 0.93 | 1.05 | 0.035229 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NEOSHON2 | 0.95346 | 0.91533 | -0.038133 |  | 0.93 | 1.05 | 0.094783 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEOSHON2 | 0.95346 | 0.91533 | -0.038133 |  | 0.93 | 1.05 | 0.03645 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEOSHON2 | 0.95346 | 0.91533 | -0.038133 |  | 0.93 | 1.05 | 0.04755 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NEOSHON2 | 0.95346 | 0.91533 | -0.038133 |  | 0.93 | 1.05 | 0.06097 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEOSHON2 | 0.95346 | 0.91533 | -0.038133 |  | 0.93 | 1.05 | 0.061051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NEOSHON2 | 0.95346 | 0.91533 | -0.038133 |  | 0.93 | 1.05 | 0.04456 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NEOSHON2 | 0.95346 | 0.91533 | -0.038133 |  | 0.93 | 1.05 | 0.048811 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEOSHON2 | 0.95346 | 0.91533 | -0.038133 |  | 0.93 | 1.05 | 0.13004 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NEOSHON2 | 0.95346 | 0.91533 | -0.038133 |  | 0.93 | 1.05 | 0.049018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NEOSHON2 | 0.95346 | 0.91533 | -0.038133 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NEOSHON2 | 0.95346 | 0.91533 | -0.038133 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NEOSHON2 | 0.95346 | 0.91533 | -0.038133 |  | 0.93 | 1.05 | 0.05974 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NEOSHON2 | 0.95346 | 0.91533 | -0.038133 |  | 0.93 | 1.05 | 0.076949 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEOSHON2 | 0.95346 | 0.91533 | -0.038133 |  | 0.93 | 1.05 | 0.042157 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEOSHON2 | 0.95346 | 0.91533 | -0.038133 |  | 0.93 | 1.05 | 0.040957 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NEOSHON2 | 0.95346 | 0.91533 | -0.038133 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NEOSHON2 | 0.95346 | 0.91533 | -0.038133 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEOSHON2 | 0.95346 | 0.91533 | -0.038133 |  | 0.93 | 1.05 | 0.054637 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NEOSHON2 | 0.95346 | 0.91533 | -0.038133 |  | 0.93 | 1.05 | 0.060597 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NEOSHON2 | 0.95346 | 0.91533 | -0.038133 |  | 0.93 | 1.05 | 0.044286 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEOSHON2 | 0.95346 | 0.91533 | -0.038133 |  | 0.93 | 1.05 | 0.059107 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NEOSHON2 | 0.95346 | 0.91533 | -0.038133 |  | 0.93 | 1.05 | 0.052698 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEOSHON2 | 0.95346 | 0.91533 | -0.038133 |  | 0.93 | 1.05 | 0.067422 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NEOSHON2 | 0.95346 | 0.91533 | -0.038133 |  | 0.93 | 1.05 | 0.053768 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | NEOSHON2 | 0.95346 | 0.91533 | -0.038133 |  | 0.93 | 1.05 | 0.03909 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NEOSHON2 | 0.95235 | 0.91133 | -0.041023 |  | 0.93 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEOSHON2 | 0.95235 | 0.91133 | -0.041023 |  | 0.93 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NEOSHON2 | 0.95235 | 0.91133 | -0.041023 |  | 0.93 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEOSHON2 | 0.95235 | 0.91133 | -0.041023 |  | 0.93 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NEOSHON2 | 0.95235 | 0.91133 | -0.041023 |  | 0.93 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NEOSHON2 | 0.95235 | 0.91133 | -0.041023 |  | 0.93 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEOSHON2 | 0.95235 | 0.91133 | -0.041023 |  | 0.93 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NEOSHON2 | 0.95235 | 0.91133 | -0.041023 |  | 0.93 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEOSHON2 | 0.95235 | 0.91133 | -0.041023 |  | 0.93 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NEOSHON2 | 0.95235 | 0.91133 | -0.041023 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NEOSHON2 | 0.95235 | 0.91133 | -0.041023 |  | 0.93 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NEOSHON2 | 0.95235 | 0.91133 | -0.041023 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NEOSHON2 | 0.95235 | 0.91133 | -0.041023 |  | 0.93 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NEOSHON2 | 0.95235 | 0.91133 | -0.041023 |  | 0.93 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEOSHON2 | 0.95235 | 0.91133 | -0.041023 |  | 0.93 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEOSHON2 | 0.95235 | 0.91133 | -0.041023 |  | 0.93 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEOSHON2 | 0.95235 | 0.91133 | -0.041023 |  | 0.93 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NEOSHON2 | 0.95235 | 0.91133 | -0.041023 |  | 0.93 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEOSHON2 | 0.95235 | 0.91133 | -0.041023 |  | 0.93 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NEOSHON2 | 0.95235 | 0.91133 | -0.041023 |  | 0.93 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEOSHON2 | 0.95235 | 0.91133 | -0.041023 |  | 0.93 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NEOSHON2 | 0.95235 | 0.91133 | -0.041023 |  | 0.93 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NEOSHON2 | 0.95268 | 0.89687 | -0.055818 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEOSHON2 | 0.95268 | 0.89687 | -0.055818 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NEOSHON2 | 0.95268 | 0.89687 | -0.055818 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEOSHON2 | 0.95268 | 0.89687 | -0.055818 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NEOSHON2 | 0.95268 | 0.89687 | -0.055818 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NEOSHON2 | 0.95268 | 0.89687 | -0.055818 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEOSHON2 | 0.95268 | 0.89687 | -0.055818 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NEOSHON2 | 0.95268 | 0.89687 | -0.055818 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NEOSHON2 | 0.95268 | 0.89687 | -0.055818 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEOSHON2 | 0.95268 | 0.89687 | -0.055818 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NEOSHON2 | 0.95268 | 0.89687 | -0.055818 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NEOSHON2 | 0.95268 | 0.89687 | -0.055818 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NEOSHON2 | 0.95268 | 0.89687 | -0.055818 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NEOSHON2 | 0.95268 | 0.89687 | -0.055818 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NEOSHON2 | 0.95268 | 0.89687 | -0.055818 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NEOSHON2 | 0.95268 | 0.89687 | -0.055818 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEOSHON2 | 0.95268 | 0.89687 | -0.055818 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEOSHON2 | 0.95268 | 0.89687 | -0.055818 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NEOSHON2 | 0.95268 | 0.89687 | -0.055818 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NEOSHON2 | 0.95268 | 0.89687 | -0.055818 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEOSHON2 | 0.95268 | 0.89687 | -0.055818 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NEOSHON2 | 0.95268 | 0.89687 | -0.055818 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NEOSHON2 | 0.95268 | 0.89687 | -0.055818 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEOSHON2 | 0.95268 | 0.89687 | -0.055818 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NEOSHON2 | 0.95268 | 0.89687 | -0.055818 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEOSHON2 | 0.95268 | 0.89687 | -0.055818 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NEOSHON2 | 0.95268 | 0.89687 | -0.055818 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | NEOSHON2 | 0.95268 | 0.89687 | -0.055818 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | NEOSHON4 | 0.94953 | 0.90389 | -0.045644 |  | 0.93 | 1.05 | 0.077629 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | NEOSHON4 | 0.94953 | 0.90389 | -0.045644 |  | 0.93 | 1.05 | 0.06446 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | NEOSHON4 | 0.94953 | 0.90389 | -0.045644 |  | 0.93 | 1.05 | 0.066434 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | NEOSHON4 | 0.94953 | 0.90389 | -0.045644 |  | 0.93 | 1.05 | 0.073293 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEOSHON4 | 0.94953 | 0.90389 | -0.045644 |  | 0.93 | 1.05 | 0.053415 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-122 | NEOSHON4 | 0.94953 | 0.90389 | -0.045644 |  | 0.93 | 1.05 | 0.08103 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-177 | NEOSHON4 | 0.94953 | 0.90389 | -0.045644 |  | 0.93 | 1.05 | 0.08268 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-178 | NEOSHON4 | 0.94953 | 0.90389 | -0.045644 |  | 0.93 | 1.05 | 0.077122 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NEOSHON4 | 0.94953 | 0.90389 | -0.045644 |  | 0.93 | 1.05 | 0.032185 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | NEOSHON4 | 0.94953 | 0.90389 | -0.045644 |  | 0.93 | 1.05 | 0.073922 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-232 | NEOSHON4 | 0.94953 | 0.90389 | -0.045644 |  | 0.93 | 1.05 | 0.076776 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | NEOSHON4 | 0.94953 | 0.90389 | -0.045644 |  | 0.93 | 1.05 | 0.06446 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEOSHON4 | 0.94953 | 0.90389 | -0.045644 |  | 0.93 | 1.05 | 0.038841 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NEOSHON4 | 0.94953 | 0.90389 | -0.045644 |  | 0.93 | 1.05 | 0.034687 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NEOSHON4 | 0.94953 | 0.90389 | -0.045644 |  | 0.93 | 1.05 | 0.034687 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NEOSHON4 | 0.94953 | 0.90389 | -0.045644 |  | 0.93 | 1.05 | 0.031574 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | NEOSHON4 | 0.94953 | 0.90389 | -0.045644 |  | 0.93 | 1.05 | 0.042889 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-376 | NEOSHON4 | 0.94953 | 0.90389 | -0.045644 |  | 0.93 | 1.05 | 0.079908 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEOSHON4 | 0.94641 | 0.9048 | -0.041609 |  | 0.93 | 1.05 | 0.040299 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NEOSHON4 | 0.94641 | 0.9048 | -0.041609 |  | 0.93 | 1.05 | 0.048812 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEOSHON4 | 0.94641 | 0.9048 | -0.041609 |  | 0.93 | 1.05 | 0.076211 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEOSHON4 | 0.94641 | 0.9048 | -0.041609 |  | 0.93 | 1.05 | 0.069331 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEOSHON4 | 0.94641 | 0.9048 | -0.041609 |  | 0.93 | 1.05 | 0.035943 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NEOSHON4 | 0.94641 | 0.9048 | -0.041609 |  | 0.93 | 1.05 | 0.034061 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NEOSHON4 | 0.94641 | 0.9048 | -0.041609 |  | 0.93 | 1.05 | 0.064216 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEOSHON4 | 0.94641 | 0.9048 | -0.041609 |  | 0.93 | 1.05 | 0.045005 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEOSHON4 | 0.94641 | 0.9048 | -0.041609 |  | 0.93 | 1.05 | 0.13572 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NEOSHON4 | 0.94641 | 0.9048 | -0.041609 |  | 0.93 | 1.05 | 0.037472 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NEOSHON4 | 0.94641 | 0.9048 | -0.041609 |  | 0.93 | 1.05 | 0.037472 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEOSHON4 | 0.94641 | 0.9048 | -0.041609 |  | 0.93 | 1.05 | 0.06894 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEOSHON4 | 0.94641 | 0.9048 | -0.041609 |  | 0.93 | 1.05 | 0.034713 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEOSHON4 | 0.94641 | 0.9048 | -0.041609 |  | 0.93 | 1.05 | 0.035229 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NEOSHON4 | 0.94647 | 0.90512 | -0.041345 |  | 0.93 | 1.05 | 0.094783 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEOSHON4 | 0.94647 | 0.90512 | -0.041345 |  | 0.93 | 1.05 | 0.03645 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEOSHON4 | 0.94647 | 0.90512 | -0.041345 |  | 0.93 | 1.05 | 0.04755 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NEOSHON4 | 0.94647 | 0.90512 | -0.041345 |  | 0.93 | 1.05 | 0.06097 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEOSHON4 | 0.94647 | 0.90512 | -0.041345 |  | 0.93 | 1.05 | 0.061051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NEOSHON4 | 0.94647 | 0.90512 | -0.041345 |  | 0.93 | 1.05 | 0.04456 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NEOSHON4 | 0.94647 | 0.90512 | -0.041345 |  | 0.93 | 1.05 | 0.048811 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEOSHON4 | 0.94647 | 0.90512 | -0.041345 |  | 0.93 | 1.05 | 0.13004 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NEOSHON4 | 0.94647 | 0.90512 | -0.041345 |  | 0.93 | 1.05 | 0.049018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NEOSHON4 | 0.94647 | 0.90512 | -0.041345 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NEOSHON4 | 0.94647 | 0.90512 | -0.041345 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NEOSHON4 | 0.94647 | 0.90512 | -0.041345 |  | 0.93 | 1.05 | 0.05974 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NEOSHON4 | 0.94647 | 0.90512 | -0.041345 |  | 0.93 | 1.05 | 0.076949 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEOSHON4 | 0.94647 | 0.90512 | -0.041345 |  | 0.93 | 1.05 | 0.042157 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEOSHON4 | 0.94647 | 0.90512 | -0.041345 |  | 0.93 | 1.05 | 0.040957 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NEOSHON4 | 0.94647 | 0.90512 | -0.041345 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NEOSHON4 | 0.94647 | 0.90512 | -0.041345 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEOSHON4 | 0.94647 | 0.90512 | -0.041345 |  | 0.93 | 1.05 | 0.054637 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NEOSHON4 | 0.94647 | 0.90512 | -0.041345 |  | 0.93 | 1.05 | 0.060597 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NEOSHON4 | 0.94647 | 0.90512 | -0.041345 |  | 0.93 | 1.05 | 0.044286 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEOSHON4 | 0.94647 | 0.90512 | -0.041345 |  | 0.93 | 1.05 | 0.059107 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NEOSHON4 | 0.94647 | 0.90512 | -0.041345 |  | 0.93 | 1.05 | 0.052698 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEOSHON4 | 0.94647 | 0.90512 | -0.041345 |  | 0.93 | 1.05 | 0.067422 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NEOSHON4 | 0.94647 | 0.90512 | -0.041345 |  | 0.93 | 1.05 | 0.053768 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | NEOSHON4 | 0.94647 | 0.90512 | -0.041345 |  | 0.93 | 1.05 | 0.03909 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NEOSHON4 | 0.94531 | 0.90065 | -0.044664 |  | 0.93 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEOSHON4 | 0.94531 | 0.90065 | -0.044664 |  | 0.93 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NEOSHON4 | 0.94531 | 0.90065 | -0.044664 |  | 0.93 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEOSHON4 | 0.94531 | 0.90065 | -0.044664 |  | 0.93 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NEOSHON4 | 0.94531 | 0.90065 | -0.044664 |  | 0.93 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NEOSHON4 | 0.94531 | 0.90065 | -0.044664 |  | 0.93 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEOSHON4 | 0.94531 | 0.90065 | -0.044664 |  | 0.93 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NEOSHON4 | 0.94531 | 0.90065 | -0.044664 |  | 0.93 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEOSHON4 | 0.94531 | 0.90065 | -0.044664 |  | 0.93 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NEOSHON4 | 0.94531 | 0.90065 | -0.044664 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NEOSHON4 | 0.94531 | 0.90065 | -0.044664 |  | 0.93 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NEOSHON4 | 0.94531 | 0.90065 | -0.044664 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NEOSHON4 | 0.94531 | 0.90065 | -0.044664 |  | 0.93 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NEOSHON4 | 0.94531 | 0.90065 | -0.044664 |  | 0.93 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEOSHON4 | 0.94531 | 0.90065 | -0.044664 |  | 0.93 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEOSHON4 | 0.94531 | 0.90065 | -0.044664 |  | 0.93 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEOSHON4 | 0.94531 | 0.90065 | -0.044664 |  | 0.93 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NEOSHON4 | 0.94531 | 0.90065 | -0.044664 |  | 0.93 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEOSHON4 | 0.94531 | 0.90065 | -0.044664 |  | 0.93 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NEOSHON4 | 0.94531 | 0.90065 | -0.044664 |  | 0.93 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEOSHON4 | 0.94531 | 0.90065 | -0.044664 |  | 0.93 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NEOSHON4 | 0.94531 | 0.90065 | -0.044664 |  | 0.93 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NEOSHON4 | 0.94564 | 0.88507 | -0.060565 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEOSHON4 | 0.94564 | 0.88507 | -0.060565 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NEOSHON4 | 0.94564 | 0.88507 | -0.060565 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEOSHON4 | 0.94564 | 0.88507 | -0.060565 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NEOSHON4 | 0.94564 | 0.88507 | -0.060565 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NEOSHON4 | 0.94564 | 0.88507 | -0.060565 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEOSHON4 | 0.94564 | 0.88507 | -0.060565 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NEOSHON4 | 0.94564 | 0.88507 | -0.060565 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NEOSHON4 | 0.94564 | 0.88507 | -0.060565 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEOSHON4 | 0.94564 | 0.88507 | -0.060565 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NEOSHON4 | 0.94564 | 0.88507 | -0.060565 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NEOSHON4 | 0.94564 | 0.88507 | -0.060565 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NEOSHON4 | 0.94564 | 0.88507 | -0.060565 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NEOSHON4 | 0.94564 | 0.88507 | -0.060565 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NEOSHON4 | 0.94564 | 0.88507 | -0.060565 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NEOSHON4 | 0.94564 | 0.88507 | -0.060565 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEOSHON4 | 0.94564 | 0.88507 | -0.060565 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEOSHON4 | 0.94564 | 0.88507 | -0.060565 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NEOSHON4 | 0.94564 | 0.88507 | -0.060565 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NEOSHON4 | 0.94564 | 0.88507 | -0.060565 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEOSHON4 | 0.94564 | 0.88507 | -0.060565 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NEOSHON4 | 0.94564 | 0.88507 | -0.060565 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NEOSHON4 | 0.94564 | 0.88507 | -0.060565 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEOSHON4 | 0.94564 | 0.88507 | -0.060565 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NEOSHON4 | 0.94564 | 0.88507 | -0.060565 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEOSHON4 | 0.94564 | 0.88507 | -0.060565 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NEOSHON4 | 0.94564 | 0.88507 | -0.060565 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | NEOSHON4 | 0.94564 | 0.88507 | -0.060565 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | NEOSHOS2 | 0.95639 | 0.91414 | -0.042246 |  | 0.93 | 1.05 | 0.077629 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | NEOSHOS2 | 0.95639 | 0.91414 | -0.042246 |  | 0.93 | 1.05 | 0.06446 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | NEOSHOS2 | 0.95639 | 0.91414 | -0.042246 |  | 0.93 | 1.05 | 0.066434 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | NEOSHOS2 | 0.95639 | 0.91414 | -0.042246 |  | 0.93 | 1.05 | 0.073293 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEOSHOS2 | 0.95639 | 0.91414 | -0.042246 |  | 0.93 | 1.05 | 0.053415 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-122 | NEOSHOS2 | 0.95639 | 0.91414 | -0.042246 |  | 0.93 | 1.05 | 0.08103 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-177 | NEOSHOS2 | 0.95639 | 0.91414 | -0.042246 |  | 0.93 | 1.05 | 0.08268 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-178 | NEOSHOS2 | 0.95639 | 0.91414 | -0.042246 |  | 0.93 | 1.05 | 0.077122 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NEOSHOS2 | 0.95639 | 0.91414 | -0.042246 |  | 0.93 | 1.05 | 0.032185 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | NEOSHOS2 | 0.95639 | 0.91414 | -0.042246 |  | 0.93 | 1.05 | 0.073922 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-232 | NEOSHOS2 | 0.95639 | 0.91414 | -0.042246 |  | 0.93 | 1.05 | 0.076776 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | NEOSHOS2 | 0.95639 | 0.91414 | -0.042246 |  | 0.93 | 1.05 | 0.06446 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEOSHOS2 | 0.95639 | 0.91414 | -0.042246 |  | 0.93 | 1.05 | 0.038841 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NEOSHOS2 | 0.95639 | 0.91414 | -0.042246 |  | 0.93 | 1.05 | 0.034687 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NEOSHOS2 | 0.95639 | 0.91414 | -0.042246 |  | 0.93 | 1.05 | 0.034687 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NEOSHOS2 | 0.95639 | 0.91414 | -0.042246 |  | 0.93 | 1.05 | 0.031574 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | NEOSHOS2 | 0.95639 | 0.91414 | -0.042246 |  | 0.93 | 1.05 | 0.042889 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-376 | NEOSHOS2 | 0.95639 | 0.91414 | -0.042246 |  | 0.93 | 1.05 | 0.079908 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEOSHOS2 | 0.95347 | 0.91513 | -0.038337 |  | 0.93 | 1.05 | 0.040299 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NEOSHOS2 | 0.95347 | 0.91513 | -0.038337 |  | 0.93 | 1.05 | 0.048812 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEOSHOS2 | 0.95347 | 0.91513 | -0.038337 |  | 0.93 | 1.05 | 0.076211 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEOSHOS2 | 0.95347 | 0.91513 | -0.038337 |  | 0.93 | 1.05 | 0.069331 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEOSHOS2 | 0.95347 | 0.91513 | -0.038337 |  | 0.93 | 1.05 | 0.035943 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NEOSHOS2 | 0.95347 | 0.91513 | -0.038337 |  | 0.93 | 1.05 | 0.034061 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NEOSHOS2 | 0.95347 | 0.91513 | -0.038337 |  | 0.93 | 1.05 | 0.064216 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEOSHOS2 | 0.95347 | 0.91513 | -0.038337 |  | 0.93 | 1.05 | 0.045005 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEOSHOS2 | 0.95347 | 0.91513 | -0.038337 |  | 0.93 | 1.05 | 0.13572 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NEOSHOS2 | 0.95347 | 0.91513 | -0.038337 |  | 0.93 | 1.05 | 0.037472 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NEOSHOS2 | 0.95347 | 0.91513 | -0.038337 |  | 0.93 | 1.05 | 0.037472 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEOSHOS2 | 0.95347 | 0.91513 | -0.038337 |  | 0.93 | 1.05 | 0.06894 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEOSHOS2 | 0.95347 | 0.91513 | -0.038337 |  | 0.93 | 1.05 | 0.034713 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEOSHOS2 | 0.95347 | 0.91513 | -0.038337 |  | 0.93 | 1.05 | 0.035229 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NEOSHOS2 | 0.95347 | 0.91534 | -0.038128 |  | 0.93 | 1.05 | 0.094783 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEOSHOS2 | 0.95347 | 0.91534 | -0.038128 |  | 0.93 | 1.05 | 0.03645 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEOSHOS2 | 0.95347 | 0.91534 | -0.038128 |  | 0.93 | 1.05 | 0.04755 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NEOSHOS2 | 0.95347 | 0.91534 | -0.038128 |  | 0.93 | 1.05 | 0.06097 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEOSHOS2 | 0.95347 | 0.91534 | -0.038128 |  | 0.93 | 1.05 | 0.061051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NEOSHOS2 | 0.95347 | 0.91534 | -0.038128 |  | 0.93 | 1.05 | 0.04456 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NEOSHOS2 | 0.95347 | 0.91534 | -0.038128 |  | 0.93 | 1.05 | 0.048811 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEOSHOS2 | 0.95347 | 0.91534 | -0.038128 |  | 0.93 | 1.05 | 0.13004 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NEOSHOS2 | 0.95347 | 0.91534 | -0.038128 |  | 0.93 | 1.05 | 0.049018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NEOSHOS2 | 0.95347 | 0.91534 | -0.038128 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NEOSHOS2 | 0.95347 | 0.91534 | -0.038128 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NEOSHOS2 | 0.95347 | 0.91534 | -0.038128 |  | 0.93 | 1.05 | 0.05974 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NEOSHOS2 | 0.95347 | 0.91534 | -0.038128 |  | 0.93 | 1.05 | 0.076949 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEOSHOS2 | 0.95347 | 0.91534 | -0.038128 |  | 0.93 | 1.05 | 0.042157 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEOSHOS2 | 0.95347 | 0.91534 | -0.038128 |  | 0.93 | 1.05 | 0.040957 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NEOSHOS2 | 0.95347 | 0.91534 | -0.038128 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NEOSHOS2 | 0.95347 | 0.91534 | -0.038128 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEOSHOS2 | 0.95347 | 0.91534 | -0.038128 |  | 0.93 | 1.05 | 0.054637 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NEOSHOS2 | 0.95347 | 0.91534 | -0.038128 |  | 0.93 | 1.05 | 0.060597 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NEOSHOS2 | 0.95347 | 0.91534 | -0.038128 |  | 0.93 | 1.05 | 0.044286 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEOSHOS2 | 0.95347 | 0.91534 | -0.038128 |  | 0.93 | 1.05 | 0.059107 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NEOSHOS2 | 0.95347 | 0.91534 | -0.038128 |  | 0.93 | 1.05 | 0.052698 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEOSHOS2 | 0.95347 | 0.91534 | -0.038128 |  | 0.93 | 1.05 | 0.067422 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NEOSHOS2 | 0.95347 | 0.91534 | -0.038128 |  | 0.93 | 1.05 | 0.053768 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | NEOSHOS2 | 0.95347 | 0.91534 | -0.038128 |  | 0.93 | 1.05 | 0.03909 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NEOSHOS2 | 0.95236 | 0.91135 | -0.041017 |  | 0.93 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEOSHOS2 | 0.95236 | 0.91135 | -0.041017 |  | 0.93 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NEOSHOS2 | 0.95236 | 0.91135 | -0.041017 |  | 0.93 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEOSHOS2 | 0.95236 | 0.91135 | -0.041017 |  | 0.93 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NEOSHOS2 | 0.95236 | 0.91135 | -0.041017 |  | 0.93 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NEOSHOS2 | 0.95236 | 0.91135 | -0.041017 |  | 0.93 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEOSHOS2 | 0.95236 | 0.91135 | -0.041017 |  | 0.93 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NEOSHOS2 | 0.95236 | 0.91135 | -0.041017 |  | 0.93 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEOSHOS2 | 0.95236 | 0.91135 | -0.041017 |  | 0.93 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NEOSHOS2 | 0.95236 | 0.91135 | -0.041017 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NEOSHOS2 | 0.95236 | 0.91135 | -0.041017 |  | 0.93 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NEOSHOS2 | 0.95236 | 0.91135 | -0.041017 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NEOSHOS2 | 0.95236 | 0.91135 | -0.041017 |  | 0.93 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NEOSHOS2 | 0.95236 | 0.91135 | -0.041017 |  | 0.93 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEOSHOS2 | 0.95236 | 0.91135 | -0.041017 |  | 0.93 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEOSHOS2 | 0.95236 | 0.91135 | -0.041017 |  | 0.93 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEOSHOS2 | 0.95236 | 0.91135 | -0.041017 |  | 0.93 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NEOSHOS2 | 0.95236 | 0.91135 | -0.041017 |  | 0.93 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEOSHOS2 | 0.95236 | 0.91135 | -0.041017 |  | 0.93 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NEOSHOS2 | 0.95236 | 0.91135 | -0.041017 |  | 0.93 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEOSHOS2 | 0.95236 | 0.91135 | -0.041017 |  | 0.93 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NEOSHOS2 | 0.95236 | 0.91135 | -0.041017 |  | 0.93 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NEOSHOS2 | 0.95269 | 0.89688 | -0.055811 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEOSHOS2 | 0.95269 | 0.89688 | -0.055811 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NEOSHOS2 | 0.95269 | 0.89688 | -0.055811 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEOSHOS2 | 0.95269 | 0.89688 | -0.055811 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NEOSHOS2 | 0.95269 | 0.89688 | -0.055811 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NEOSHOS2 | 0.95269 | 0.89688 | -0.055811 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEOSHOS2 | 0.95269 | 0.89688 | -0.055811 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NEOSHOS2 | 0.95269 | 0.89688 | -0.055811 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NEOSHOS2 | 0.95269 | 0.89688 | -0.055811 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEOSHOS2 | 0.95269 | 0.89688 | -0.055811 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NEOSHOS2 | 0.95269 | 0.89688 | -0.055811 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NEOSHOS2 | 0.95269 | 0.89688 | -0.055811 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NEOSHOS2 | 0.95269 | 0.89688 | -0.055811 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NEOSHOS2 | 0.95269 | 0.89688 | -0.055811 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NEOSHOS2 | 0.95269 | 0.89688 | -0.055811 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NEOSHOS2 | 0.95269 | 0.89688 | -0.055811 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEOSHOS2 | 0.95269 | 0.89688 | -0.055811 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEOSHOS2 | 0.95269 | 0.89688 | -0.055811 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NEOSHOS2 | 0.95269 | 0.89688 | -0.055811 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NEOSHOS2 | 0.95269 | 0.89688 | -0.055811 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEOSHOS2 | 0.95269 | 0.89688 | -0.055811 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NEOSHOS2 | 0.95269 | 0.89688 | -0.055811 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NEOSHOS2 | 0.95269 | 0.89688 | -0.055811 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEOSHOS2 | 0.95269 | 0.89688 | -0.055811 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NEOSHOS2 | 0.95269 | 0.89688 | -0.055811 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEOSHOS2 | 0.95269 | 0.89688 | -0.055811 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NEOSHOS2 | 0.95269 | 0.89688 | -0.055811 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | NEOSHOS2 | 0.95269 | 0.89688 | -0.055811 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | NEOSHOS4 | 0.94964 | 0.90397 | -0.045664 |  | 0.93 | 1.05 | 0.077629 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | NEOSHOS4 | 0.94964 | 0.90397 | -0.045664 |  | 0.93 | 1.05 | 0.06446 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | NEOSHOS4 | 0.94964 | 0.90397 | -0.045664 |  | 0.93 | 1.05 | 0.066434 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | NEOSHOS4 | 0.94964 | 0.90397 | -0.045664 |  | 0.93 | 1.05 | 0.073293 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEOSHOS4 | 0.94964 | 0.90397 | -0.045664 |  | 0.93 | 1.05 | 0.053415 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-122 | NEOSHOS4 | 0.94964 | 0.90397 | -0.045664 |  | 0.93 | 1.05 | 0.08103 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-177 | NEOSHOS4 | 0.94964 | 0.90397 | -0.045664 |  | 0.93 | 1.05 | 0.08268 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-178 | NEOSHOS4 | 0.94964 | 0.90397 | -0.045664 |  | 0.93 | 1.05 | 0.077122 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NEOSHOS4 | 0.94964 | 0.90397 | -0.045664 |  | 0.93 | 1.05 | 0.032185 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | NEOSHOS4 | 0.94964 | 0.90397 | -0.045664 |  | 0.93 | 1.05 | 0.073922 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-232 | NEOSHOS4 | 0.94964 | 0.90397 | -0.045664 |  | 0.93 | 1.05 | 0.076776 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | NEOSHOS4 | 0.94964 | 0.90397 | -0.045664 |  | 0.93 | 1.05 | 0.06446 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEOSHOS4 | 0.94964 | 0.90397 | -0.045664 |  | 0.93 | 1.05 | 0.038841 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NEOSHOS4 | 0.94964 | 0.90397 | -0.045664 |  | 0.93 | 1.05 | 0.034687 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NEOSHOS4 | 0.94964 | 0.90397 | -0.045664 |  | 0.93 | 1.05 | 0.034687 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NEOSHOS4 | 0.94964 | 0.90397 | -0.045664 |  | 0.93 | 1.05 | 0.031574 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | NEOSHOS4 | 0.94964 | 0.90397 | -0.045664 |  | 0.93 | 1.05 | 0.042889 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-376 | NEOSHOS4 | 0.94964 | 0.90397 | -0.045664 |  | 0.93 | 1.05 | 0.079908 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEOSHOS4 | 0.94652 | 0.90489 | -0.04163 |  | 0.93 | 1.05 | 0.040299 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NEOSHOS4 | 0.94652 | 0.90489 | -0.04163 |  | 0.93 | 1.05 | 0.048812 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEOSHOS4 | 0.94652 | 0.90489 | -0.04163 |  | 0.93 | 1.05 | 0.076211 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEOSHOS4 | 0.94652 | 0.90489 | -0.04163 |  | 0.93 | 1.05 | 0.069331 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEOSHOS4 | 0.94652 | 0.90489 | -0.04163 |  | 0.93 | 1.05 | 0.035943 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NEOSHOS4 | 0.94652 | 0.90489 | -0.04163 |  | 0.93 | 1.05 | 0.034061 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NEOSHOS4 | 0.94652 | 0.90489 | -0.04163 |  | 0.93 | 1.05 | 0.064216 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEOSHOS4 | 0.94652 | 0.90489 | -0.04163 |  | 0.93 | 1.05 | 0.045005 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEOSHOS4 | 0.94652 | 0.90489 | -0.04163 |  | 0.93 | 1.05 | 0.13572 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NEOSHOS4 | 0.94652 | 0.90489 | -0.04163 |  | 0.93 | 1.05 | 0.037472 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NEOSHOS4 | 0.94652 | 0.90489 | -0.04163 |  | 0.93 | 1.05 | 0.037472 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEOSHOS4 | 0.94652 | 0.90489 | -0.04163 |  | 0.93 | 1.05 | 0.06894 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEOSHOS4 | 0.94652 | 0.90489 | -0.04163 |  | 0.93 | 1.05 | 0.034713 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEOSHOS4 | 0.94652 | 0.90489 | -0.04163 |  | 0.93 | 1.05 | 0.035229 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NEOSHOS4 | 0.94657 | 0.9052 | -0.041369 |  | 0.93 | 1.05 | 0.094783 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEOSHOS4 | 0.94657 | 0.9052 | -0.041369 |  | 0.93 | 1.05 | 0.03645 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEOSHOS4 | 0.94657 | 0.9052 | -0.041369 |  | 0.93 | 1.05 | 0.04755 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NEOSHOS4 | 0.94657 | 0.9052 | -0.041369 |  | 0.93 | 1.05 | 0.06097 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEOSHOS4 | 0.94657 | 0.9052 | -0.041369 |  | 0.93 | 1.05 | 0.061051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NEOSHOS4 | 0.94657 | 0.9052 | -0.041369 |  | 0.93 | 1.05 | 0.04456 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NEOSHOS4 | 0.94657 | 0.9052 | -0.041369 |  | 0.93 | 1.05 | 0.048811 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEOSHOS4 | 0.94657 | 0.9052 | -0.041369 |  | 0.93 | 1.05 | 0.13004 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NEOSHOS4 | 0.94657 | 0.9052 | -0.041369 |  | 0.93 | 1.05 | 0.049018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NEOSHOS4 | 0.94657 | 0.9052 | -0.041369 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NEOSHOS4 | 0.94657 | 0.9052 | -0.041369 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NEOSHOS4 | 0.94657 | 0.9052 | -0.041369 |  | 0.93 | 1.05 | 0.05974 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NEOSHOS4 | 0.94657 | 0.9052 | -0.041369 |  | 0.93 | 1.05 | 0.076949 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEOSHOS4 | 0.94657 | 0.9052 | -0.041369 |  | 0.93 | 1.05 | 0.042157 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEOSHOS4 | 0.94657 | 0.9052 | -0.041369 |  | 0.93 | 1.05 | 0.040957 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NEOSHOS4 | 0.94657 | 0.9052 | -0.041369 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NEOSHOS4 | 0.94657 | 0.9052 | -0.041369 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEOSHOS4 | 0.94657 | 0.9052 | -0.041369 |  | 0.93 | 1.05 | 0.054637 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NEOSHOS4 | 0.94657 | 0.9052 | -0.041369 |  | 0.93 | 1.05 | 0.060597 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NEOSHOS4 | 0.94657 | 0.9052 | -0.041369 |  | 0.93 | 1.05 | 0.044286 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEOSHOS4 | 0.94657 | 0.9052 | -0.041369 |  | 0.93 | 1.05 | 0.059107 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NEOSHOS4 | 0.94657 | 0.9052 | -0.041369 |  | 0.93 | 1.05 | 0.052698 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEOSHOS4 | 0.94657 | 0.9052 | -0.041369 |  | 0.93 | 1.05 | 0.067422 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NEOSHOS4 | 0.94657 | 0.9052 | -0.041369 |  | 0.93 | 1.05 | 0.053768 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | NEOSHOS4 | 0.94657 | 0.9052 | -0.041369 |  | 0.93 | 1.05 | 0.03909 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NEOSHOS4 | 0.95531 | 0.92775 | -0.027553 |  | 0.95 | 1.05 | 0.14625 | System Intact | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NEOSHOS4 | 0.94542 | 0.90074 | -0.044684 |  | 0.93 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEOSHOS4 | 0.94542 | 0.90074 | -0.044684 |  | 0.93 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NEOSHOS4 | 0.94542 | 0.90074 | -0.044684 |  | 0.93 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEOSHOS4 | 0.94542 | 0.90074 | -0.044684 |  | 0.93 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NEOSHOS4 | 0.94542 | 0.90074 | -0.044684 |  | 0.93 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NEOSHOS4 | 0.94542 | 0.90074 | -0.044684 |  | 0.93 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEOSHOS4 | 0.94542 | 0.90074 | -0.044684 |  | 0.93 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NEOSHOS4 | 0.94542 | 0.90074 | -0.044684 |  | 0.93 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEOSHOS4 | 0.94542 | 0.90074 | -0.044684 |  | 0.93 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NEOSHOS4 | 0.94542 | 0.90074 | -0.044684 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NEOSHOS4 | 0.94542 | 0.90074 | -0.044684 |  | 0.93 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NEOSHOS4 | 0.94542 | 0.90074 | -0.044684 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NEOSHOS4 | 0.94542 | 0.90074 | -0.044684 |  | 0.93 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NEOSHOS4 | 0.94542 | 0.90074 | -0.044684 |  | 0.93 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEOSHOS4 | 0.94542 | 0.90074 | -0.044684 |  | 0.93 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEOSHOS4 | 0.94542 | 0.90074 | -0.044684 |  | 0.93 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEOSHOS4 | 0.94542 | 0.90074 | -0.044684 |  | 0.93 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NEOSHOS4 | 0.94542 | 0.90074 | -0.044684 |  | 0.93 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEOSHOS4 | 0.94542 | 0.90074 | -0.044684 |  | 0.93 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NEOSHOS4 | 0.94542 | 0.90074 | -0.044684 |  | 0.93 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEOSHOS4 | 0.94542 | 0.90074 | -0.044684 |  | 0.93 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NEOSHOS4 | 0.94542 | 0.90074 | -0.044684 |  | 0.93 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NEOSHOS4 | 0.94575 | 0.88517 | -0.060575 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEOSHOS4 | 0.94575 | 0.88517 | -0.060575 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NEOSHOS4 | 0.94575 | 0.88517 | -0.060575 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEOSHOS4 | 0.94575 | 0.88517 | -0.060575 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NEOSHOS4 | 0.94575 | 0.88517 | -0.060575 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NEOSHOS4 | 0.94575 | 0.88517 | -0.060575 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEOSHOS4 | 0.94575 | 0.88517 | -0.060575 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NEOSHOS4 | 0.94575 | 0.88517 | -0.060575 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NEOSHOS4 | 0.94575 | 0.88517 | -0.060575 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEOSHOS4 | 0.94575 | 0.88517 | -0.060575 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NEOSHOS4 | 0.94575 | 0.88517 | -0.060575 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NEOSHOS4 | 0.94575 | 0.88517 | -0.060575 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NEOSHOS4 | 0.94575 | 0.88517 | -0.060575 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NEOSHOS4 | 0.94575 | 0.88517 | -0.060575 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NEOSHOS4 | 0.94575 | 0.88517 | -0.060575 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NEOSHOS4 | 0.94575 | 0.88517 | -0.060575 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEOSHOS4 | 0.94575 | 0.88517 | -0.060575 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEOSHOS4 | 0.94575 | 0.88517 | -0.060575 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NEOSHOS4 | 0.94575 | 0.88517 | -0.060575 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NEOSHOS4 | 0.94575 | 0.88517 | -0.060575 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEOSHOS4 | 0.94575 | 0.88517 | -0.060575 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NEOSHOS4 | 0.94575 | 0.88517 | -0.060575 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NEOSHOS4 | 0.94575 | 0.88517 | -0.060575 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEOSHOS4 | 0.94575 | 0.88517 | -0.060575 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NEOSHOS4 | 0.94575 | 0.88517 | -0.060575 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEOSHOS4 | 0.94575 | 0.88517 | -0.060575 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NEOSHOS4 | 0.94575 | 0.88517 | -0.060575 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | NEOSHOS4 | 0.94575 | 0.88517 | -0.060575 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NESCTY 3 | 0.9416 | 0.88679 | -0.054813 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NESCTY 3 | 0.9416 | 0.88679 | -0.054813 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NESCTY 3 | 0.9505 | 0.89323 | -0.057265 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NESCTY 3 | 0.9505 | 0.89323 | -0.057265 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NESCTY 3 | 0.9505 | 0.89323 | -0.057265 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NESCTY 3 | 0.9505 | 0.89323 | -0.057265 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NESCTY 3 | 0.9505 | 0.89323 | -0.057265 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NESCTY 3 | 0.9505 | 0.89323 | -0.057265 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NESSCTY3 | 0.94156 | 0.88672 | -0.054841 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NESSCTY3 | 0.94156 | 0.88672 | -0.054841 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NESSCTY3 | 0.95046 | 0.89316 | -0.057297 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NESSCTY3 | 0.95046 | 0.89316 | -0.057297 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NESSCTY3 | 0.95046 | 0.89316 | -0.057298 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NESSCTY3 | 0.95046 | 0.89316 | -0.057298 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NESSCTY3 | 0.95046 | 0.89316 | -0.057298 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NESSCTY3 | 0.95046 | 0.89316 | -0.057298 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NEVADA 5 | 0.94709 | 0.91074 | -0.036348 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NEVADA 5 | 0.94709 | 0.91074 | -0.036348 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEVADA 5 | 0.94709 | 0.91074 | -0.036348 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NEVADA 5 | 0.94709 | 0.91074 | -0.036348 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEVADA 5 | 0.94709 | 0.91074 | -0.036348 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEVADA 5 | 0.94709 | 0.91074 | -0.036348 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NEVADA 5 | 0.94709 | 0.91074 | -0.036348 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NEVADA 5 | 0.94709 | 0.91074 | -0.036348 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NEVADA 5 | 0.94709 | 0.91074 | -0.036348 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NEVADA 5 | 0.94709 | 0.91074 | -0.036348 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NEVADA 5 | 0.94709 | 0.91074 | -0.036348 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NEVADA 5 | 0.94709 | 0.91074 | -0.036348 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEVADA 5 | 0.94709 | 0.91074 | -0.036348 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEVADA 5 | 0.94709 | 0.91074 | -0.036348 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEVADA 5 | 0.94709 | 0.91074 | -0.036348 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NEVADA 5 | 0.94709 | 0.91074 | -0.036348 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEVADA 5 | 0.94709 | 0.91074 | -0.036348 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NEVADA 5 | 0.94709 | 0.91074 | -0.036348 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEVADA 5 | 0.94709 | 0.91074 | -0.036348 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NEVADA 5 | 0.94709 | 0.91074 | -0.036348 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NEVADA 5 | 0.94258 | 0.91209 | -0.030487 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NEVADA 5 | 0.94258 | 0.91209 | -0.030487 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEVADA 5 | 0.94258 | 0.91209 | -0.030487 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NEVADA 5 | 0.94258 | 0.91209 | -0.030487 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEVADA 5 | 0.94258 | 0.91209 | -0.030487 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEVADA 5 | 0.94258 | 0.91209 | -0.030487 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NEVADA 5 | 0.94258 | 0.91209 | -0.030487 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NEVADA 5 | 0.94258 | 0.91209 | -0.030487 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NEVADA 5 | 0.94258 | 0.91209 | -0.030487 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NEVADA 5 | 0.94258 | 0.91209 | -0.030487 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NEVADA 5 | 0.94258 | 0.91209 | -0.030487 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NEVADA 5 | 0.94258 | 0.91209 | -0.030487 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEVADA 5 | 0.94258 | 0.91209 | -0.030487 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEVADA 5 | 0.94258 | 0.91209 | -0.030487 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEVADA 5 | 0.94258 | 0.91209 | -0.030487 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NEVADA 5 | 0.94258 | 0.91209 | -0.030487 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEVADA 5 | 0.94258 | 0.91209 | -0.030487 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NEVADA 5 | 0.94258 | 0.91209 | -0.030487 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEVADA 5 | 0.94258 | 0.91209 | -0.030487 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NEVADA 5 | 0.94258 | 0.91209 | -0.030487 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | NEVADA 5 | 0.95127 | 0.91242 | -0.038849 |  | 0.93 | 1.05 | 0.030773 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | NEVADA 5 | 0.95127 | 0.91242 | -0.038849 |  | 0.93 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NEVADA 5 | 0.95127 | 0.91242 | -0.038849 |  | 0.93 | 1.05 | 0.046711 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | NEVADA 5 | 0.95127 | 0.91242 | -0.038849 |  | 0.93 | 1.05 | 0.032369 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | NEVADA 5 | 0.95127 | 0.91242 | -0.038849 |  | 0.93 | 1.05 | 0.030466 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEVADA 5 | 0.95127 | 0.91242 | -0.038849 |  | 0.93 | 1.05 | 0.04987 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NEVADA 5 | 0.95127 | 0.91242 | -0.038849 |  | 0.93 | 1.05 | 0.099365 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEVADA 5 | 0.95127 | 0.91242 | -0.038849 |  | 0.93 | 1.05 | 0.071132 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NEVADA 5 | 0.95127 | 0.91242 | -0.038849 |  | 0.93 | 1.05 | 0.043927 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NEVADA 5 | 0.95127 | 0.91242 | -0.038849 |  | 0.93 | 1.05 | 0.030565 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEVADA 5 | 0.95127 | 0.91242 | -0.038849 |  | 0.93 | 1.05 | 0.072847 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NEVADA 5 | 0.95127 | 0.91242 | -0.038849 |  | 0.93 | 1.05 | 0.041148 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NEVADA 5 | 0.95127 | 0.91242 | -0.038849 |  | 0.93 | 1.05 | 0.042015 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | NEVADA 5 | 0.95127 | 0.91242 | -0.038849 |  | 0.93 | 1.05 | 0.030318 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEVADA 5 | 0.95127 | 0.91242 | -0.038849 |  | 0.93 | 1.05 | 0.054104 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NEVADA 5 | 0.95127 | 0.91242 | -0.038849 |  | 0.93 | 1.05 | 0.047089 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NEVADA 5 | 0.95127 | 0.91242 | -0.038849 |  | 0.93 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NEVADA 5 | 0.95127 | 0.91242 | -0.038849 |  | 0.93 | 1.05 | 0.13688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | NEVADA 5 | 0.95127 | 0.91242 | -0.038849 |  | 0.93 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NEVADA 5 | 0.95127 | 0.91242 | -0.038849 |  | 0.93 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NEVADA 5 | 0.95127 | 0.91242 | -0.038849 |  | 0.93 | 1.05 | 0.039752 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NEVADA 5 | 0.95127 | 0.91242 | -0.038849 |  | 0.93 | 1.05 | 0.041972 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEVADA 5 | 0.95127 | 0.91242 | -0.038849 |  | 0.93 | 1.05 | 0.054397 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEVADA 5 | 0.95127 | 0.91242 | -0.038849 |  | 0.93 | 1.05 | 0.073688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NEVADA 5 | 0.95127 | 0.91242 | -0.038849 |  | 0.93 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NEVADA 5 | 0.95127 | 0.91242 | -0.038849 |  | 0.93 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEVADA 5 | 0.95127 | 0.91242 | -0.038849 |  | 0.93 | 1.05 | 0.072188 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NEVADA 5 | 0.95127 | 0.91242 | -0.038849 |  | 0.93 | 1.05 | 0.042186 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NEVADA 5 | 0.95127 | 0.91242 | -0.038849 |  | 0.93 | 1.05 | 0.041423 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEVADA 5 | 0.95127 | 0.91242 | -0.038849 |  | 0.93 | 1.05 | 0.050171 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NEVADA 5 | 0.95127 | 0.91242 | -0.038849 |  | 0.93 | 1.05 | 0.04386 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEVADA 5 | 0.95127 | 0.91242 | -0.038849 |  | 0.93 | 1.05 | 0.050218 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NEVADA 5 | 0.95127 | 0.91242 | -0.038849 |  | 0.93 | 1.05 | 0.040041 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | NEVADA 5 | 0.95127 | 0.91242 | -0.038849 |  | 0.93 | 1.05 | 0.038784 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NEVADA 5 | 0.94671 | 0.91416 | -0.032553 |  | 0.93 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NEVADA 5 | 0.94671 | 0.91416 | -0.032553 |  | 0.93 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEVADA 5 | 0.94671 | 0.91416 | -0.032553 |  | 0.93 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NEVADA 5 | 0.94671 | 0.91416 | -0.032553 |  | 0.93 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEVADA 5 | 0.94671 | 0.91416 | -0.032553 |  | 0.93 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEVADA 5 | 0.94671 | 0.91416 | -0.032553 |  | 0.93 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NEVADA 5 | 0.94671 | 0.91416 | -0.032553 |  | 0.93 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NEVADA 5 | 0.94671 | 0.91416 | -0.032553 |  | 0.93 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NEVADA 5 | 0.94671 | 0.91416 | -0.032553 |  | 0.93 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NEVADA 5 | 0.94671 | 0.91416 | -0.032553 |  | 0.93 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NEVADA 5 | 0.94671 | 0.91416 | -0.032553 |  | 0.93 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NEVADA 5 | 0.94671 | 0.91416 | -0.032553 |  | 0.93 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEVADA 5 | 0.94671 | 0.91416 | -0.032553 |  | 0.93 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEVADA 5 | 0.94671 | 0.91416 | -0.032553 |  | 0.93 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEVADA 5 | 0.94671 | 0.91416 | -0.032553 |  | 0.93 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NEVADA 5 | 0.94671 | 0.91416 | -0.032553 |  | 0.93 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEVADA 5 | 0.94671 | 0.91416 | -0.032553 |  | 0.93 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NEVADA 5 | 0.94671 | 0.91416 | -0.032553 |  | 0.93 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEVADA 5 | 0.94671 | 0.91416 | -0.032553 |  | 0.93 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NEVADA 5 | 0.94671 | 0.91416 | -0.032553 |  | 0.93 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NEVADA 5 | 0.94712 | 0.8875 | -0.059626 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NEVADA 5 | 0.94712 | 0.8875 | -0.059626 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NEVADA 5 | 0.94712 | 0.8875 | -0.059626 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NEVADA 5 | 0.94712 | 0.8875 | -0.059626 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NEVADA 5 | 0.94712 | 0.8875 | -0.059626 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NEVADA 5 | 0.94712 | 0.8875 | -0.059626 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NEVADA 5 | 0.94712 | 0.8875 | -0.059626 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NEVADA 5 | 0.94712 | 0.8875 | -0.059626 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NEVADA 5 | 0.94712 | 0.8875 | -0.059626 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NEVADA 5 | 0.94712 | 0.8875 | -0.059626 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NEVADA 5 | 0.94712 | 0.8875 | -0.059626 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NEVADA 5 | 0.94712 | 0.8875 | -0.059626 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NEVADA 5 | 0.94712 | 0.8875 | -0.059626 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NEVADA 5 | 0.94712 | 0.8875 | -0.059626 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NEVADA 5 | 0.94712 | 0.8875 | -0.059626 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NEVADA 5 | 0.94712 | 0.8875 | -0.059626 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NEVADA 5 | 0.94712 | 0.8875 | -0.059626 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NEVADA 5 | 0.94712 | 0.8875 | -0.059626 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NEVADA 5 | 0.94712 | 0.8875 | -0.059626 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NEVADA 5 | 0.94712 | 0.8875 | -0.059626 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NEVADA 5 | 0.94712 | 0.8875 | -0.059626 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NEVADA 5 | 0.94712 | 0.8875 | -0.059626 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NEVADA 5 | 0.94712 | 0.8875 | -0.059626 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NEVADA 5 | 0.94712 | 0.8875 | -0.059626 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NEVADA 5 | 0.94712 | 0.8875 | -0.059626 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NEVADA 5 | 0.94712 | 0.8875 | -0.059626 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NEVADA 5 | 0.94712 | 0.8875 | -0.059626 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | NEVADA 5 | 0.94712 | 0.8875 | -0.059626 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NLOUISB5 | 0.97702 | 0.92928 | -0.047741 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NLOUISB5 | 0.97702 | 0.92928 | -0.047741 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NLOUISB5 | 0.97702 | 0.92928 | -0.047741 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NLOUISB5 | 0.97702 | 0.92928 | -0.047741 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NLOUISB5 | 0.97702 | 0.92928 | -0.047741 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NLOUISB5 | 0.97702 | 0.92928 | -0.047741 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NLOUISB5 | 0.97702 | 0.92928 | -0.047741 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NLOUISB5 | 0.97702 | 0.92928 | -0.047741 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NLOUISB5 | 0.97702 | 0.92928 | -0.047741 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NLOUISB5 | 0.97702 | 0.92928 | -0.047741 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NLOUISB5 | 0.97702 | 0.92928 | -0.047741 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NLOUISB5 | 0.97702 | 0.92928 | -0.047741 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NLOUISB5 | 0.97702 | 0.92928 | -0.047741 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NLOUISB5 | 0.97702 | 0.92928 | -0.047741 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NLOUISB5 | 0.97702 | 0.92928 | -0.047741 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NLOUISB5 | 0.97702 | 0.92928 | -0.047741 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NLOUISB5 | 0.97702 | 0.92928 | -0.047741 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NLOUISB5 | 0.97702 | 0.92928 | -0.047741 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NLOUISB5 | 0.97702 | 0.92928 | -0.047741 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NLOUISB5 | 0.97702 | 0.92928 | -0.047741 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NLOUISB5 | 0.99015 | 0.90506 | -0.085095 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NLOUISB5 | 0.99015 | 0.90506 | -0.085095 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NLOUISB5 | 0.99015 | 0.90506 | -0.085095 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NLOUISB5 | 0.99015 | 0.90506 | -0.085095 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NLOUISB5 | 0.99015 | 0.90506 | -0.085095 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NLOUISB5 | 0.99015 | 0.90506 | -0.085095 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NLOUISB5 | 0.99015 | 0.90506 | -0.085095 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NLOUISB5 | 0.99015 | 0.90506 | -0.085095 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NLOUISB5 | 0.99015 | 0.90506 | -0.085095 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NLOUISB5 | 0.99015 | 0.90506 | -0.085095 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NLOUISB5 | 0.99015 | 0.90506 | -0.085095 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NLOUISB5 | 0.99015 | 0.90506 | -0.085095 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NLOUISB5 | 0.99015 | 0.90506 | -0.085095 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NLOUISB5 | 0.99015 | 0.90506 | -0.085095 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NLOUISB5 | 0.99015 | 0.90506 | -0.085095 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NLOUISB5 | 0.99015 | 0.90506 | -0.085095 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NLOUISB5 | 0.99015 | 0.90506 | -0.085095 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NLOUISB5 | 0.99015 | 0.90506 | -0.085095 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NLOUISB5 | 0.99015 | 0.90506 | -0.085095 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NLOUISB5 | 0.99015 | 0.90506 | -0.085095 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NLOUISB5 | 0.99015 | 0.90506 | -0.085095 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NLOUISB5 | 0.99015 | 0.90506 | -0.085095 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NLOUISB5 | 0.99015 | 0.90506 | -0.085095 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NLOUISB5 | 0.99015 | 0.90506 | -0.085095 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NLOUISB5 | 0.99015 | 0.90506 | -0.085095 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NLOUISB5 | 0.99015 | 0.90506 | -0.085095 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NLOUISB5 | 0.99015 | 0.90506 | -0.085095 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | NLOUISB5 | 0.99015 | 0.90506 | -0.085095 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NOL435 5 | 0.97139 | 0.90793 | -0.063457 |  | 0.925 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NOL435 5 | 0.97139 | 0.90793 | -0.063457 |  | 0.925 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NOL435 5 | 0.97139 | 0.90793 | -0.063457 |  | 0.925 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NOL435 5 | 0.97139 | 0.90793 | -0.063457 |  | 0.925 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NOL435 5 | 0.97139 | 0.90793 | -0.063457 |  | 0.925 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NOL435 5 | 0.97139 | 0.90793 | -0.063457 |  | 0.925 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NOL435 5 | 0.97139 | 0.90793 | -0.063457 |  | 0.925 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NOL435 5 | 0.97139 | 0.90793 | -0.063457 |  | 0.925 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NOL435 5 | 0.97139 | 0.90793 | -0.063457 |  | 0.925 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NOL435 5 | 0.97139 | 0.90793 | -0.063457 |  | 0.925 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NOL435 5 | 0.97139 | 0.90793 | -0.063457 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NOL435 5 | 0.97139 | 0.90793 | -0.063457 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NOL435 5 | 0.97139 | 0.90793 | -0.063457 |  | 0.925 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NOL435 5 | 0.97139 | 0.90793 | -0.063457 |  | 0.925 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NOL435 5 | 0.97139 | 0.90793 | -0.063457 |  | 0.925 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NOL435 5 | 0.97186 | 0.90887 | -0.062989 |  | 0.925 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NOL435 5 | 0.97186 | 0.90887 | -0.062989 |  | 0.925 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NOL435 5 | 0.97186 | 0.90887 | -0.062989 |  | 0.925 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NOL435 5 | 0.97186 | 0.90887 | -0.062989 |  | 0.925 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NOL435 5 | 0.97186 | 0.90887 | -0.062989 |  | 0.925 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NOL435 5 | 0.97186 | 0.90887 | -0.062989 |  | 0.925 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NOL435 5 | 0.97186 | 0.90887 | -0.062989 |  | 0.925 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NOL435 5 | 0.97186 | 0.90887 | -0.062989 |  | 0.925 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NOL435 5 | 0.97186 | 0.90887 | -0.062989 |  | 0.925 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NOL435 5 | 0.97186 | 0.90887 | -0.062989 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NOL435 5 | 0.97186 | 0.90887 | -0.062989 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NOL435 5 | 0.97186 | 0.90887 | -0.062989 |  | 0.925 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NOL435 5 | 0.97186 | 0.90887 | -0.062989 |  | 0.925 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NOL435 5 | 0.97186 | 0.90887 | -0.062989 |  | 0.925 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NOL435 5 | 0.97209 | 0.91293 | -0.059155 |  | 0.925 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NOL435 5 | 0.97209 | 0.91293 | -0.059155 |  | 0.925 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NOL435 5 | 0.97209 | 0.91293 | -0.059155 |  | 0.925 | 1.05 | 0.055405 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NOL435 5 | 0.97209 | 0.91293 | -0.059155 |  | 0.925 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NOL435 5 | 0.97209 | 0.91293 | -0.059155 |  | 0.925 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NOL435 5 | 0.97209 | 0.91293 | -0.059155 |  | 0.925 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NOL435 5 | 0.97209 | 0.91293 | -0.059155 |  | 0.925 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NOL435 5 | 0.97209 | 0.91293 | -0.059155 |  | 0.925 | 1.05 | 0.082012 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NOL435 5 | 0.97209 | 0.91293 | -0.059155 |  | 0.925 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NOL435 5 | 0.97209 | 0.91293 | -0.059155 |  | 0.925 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NOL435 5 | 0.97209 | 0.91293 | -0.059155 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NOL435 5 | 0.97209 | 0.91293 | -0.059155 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NOL435 5 | 0.97209 | 0.91293 | -0.059155 |  | 0.925 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NOL435 5 | 0.97209 | 0.91293 | -0.059155 |  | 0.925 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NOL435 5 | 0.97209 | 0.91293 | -0.059155 |  | 0.925 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NORCATR3 | 0.96311 | 0.89965 | -0.063453 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NORCATR3 | 0.96311 | 0.89965 | -0.063453 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NORCATR3 | 0.96311 | 0.89965 | -0.063453 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NORCATR3 | 0.96311 | 0.89965 | -0.063453 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NORCATR3 | 0.96311 | 0.89966 | -0.063454 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NORCATR3 | 0.96311 | 0.89966 | -0.063454 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NP-GLAZIR_G2 | 0.66462 | 0.65018 | -0.014441 |  | 0.9 | 1.05 | 0.034054 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NP-GLAZIR_G2 | 0.66462 | 0.65018 | -0.014441 |  | 0.9 | 1.05 | 0.093247 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NP-GLAZIR_G2 | 0.66462 | 0.65018 | -0.014441 |  | 0.9 | 1.05 | 0.030563 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NP-GLAZIR_G2 | 0.66462 | 0.65018 | -0.014441 |  | 0.9 | 1.05 | 0.033696 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NP-GLAZIR_G2 | 0.66462 | 0.65018 | -0.014441 |  | 0.9 | 1.05 | 0.044425 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NP-GLAZIR_G2 | 0.66462 | 0.65018 | -0.014441 |  | 0.9 | 1.05 | 0.044425 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NP-GLAZIR_G2 | 0.66462 | 0.65018 | -0.014441 |  | 0.9 | 1.05 | 0.046653 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NP-GLAZIR_G2 | 0.66462 | 0.65018 | -0.014441 |  | 0.9 | 1.05 | 0.036737 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NP-GLAZIR_G2 | 0.66462 | 0.65018 | -0.014441 |  | 0.9 | 1.05 | 0.037864 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NP-GLAZIR_G2 | 0.66462 | 0.65018 | -0.014441 |  | 0.9 | 1.05 | 0.031064 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NP-GLAZIR_G2 | 0.66462 | 0.65018 | -0.014441 |  | 0.9 | 1.05 | 0.032715 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NP-GLAZIR_G2 | 0.66462 | 0.65018 | -0.014441 |  | 0.9 | 1.05 | 0.044267 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NP-GLAZIR_G2 | 0.65387 | 0.63691 | -0.016957 |  | 0.9 | 1.05 | 0.040027 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NP-GLAZIR_G2 | 0.65387 | 0.63691 | -0.016957 |  | 0.9 | 1.05 | 0.090773 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NP-GLAZIR_G2 | 0.65387 | 0.63691 | -0.016957 |  | 0.9 | 1.05 | 0.034521 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NP-GLAZIR_G2 | 0.65387 | 0.63691 | -0.016957 |  | 0.9 | 1.05 | 0.038035 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NP-GLAZIR_G2 | 0.65387 | 0.63691 | -0.016957 |  | 0.9 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NP-GLAZIR_G2 | 0.65387 | 0.63691 | -0.016957 |  | 0.9 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NP-GLAZIR_G2 | 0.65387 | 0.63691 | -0.016957 |  | 0.9 | 1.05 | 0.050618 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NP-GLAZIR_G2 | 0.65387 | 0.63691 | -0.016957 |  | 0.9 | 1.05 | 0.04163 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NP-GLAZIR_G2 | 0.65387 | 0.63691 | -0.016957 |  | 0.9 | 1.05 | 0.043776 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NP-GLAZIR_G2 | 0.65387 | 0.63691 | -0.016957 |  | 0.9 | 1.05 | 0.034868 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NP-GLAZIR_G2 | 0.65387 | 0.63691 | -0.016957 |  | 0.9 | 1.05 | 0.031975 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NP-GLAZIR_G2 | 0.65387 | 0.63691 | -0.016957 |  | 0.9 | 1.05 | 0.037422 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NP-GLAZIR_G2 | 0.65387 | 0.63691 | -0.016957 |  | 0.9 | 1.05 | 0.050095 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NP-LIPSCOMB2 | 0.62328 | 0.60837 | -0.014914 |  | 0.9 | 1.05 | 0.034054 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NP-LIPSCOMB2 | 0.62328 | 0.60837 | -0.014914 |  | 0.9 | 1.05 | 0.093247 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NP-LIPSCOMB2 | 0.62328 | 0.60837 | -0.014914 |  | 0.9 | 1.05 | 0.030563 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NP-LIPSCOMB2 | 0.62328 | 0.60837 | -0.014914 |  | 0.9 | 1.05 | 0.033696 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NP-LIPSCOMB2 | 0.62328 | 0.60837 | -0.014914 |  | 0.9 | 1.05 | 0.044425 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NP-LIPSCOMB2 | 0.62328 | 0.60837 | -0.014914 |  | 0.9 | 1.05 | 0.044425 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NP-LIPSCOMB2 | 0.62328 | 0.60837 | -0.014914 |  | 0.9 | 1.05 | 0.046653 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NP-LIPSCOMB2 | 0.62328 | 0.60837 | -0.014914 |  | 0.9 | 1.05 | 0.036737 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NP-LIPSCOMB2 | 0.62328 | 0.60837 | -0.014914 |  | 0.9 | 1.05 | 0.037864 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NP-LIPSCOMB2 | 0.62328 | 0.60837 | -0.014914 |  | 0.9 | 1.05 | 0.031064 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NP-LIPSCOMB2 | 0.62328 | 0.60837 | -0.014914 |  | 0.9 | 1.05 | 0.032715 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NP-LIPSCOMB2 | 0.62328 | 0.60837 | -0.014914 |  | 0.9 | 1.05 | 0.044267 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NP-LIPSCOMB2 | 0.61217 | 0.59473 | -0.017444 |  | 0.9 | 1.05 | 0.040027 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NP-LIPSCOMB2 | 0.61217 | 0.59473 | -0.017444 |  | 0.9 | 1.05 | 0.090773 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NP-LIPSCOMB2 | 0.61217 | 0.59473 | -0.017444 |  | 0.9 | 1.05 | 0.034521 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NP-LIPSCOMB2 | 0.61217 | 0.59473 | -0.017444 |  | 0.9 | 1.05 | 0.038035 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NP-LIPSCOMB2 | 0.61217 | 0.59473 | -0.017444 |  | 0.9 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NP-LIPSCOMB2 | 0.61217 | 0.59473 | -0.017444 |  | 0.9 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NP-LIPSCOMB2 | 0.61217 | 0.59473 | -0.017444 |  | 0.9 | 1.05 | 0.050618 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NP-LIPSCOMB2 | 0.61217 | 0.59473 | -0.017444 |  | 0.9 | 1.05 | 0.04163 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NP-LIPSCOMB2 | 0.61217 | 0.59473 | -0.017444 |  | 0.9 | 1.05 | 0.043776 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NP-LIPSCOMB2 | 0.61217 | 0.59473 | -0.017444 |  | 0.9 | 1.05 | 0.034868 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NP-LIPSCOMB2 | 0.61217 | 0.59473 | -0.017444 |  | 0.9 | 1.05 | 0.031975 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NP-LIPSCOMB2 | 0.61217 | 0.59473 | -0.017444 |  | 0.9 | 1.05 | 0.037422 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NP-LIPSCOMB2 | 0.61217 | 0.59473 | -0.017444 |  | 0.9 | 1.05 | 0.050095 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NP-LIPS_SHA2 | 0.62328 | 0.60837 | -0.014914 |  | 0.9 | 1.05 | 0.034054 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NP-LIPS_SHA2 | 0.62328 | 0.60837 | -0.014914 |  | 0.9 | 1.05 | 0.093247 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NP-LIPS_SHA2 | 0.62328 | 0.60837 | -0.014914 |  | 0.9 | 1.05 | 0.030563 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NP-LIPS_SHA2 | 0.62328 | 0.60837 | -0.014914 |  | 0.9 | 1.05 | 0.033696 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NP-LIPS_SHA2 | 0.62328 | 0.60837 | -0.014914 |  | 0.9 | 1.05 | 0.044425 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NP-LIPS_SHA2 | 0.62328 | 0.60837 | -0.014914 |  | 0.9 | 1.05 | 0.044425 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NP-LIPS_SHA2 | 0.62328 | 0.60837 | -0.014914 |  | 0.9 | 1.05 | 0.046653 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NP-LIPS_SHA2 | 0.62328 | 0.60837 | -0.014914 |  | 0.9 | 1.05 | 0.036737 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NP-LIPS_SHA2 | 0.62328 | 0.60837 | -0.014914 |  | 0.9 | 1.05 | 0.037864 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NP-LIPS_SHA2 | 0.62328 | 0.60837 | -0.014914 |  | 0.9 | 1.05 | 0.031064 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NP-LIPS_SHA2 | 0.62328 | 0.60837 | -0.014914 |  | 0.9 | 1.05 | 0.032715 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NP-LIPS_SHA2 | 0.62328 | 0.60837 | -0.014914 |  | 0.9 | 1.05 | 0.044267 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NP-LIPS_SHA2 | 0.61217 | 0.59473 | -0.017444 |  | 0.9 | 1.05 | 0.040027 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NP-LIPS_SHA2 | 0.61217 | 0.59473 | -0.017444 |  | 0.9 | 1.05 | 0.090773 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NP-LIPS_SHA2 | 0.61217 | 0.59473 | -0.017444 |  | 0.9 | 1.05 | 0.034521 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NP-LIPS_SHA2 | 0.61217 | 0.59473 | -0.017444 |  | 0.9 | 1.05 | 0.038035 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NP-LIPS_SHA2 | 0.61217 | 0.59473 | -0.017444 |  | 0.9 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NP-LIPS_SHA2 | 0.61217 | 0.59473 | -0.017444 |  | 0.9 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NP-LIPS_SHA2 | 0.61217 | 0.59473 | -0.017444 |  | 0.9 | 1.05 | 0.050618 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NP-LIPS_SHA2 | 0.61217 | 0.59473 | -0.017444 |  | 0.9 | 1.05 | 0.04163 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NP-LIPS_SHA2 | 0.61217 | 0.59473 | -0.017444 |  | 0.9 | 1.05 | 0.043776 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NP-LIPS_SHA2 | 0.61217 | 0.59473 | -0.017444 |  | 0.9 | 1.05 | 0.034868 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NP-LIPS_SHA2 | 0.61217 | 0.59473 | -0.017444 |  | 0.9 | 1.05 | 0.031975 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NP-LIPS_SHA2 | 0.61217 | 0.59473 | -0.017444 |  | 0.9 | 1.05 | 0.037422 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NP-LIPS_SHA2 | 0.61217 | 0.59473 | -0.017444 |  | 0.9 | 1.05 | 0.050095 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NP-LUCKY_CR2 | 0.75188 | 0.73628 | -0.015598 |  | 0.9 | 1.05 | 0.040027 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NP-LUCKY_CR2 | 0.75188 | 0.73628 | -0.015598 |  | 0.9 | 1.05 | 0.090773 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NP-LUCKY_CR2 | 0.75188 | 0.73628 | -0.015598 |  | 0.9 | 1.05 | 0.034521 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NP-LUCKY_CR2 | 0.75188 | 0.73628 | -0.015598 |  | 0.9 | 1.05 | 0.038035 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NP-LUCKY_CR2 | 0.75188 | 0.73628 | -0.015598 |  | 0.9 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NP-LUCKY_CR2 | 0.75188 | 0.73628 | -0.015598 |  | 0.9 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NP-LUCKY_CR2 | 0.75188 | 0.73628 | -0.015598 |  | 0.9 | 1.05 | 0.050618 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NP-LUCKY_CR2 | 0.75188 | 0.73628 | -0.015598 |  | 0.9 | 1.05 | 0.04163 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NP-LUCKY_CR2 | 0.75188 | 0.73628 | -0.015598 |  | 0.9 | 1.05 | 0.043776 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NP-LUCKY_CR2 | 0.75188 | 0.73628 | -0.015598 |  | 0.9 | 1.05 | 0.034868 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NP-LUCKY_CR2 | 0.75188 | 0.73628 | -0.015598 |  | 0.9 | 1.05 | 0.031975 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NP-LUCKY_CR2 | 0.75188 | 0.73628 | -0.015598 |  | 0.9 | 1.05 | 0.037422 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NP-LUCKY_CR2 | 0.75188 | 0.73628 | -0.015598 |  | 0.9 | 1.05 | 0.050095 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NP-LUCKY_G 2 | 0.75204 | 0.73644 | -0.015595 |  | 0.9 | 1.05 | 0.040027 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NP-LUCKY_G 2 | 0.75204 | 0.73644 | -0.015595 |  | 0.9 | 1.05 | 0.090773 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NP-LUCKY_G 2 | 0.75204 | 0.73644 | -0.015595 |  | 0.9 | 1.05 | 0.034521 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NP-LUCKY_G 2 | 0.75204 | 0.73644 | -0.015595 |  | 0.9 | 1.05 | 0.038035 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NP-LUCKY_G 2 | 0.75204 | 0.73644 | -0.015595 |  | 0.9 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NP-LUCKY_G 2 | 0.75204 | 0.73644 | -0.015595 |  | 0.9 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NP-LUCKY_G 2 | 0.75204 | 0.73644 | -0.015595 |  | 0.9 | 1.05 | 0.050618 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NP-LUCKY_G 2 | 0.75204 | 0.73644 | -0.015595 |  | 0.9 | 1.05 | 0.04163 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NP-LUCKY_G 2 | 0.75204 | 0.73644 | -0.015595 |  | 0.9 | 1.05 | 0.043776 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NP-LUCKY_G 2 | 0.75204 | 0.73644 | -0.015595 |  | 0.9 | 1.05 | 0.034868 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NP-LUCKY_G 2 | 0.75204 | 0.73644 | -0.015595 |  | 0.9 | 1.05 | 0.031975 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NP-LUCKY_G 2 | 0.75204 | 0.73644 | -0.015595 |  | 0.9 | 1.05 | 0.037422 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NP-LUCKY_G 2 | 0.75204 | 0.73644 | -0.015595 |  | 0.9 | 1.05 | 0.050095 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NP-SHATTUCK2 | 0.60032 | 0.58518 | -0.015141 |  | 0.9 | 1.05 | 0.034054 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NP-SHATTUCK2 | 0.60032 | 0.58518 | -0.015141 |  | 0.9 | 1.05 | 0.093247 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NP-SHATTUCK2 | 0.60032 | 0.58518 | -0.015141 |  | 0.9 | 1.05 | 0.030563 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NP-SHATTUCK2 | 0.60032 | 0.58518 | -0.015141 |  | 0.9 | 1.05 | 0.033696 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NP-SHATTUCK2 | 0.60032 | 0.58518 | -0.015141 |  | 0.9 | 1.05 | 0.044425 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NP-SHATTUCK2 | 0.60032 | 0.58518 | -0.015141 |  | 0.9 | 1.05 | 0.044425 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NP-SHATTUCK2 | 0.60032 | 0.58518 | -0.015141 |  | 0.9 | 1.05 | 0.046653 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NP-SHATTUCK2 | 0.60032 | 0.58518 | -0.015141 |  | 0.9 | 1.05 | 0.036737 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NP-SHATTUCK2 | 0.60032 | 0.58518 | -0.015141 |  | 0.9 | 1.05 | 0.037864 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NP-SHATTUCK2 | 0.60032 | 0.58518 | -0.015141 |  | 0.9 | 1.05 | 0.031064 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NP-SHATTUCK2 | 0.60032 | 0.58518 | -0.015141 |  | 0.9 | 1.05 | 0.032715 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NP-SHATTUCK2 | 0.60032 | 0.58518 | -0.015141 |  | 0.9 | 1.05 | 0.044267 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NP-SHATTUCK2 | 0.58904 | 0.57137 | -0.017672 |  | 0.9 | 1.05 | 0.040027 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NP-SHATTUCK2 | 0.58904 | 0.57137 | -0.017672 |  | 0.9 | 1.05 | 0.090773 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NP-SHATTUCK2 | 0.58904 | 0.57137 | -0.017672 |  | 0.9 | 1.05 | 0.034521 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NP-SHATTUCK2 | 0.58904 | 0.57137 | -0.017672 |  | 0.9 | 1.05 | 0.038035 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NP-SHATTUCK2 | 0.58904 | 0.57137 | -0.017672 |  | 0.9 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NP-SHATTUCK2 | 0.58904 | 0.57137 | -0.017672 |  | 0.9 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NP-SHATTUCK2 | 0.58904 | 0.57137 | -0.017672 |  | 0.9 | 1.05 | 0.050618 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NP-SHATTUCK2 | 0.58904 | 0.57137 | -0.017672 |  | 0.9 | 1.05 | 0.04163 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NP-SHATTUCK2 | 0.58904 | 0.57137 | -0.017672 |  | 0.9 | 1.05 | 0.043776 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NP-SHATTUCK2 | 0.58904 | 0.57137 | -0.017672 |  | 0.9 | 1.05 | 0.034868 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NP-SHATTUCK2 | 0.58904 | 0.57137 | -0.017672 |  | 0.9 | 1.05 | 0.031975 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NP-SHATTUCK2 | 0.58904 | 0.57137 | -0.017672 |  | 0.9 | 1.05 | 0.037422 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NP-SHATTUCK2 | 0.58904 | 0.57137 | -0.017672 |  | 0.9 | 1.05 | 0.050095 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NP-VALERO_P2 | 0.63195 | 0.61713 | -0.014821 |  | 0.9 | 1.05 | 0.034054 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NP-VALERO_P2 | 0.63195 | 0.61713 | -0.014821 |  | 0.9 | 1.05 | 0.093247 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NP-VALERO_P2 | 0.63195 | 0.61713 | -0.014821 |  | 0.9 | 1.05 | 0.030563 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NP-VALERO_P2 | 0.63195 | 0.61713 | -0.014821 |  | 0.9 | 1.05 | 0.033696 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NP-VALERO_P2 | 0.63195 | 0.61713 | -0.014821 |  | 0.9 | 1.05 | 0.044425 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NP-VALERO_P2 | 0.63195 | 0.61713 | -0.014821 |  | 0.9 | 1.05 | 0.044425 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NP-VALERO_P2 | 0.63195 | 0.61713 | -0.014821 |  | 0.9 | 1.05 | 0.046653 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NP-VALERO_P2 | 0.63195 | 0.61713 | -0.014821 |  | 0.9 | 1.05 | 0.036737 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NP-VALERO_P2 | 0.63195 | 0.61713 | -0.014821 |  | 0.9 | 1.05 | 0.037864 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NP-VALERO_P2 | 0.63195 | 0.61713 | -0.014821 |  | 0.9 | 1.05 | 0.031064 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NP-VALERO_P2 | 0.63195 | 0.61713 | -0.014821 |  | 0.9 | 1.05 | 0.032715 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NP-VALERO_P2 | 0.63195 | 0.61713 | -0.014821 |  | 0.9 | 1.05 | 0.044267 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NP-VALERO_P2 | 0.62091 | 0.60356 | -0.017349 |  | 0.9 | 1.05 | 0.040027 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NP-VALERO_P2 | 0.62091 | 0.60356 | -0.017349 |  | 0.9 | 1.05 | 0.090773 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NP-VALERO_P2 | 0.62091 | 0.60356 | -0.017349 |  | 0.9 | 1.05 | 0.034521 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NP-VALERO_P2 | 0.62091 | 0.60356 | -0.017349 |  | 0.9 | 1.05 | 0.038035 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NP-VALERO_P2 | 0.62091 | 0.60356 | -0.017349 |  | 0.9 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NP-VALERO_P2 | 0.62091 | 0.60356 | -0.017349 |  | 0.9 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NP-VALERO_P2 | 0.62091 | 0.60356 | -0.017349 |  | 0.9 | 1.05 | 0.050618 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NP-VALERO_P2 | 0.62091 | 0.60356 | -0.017349 |  | 0.9 | 1.05 | 0.04163 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NP-VALERO_P2 | 0.62091 | 0.60356 | -0.017349 |  | 0.9 | 1.05 | 0.043776 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NP-VALERO_P2 | 0.62091 | 0.60356 | -0.017349 |  | 0.9 | 1.05 | 0.034868 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NP-VALERO_P2 | 0.62091 | 0.60356 | -0.017349 |  | 0.9 | 1.05 | 0.031975 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NP-VALERO_P2 | 0.62091 | 0.60356 | -0.017349 |  | 0.9 | 1.05 | 0.037422 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NP-VALERO_P2 | 0.62091 | 0.60356 | -0.017349 |  | 0.9 | 1.05 | 0.050095 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NRAYMORE | 0.99084 | 0.92453 | -0.066302 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NRAYMORE | 0.99084 | 0.92453 | -0.066302 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NRAYMORE | 0.99084 | 0.92453 | -0.066302 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NRAYMORE | 0.99084 | 0.92453 | -0.066302 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NRAYMORE | 0.99084 | 0.92453 | -0.066302 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NRAYMORE | 0.99084 | 0.92453 | -0.066302 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NRAYMORE | 0.99084 | 0.92453 | -0.066302 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NRAYMORE | 0.99084 | 0.92453 | -0.066302 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NRAYMORE | 0.99084 | 0.92453 | -0.066302 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NRAYMORE | 0.99084 | 0.92453 | -0.066302 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NRAYMORE | 0.99084 | 0.92453 | -0.066302 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NRAYMORE | 0.99084 | 0.92453 | -0.066302 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NRAYMORE | 0.99084 | 0.92453 | -0.066302 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NRAYMORE | 0.99084 | 0.92453 | -0.066302 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NRAYMORE | 0.99084 | 0.92453 | -0.066302 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NRAYMORE | 0.99084 | 0.92453 | -0.066302 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NRAYMORE | 0.99084 | 0.92453 | -0.066302 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NRAYMORE | 0.99084 | 0.92453 | -0.066302 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NRAYMORE | 0.99084 | 0.92453 | -0.066302 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NRAYMORE | 0.99084 | 0.92453 | -0.066302 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NRAYMORE | 0.99084 | 0.92453 | -0.066302 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NRAYMORE | 0.99084 | 0.92453 | -0.066302 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NRAYMORE | 0.99084 | 0.92453 | -0.066302 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NRAYMORE | 0.99084 | 0.92453 | -0.066302 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NRAYMORE | 0.99084 | 0.92453 | -0.066302 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NRAYMORE | 0.99084 | 0.92453 | -0.066302 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NRAYMORE | 0.99084 | 0.92453 | -0.066302 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | NRAYMORE | 0.99084 | 0.92453 | -0.066302 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NRAYMORETP 5 | 0.99157 | 0.92477 | -0.066804 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NRAYMORETP 5 | 0.99157 | 0.92477 | -0.066804 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NRAYMORETP 5 | 0.99157 | 0.92477 | -0.066804 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NRAYMORETP 5 | 0.99157 | 0.92477 | -0.066804 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NRAYMORETP 5 | 0.99157 | 0.92477 | -0.066804 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NRAYMORETP 5 | 0.99157 | 0.92477 | -0.066804 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NRAYMORETP 5 | 0.99157 | 0.92477 | -0.066804 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NRAYMORETP 5 | 0.99157 | 0.92477 | -0.066804 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NRAYMORETP 5 | 0.99157 | 0.92477 | -0.066804 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NRAYMORETP 5 | 0.99157 | 0.92477 | -0.066804 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NRAYMORETP 5 | 0.99157 | 0.92477 | -0.066804 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NRAYMORETP 5 | 0.99157 | 0.92477 | -0.066804 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NRAYMORETP 5 | 0.99157 | 0.92477 | -0.066804 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NRAYMORETP 5 | 0.99157 | 0.92477 | -0.066804 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NRAYMORETP 5 | 0.99157 | 0.92477 | -0.066804 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NRAYMORETP 5 | 0.99157 | 0.92477 | -0.066804 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NRAYMORETP 5 | 0.99157 | 0.92477 | -0.066804 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NRAYMORETP 5 | 0.99157 | 0.92477 | -0.066804 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NRAYMORETP 5 | 0.99157 | 0.92477 | -0.066804 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NRAYMORETP 5 | 0.99157 | 0.92477 | -0.066804 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NRAYMORETP 5 | 0.99157 | 0.92477 | -0.066804 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NRAYMORETP 5 | 0.99157 | 0.92477 | -0.066804 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NRAYMORETP 5 | 0.99157 | 0.92477 | -0.066804 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NRAYMORETP 5 | 0.99157 | 0.92477 | -0.066804 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NRAYMORETP 5 | 0.99157 | 0.92477 | -0.066804 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NRAYMORETP 5 | 0.99157 | 0.92477 | -0.066804 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NRAYMORETP 5 | 0.99157 | 0.92477 | -0.066804 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | NRAYMORETP 5 | 0.99157 | 0.92477 | -0.066804 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NRSS7 | 0.99575 | 0.94771 | -0.04804 |  | 0.95 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NRSS7 | 0.99575 | 0.94771 | -0.04804 |  | 0.95 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NRSS7 | 0.99575 | 0.94771 | -0.04804 |  | 0.95 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NRSS7 | 0.99575 | 0.94771 | -0.04804 |  | 0.95 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NRSS7 | 0.99575 | 0.94771 | -0.04804 |  | 0.95 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NRSS7 | 0.99575 | 0.94771 | -0.04804 |  | 0.95 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NRSS7 | 0.99575 | 0.94771 | -0.04804 |  | 0.95 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NRSS7 | 0.99575 | 0.94771 | -0.04804 |  | 0.95 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NRSS7 | 0.99575 | 0.94771 | -0.04804 |  | 0.95 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NRSS7 | 0.99575 | 0.94771 | -0.04804 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NRSS7 | 0.99575 | 0.94771 | -0.04804 |  | 0.95 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NRSS7 | 0.99575 | 0.94771 | -0.04804 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NRSS7 | 0.99575 | 0.94771 | -0.04804 |  | 0.95 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NRSS7 | 0.99575 | 0.94771 | -0.04804 |  | 0.95 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NRSS7 | 0.99575 | 0.94771 | -0.04804 |  | 0.95 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NRSS7 | 0.99575 | 0.94771 | -0.04804 |  | 0.95 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NRSS7 | 0.99575 | 0.94771 | -0.04804 |  | 0.95 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NRSS7 | 0.99575 | 0.94771 | -0.04804 |  | 0.95 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NRSS7 | 0.99575 | 0.94771 | -0.04804 |  | 0.95 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NRSS7 | 0.99575 | 0.94771 | -0.04804 |  | 0.95 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NRSS7 | 0.99575 | 0.94771 | -0.04804 |  | 0.95 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NRSS7 | 0.99575 | 0.94771 | -0.04804 |  | 0.95 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | NRSS7 | 0.99823 | 0.9356 | -0.062631 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | NRSS7 | 0.99823 | 0.9356 | -0.062631 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | NRSS7 | 0.99823 | 0.9356 | -0.062631 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | NRSS7 | 0.99823 | 0.9356 | -0.062631 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | NRSS7 | 0.99823 | 0.9356 | -0.062631 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NRSS7 | 0.99823 | 0.9356 | -0.062631 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | NRSS7 | 0.99823 | 0.9356 | -0.062631 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | NRSS7 | 0.99823 | 0.9356 | -0.062631 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | NRSS7 | 0.99823 | 0.9356 | -0.062631 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | NRSS7 | 0.99823 | 0.9356 | -0.062631 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | NRSS7 | 0.99823 | 0.9356 | -0.062631 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NRSS7 | 0.99823 | 0.9356 | -0.062631 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | NRSS7 | 0.99823 | 0.9356 | -0.062631 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NRSS7 | 0.99823 | 0.9356 | -0.062631 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NRSS7 | 0.99823 | 0.9356 | -0.062631 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NRSS7 | 0.99823 | 0.9356 | -0.062631 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | NRSS7 | 0.99823 | 0.9356 | -0.062631 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | NRSS7 | 0.99823 | 0.9356 | -0.062631 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | NRSS7 | 0.99823 | 0.9356 | -0.062631 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | NRSS7 | 0.99823 | 0.9356 | -0.062631 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | NRSS7 | 0.99823 | 0.9356 | -0.062631 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NRSS7 | 0.99823 | 0.9356 | -0.062631 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | NRSS7 | 0.99823 | 0.9356 | -0.062631 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | NRSS7 | 0.99823 | 0.9356 | -0.062631 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | NRSS7 | 0.99823 | 0.9356 | -0.062631 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | NRSS7 | 0.99823 | 0.9356 | -0.062631 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NRSS7 | 0.99823 | 0.9356 | -0.062631 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | NRSS7 | 0.99823 | 0.9356 | -0.062631 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NSI 3 | 0.96376 | 0.89527 | -0.068486 |  | 0.9 | 1.05 | 0.041569 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NSI 3 | 0.96376 | 0.89527 | -0.068486 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NSI 3 | 0.96376 | 0.89527 | -0.068486 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NSI 3 | 0.96376 | 0.89527 | -0.068486 |  | 0.9 | 1.05 | 0.03222 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NSI 3 | 0.96376 | 0.89527 | -0.068486 |  | 0.9 | 1.05 | 0.030633 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NSI 3 | 0.96376 | 0.89527 | -0.068486 |  | 0.9 | 1.05 | 0.030061 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NSI 3 | 0.96376 | 0.89527 | -0.068486 |  | 0.9 | 1.05 | 0.031207 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NSI 3 | 0.93801 | 0.86041 | -0.077595 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NSI 3 | 0.93801 | 0.86041 | -0.077595 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NSI 3 | 0.9394 | 0.85279 | -0.086614 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NSI 3 | 0.9394 | 0.85279 | -0.086614 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NSI 3 | 0.9394 | 0.85279 | -0.086614 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NSI 3 | 0.9394 | 0.85279 | -0.086614 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NSI 3 | 0.9394 | 0.85279 | -0.086615 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NSI 3 | 0.9394 | 0.85279 | -0.086615 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NSI TAP3 | 0.96485 | 0.89646 | -0.068394 |  | 0.9 | 1.05 | 0.041569 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | NSI TAP3 | 0.96485 | 0.89646 | -0.068394 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | NSI TAP3 | 0.96485 | 0.89646 | -0.068394 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | NSI TAP3 | 0.96485 | 0.89646 | -0.068394 |  | 0.9 | 1.05 | 0.03222 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | NSI TAP3 | 0.96485 | 0.89646 | -0.068394 |  | 0.9 | 1.05 | 0.030633 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | NSI TAP3 | 0.96485 | 0.89646 | -0.068394 |  | 0.9 | 1.05 | 0.030061 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NSI TAP3 | 0.96485 | 0.89646 | -0.068394 |  | 0.9 | 1.05 | 0.031207 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NSI TAP3 | 0.93914 | 0.86165 | -0.077483 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NSI TAP3 | 0.93914 | 0.86165 | -0.077483 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NSI TAP3 | 0.94052 | 0.85404 | -0.086488 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NSI TAP3 | 0.94052 | 0.85404 | -0.086488 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NSI TAP3 | 0.94052 | 0.85404 | -0.086489 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NSI TAP3 | 0.94052 | 0.85404 | -0.086489 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | NSI TAP3 | 0.94053 | 0.85404 | -0.086489 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | NSI TAP3 | 0.94053 | 0.85404 | -0.086489 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | OAKGRV 5 | 0.99038 | 0.92981 | -0.060575 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | OAKGRV 5 | 0.99038 | 0.92981 | -0.060575 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | OAKGRV 5 | 0.99038 | 0.92981 | -0.060575 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | OAKGRV 5 | 0.99038 | 0.92981 | -0.060575 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | OAKGRV 5 | 0.99038 | 0.92981 | -0.060575 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | OAKGRV 5 | 0.99038 | 0.92981 | -0.060575 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | OAKGRV 5 | 0.99038 | 0.92981 | -0.060575 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | OAKGRV 5 | 0.99038 | 0.92981 | -0.060575 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | OAKGRV 5 | 0.99038 | 0.92981 | -0.060575 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | OAKGRV 5 | 0.99038 | 0.92981 | -0.060575 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | OAKGRV 5 | 0.99038 | 0.92981 | -0.060575 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | OAKGRV 5 | 0.99038 | 0.92981 | -0.060575 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | OAKGRV 5 | 0.99038 | 0.92981 | -0.060575 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | OAKGRV 5 | 0.99038 | 0.92981 | -0.060575 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | OAKGRV 5 | 0.99038 | 0.92981 | -0.060575 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | OAKGRV 5 | 0.99038 | 0.92981 | -0.060575 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | OAKGRV 5 | 0.99038 | 0.92981 | -0.060575 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | OAKGRV 5 | 0.99038 | 0.92981 | -0.060575 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | OAKGRV 5 | 0.99038 | 0.92981 | -0.060575 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | OAKGRV 5 | 0.99038 | 0.92981 | -0.060575 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | OAKGRV 5 | 0.99038 | 0.92981 | -0.060575 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | OAKGRV 5 | 0.99038 | 0.92981 | -0.060575 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | OAKGRV 5 | 0.99038 | 0.92981 | -0.060575 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | OAKGRV 5 | 0.99038 | 0.92981 | -0.060575 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | OAKGRV 5 | 0.99038 | 0.92981 | -0.060575 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | OAKGRV 5 | 0.99038 | 0.92981 | -0.060575 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | OAKGRV 5 | 0.99038 | 0.92981 | -0.060575 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | OAKGRV 5 | 0.99038 | 0.92981 | -0.060575 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | OBER T 3 | 0.95862 | 0.89497 | -0.06365 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | OBER T 3 | 0.95862 | 0.89497 | -0.06365 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | OBER T 3 | 0.95987 | 0.89309 | -0.066773 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | OBER T 3 | 0.95987 | 0.89309 | -0.066773 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | OBER T 3 | 0.95987 | 0.89309 | -0.066773 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | OBER T 3 | 0.95987 | 0.89309 | -0.066773 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | OBER T 3 | 0.95987 | 0.8931 | -0.066774 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | OBER T 3 | 0.95987 | 0.8931 | -0.066774 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | OBERLIN3 | 0.95841 | 0.89475 | -0.063666 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | OBERLIN3 | 0.95841 | 0.89475 | -0.063666 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | OBERLIN3 | 0.95966 | 0.89287 | -0.066789 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | OBERLIN3 | 0.95966 | 0.89287 | -0.066789 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | OBERLIN3 | 0.95966 | 0.89287 | -0.066789 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | OBERLIN3 | 0.95966 | 0.89287 | -0.066789 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | OBERLIN3 | 0.95966 | 0.89287 | -0.06679 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | OBERLIN3 | 0.95966 | 0.89287 | -0.06679 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | OLATHE 5 | 0.96683 | 0.92825 | -0.038584 |  | 0.93 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | OLATHE 5 | 0.96683 | 0.92825 | -0.038584 |  | 0.93 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | OLATHE 5 | 0.96683 | 0.92825 | -0.038584 |  | 0.93 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | OLATHE 5 | 0.96683 | 0.92825 | -0.038584 |  | 0.93 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | OLATHE 5 | 0.96683 | 0.92825 | -0.038584 |  | 0.93 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | OLATHE 5 | 0.96683 | 0.92825 | -0.038584 |  | 0.93 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | OLATHE 5 | 0.96683 | 0.92825 | -0.038584 |  | 0.93 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | OLATHE 5 | 0.96683 | 0.92825 | -0.038584 |  | 0.93 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | OLATHE 5 | 0.96683 | 0.92825 | -0.038584 |  | 0.93 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | OLATHE 5 | 0.96683 | 0.92825 | -0.038584 |  | 0.93 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | OLATHE 5 | 0.96683 | 0.92825 | -0.038584 |  | 0.93 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | OLATHE 5 | 0.96683 | 0.92825 | -0.038584 |  | 0.93 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | OLATHE 5 | 0.96683 | 0.92825 | -0.038584 |  | 0.93 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | OLATHE 5 | 0.96683 | 0.92825 | -0.038584 |  | 0.93 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | OLATHE 5 | 0.96683 | 0.92825 | -0.038584 |  | 0.93 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | OLATHE 5 | 0.96683 | 0.92825 | -0.038584 |  | 0.93 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | OLATHE 5 | 0.96683 | 0.92825 | -0.038584 |  | 0.93 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | OLATHE 5 | 0.96683 | 0.92825 | -0.038584 |  | 0.93 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | OLATHE 5 | 0.96683 | 0.92825 | -0.038584 |  | 0.93 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | OLATHE 5 | 0.96683 | 0.92825 | -0.038584 |  | 0.93 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | OLATHE 5 | 0.96 | 0.91744 | -0.042558 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | OLATHE 5 | 0.96 | 0.91744 | -0.042558 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | OLATHE 5 | 0.96 | 0.91744 | -0.042558 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | OLATHE 5 | 0.96 | 0.91744 | -0.042558 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | OLATHE 5 | 0.96 | 0.91744 | -0.042558 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | OLATHE 5 | 0.96 | 0.91744 | -0.042558 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | OLATHE 5 | 0.96 | 0.91744 | -0.042558 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | OLATHE 5 | 0.96 | 0.91744 | -0.042558 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | OLATHE 5 | 0.96 | 0.91744 | -0.042558 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | OLATHE 5 | 0.96 | 0.91744 | -0.042558 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | OLATHE 5 | 0.96 | 0.91744 | -0.042558 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | OLATHE 5 | 0.96 | 0.91744 | -0.042558 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | OLATHE 5 | 0.96 | 0.91744 | -0.042558 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | OLATHE 5 | 0.96 | 0.91744 | -0.042558 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | OLATHE 5 | 0.96 | 0.91744 | -0.042558 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | OLATHE 5 | 0.96 | 0.91744 | -0.042558 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | OLATHE 5 | 0.96 | 0.91744 | -0.042558 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | OLATHE 5 | 0.96 | 0.91744 | -0.042558 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | OLATHE 5 | 0.96 | 0.91744 | -0.042558 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | OLATHE 5 | 0.96 | 0.91744 | -0.042558 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | OLATHE 5 | 0.97046 | 0.92328 | -0.047184 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | OLATHE 5 | 0.97046 | 0.92328 | -0.047184 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | OLATHE 5 | 0.97046 | 0.92328 | -0.047184 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | OLATHE 5 | 0.97046 | 0.92328 | -0.047184 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | OLATHE 5 | 0.97046 | 0.92328 | -0.047184 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | OLATHE 5 | 0.97046 | 0.92328 | -0.047184 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | OLATHE 5 | 0.97046 | 0.92328 | -0.047184 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | OLATHE 5 | 0.97046 | 0.92328 | -0.047184 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | OLATHE 5 | 0.97046 | 0.92328 | -0.047184 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | OLATHE 5 | 0.97046 | 0.92328 | -0.047184 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | OLATHE 5 | 0.97046 | 0.92328 | -0.047184 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | OLATHE 5 | 0.97046 | 0.92328 | -0.047184 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | OLATHE 5 | 0.97046 | 0.92328 | -0.047184 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | OLATHE 5 | 0.97046 | 0.92328 | -0.047184 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | OLATHE 5 | 0.97046 | 0.92328 | -0.047184 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | OLATHE 5 | 0.97046 | 0.92328 | -0.047184 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | OLATHE 5 | 0.97046 | 0.92328 | -0.047184 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | OLATHE 5 | 0.97046 | 0.92328 | -0.047184 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | OLATHE 5 | 0.97046 | 0.92328 | -0.047184 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | OLATHE 5 | 0.97046 | 0.92328 | -0.047184 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | OLATHE 5 | 0.97311 | 0.89982 | -0.073294 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | OLATHE 5 | 0.97311 | 0.89982 | -0.073294 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | OLATHE 5 | 0.97311 | 0.89982 | -0.073294 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | OLATHE 5 | 0.97311 | 0.89982 | -0.073294 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | OLATHE 5 | 0.97311 | 0.89982 | -0.073294 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | OLATHE 5 | 0.97311 | 0.89982 | -0.073294 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | OLATHE 5 | 0.97311 | 0.89982 | -0.073294 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | OLATHE 5 | 0.97311 | 0.89982 | -0.073294 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | OLATHE 5 | 0.97311 | 0.89982 | -0.073294 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | OLATHE 5 | 0.97311 | 0.89982 | -0.073294 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | OLATHE 5 | 0.97311 | 0.89982 | -0.073294 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | OLATHE 5 | 0.97311 | 0.89982 | -0.073294 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | OLATHE 5 | 0.97311 | 0.89982 | -0.073294 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | OLATHE 5 | 0.97311 | 0.89982 | -0.073294 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | OLATHE 5 | 0.97311 | 0.89982 | -0.073294 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | OLATHE 5 | 0.97311 | 0.89982 | -0.073294 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | OLATHE 5 | 0.97311 | 0.89982 | -0.073294 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | OLATHE 5 | 0.97311 | 0.89982 | -0.073294 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | OLATHE 5 | 0.97311 | 0.89982 | -0.073294 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | OLATHE 5 | 0.97311 | 0.89982 | -0.073294 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | OLATHE 5 | 0.97311 | 0.89982 | -0.073294 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | OLATHE 5 | 0.97311 | 0.89982 | -0.073294 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | OLATHE 5 | 0.97311 | 0.89982 | -0.073294 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | OLATHE 5 | 0.97311 | 0.89982 | -0.073294 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | OLATHE 5 | 0.97311 | 0.89982 | -0.073294 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | OLATHE 5 | 0.97311 | 0.89982 | -0.073294 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | OLATHE 5 | 0.97311 | 0.89982 | -0.073294 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | OLATHE 5 | 0.97311 | 0.89982 | -0.073294 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | OLATHE 5 | 0.96602 | 0.92647 | -0.039552 |  | 0.93 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | OLATHE 5 | 0.96602 | 0.92647 | -0.039552 |  | 0.93 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | OLATHE 5 | 0.96602 | 0.92647 | -0.039552 |  | 0.93 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | OLATHE 5 | 0.96602 | 0.92647 | -0.039552 |  | 0.93 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | OLATHE 5 | 0.96602 | 0.92647 | -0.039552 |  | 0.93 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | OLATHE 5 | 0.96602 | 0.92647 | -0.039552 |  | 0.93 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | OLATHE 5 | 0.96602 | 0.92647 | -0.039552 |  | 0.93 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | OLATHE 5 | 0.96602 | 0.92647 | -0.039552 |  | 0.93 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | OLATHE 5 | 0.96602 | 0.92647 | -0.039552 |  | 0.93 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | OLATHE 5 | 0.96602 | 0.92647 | -0.039552 |  | 0.93 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | OLATHE 5 | 0.96602 | 0.92647 | -0.039552 |  | 0.93 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | OLATHE 5 | 0.96602 | 0.92647 | -0.039552 |  | 0.93 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | OLATHE 5 | 0.96602 | 0.92647 | -0.039552 |  | 0.93 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | OLATHE 5 | 0.96602 | 0.92647 | -0.039552 |  | 0.93 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | OLATHE 5 | 0.96602 | 0.92647 | -0.039552 |  | 0.93 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | OLATHE 5 | 0.96602 | 0.92647 | -0.039552 |  | 0.93 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | OLATHE 5 | 0.96602 | 0.92647 | -0.039552 |  | 0.93 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | OLATHE 5 | 0.96602 | 0.92647 | -0.039552 |  | 0.93 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | OLATHE 5 | 0.96602 | 0.92647 | -0.039552 |  | 0.93 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | OLATHE 5 | 0.96602 | 0.92647 | -0.039552 |  | 0.93 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | ORDNCE 2 | 0.95211 | 0.90921 | -0.042903 |  | 0.93 | 1.05 | 0.077629 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | ORDNCE 2 | 0.95211 | 0.90921 | -0.042903 |  | 0.93 | 1.05 | 0.06446 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | ORDNCE 2 | 0.95211 | 0.90921 | -0.042903 |  | 0.93 | 1.05 | 0.066434 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | ORDNCE 2 | 0.95211 | 0.90921 | -0.042903 |  | 0.93 | 1.05 | 0.073293 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ORDNCE 2 | 0.95211 | 0.90921 | -0.042903 |  | 0.93 | 1.05 | 0.053415 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-122 | ORDNCE 2 | 0.95211 | 0.90921 | -0.042903 |  | 0.93 | 1.05 | 0.08103 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-177 | ORDNCE 2 | 0.95211 | 0.90921 | -0.042903 |  | 0.93 | 1.05 | 0.08268 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-178 | ORDNCE 2 | 0.95211 | 0.90921 | -0.042903 |  | 0.93 | 1.05 | 0.077122 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | ORDNCE 2 | 0.95211 | 0.90921 | -0.042903 |  | 0.93 | 1.05 | 0.032185 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | ORDNCE 2 | 0.95211 | 0.90921 | -0.042903 |  | 0.93 | 1.05 | 0.073922 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-232 | ORDNCE 2 | 0.95211 | 0.90921 | -0.042903 |  | 0.93 | 1.05 | 0.076776 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | ORDNCE 2 | 0.95211 | 0.90921 | -0.042903 |  | 0.93 | 1.05 | 0.06446 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ORDNCE 2 | 0.95211 | 0.90921 | -0.042903 |  | 0.93 | 1.05 | 0.038841 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | ORDNCE 2 | 0.95211 | 0.90921 | -0.042903 |  | 0.93 | 1.05 | 0.034687 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | ORDNCE 2 | 0.95211 | 0.90921 | -0.042903 |  | 0.93 | 1.05 | 0.034687 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | ORDNCE 2 | 0.95211 | 0.90921 | -0.042903 |  | 0.93 | 1.05 | 0.031574 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | ORDNCE 2 | 0.95211 | 0.90921 | -0.042903 |  | 0.93 | 1.05 | 0.042889 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-376 | ORDNCE 2 | 0.95211 | 0.90921 | -0.042903 |  | 0.93 | 1.05 | 0.079908 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ORDNCE 2 | 0.94915 | 0.91021 | -0.038934 |  | 0.93 | 1.05 | 0.040299 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ORDNCE 2 | 0.94915 | 0.91021 | -0.038934 |  | 0.93 | 1.05 | 0.048812 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ORDNCE 2 | 0.94915 | 0.91021 | -0.038934 |  | 0.93 | 1.05 | 0.076211 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ORDNCE 2 | 0.94915 | 0.91021 | -0.038934 |  | 0.93 | 1.05 | 0.069331 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ORDNCE 2 | 0.94915 | 0.91021 | -0.038934 |  | 0.93 | 1.05 | 0.035943 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ORDNCE 2 | 0.94915 | 0.91021 | -0.038934 |  | 0.93 | 1.05 | 0.034061 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ORDNCE 2 | 0.94915 | 0.91021 | -0.038934 |  | 0.93 | 1.05 | 0.064216 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ORDNCE 2 | 0.94915 | 0.91021 | -0.038934 |  | 0.93 | 1.05 | 0.045005 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ORDNCE 2 | 0.94915 | 0.91021 | -0.038934 |  | 0.93 | 1.05 | 0.13572 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | ORDNCE 2 | 0.94915 | 0.91021 | -0.038934 |  | 0.93 | 1.05 | 0.037472 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | ORDNCE 2 | 0.94915 | 0.91021 | -0.038934 |  | 0.93 | 1.05 | 0.037472 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ORDNCE 2 | 0.94915 | 0.91021 | -0.038934 |  | 0.93 | 1.05 | 0.06894 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ORDNCE 2 | 0.94915 | 0.91021 | -0.038934 |  | 0.93 | 1.05 | 0.034713 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ORDNCE 2 | 0.94915 | 0.91021 | -0.038934 |  | 0.93 | 1.05 | 0.035229 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ORDNCE 2 | 0.94915 | 0.91043 | -0.038722 |  | 0.93 | 1.05 | 0.094783 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ORDNCE 2 | 0.94915 | 0.91043 | -0.038722 |  | 0.93 | 1.05 | 0.03645 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ORDNCE 2 | 0.94915 | 0.91043 | -0.038722 |  | 0.93 | 1.05 | 0.04755 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ORDNCE 2 | 0.94915 | 0.91043 | -0.038722 |  | 0.93 | 1.05 | 0.06097 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ORDNCE 2 | 0.94915 | 0.91043 | -0.038722 |  | 0.93 | 1.05 | 0.061051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | ORDNCE 2 | 0.94915 | 0.91043 | -0.038722 |  | 0.93 | 1.05 | 0.04456 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | ORDNCE 2 | 0.94915 | 0.91043 | -0.038722 |  | 0.93 | 1.05 | 0.048811 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ORDNCE 2 | 0.94915 | 0.91043 | -0.038722 |  | 0.93 | 1.05 | 0.13004 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ORDNCE 2 | 0.94915 | 0.91043 | -0.038722 |  | 0.93 | 1.05 | 0.049018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ORDNCE 2 | 0.94915 | 0.91043 | -0.038722 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ORDNCE 2 | 0.94915 | 0.91043 | -0.038722 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ORDNCE 2 | 0.94915 | 0.91043 | -0.038722 |  | 0.93 | 1.05 | 0.05974 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ORDNCE 2 | 0.94915 | 0.91043 | -0.038722 |  | 0.93 | 1.05 | 0.076949 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ORDNCE 2 | 0.94915 | 0.91043 | -0.038722 |  | 0.93 | 1.05 | 0.042157 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ORDNCE 2 | 0.94915 | 0.91043 | -0.038722 |  | 0.93 | 1.05 | 0.040957 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | ORDNCE 2 | 0.94915 | 0.91043 | -0.038722 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | ORDNCE 2 | 0.94915 | 0.91043 | -0.038722 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ORDNCE 2 | 0.94915 | 0.91043 | -0.038722 |  | 0.93 | 1.05 | 0.054637 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ORDNCE 2 | 0.94915 | 0.91043 | -0.038722 |  | 0.93 | 1.05 | 0.060597 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | ORDNCE 2 | 0.94915 | 0.91043 | -0.038722 |  | 0.93 | 1.05 | 0.044286 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ORDNCE 2 | 0.94915 | 0.91043 | -0.038722 |  | 0.93 | 1.05 | 0.059107 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ORDNCE 2 | 0.94915 | 0.91043 | -0.038722 |  | 0.93 | 1.05 | 0.052698 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ORDNCE 2 | 0.94915 | 0.91043 | -0.038722 |  | 0.93 | 1.05 | 0.067422 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ORDNCE 2 | 0.94915 | 0.91043 | -0.038722 |  | 0.93 | 1.05 | 0.053768 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | ORDNCE 2 | 0.94915 | 0.91043 | -0.038722 |  | 0.93 | 1.05 | 0.03909 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ORDNCE 2 | 0.94803 | 0.90637 | -0.041659 |  | 0.93 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ORDNCE 2 | 0.94803 | 0.90637 | -0.041659 |  | 0.93 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ORDNCE 2 | 0.94803 | 0.90637 | -0.041659 |  | 0.93 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ORDNCE 2 | 0.94803 | 0.90637 | -0.041659 |  | 0.93 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ORDNCE 2 | 0.94803 | 0.90637 | -0.041659 |  | 0.93 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ORDNCE 2 | 0.94803 | 0.90637 | -0.041659 |  | 0.93 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ORDNCE 2 | 0.94803 | 0.90637 | -0.041659 |  | 0.93 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | ORDNCE 2 | 0.94803 | 0.90637 | -0.041659 |  | 0.93 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ORDNCE 2 | 0.94803 | 0.90637 | -0.041659 |  | 0.93 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ORDNCE 2 | 0.94803 | 0.90637 | -0.041659 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ORDNCE 2 | 0.94803 | 0.90637 | -0.041659 |  | 0.93 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ORDNCE 2 | 0.94803 | 0.90637 | -0.041659 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ORDNCE 2 | 0.94803 | 0.90637 | -0.041659 |  | 0.93 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ORDNCE 2 | 0.94803 | 0.90637 | -0.041659 |  | 0.93 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ORDNCE 2 | 0.94803 | 0.90637 | -0.041659 |  | 0.93 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ORDNCE 2 | 0.94803 | 0.90637 | -0.041659 |  | 0.93 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ORDNCE 2 | 0.94803 | 0.90637 | -0.041659 |  | 0.93 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ORDNCE 2 | 0.94803 | 0.90637 | -0.041659 |  | 0.93 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ORDNCE 2 | 0.94803 | 0.90637 | -0.041659 |  | 0.93 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ORDNCE 2 | 0.94803 | 0.90637 | -0.041659 |  | 0.93 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ORDNCE 2 | 0.94803 | 0.90637 | -0.041659 |  | 0.93 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ORDNCE 2 | 0.94803 | 0.90637 | -0.041659 |  | 0.93 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ORDNCE 2 | 0.94836 | 0.89167 | -0.056694 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ORDNCE 2 | 0.94836 | 0.89167 | -0.056694 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ORDNCE 2 | 0.94836 | 0.89167 | -0.056694 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ORDNCE 2 | 0.94836 | 0.89167 | -0.056694 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ORDNCE 2 | 0.94836 | 0.89167 | -0.056694 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ORDNCE 2 | 0.94836 | 0.89167 | -0.056694 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ORDNCE 2 | 0.94836 | 0.89167 | -0.056694 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | ORDNCE 2 | 0.94836 | 0.89167 | -0.056694 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | ORDNCE 2 | 0.94836 | 0.89167 | -0.056694 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ORDNCE 2 | 0.94836 | 0.89167 | -0.056694 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ORDNCE 2 | 0.94836 | 0.89167 | -0.056694 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ORDNCE 2 | 0.94836 | 0.89167 | -0.056694 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ORDNCE 2 | 0.94836 | 0.89167 | -0.056694 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ORDNCE 2 | 0.94836 | 0.89167 | -0.056694 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ORDNCE 2 | 0.94836 | 0.89167 | -0.056694 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ORDNCE 2 | 0.94836 | 0.89167 | -0.056694 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ORDNCE 2 | 0.94836 | 0.89167 | -0.056694 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ORDNCE 2 | 0.94836 | 0.89167 | -0.056694 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | ORDNCE 2 | 0.94836 | 0.89167 | -0.056694 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | ORDNCE 2 | 0.94836 | 0.89167 | -0.056694 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ORDNCE 2 | 0.94836 | 0.89167 | -0.056694 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ORDNCE 2 | 0.94836 | 0.89167 | -0.056694 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | ORDNCE 2 | 0.94836 | 0.89167 | -0.056694 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ORDNCE 2 | 0.94836 | 0.89167 | -0.056694 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ORDNCE 2 | 0.94836 | 0.89167 | -0.056694 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ORDNCE 2 | 0.94836 | 0.89167 | -0.056694 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ORDNCE 2 | 0.94836 | 0.89167 | -0.056694 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | ORDNCE 2 | 0.94836 | 0.89167 | -0.056694 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | ORDNJCT2 | 0.95261 | 0.90973 | -0.042879 |  | 0.93 | 1.05 | 0.077629 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | ORDNJCT2 | 0.95261 | 0.90973 | -0.042879 |  | 0.93 | 1.05 | 0.06446 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | ORDNJCT2 | 0.95261 | 0.90973 | -0.042879 |  | 0.93 | 1.05 | 0.066434 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | ORDNJCT2 | 0.95261 | 0.90973 | -0.042879 |  | 0.93 | 1.05 | 0.073293 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ORDNJCT2 | 0.95261 | 0.90973 | -0.042879 |  | 0.93 | 1.05 | 0.053415 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-122 | ORDNJCT2 | 0.95261 | 0.90973 | -0.042879 |  | 0.93 | 1.05 | 0.08103 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-177 | ORDNJCT2 | 0.95261 | 0.90973 | -0.042879 |  | 0.93 | 1.05 | 0.08268 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-178 | ORDNJCT2 | 0.95261 | 0.90973 | -0.042879 |  | 0.93 | 1.05 | 0.077122 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | ORDNJCT2 | 0.95261 | 0.90973 | -0.042879 |  | 0.93 | 1.05 | 0.032185 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | ORDNJCT2 | 0.95261 | 0.90973 | -0.042879 |  | 0.93 | 1.05 | 0.073922 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-232 | ORDNJCT2 | 0.95261 | 0.90973 | -0.042879 |  | 0.93 | 1.05 | 0.076776 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | ORDNJCT2 | 0.95261 | 0.90973 | -0.042879 |  | 0.93 | 1.05 | 0.06446 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ORDNJCT2 | 0.95261 | 0.90973 | -0.042879 |  | 0.93 | 1.05 | 0.038841 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | ORDNJCT2 | 0.95261 | 0.90973 | -0.042879 |  | 0.93 | 1.05 | 0.034687 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | ORDNJCT2 | 0.95261 | 0.90973 | -0.042879 |  | 0.93 | 1.05 | 0.034687 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | ORDNJCT2 | 0.95261 | 0.90973 | -0.042879 |  | 0.93 | 1.05 | 0.031574 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | ORDNJCT2 | 0.95261 | 0.90973 | -0.042879 |  | 0.93 | 1.05 | 0.042889 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-376 | ORDNJCT2 | 0.95261 | 0.90973 | -0.042879 |  | 0.93 | 1.05 | 0.079908 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ORDNJCT2 | 0.94965 | 0.91073 | -0.038912 |  | 0.93 | 1.05 | 0.040299 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ORDNJCT2 | 0.94965 | 0.91073 | -0.038912 |  | 0.93 | 1.05 | 0.048812 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ORDNJCT2 | 0.94965 | 0.91073 | -0.038912 |  | 0.93 | 1.05 | 0.076211 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ORDNJCT2 | 0.94965 | 0.91073 | -0.038912 |  | 0.93 | 1.05 | 0.069331 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ORDNJCT2 | 0.94965 | 0.91073 | -0.038912 |  | 0.93 | 1.05 | 0.035943 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ORDNJCT2 | 0.94965 | 0.91073 | -0.038912 |  | 0.93 | 1.05 | 0.034061 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ORDNJCT2 | 0.94965 | 0.91073 | -0.038912 |  | 0.93 | 1.05 | 0.064216 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ORDNJCT2 | 0.94965 | 0.91073 | -0.038912 |  | 0.93 | 1.05 | 0.045005 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ORDNJCT2 | 0.94965 | 0.91073 | -0.038912 |  | 0.93 | 1.05 | 0.13572 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | ORDNJCT2 | 0.94965 | 0.91073 | -0.038912 |  | 0.93 | 1.05 | 0.037472 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | ORDNJCT2 | 0.94965 | 0.91073 | -0.038912 |  | 0.93 | 1.05 | 0.037472 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ORDNJCT2 | 0.94965 | 0.91073 | -0.038912 |  | 0.93 | 1.05 | 0.06894 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ORDNJCT2 | 0.94965 | 0.91073 | -0.038912 |  | 0.93 | 1.05 | 0.034713 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ORDNJCT2 | 0.94965 | 0.91073 | -0.038912 |  | 0.93 | 1.05 | 0.035229 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ORDNJCT2 | 0.94965 | 0.91095 | -0.0387 |  | 0.93 | 1.05 | 0.094783 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ORDNJCT2 | 0.94965 | 0.91095 | -0.0387 |  | 0.93 | 1.05 | 0.03645 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ORDNJCT2 | 0.94965 | 0.91095 | -0.0387 |  | 0.93 | 1.05 | 0.04755 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ORDNJCT2 | 0.94965 | 0.91095 | -0.0387 |  | 0.93 | 1.05 | 0.06097 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ORDNJCT2 | 0.94965 | 0.91095 | -0.0387 |  | 0.93 | 1.05 | 0.061051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | ORDNJCT2 | 0.94965 | 0.91095 | -0.0387 |  | 0.93 | 1.05 | 0.04456 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | ORDNJCT2 | 0.94965 | 0.91095 | -0.0387 |  | 0.93 | 1.05 | 0.048811 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ORDNJCT2 | 0.94965 | 0.91095 | -0.0387 |  | 0.93 | 1.05 | 0.13004 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ORDNJCT2 | 0.94965 | 0.91095 | -0.0387 |  | 0.93 | 1.05 | 0.049018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ORDNJCT2 | 0.94965 | 0.91095 | -0.0387 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ORDNJCT2 | 0.94965 | 0.91095 | -0.0387 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ORDNJCT2 | 0.94965 | 0.91095 | -0.0387 |  | 0.93 | 1.05 | 0.05974 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ORDNJCT2 | 0.94965 | 0.91095 | -0.0387 |  | 0.93 | 1.05 | 0.076949 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ORDNJCT2 | 0.94965 | 0.91095 | -0.0387 |  | 0.93 | 1.05 | 0.042157 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ORDNJCT2 | 0.94965 | 0.91095 | -0.0387 |  | 0.93 | 1.05 | 0.040957 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | ORDNJCT2 | 0.94965 | 0.91095 | -0.0387 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | ORDNJCT2 | 0.94965 | 0.91095 | -0.0387 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ORDNJCT2 | 0.94965 | 0.91095 | -0.0387 |  | 0.93 | 1.05 | 0.054637 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ORDNJCT2 | 0.94965 | 0.91095 | -0.0387 |  | 0.93 | 1.05 | 0.060597 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | ORDNJCT2 | 0.94965 | 0.91095 | -0.0387 |  | 0.93 | 1.05 | 0.044286 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ORDNJCT2 | 0.94965 | 0.91095 | -0.0387 |  | 0.93 | 1.05 | 0.059107 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ORDNJCT2 | 0.94965 | 0.91095 | -0.0387 |  | 0.93 | 1.05 | 0.052698 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ORDNJCT2 | 0.94965 | 0.91095 | -0.0387 |  | 0.93 | 1.05 | 0.067422 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ORDNJCT2 | 0.94965 | 0.91095 | -0.0387 |  | 0.93 | 1.05 | 0.053768 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | ORDNJCT2 | 0.94965 | 0.91095 | -0.0387 |  | 0.93 | 1.05 | 0.03909 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ORDNJCT2 | 0.94853 | 0.90689 | -0.041635 |  | 0.93 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ORDNJCT2 | 0.94853 | 0.90689 | -0.041635 |  | 0.93 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ORDNJCT2 | 0.94853 | 0.90689 | -0.041635 |  | 0.93 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ORDNJCT2 | 0.94853 | 0.90689 | -0.041635 |  | 0.93 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ORDNJCT2 | 0.94853 | 0.90689 | -0.041635 |  | 0.93 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ORDNJCT2 | 0.94853 | 0.90689 | -0.041635 |  | 0.93 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ORDNJCT2 | 0.94853 | 0.90689 | -0.041635 |  | 0.93 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | ORDNJCT2 | 0.94853 | 0.90689 | -0.041635 |  | 0.93 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ORDNJCT2 | 0.94853 | 0.90689 | -0.041635 |  | 0.93 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ORDNJCT2 | 0.94853 | 0.90689 | -0.041635 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ORDNJCT2 | 0.94853 | 0.90689 | -0.041635 |  | 0.93 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ORDNJCT2 | 0.94853 | 0.90689 | -0.041635 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ORDNJCT2 | 0.94853 | 0.90689 | -0.041635 |  | 0.93 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ORDNJCT2 | 0.94853 | 0.90689 | -0.041635 |  | 0.93 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ORDNJCT2 | 0.94853 | 0.90689 | -0.041635 |  | 0.93 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ORDNJCT2 | 0.94853 | 0.90689 | -0.041635 |  | 0.93 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ORDNJCT2 | 0.94853 | 0.90689 | -0.041635 |  | 0.93 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ORDNJCT2 | 0.94853 | 0.90689 | -0.041635 |  | 0.93 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ORDNJCT2 | 0.94853 | 0.90689 | -0.041635 |  | 0.93 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ORDNJCT2 | 0.94853 | 0.90689 | -0.041635 |  | 0.93 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ORDNJCT2 | 0.94853 | 0.90689 | -0.041635 |  | 0.93 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ORDNJCT2 | 0.94853 | 0.90689 | -0.041635 |  | 0.93 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ORDNJCT2 | 0.94886 | 0.8922 | -0.056662 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ORDNJCT2 | 0.94886 | 0.8922 | -0.056662 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ORDNJCT2 | 0.94886 | 0.8922 | -0.056662 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ORDNJCT2 | 0.94886 | 0.8922 | -0.056662 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ORDNJCT2 | 0.94886 | 0.8922 | -0.056662 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ORDNJCT2 | 0.94886 | 0.8922 | -0.056662 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ORDNJCT2 | 0.94886 | 0.8922 | -0.056662 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | ORDNJCT2 | 0.94886 | 0.8922 | -0.056662 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | ORDNJCT2 | 0.94886 | 0.8922 | -0.056662 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ORDNJCT2 | 0.94886 | 0.8922 | -0.056662 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ORDNJCT2 | 0.94886 | 0.8922 | -0.056662 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ORDNJCT2 | 0.94886 | 0.8922 | -0.056662 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ORDNJCT2 | 0.94886 | 0.8922 | -0.056662 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ORDNJCT2 | 0.94886 | 0.8922 | -0.056662 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ORDNJCT2 | 0.94886 | 0.8922 | -0.056662 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ORDNJCT2 | 0.94886 | 0.8922 | -0.056662 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ORDNJCT2 | 0.94886 | 0.8922 | -0.056662 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ORDNJCT2 | 0.94886 | 0.8922 | -0.056662 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | ORDNJCT2 | 0.94886 | 0.8922 | -0.056662 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | ORDNJCT2 | 0.94886 | 0.8922 | -0.056662 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ORDNJCT2 | 0.94886 | 0.8922 | -0.056662 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ORDNJCT2 | 0.94886 | 0.8922 | -0.056662 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | ORDNJCT2 | 0.94886 | 0.8922 | -0.056662 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ORDNJCT2 | 0.94886 | 0.8922 | -0.056662 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ORDNJCT2 | 0.94886 | 0.8922 | -0.056662 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ORDNJCT2 | 0.94886 | 0.8922 | -0.056662 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ORDNJCT2 | 0.94886 | 0.8922 | -0.056662 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | ORDNJCT2 | 0.94886 | 0.8922 | -0.056662 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | OSAGE 3 | 0.95557 | 0.88092 | -0.074653 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | OSAGE 3 | 0.95557 | 0.88092 | -0.074653 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | OSAGE 3 | 0.95557 | 0.88092 | -0.074653 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | OSAGE 3 | 0.95557 | 0.88092 | -0.074653 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | OSAGE 3 | 0.95557 | 0.88092 | -0.074653 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | OSAGE 3 | 0.95557 | 0.88092 | -0.074653 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | OSAGE 3 | 0.95557 | 0.88092 | -0.074653 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | OSAGE 3 | 0.95557 | 0.88092 | -0.074653 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | OSAGE 3 | 0.95557 | 0.88092 | -0.074653 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | OSAGE 3 | 0.95557 | 0.88092 | -0.074653 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | OSAGE 3 | 0.95557 | 0.88092 | -0.074653 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | OSAGE 3 | 0.95557 | 0.88092 | -0.074653 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | OSAGE 3 | 0.95557 | 0.88092 | -0.074653 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | OSAGE 3 | 0.95557 | 0.88092 | -0.074653 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | OSAGE 3 | 0.95557 | 0.88092 | -0.074653 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | OSAGE 3 | 0.95557 | 0.88092 | -0.074653 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | OSAGE 3 | 0.95557 | 0.88092 | -0.074653 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | OSAGE 3 | 0.95557 | 0.88092 | -0.074653 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | OSAGE 3 | 0.95557 | 0.88092 | -0.074653 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | OSAGE 3 | 0.95557 | 0.88092 | -0.074653 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | OSAGE 3 | 0.95557 | 0.88092 | -0.074653 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | OSAGE 3 | 0.95557 | 0.88092 | -0.074653 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | OSAGE 3 | 0.95557 | 0.88092 | -0.074653 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | OSAGE 3 | 0.95557 | 0.88092 | -0.074653 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | OSAGE 3 | 0.95557 | 0.88092 | -0.074653 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | OSAGE 3 | 0.95557 | 0.88092 | -0.074653 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | OSAGE 3 | 0.95557 | 0.88092 | -0.074653 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | OSAGE 3 | 0.95557 | 0.88092 | -0.074653 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | OSAGE J3 | 0.95656 | 0.88199 | -0.074568 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | OSAGE J3 | 0.95656 | 0.88199 | -0.074568 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | OSAGE J3 | 0.95656 | 0.88199 | -0.074568 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | OSAGE J3 | 0.95656 | 0.88199 | -0.074568 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | OSAGE J3 | 0.95656 | 0.88199 | -0.074568 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | OSAGE J3 | 0.95656 | 0.88199 | -0.074568 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | OSAGE J3 | 0.95656 | 0.88199 | -0.074568 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | OSAGE J3 | 0.95656 | 0.88199 | -0.074568 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | OSAGE J3 | 0.95656 | 0.88199 | -0.074568 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | OSAGE J3 | 0.95656 | 0.88199 | -0.074568 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | OSAGE J3 | 0.95656 | 0.88199 | -0.074568 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | OSAGE J3 | 0.95656 | 0.88199 | -0.074568 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | OSAGE J3 | 0.95656 | 0.88199 | -0.074568 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | OSAGE J3 | 0.95656 | 0.88199 | -0.074568 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | OSAGE J3 | 0.95656 | 0.88199 | -0.074568 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | OSAGE J3 | 0.95656 | 0.88199 | -0.074568 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | OSAGE J3 | 0.95656 | 0.88199 | -0.074568 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | OSAGE J3 | 0.95656 | 0.88199 | -0.074568 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | OSAGE J3 | 0.95656 | 0.88199 | -0.074568 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | OSAGE J3 | 0.95656 | 0.88199 | -0.074568 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | OSAGE J3 | 0.95656 | 0.88199 | -0.074568 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | OSAGE J3 | 0.95656 | 0.88199 | -0.074568 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | OSAGE J3 | 0.95656 | 0.88199 | -0.074568 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | OSAGE J3 | 0.95656 | 0.88199 | -0.074568 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | OSAGE J3 | 0.95656 | 0.88199 | -0.074568 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | OSAGE J3 | 0.95656 | 0.88199 | -0.074568 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | OSAGE J3 | 0.95656 | 0.88199 | -0.074568 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | OSAGE J3 | 0.95656 | 0.88199 | -0.074568 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | OSAWTM_CAP5 | 1.0146 | 0.92319 | -0.091413 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | OSAWTM_CAP5 | 1.0146 | 0.92319 | -0.091413 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | OSAWTM_CAP5 | 1.0146 | 0.92319 | -0.091413 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | OSAWTM_CAP5 | 1.0146 | 0.92319 | -0.091413 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | OSAWTM_CAP5 | 1.0146 | 0.92319 | -0.091413 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | OSAWTM_CAP5 | 1.0146 | 0.92319 | -0.091413 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | OSAWTM_CAP5 | 1.0146 | 0.92319 | -0.091413 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | OSAWTM_CAP5 | 1.0146 | 0.92319 | -0.091413 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | OSAWTM_CAP5 | 1.0146 | 0.92319 | -0.091413 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | OSAWTM_CAP5 | 1.0146 | 0.92319 | -0.091413 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | OSAWTM_CAP5 | 1.0146 | 0.92319 | -0.091413 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | OSAWTM_CAP5 | 1.0146 | 0.92319 | -0.091413 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | OSAWTM_CAP5 | 1.0146 | 0.92319 | -0.091413 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | OSAWTM_CAP5 | 1.0146 | 0.92319 | -0.091413 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | OSAWTM_CAP5 | 1.0146 | 0.92319 | -0.091413 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | OSAWTM_CAP5 | 1.0146 | 0.92319 | -0.091413 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | OSAWTM_CAP5 | 1.0146 | 0.92319 | -0.091413 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | OSAWTM_CAP5 | 1.0146 | 0.92319 | -0.091413 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | OSAWTM_CAP5 | 1.0146 | 0.92319 | -0.091413 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | OSAWTM_CAP5 | 1.0146 | 0.92319 | -0.091413 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | OSAWTM_CAP5 | 1.0146 | 0.92319 | -0.091413 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | OSAWTM_CAP5 | 1.0146 | 0.92319 | -0.091413 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | OSAWTM_CAP5 | 1.0146 | 0.92319 | -0.091413 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | OSAWTM_CAP5 | 1.0146 | 0.92319 | -0.091413 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | OSAWTM_CAP5 | 1.0146 | 0.92319 | -0.091413 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | OSAWTM_CAP5 | 1.0146 | 0.92319 | -0.091413 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | OSAWTM_CAP5 | 1.0146 | 0.92319 | -0.091413 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | OSAWTM_CAP5 | 1.0146 | 0.92319 | -0.091413 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | OTTRCRK3 | 0.9704 | 0.91535 | -0.055051 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | OTTRCRK3 | 0.9704 | 0.91535 | -0.055051 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | OTTRCRK3 | 0.9704 | 0.91535 | -0.055051 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | OTTRCRK3 | 0.9704 | 0.91535 | -0.055051 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | OTTRCRK3 | 0.9704 | 0.91535 | -0.055051 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | OTTRCRK3 | 0.9704 | 0.91535 | -0.055051 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | OTTRCRK3 | 0.9704 | 0.91535 | -0.055051 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | OTTRCRK3 | 0.9704 | 0.91535 | -0.055051 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | OTTRCRK3 | 0.9704 | 0.91535 | -0.055051 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | OTTRCRK3 | 0.9704 | 0.91535 | -0.055051 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | OTTRCRK3 | 0.9704 | 0.91535 | -0.055051 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | OTTRCRK3 | 0.9704 | 0.91535 | -0.055051 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | OTTRCRK3 | 0.9704 | 0.91535 | -0.055051 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | OTTRCRK3 | 0.9704 | 0.91535 | -0.055051 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | OTTRCRK3 | 0.9704 | 0.91535 | -0.055051 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | OTTRCRK3 | 0.9704 | 0.91535 | -0.055051 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | OTTRCRK3 | 0.9704 | 0.91535 | -0.055051 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | OTTRCRK3 | 0.9704 | 0.91535 | -0.055051 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | OTTRCRK3 | 0.9704 | 0.91535 | -0.055051 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | OTTRCRK3 | 0.9704 | 0.91535 | -0.055051 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | OTTRCRK3 | 0.9704 | 0.91535 | -0.055051 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | OTTRCRK3 | 0.9704 | 0.91535 | -0.055051 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | OTTRCRK3 | 0.9704 | 0.91535 | -0.055051 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | OTTRCRK3 | 0.9704 | 0.91535 | -0.055051 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | OTTRCRK3 | 0.9704 | 0.91535 | -0.055051 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | OTTRCRK3 | 0.9704 | 0.91535 | -0.055051 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | OTTRCRK3 | 0.9704 | 0.91535 | -0.055051 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | OTTRCRK3 | 0.9704 | 0.91535 | -0.055051 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | OTTRCRK4 | 0.96783 | 0.91783 | -0.049995 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | OTTRCRK4 | 0.96783 | 0.91783 | -0.049995 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | OTTRCRK4 | 0.96783 | 0.91783 | -0.049995 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | OTTRCRK4 | 0.96783 | 0.91783 | -0.049995 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | OTTRCRK4 | 0.96783 | 0.91783 | -0.049995 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | OTTRCRK4 | 0.96783 | 0.91783 | -0.049995 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | OTTRCRK4 | 0.96783 | 0.91783 | -0.049995 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | OTTRCRK4 | 0.96783 | 0.91783 | -0.049995 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | OTTRCRK4 | 0.96783 | 0.91783 | -0.049995 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | OTTRCRK4 | 0.96783 | 0.91783 | -0.049995 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | OTTRCRK4 | 0.96783 | 0.91783 | -0.049995 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | OTTRCRK4 | 0.96783 | 0.91783 | -0.049995 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | OTTRCRK4 | 0.96783 | 0.91783 | -0.049995 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | OTTRCRK4 | 0.96783 | 0.91783 | -0.049995 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | OTTRCRK4 | 0.96783 | 0.91783 | -0.049995 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | OTTRCRK4 | 0.96783 | 0.91783 | -0.049995 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | OTTRCRK4 | 0.96783 | 0.91783 | -0.049995 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | OTTRCRK4 | 0.96783 | 0.91783 | -0.049995 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | OTTRCRK4 | 0.96783 | 0.91783 | -0.049995 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | OTTRCRK4 | 0.96783 | 0.91783 | -0.049995 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | OTTRCRK4 | 0.96783 | 0.91783 | -0.049995 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | OTTRCRK4 | 0.96783 | 0.91783 | -0.049995 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | OTTRCRK4 | 0.96783 | 0.91783 | -0.049995 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | OTTRCRK4 | 0.96783 | 0.91783 | -0.049995 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | OTTRCRK4 | 0.96783 | 0.91783 | -0.049995 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | OTTRCRK4 | 0.96783 | 0.91783 | -0.049995 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | OTTRCRK4 | 0.96783 | 0.91783 | -0.049995 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | OTTRCRK4 | 0.96783 | 0.91783 | -0.049995 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | OVERLPK5 | 0.96448 | 0.92619 | -0.038287 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | OVERLPK5 | 0.96448 | 0.92619 | -0.038287 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | OVERLPK5 | 0.96448 | 0.92619 | -0.038287 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | OVERLPK5 | 0.96448 | 0.92619 | -0.038287 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | OVERLPK5 | 0.96448 | 0.92619 | -0.038287 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | OVERLPK5 | 0.96448 | 0.92619 | -0.038287 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | OVERLPK5 | 0.96448 | 0.92619 | -0.038287 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | OVERLPK5 | 0.96448 | 0.92619 | -0.038287 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | OVERLPK5 | 0.96448 | 0.92619 | -0.038287 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | OVERLPK5 | 0.96448 | 0.92619 | -0.038287 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | OVERLPK5 | 0.96448 | 0.92619 | -0.038287 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | OVERLPK5 | 0.96448 | 0.92619 | -0.038287 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | OVERLPK5 | 0.96448 | 0.92619 | -0.038287 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | OVERLPK5 | 0.96448 | 0.92619 | -0.038287 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | OVERLPK5 | 0.96448 | 0.92619 | -0.038287 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | OVERLPK5 | 0.96448 | 0.92619 | -0.038287 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | OVERLPK5 | 0.96448 | 0.92619 | -0.038287 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | OVERLPK5 | 0.96448 | 0.92619 | -0.038287 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | OVERLPK5 | 0.96448 | 0.92619 | -0.038287 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | OVERLPK5 | 0.96448 | 0.92619 | -0.038287 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | OVERLPK5 | 0.97264 | 0.92989 | -0.042758 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | OVERLPK5 | 0.97264 | 0.92989 | -0.042758 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | OVERLPK5 | 0.97264 | 0.92989 | -0.042758 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | OVERLPK5 | 0.97264 | 0.92989 | -0.042758 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | OVERLPK5 | 0.97264 | 0.92989 | -0.042758 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | OVERLPK5 | 0.97264 | 0.92989 | -0.042758 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | OVERLPK5 | 0.97264 | 0.92989 | -0.042758 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | OVERLPK5 | 0.97264 | 0.92989 | -0.042758 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | OVERLPK5 | 0.97264 | 0.92989 | -0.042758 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | OVERLPK5 | 0.97264 | 0.92989 | -0.042758 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | OVERLPK5 | 0.97264 | 0.92989 | -0.042758 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | OVERLPK5 | 0.97264 | 0.92989 | -0.042758 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | OVERLPK5 | 0.97264 | 0.92989 | -0.042758 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | OVERLPK5 | 0.97264 | 0.92989 | -0.042758 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | OVERLPK5 | 0.97264 | 0.92989 | -0.042758 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | OVERLPK5 | 0.97264 | 0.92989 | -0.042758 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | OVERLPK5 | 0.97264 | 0.92989 | -0.042758 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | OVERLPK5 | 0.97264 | 0.92989 | -0.042758 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | OVERLPK5 | 0.97264 | 0.92989 | -0.042758 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | OVERLPK5 | 0.97264 | 0.92989 | -0.042758 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | OVERLPK5 | 0.97523 | 0.90858 | -0.066646 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | OVERLPK5 | 0.97523 | 0.90858 | -0.066646 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | OVERLPK5 | 0.97523 | 0.90858 | -0.066646 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | OVERLPK5 | 0.97523 | 0.90858 | -0.066646 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | OVERLPK5 | 0.97523 | 0.90858 | -0.066646 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | OVERLPK5 | 0.97523 | 0.90858 | -0.066646 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | OVERLPK5 | 0.97523 | 0.90858 | -0.066646 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | OVERLPK5 | 0.97523 | 0.90858 | -0.066646 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | OVERLPK5 | 0.97523 | 0.90858 | -0.066646 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | OVERLPK5 | 0.97523 | 0.90858 | -0.066646 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | OVERLPK5 | 0.97523 | 0.90858 | -0.066646 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | OVERLPK5 | 0.97523 | 0.90858 | -0.066646 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | OVERLPK5 | 0.97523 | 0.90858 | -0.066646 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | OVERLPK5 | 0.97523 | 0.90858 | -0.066646 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | OVERLPK5 | 0.97523 | 0.90858 | -0.066646 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | OVERLPK5 | 0.97523 | 0.90858 | -0.066646 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | OVERLPK5 | 0.97523 | 0.90858 | -0.066646 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | OVERLPK5 | 0.97523 | 0.90858 | -0.066646 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | OVERLPK5 | 0.97523 | 0.90858 | -0.066646 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | OVERLPK5 | 0.97523 | 0.90858 | -0.066646 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | OVERLPK5 | 0.97523 | 0.90858 | -0.066646 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | OVERLPK5 | 0.97523 | 0.90858 | -0.066646 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | OVERLPK5 | 0.97523 | 0.90858 | -0.066646 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | OVERLPK5 | 0.97523 | 0.90858 | -0.066646 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | OVERLPK5 | 0.97523 | 0.90858 | -0.066646 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | OVERLPK5 | 0.97523 | 0.90858 | -0.066646 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | OVERLPK5 | 0.97523 | 0.90858 | -0.066646 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | OVERLPK5 | 0.97523 | 0.90858 | -0.066646 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | OXFORD 5 | 0.9694 | 0.92966 | -0.039739 |  | 0.93 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | OXFORD 5 | 0.9694 | 0.92966 | -0.039739 |  | 0.93 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | OXFORD 5 | 0.9694 | 0.92966 | -0.039739 |  | 0.93 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | OXFORD 5 | 0.9694 | 0.92966 | -0.039739 |  | 0.93 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | OXFORD 5 | 0.9694 | 0.92966 | -0.039739 |  | 0.93 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | OXFORD 5 | 0.9694 | 0.92966 | -0.039739 |  | 0.93 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | OXFORD 5 | 0.9694 | 0.92966 | -0.039739 |  | 0.93 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | OXFORD 5 | 0.9694 | 0.92966 | -0.039739 |  | 0.93 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | OXFORD 5 | 0.9694 | 0.92966 | -0.039739 |  | 0.93 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | OXFORD 5 | 0.9694 | 0.92966 | -0.039739 |  | 0.93 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | OXFORD 5 | 0.9694 | 0.92966 | -0.039739 |  | 0.93 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | OXFORD 5 | 0.9694 | 0.92966 | -0.039739 |  | 0.93 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | OXFORD 5 | 0.9694 | 0.92966 | -0.039739 |  | 0.93 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | OXFORD 5 | 0.9694 | 0.92966 | -0.039739 |  | 0.93 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | OXFORD 5 | 0.9694 | 0.92966 | -0.039739 |  | 0.93 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | OXFORD 5 | 0.9694 | 0.92966 | -0.039739 |  | 0.93 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | OXFORD 5 | 0.9694 | 0.92966 | -0.039739 |  | 0.93 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | OXFORD 5 | 0.9694 | 0.92966 | -0.039739 |  | 0.93 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | OXFORD 5 | 0.9694 | 0.92966 | -0.039739 |  | 0.93 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | OXFORD 5 | 0.9694 | 0.92966 | -0.039739 |  | 0.93 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | OXFORD 5 | 0.96166 | 0.918 | -0.043663 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | OXFORD 5 | 0.96166 | 0.918 | -0.043663 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | OXFORD 5 | 0.96166 | 0.918 | -0.043663 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | OXFORD 5 | 0.96166 | 0.918 | -0.043663 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | OXFORD 5 | 0.96166 | 0.918 | -0.043663 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | OXFORD 5 | 0.96166 | 0.918 | -0.043663 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | OXFORD 5 | 0.96166 | 0.918 | -0.043663 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | OXFORD 5 | 0.96166 | 0.918 | -0.043663 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | OXFORD 5 | 0.96166 | 0.918 | -0.043663 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | OXFORD 5 | 0.96166 | 0.918 | -0.043663 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | OXFORD 5 | 0.96166 | 0.918 | -0.043663 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | OXFORD 5 | 0.96166 | 0.918 | -0.043663 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | OXFORD 5 | 0.96166 | 0.918 | -0.043663 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | OXFORD 5 | 0.96166 | 0.918 | -0.043663 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | OXFORD 5 | 0.96166 | 0.918 | -0.043663 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | OXFORD 5 | 0.96166 | 0.918 | -0.043663 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | OXFORD 5 | 0.96166 | 0.918 | -0.043663 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | OXFORD 5 | 0.96166 | 0.918 | -0.043663 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | OXFORD 5 | 0.96166 | 0.918 | -0.043663 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | OXFORD 5 | 0.96166 | 0.918 | -0.043663 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | OXFORD 5 | 0.97291 | 0.92466 | -0.048247 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | OXFORD 5 | 0.97291 | 0.92466 | -0.048247 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | OXFORD 5 | 0.97291 | 0.92466 | -0.048247 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | OXFORD 5 | 0.97291 | 0.92466 | -0.048247 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | OXFORD 5 | 0.97291 | 0.92466 | -0.048247 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | OXFORD 5 | 0.97291 | 0.92466 | -0.048247 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | OXFORD 5 | 0.97291 | 0.92466 | -0.048247 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | OXFORD 5 | 0.97291 | 0.92466 | -0.048247 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | OXFORD 5 | 0.97291 | 0.92466 | -0.048247 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | OXFORD 5 | 0.97291 | 0.92466 | -0.048247 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | OXFORD 5 | 0.97291 | 0.92466 | -0.048247 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | OXFORD 5 | 0.97291 | 0.92466 | -0.048247 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | OXFORD 5 | 0.97291 | 0.92466 | -0.048247 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | OXFORD 5 | 0.97291 | 0.92466 | -0.048247 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | OXFORD 5 | 0.97291 | 0.92466 | -0.048247 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | OXFORD 5 | 0.97291 | 0.92466 | -0.048247 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | OXFORD 5 | 0.97291 | 0.92466 | -0.048247 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | OXFORD 5 | 0.97291 | 0.92466 | -0.048247 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | OXFORD 5 | 0.97291 | 0.92466 | -0.048247 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | OXFORD 5 | 0.97291 | 0.92466 | -0.048247 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | OXFORD 5 | 0.9743 | 0.89698 | -0.077323 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | OXFORD 5 | 0.9743 | 0.89698 | -0.077323 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | OXFORD 5 | 0.9743 | 0.89698 | -0.077323 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | OXFORD 5 | 0.9743 | 0.89698 | -0.077323 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | OXFORD 5 | 0.9743 | 0.89698 | -0.077323 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | OXFORD 5 | 0.9743 | 0.89698 | -0.077323 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | OXFORD 5 | 0.9743 | 0.89698 | -0.077323 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | OXFORD 5 | 0.9743 | 0.89698 | -0.077323 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | OXFORD 5 | 0.9743 | 0.89698 | -0.077323 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | OXFORD 5 | 0.9743 | 0.89698 | -0.077323 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | OXFORD 5 | 0.9743 | 0.89698 | -0.077323 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | OXFORD 5 | 0.9743 | 0.89698 | -0.077323 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | OXFORD 5 | 0.9743 | 0.89698 | -0.077323 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | OXFORD 5 | 0.9743 | 0.89698 | -0.077323 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | OXFORD 5 | 0.9743 | 0.89698 | -0.077323 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | OXFORD 5 | 0.9743 | 0.89698 | -0.077323 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | OXFORD 5 | 0.9743 | 0.89698 | -0.077323 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | OXFORD 5 | 0.9743 | 0.89698 | -0.077323 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | OXFORD 5 | 0.9743 | 0.89698 | -0.077323 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | OXFORD 5 | 0.9743 | 0.89698 | -0.077323 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | OXFORD 5 | 0.9743 | 0.89698 | -0.077323 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | OXFORD 5 | 0.9743 | 0.89698 | -0.077323 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | OXFORD 5 | 0.9743 | 0.89698 | -0.077323 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | OXFORD 5 | 0.9743 | 0.89698 | -0.077323 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | OXFORD 5 | 0.9743 | 0.89698 | -0.077323 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | OXFORD 5 | 0.9743 | 0.89698 | -0.077323 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | OXFORD 5 | 0.9743 | 0.89698 | -0.077323 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | OXFORD 5 | 0.9743 | 0.89698 | -0.077323 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | OXFORD 5 | 0.96845 | 0.92783 | -0.040628 |  | 0.93 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | OXFORD 5 | 0.96845 | 0.92783 | -0.040628 |  | 0.93 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | OXFORD 5 | 0.96845 | 0.92783 | -0.040628 |  | 0.93 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | OXFORD 5 | 0.96845 | 0.92783 | -0.040628 |  | 0.93 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | OXFORD 5 | 0.96845 | 0.92783 | -0.040628 |  | 0.93 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | OXFORD 5 | 0.96845 | 0.92783 | -0.040628 |  | 0.93 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | OXFORD 5 | 0.96845 | 0.92783 | -0.040628 |  | 0.93 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | OXFORD 5 | 0.96845 | 0.92783 | -0.040628 |  | 0.93 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | OXFORD 5 | 0.96845 | 0.92783 | -0.040628 |  | 0.93 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | OXFORD 5 | 0.96845 | 0.92783 | -0.040628 |  | 0.93 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | OXFORD 5 | 0.96845 | 0.92783 | -0.040628 |  | 0.93 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | OXFORD 5 | 0.96845 | 0.92783 | -0.040628 |  | 0.93 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | OXFORD 5 | 0.96845 | 0.92783 | -0.040628 |  | 0.93 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | OXFORD 5 | 0.96845 | 0.92783 | -0.040628 |  | 0.93 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | OXFORD 5 | 0.96845 | 0.92783 | -0.040628 |  | 0.93 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | OXFORD 5 | 0.96845 | 0.92783 | -0.040628 |  | 0.93 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | OXFORD 5 | 0.96845 | 0.92783 | -0.040628 |  | 0.93 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | OXFORD 5 | 0.96845 | 0.92783 | -0.040628 |  | 0.93 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | OXFORD 5 | 0.96845 | 0.92783 | -0.040628 |  | 0.93 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | OXFORD 5 | 0.96845 | 0.92783 | -0.040628 |  | 0.93 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | PALMER3 | 0.96416 | 0.89856 | -0.065601 |  | 0.9 | 1.05 | 0.064516 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 3.3 MVAR switched shunt at CHASE 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | PALMER3 | 0.93972 | 0.88658 | -0.05314 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | PALMER3 | 0.93972 | 0.88658 | -0.05314 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | PAOLA 5 | 1.013 | 0.92174 | -0.091304 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | PAOLA 5 | 1.013 | 0.92174 | -0.091304 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | PAOLA 5 | 1.013 | 0.92174 | -0.091304 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | PAOLA 5 | 1.013 | 0.92174 | -0.091304 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | PAOLA 5 | 1.013 | 0.92174 | -0.091304 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | PAOLA 5 | 1.013 | 0.92174 | -0.091304 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | PAOLA 5 | 1.013 | 0.92174 | -0.091304 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | PAOLA 5 | 1.013 | 0.92174 | -0.091304 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | PAOLA 5 | 1.013 | 0.92174 | -0.091304 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | PAOLA 5 | 1.013 | 0.92174 | -0.091304 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | PAOLA 5 | 1.013 | 0.92174 | -0.091304 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | PAOLA 5 | 1.013 | 0.92174 | -0.091304 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | PAOLA 5 | 1.013 | 0.92174 | -0.091304 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | PAOLA 5 | 1.013 | 0.92174 | -0.091304 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | PAOLA 5 | 1.013 | 0.92174 | -0.091304 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | PAOLA 5 | 1.013 | 0.92174 | -0.091304 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | PAOLA 5 | 1.013 | 0.92174 | -0.091304 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | PAOLA 5 | 1.013 | 0.92174 | -0.091304 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | PAOLA 5 | 1.013 | 0.92174 | -0.091304 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | PAOLA 5 | 1.013 | 0.92174 | -0.091304 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | PAOLA 5 | 1.013 | 0.92174 | -0.091304 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | PAOLA 5 | 1.013 | 0.92174 | -0.091304 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | PAOLA 5 | 1.013 | 0.92174 | -0.091304 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | PAOLA 5 | 1.013 | 0.92174 | -0.091304 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | PAOLA 5 | 1.013 | 0.92174 | -0.091304 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | PAOLA 5 | 1.013 | 0.92174 | -0.091304 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | PAOLA 5 | 1.013 | 0.92174 | -0.091304 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | PAOLA 5 | 1.013 | 0.92174 | -0.091304 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | PECULR 5 | 0.99817 | 0.91957 | -0.078603 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | PECULR 5 | 0.99817 | 0.91957 | -0.078603 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | PECULR 5 | 0.99817 | 0.91957 | -0.078603 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | PECULR 5 | 0.99817 | 0.91957 | -0.078603 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | PECULR 5 | 0.99817 | 0.91957 | -0.078603 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | PECULR 5 | 0.99817 | 0.91957 | -0.078603 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | PECULR 5 | 0.99817 | 0.91957 | -0.078603 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | PECULR 5 | 0.99817 | 0.91957 | -0.078603 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | PECULR 5 | 0.99817 | 0.91957 | -0.078603 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | PECULR 5 | 0.99817 | 0.91957 | -0.078603 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | PECULR 5 | 0.99817 | 0.91957 | -0.078603 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | PECULR 5 | 0.99817 | 0.91957 | -0.078603 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | PECULR 5 | 0.99817 | 0.91957 | -0.078603 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | PECULR 5 | 0.99817 | 0.91957 | -0.078603 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | PECULR 5 | 0.99817 | 0.91957 | -0.078603 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | PECULR 5 | 0.99817 | 0.91957 | -0.078603 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | PECULR 5 | 0.99817 | 0.91957 | -0.078603 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | PECULR 5 | 0.99817 | 0.91957 | -0.078603 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | PECULR 5 | 0.99817 | 0.91957 | -0.078603 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | PECULR 5 | 0.99817 | 0.91957 | -0.078603 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | PECULR 5 | 0.99817 | 0.91957 | -0.078603 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | PECULR 5 | 0.99817 | 0.91957 | -0.078603 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | PECULR 5 | 0.99817 | 0.91957 | -0.078603 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | PECULR 5 | 0.99817 | 0.91957 | -0.078603 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | PECULR 5 | 0.99817 | 0.91957 | -0.078603 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | PECULR 5 | 0.99817 | 0.91957 | -0.078603 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | PECULR 5 | 0.99817 | 0.91957 | -0.078603 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | PECULR 5 | 0.99817 | 0.91957 | -0.078603 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | PECULR 7 | 0.96662 | 0.92827 | -0.038351 |  | 0.95 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | PECULR 7 | 0.96662 | 0.92827 | -0.038351 |  | 0.95 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | PECULR 7 | 0.96662 | 0.92827 | -0.038351 |  | 0.95 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | PECULR 7 | 0.96662 | 0.92827 | -0.038351 |  | 0.95 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | PECULR 7 | 0.96662 | 0.92827 | -0.038351 |  | 0.95 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | PECULR 7 | 0.96662 | 0.92827 | -0.038351 |  | 0.95 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | PECULR 7 | 0.96662 | 0.92827 | -0.038351 |  | 0.95 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | PECULR 7 | 0.96662 | 0.92827 | -0.038351 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | PECULR 7 | 0.96662 | 0.92827 | -0.038351 |  | 0.95 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | PECULR 7 | 0.96662 | 0.92827 | -0.038351 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | PECULR 7 | 0.96662 | 0.92827 | -0.038351 |  | 0.95 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | PECULR 7 | 0.96662 | 0.92827 | -0.038351 |  | 0.95 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | PECULR 7 | 0.96662 | 0.92827 | -0.038351 |  | 0.95 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | PECULR 7 | 0.96662 | 0.92827 | -0.038351 |  | 0.95 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | PECULR 7 | 0.96662 | 0.92827 | -0.038351 |  | 0.95 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | PECULR 7 | 0.96662 | 0.92827 | -0.038351 |  | 0.95 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | PECULR 7 | 0.96662 | 0.92827 | -0.038351 |  | 0.95 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | PECULR 7 | 0.96662 | 0.92827 | -0.038351 |  | 0.95 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | PECULR 7 | 0.96662 | 0.92827 | -0.038351 |  | 0.95 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | PECULR 7 | 0.96662 | 0.92827 | -0.038351 |  | 0.95 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | PECULR 7 | 0.96368 | 0.9254 | -0.038276 |  | 0.95 | 1.05 | 0.042938 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 0.13 MVAR switched shunt at PECULR 7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | PECULR 7 | 0.96368 | 0.9254 | -0.038276 |  | 0.95 | 1.05 | 0.032864 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 0.13 MVAR switched shunt at PECULR 7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | PECULR 7 | 0.96368 | 0.9254 | -0.038276 |  | 0.95 | 1.05 | 0.03396 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 0.13 MVAR switched shunt at PECULR 7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | PECULR 7 | 0.96368 | 0.9254 | -0.038276 |  | 0.95 | 1.05 | 0.055483 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 0.13 MVAR switched shunt at PECULR 7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | PECULR 7 | 0.96368 | 0.9254 | -0.038276 |  | 0.95 | 1.05 | 0.034689 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 0.13 MVAR switched shunt at PECULR 7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | PECULR 7 | 0.96368 | 0.9254 | -0.038276 |  | 0.95 | 1.05 | 0.033481 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 0.13 MVAR switched shunt at PECULR 7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | PECULR 7 | 0.97015 | 0.92362 | -0.046539 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | PECULR 7 | 0.97015 | 0.92362 | -0.046539 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | PECULR 7 | 0.97015 | 0.92362 | -0.046539 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | PECULR 7 | 0.97015 | 0.92362 | -0.046539 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | PECULR 7 | 0.97015 | 0.92362 | -0.046539 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | PECULR 7 | 0.97015 | 0.92362 | -0.046539 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | PECULR 7 | 0.97015 | 0.92362 | -0.046539 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | PECULR 7 | 0.97015 | 0.92362 | -0.046539 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | PECULR 7 | 0.97015 | 0.92362 | -0.046539 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | PECULR 7 | 0.97015 | 0.92362 | -0.046539 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | PECULR 7 | 0.97015 | 0.92362 | -0.046539 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | PECULR 7 | 0.97015 | 0.92362 | -0.046539 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | PECULR 7 | 0.97015 | 0.92362 | -0.046539 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | PECULR 7 | 0.97015 | 0.92362 | -0.046539 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | PECULR 7 | 0.97015 | 0.92362 | -0.046539 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | PECULR 7 | 0.97015 | 0.92362 | -0.046539 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | PECULR 7 | 0.97015 | 0.92362 | -0.046539 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | PECULR 7 | 0.97015 | 0.92362 | -0.046539 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | PECULR 7 | 0.97015 | 0.92362 | -0.046539 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | PECULR 7 | 0.97015 | 0.92362 | -0.046539 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | PECULR 7 | 0.96935 | 0.88757 | -0.081783 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | PECULR 7 | 0.96935 | 0.88757 | -0.081783 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | PECULR 7 | 0.96935 | 0.88757 | -0.081783 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | PECULR 7 | 0.96935 | 0.88757 | -0.081783 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | PECULR 7 | 0.96935 | 0.88757 | -0.081783 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | PECULR 7 | 0.96935 | 0.88757 | -0.081783 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | PECULR 7 | 0.96935 | 0.88757 | -0.081783 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | PECULR 7 | 0.96935 | 0.88757 | -0.081783 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | PECULR 7 | 0.96935 | 0.88757 | -0.081783 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | PECULR 7 | 0.96935 | 0.88757 | -0.081783 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | PECULR 7 | 0.96935 | 0.88757 | -0.081783 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | PECULR 7 | 0.96935 | 0.88757 | -0.081783 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | PECULR 7 | 0.96935 | 0.88757 | -0.081783 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | PECULR 7 | 0.96935 | 0.88757 | -0.081783 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | PECULR 7 | 0.96935 | 0.88757 | -0.081783 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | PECULR 7 | 0.96935 | 0.88757 | -0.081783 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | PECULR 7 | 0.96935 | 0.88757 | -0.081783 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | PECULR 7 | 0.96935 | 0.88757 | -0.081783 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | PECULR 7 | 0.96935 | 0.88757 | -0.081783 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | PECULR 7 | 0.96935 | 0.88757 | -0.081783 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | PECULR 7 | 0.96935 | 0.88757 | -0.081783 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | PECULR 7 | 0.96935 | 0.88757 | -0.081783 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | PECULR 7 | 0.96935 | 0.88757 | -0.081783 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | PECULR 7 | 0.96935 | 0.88757 | -0.081783 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | PECULR 7 | 0.96935 | 0.88757 | -0.081783 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | PECULR 7 | 0.96935 | 0.88757 | -0.081783 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | PECULR 7 | 0.96935 | 0.88757 | -0.081783 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | PECULR 7 | 0.96935 | 0.88757 | -0.081783 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | PECULR 7 | 0.96521 | 0.9261 | -0.039113 |  | 0.95 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | PECULR 7 | 0.96521 | 0.9261 | -0.039113 |  | 0.95 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | PECULR 7 | 0.96521 | 0.9261 | -0.039113 |  | 0.95 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | PECULR 7 | 0.96521 | 0.9261 | -0.039113 |  | 0.95 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | PECULR 7 | 0.96521 | 0.9261 | -0.039113 |  | 0.95 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | PECULR 7 | 0.96521 | 0.9261 | -0.039113 |  | 0.95 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | PECULR 7 | 0.96521 | 0.9261 | -0.039113 |  | 0.95 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | PECULR 7 | 0.96521 | 0.9261 | -0.039113 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | PECULR 7 | 0.96521 | 0.9261 | -0.039113 |  | 0.95 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | PECULR 7 | 0.96521 | 0.9261 | -0.039113 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | PECULR 7 | 0.96521 | 0.9261 | -0.039113 |  | 0.95 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | PECULR 7 | 0.96521 | 0.9261 | -0.039113 |  | 0.95 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | PECULR 7 | 0.96521 | 0.9261 | -0.039113 |  | 0.95 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | PECULR 7 | 0.96521 | 0.9261 | -0.039113 |  | 0.95 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | PECULR 7 | 0.96521 | 0.9261 | -0.039113 |  | 0.95 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | PECULR 7 | 0.96521 | 0.9261 | -0.039113 |  | 0.95 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | PECULR 7 | 0.96521 | 0.9261 | -0.039113 |  | 0.95 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | PECULR 7 | 0.96521 | 0.9261 | -0.039113 |  | 0.95 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | PECULR 7 | 0.96521 | 0.9261 | -0.039113 |  | 0.95 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | PECULR 7 | 0.96521 | 0.9261 | -0.039113 |  | 0.95 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | PECULRS5 | 1.0008 | 0.92286 | -0.077911 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | PECULRS5 | 1.0008 | 0.92286 | -0.077911 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | PECULRS5 | 1.0008 | 0.92286 | -0.077911 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | PECULRS5 | 1.0008 | 0.92286 | -0.077911 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | PECULRS5 | 1.0008 | 0.92286 | -0.077911 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | PECULRS5 | 1.0008 | 0.92286 | -0.077911 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | PECULRS5 | 1.0008 | 0.92286 | -0.077911 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | PECULRS5 | 1.0008 | 0.92286 | -0.077911 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | PECULRS5 | 1.0008 | 0.92286 | -0.077911 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | PECULRS5 | 1.0008 | 0.92286 | -0.077911 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | PECULRS5 | 1.0008 | 0.92286 | -0.077911 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | PECULRS5 | 1.0008 | 0.92286 | -0.077911 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | PECULRS5 | 1.0008 | 0.92286 | -0.077911 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | PECULRS5 | 1.0008 | 0.92286 | -0.077911 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | PECULRS5 | 1.0008 | 0.92286 | -0.077911 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | PECULRS5 | 1.0008 | 0.92286 | -0.077911 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | PECULRS5 | 1.0008 | 0.92286 | -0.077911 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | PECULRS5 | 1.0008 | 0.92286 | -0.077911 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | PECULRS5 | 1.0008 | 0.92286 | -0.077911 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | PECULRS5 | 1.0008 | 0.92286 | -0.077911 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | PECULRS5 | 1.0008 | 0.92286 | -0.077911 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | PECULRS5 | 1.0008 | 0.92286 | -0.077911 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | PECULRS5 | 1.0008 | 0.92286 | -0.077911 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | PECULRS5 | 1.0008 | 0.92286 | -0.077911 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | PECULRS5 | 1.0008 | 0.92286 | -0.077911 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | PECULRS5 | 1.0008 | 0.92286 | -0.077911 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | PECULRS5 | 1.0008 | 0.92286 | -0.077911 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | PECULRS5 | 1.0008 | 0.92286 | -0.077911 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | PFLUMM 5 | 0.96549 | 0.92639 | -0.039106 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | PFLUMM 5 | 0.96549 | 0.92639 | -0.039106 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | PFLUMM 5 | 0.96549 | 0.92639 | -0.039106 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | PFLUMM 5 | 0.96549 | 0.92639 | -0.039106 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | PFLUMM 5 | 0.96549 | 0.92639 | -0.039106 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | PFLUMM 5 | 0.96549 | 0.92639 | -0.039106 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | PFLUMM 5 | 0.96549 | 0.92639 | -0.039106 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | PFLUMM 5 | 0.96549 | 0.92639 | -0.039106 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | PFLUMM 5 | 0.96549 | 0.92639 | -0.039106 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | PFLUMM 5 | 0.96549 | 0.92639 | -0.039106 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | PFLUMM 5 | 0.96549 | 0.92639 | -0.039106 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | PFLUMM 5 | 0.96549 | 0.92639 | -0.039106 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | PFLUMM 5 | 0.96549 | 0.92639 | -0.039106 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | PFLUMM 5 | 0.96549 | 0.92639 | -0.039106 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | PFLUMM 5 | 0.96549 | 0.92639 | -0.039106 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | PFLUMM 5 | 0.96549 | 0.92639 | -0.039106 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | PFLUMM 5 | 0.96549 | 0.92639 | -0.039106 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | PFLUMM 5 | 0.96549 | 0.92639 | -0.039106 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | PFLUMM 5 | 0.96549 | 0.92639 | -0.039106 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | PFLUMM 5 | 0.96549 | 0.92639 | -0.039106 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | PFLUMM 5 | 0.97738 | 0.91074 | -0.066634 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | PFLUMM 5 | 0.97738 | 0.91074 | -0.066634 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | PFLUMM 5 | 0.97738 | 0.91074 | -0.066634 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | PFLUMM 5 | 0.97738 | 0.91074 | -0.066634 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | PFLUMM 5 | 0.97738 | 0.91074 | -0.066634 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | PFLUMM 5 | 0.97738 | 0.91074 | -0.066634 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | PFLUMM 5 | 0.97738 | 0.91074 | -0.066634 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | PFLUMM 5 | 0.97738 | 0.91074 | -0.066634 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | PFLUMM 5 | 0.97738 | 0.91074 | -0.066634 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | PFLUMM 5 | 0.97738 | 0.91074 | -0.066634 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | PFLUMM 5 | 0.97738 | 0.91074 | -0.066634 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | PFLUMM 5 | 0.97738 | 0.91074 | -0.066634 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | PFLUMM 5 | 0.97738 | 0.91074 | -0.066634 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | PFLUMM 5 | 0.97738 | 0.91074 | -0.066634 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | PFLUMM 5 | 0.97738 | 0.91074 | -0.066634 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | PFLUMM 5 | 0.97738 | 0.91074 | -0.066634 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | PFLUMM 5 | 0.97738 | 0.91074 | -0.066634 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | PFLUMM 5 | 0.97738 | 0.91074 | -0.066634 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | PFLUMM 5 | 0.97738 | 0.91074 | -0.066634 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | PFLUMM 5 | 0.97738 | 0.91074 | -0.066634 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | PFLUMM 5 | 0.97738 | 0.91074 | -0.066634 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | PFLUMM 5 | 0.97738 | 0.91074 | -0.066634 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | PFLUMM 5 | 0.97738 | 0.91074 | -0.066634 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | PFLUMM 5 | 0.97738 | 0.91074 | -0.066634 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | PFLUMM 5 | 0.97738 | 0.91074 | -0.066634 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | PFLUMM 5 | 0.97738 | 0.91074 | -0.066634 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | PFLUMM 5 | 0.97738 | 0.91074 | -0.066634 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | PFLUMM 5 | 0.97738 | 0.91074 | -0.066634 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | PH RUN 3 | 0.96576 | 0.89783 | -0.06793 |  | 0.9 | 1.05 | 0.041569 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | PH RUN 3 | 0.96576 | 0.89783 | -0.06793 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | PH RUN 3 | 0.96576 | 0.89783 | -0.06793 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | PH RUN 3 | 0.96576 | 0.89783 | -0.06793 |  | 0.9 | 1.05 | 0.03222 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | PH RUN 3 | 0.96576 | 0.89783 | -0.06793 |  | 0.9 | 1.05 | 0.030633 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | PH RUN 3 | 0.96576 | 0.89783 | -0.06793 |  | 0.9 | 1.05 | 0.030061 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | PH RUN 3 | 0.96576 | 0.89783 | -0.06793 |  | 0.9 | 1.05 | 0.031207 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | PH RUN 3 | 0.96895 | 0.899 | -0.069945 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | PH RUN 3 | 0.96895 | 0.899 | -0.069945 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | PH RUN 3 | 0.96895 | 0.899 | -0.069945 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | PH RUN 3 | 0.96895 | 0.899 | -0.069945 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | PH RUN 3 | 0.96895 | 0.899 | -0.069946 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | PH RUN 3 | 0.96895 | 0.899 | -0.069946 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | PHILL 7 | 0.97376 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | PHILL 7 | 0.97376 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | PHILL 7 | 0.97376 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | PHILL 7 | 0.97376 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | PHILL 7 | 0.97376 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | PHILL 7 | 0.97376 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | PHILL 7 | 0.97376 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | PHILL 7 | 0.97376 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | PHILL 7 | 0.97376 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | PHILL 7 | 0.97376 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | PHILL 7 | 0.97376 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | PHILL 7 | 0.97376 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | PHILL 7 | 0.97376 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | PHILL 7 | 0.97376 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | PHILL 7 | 0.97376 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | PHILL 7 | 0.97376 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | PHILL 7 | 0.97376 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | PHILL 7 | 0.97376 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | PHILL 7 | 0.97376 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | PHILL 7 | 0.97376 | 0.93938 | -0.034386 |  | 0.95 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | PHILL 7 | 0.96999 | 0.93511 | -0.034879 |  | 0.95 | 1.05 | 0.042938 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 0.13 MVAR switched shunt at PECULR 7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | PHILL 7 | 0.96999 | 0.93511 | -0.034879 |  | 0.95 | 1.05 | 0.032864 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 0.13 MVAR switched shunt at PECULR 7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | PHILL 7 | 0.96999 | 0.93511 | -0.034879 |  | 0.95 | 1.05 | 0.03396 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 0.13 MVAR switched shunt at PECULR 7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | PHILL 7 | 0.96999 | 0.93511 | -0.034879 |  | 0.95 | 1.05 | 0.055483 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 0.13 MVAR switched shunt at PECULR 7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | PHILL 7 | 0.96999 | 0.93511 | -0.034879 |  | 0.95 | 1.05 | 0.034689 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 0.13 MVAR switched shunt at PECULR 7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | PHILL 7 | 0.96999 | 0.93511 | -0.034879 |  | 0.95 | 1.05 | 0.033481 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 0.13 MVAR switched shunt at PECULR 7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | PHILL 7 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | PHILL 7 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | PHILL 7 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | PHILL 7 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | PHILL 7 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | PHILL 7 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | PHILL 7 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | PHILL 7 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | PHILL 7 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | PHILL 7 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | PHILL 7 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | PHILL 7 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | PHILL 7 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | PHILL 7 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | PHILL 7 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | PHILL 7 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | PHILL 7 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | PHILL 7 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | PHILL 7 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | PHILL 7 | 0.97631 | 0.93526 | -0.041049 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | PHILL 7 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | PHILL 7 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | PHILL 7 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | PHILL 7 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | PHILL 7 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | PHILL 7 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | PHILL 7 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | PHILL 7 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | PHILL 7 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | PHILL 7 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | PHILL 7 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | PHILL 7 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | PHILL 7 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | PHILL 7 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | PHILL 7 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | PHILL 7 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | PHILL 7 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | PHILL 7 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | PHILL 7 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | PHILL 7 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | PHILL 7 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | PHILL 7 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | PHILL 7 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | PHILL 7 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | PHILL 7 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | PHILL 7 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | PHILL 7 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | PHILL 7 | 0.97467 | 0.90184 | -0.072827 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | PHILL 7 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | PHILL 7 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | PHILL 7 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | PHILL 7 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | PHILL 7 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | PHILL 7 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | PHILL 7 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | PHILL 7 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | PHILL 7 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | PHILL 7 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | PHILL 7 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | PHILL 7 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | PHILL 7 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | PHILL 7 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | PHILL 7 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | PHILL 7 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | PHILL 7 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | PHILL 7 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | PHILL 7 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | PHILL 7 | 0.97279 | 0.93753 | -0.035266 |  | 0.95 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | PLSTVAL5 | 1.0102 | 0.92501 | -0.085225 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | PLSTVAL5 | 1.0102 | 0.92501 | -0.085225 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | PLSTVAL5 | 1.0102 | 0.92501 | -0.085225 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | PLSTVAL5 | 1.0102 | 0.92501 | -0.085225 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | PLSTVAL5 | 1.0102 | 0.92501 | -0.085225 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | PLSTVAL5 | 1.0102 | 0.92501 | -0.085225 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | PLSTVAL5 | 1.0102 | 0.92501 | -0.085225 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | PLSTVAL5 | 1.0102 | 0.92501 | -0.085225 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | PLSTVAL5 | 1.0102 | 0.92501 | -0.085225 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | PLSTVAL5 | 1.0102 | 0.92501 | -0.085225 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | PLSTVAL5 | 1.0102 | 0.92501 | -0.085225 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | PLSTVAL5 | 1.0102 | 0.92501 | -0.085225 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | PLSTVAL5 | 1.0102 | 0.92501 | -0.085225 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | PLSTVAL5 | 1.0102 | 0.92501 | -0.085225 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | PLSTVAL5 | 1.0102 | 0.92501 | -0.085225 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | PLSTVAL5 | 1.0102 | 0.92501 | -0.085225 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | PLSTVAL5 | 1.0102 | 0.92501 | -0.085225 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | PLSTVAL5 | 1.0102 | 0.92501 | -0.085225 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | PLSTVAL5 | 1.0102 | 0.92501 | -0.085225 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | PLSTVAL5 | 1.0102 | 0.92501 | -0.085225 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | PLSTVAL5 | 1.0102 | 0.92501 | -0.085225 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | PLSTVAL5 | 1.0102 | 0.92501 | -0.085225 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | PLSTVAL5 | 1.0102 | 0.92501 | -0.085225 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | PLSTVAL5 | 1.0102 | 0.92501 | -0.085225 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | PLSTVAL5 | 1.0102 | 0.92501 | -0.085225 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | PLSTVAL5 | 1.0102 | 0.92501 | -0.085225 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | PLSTVAL5 | 1.0102 | 0.92501 | -0.085225 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | PLSTVAL5 | 1.0102 | 0.92501 | -0.085225 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | POSTROCK6 | 0.97106 | 0.89952 | -0.071545 |  | 0.9 | 1.05 | 0.064516 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | POSTROCK7 | 0.97405 | 0.9277 | -0.046357 |  | 0.95 | 1.05 | 0.048073 | System Intact | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | POSTROCK7 | 0.97405 | 0.9277 | -0.046357 |  | 0.95 | 1.05 | 0.032207 | System Intact | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | POSTROCK7 | 0.97405 | 0.9277 | -0.046357 |  | 0.95 | 1.05 | 0.032207 | System Intact | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | POSTROCK7 | 0.97405 | 0.9277 | -0.046357 |  | 0.95 | 1.05 | 0.032907 | System Intact | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | POSTROCK7 | 0.97405 | 0.9277 | -0.046357 |  | 0.95 | 1.05 | 0.030428 | System Intact | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | POSTROCK7 | 0.97405 | 0.9277 | -0.046357 |  | 0.95 | 1.05 | 0.030314 | System Intact | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | POSTROCK7 | 0.97405 | 0.9277 | -0.046357 |  | 0.95 | 1.05 | 0.032405 | System Intact | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | POSTROCK7 | 0.95911 | 0.87906 | -0.080046 |  | 0.9 | 1.05 | 0.064516 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | POSTROCK7 | 0.96145 | 0.88928 | -0.072169 |  | 0.9 | 1.05 | 0.0326 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | POSTROCK7 | 0.96145 | 0.88928 | -0.072169 |  | 0.9 | 1.05 | 0.030348 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | POSTROCK7 | 0.96145 | 0.88928 | -0.072169 |  | 0.9 | 1.05 | 0.031036 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | POSTROCK7 | 0.96145 | 0.88928 | -0.072169 |  | 0.9 | 1.05 | 0.030059 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | POSTROCK7 | 0.96145 | 0.88928 | -0.072169 |  | 0.9 | 1.05 | 0.030059 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | POSTROCK7 | 0.96145 | 0.88928 | -0.072169 |  | 0.9 | 1.05 | 0.030771 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | POSTROCK7 | 0.96145 | 0.88928 | -0.072169 |  | 0.9 | 1.05 | 0.030685 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | POSTROCK7 | 0.9584 | 0.89541 | -0.062995 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 86 MVAR switched shunt at POSTROCK7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | POSTROCK7 | 0.9584 | 0.89541 | -0.062995 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 86 MVAR switched shunt at POSTROCK7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | POSTROCK7 | 0.96009 | 0.89775 | -0.06234 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | POSTROCK7 | 0.96009 | 0.89775 | -0.06234 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 86 MVAR switched shunt at POSTROCK7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | POSTROCK7 | 0.96747 | 0.89113 | -0.076343 |  | 0.9 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | POSTROCK7 | 0.96747 | 0.89113 | -0.076343 |  | 0.9 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | POSTROCK7 | 0.96747 | 0.89113 | -0.076343 |  | 0.9 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | POSTROCK7 | 0.96747 | 0.89113 | -0.076343 |  | 0.9 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | POSTROCK7 | 0.96747 | 0.89113 | -0.076343 |  | 0.9 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | POSTROCK7 | 0.96747 | 0.89113 | -0.076343 |  | 0.9 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | POSTROCK7 | 0.96747 | 0.89113 | -0.076343 |  | 0.9 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | POSTROCK7 | 0.96747 | 0.89113 | -0.076343 |  | 0.9 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | POSTROCK7 | 0.96747 | 0.89113 | -0.076343 |  | 0.9 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | POSTROCK7 | 0.96747 | 0.89113 | -0.076343 |  | 0.9 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | POSTROCK7 | 0.96747 | 0.89113 | -0.076343 |  | 0.9 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | POSTROCK7 | 0.96747 | 0.89113 | -0.076343 |  | 0.9 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | POSTROCK7 | 0.96747 | 0.89113 | -0.076343 |  | 0.9 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | POSTROCK7 | 0.96747 | 0.89113 | -0.076343 |  | 0.9 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | POSTROCK7 | 0.96747 | 0.89113 | -0.076343 |  | 0.9 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | POSTROCK7 | 0.96747 | 0.89113 | -0.076343 |  | 0.9 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | POSTROCK7 | 0.96747 | 0.89113 | -0.076343 |  | 0.9 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | POSTROCK7 | 0.96747 | 0.89113 | -0.076343 |  | 0.9 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | POSTROCK7 | 0.96747 | 0.89113 | -0.076343 |  | 0.9 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | POSTROCK7 | 0.96747 | 0.89113 | -0.076343 |  | 0.9 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | POSTROCK7 | 0.96747 | 0.89113 | -0.076343 |  | 0.9 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | POSTROCK7 | 0.96747 | 0.89113 | -0.076343 |  | 0.9 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | POSTROCK7 | 0.96747 | 0.89113 | -0.076343 |  | 0.9 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | POSTROCK7 | 0.96747 | 0.89113 | -0.076343 |  | 0.9 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | POSTROCK7 | 0.96747 | 0.89113 | -0.076343 |  | 0.9 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | POSTROCK7 | 0.96747 | 0.89113 | -0.076343 |  | 0.9 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | POSTROCK7 | 0.96747 | 0.89113 | -0.076343 |  | 0.9 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | POSTROCK7 | 0.96747 | 0.89113 | -0.076343 |  | 0.9 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | PRAIRIE3 | 0.94796 | 0.85933 | -0.088636 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | PRAIRIE3 | 0.94796 | 0.85933 | -0.088636 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | PRAIRIE3 | 0.94796 | 0.85933 | -0.088636 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | PRAIRIE3 | 0.94796 | 0.85933 | -0.088636 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | PRAIRIE3 | 0.94796 | 0.85933 | -0.088636 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | PRAIRIE3 | 0.94796 | 0.85933 | -0.088636 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | PRAIRIE3 | 0.94796 | 0.85933 | -0.088636 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | PRAIRIE3 | 0.94796 | 0.85933 | -0.088636 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | PRAIRIE3 | 0.94796 | 0.85933 | -0.088636 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | PRAIRIE3 | 0.94796 | 0.85933 | -0.088636 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | PRAIRIE3 | 0.94796 | 0.85933 | -0.088636 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | PRAIRIE3 | 0.94796 | 0.85933 | -0.088636 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | PRAIRIE3 | 0.94796 | 0.85933 | -0.088636 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | PRAIRIE3 | 0.94796 | 0.85933 | -0.088636 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | PRAIRIE3 | 0.94796 | 0.85933 | -0.088636 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | PRAIRIE3 | 0.94796 | 0.85933 | -0.088636 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | PRAIRIE3 | 0.94796 | 0.85933 | -0.088636 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | PRAIRIE3 | 0.94796 | 0.85933 | -0.088636 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | PRAIRIE3 | 0.94796 | 0.85933 | -0.088636 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | PRAIRIE3 | 0.94796 | 0.85933 | -0.088636 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | PRAIRIE3 | 0.94796 | 0.85933 | -0.088636 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | PRAIRIE3 | 0.94796 | 0.85933 | -0.088636 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | PRAIRIE3 | 0.94796 | 0.85933 | -0.088636 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | PRAIRIE3 | 0.94796 | 0.85933 | -0.088636 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | PRAIRIE3 | 0.94796 | 0.85933 | -0.088636 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | PRAIRIE3 | 0.94796 | 0.85933 | -0.088636 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | PRAIRIE3 | 0.94796 | 0.85933 | -0.088636 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | PRAIRIE3 | 0.94796 | 0.85933 | -0.088636 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | QUARRY 5 | 0.96668 | 0.92001 | -0.046676 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | QUARRY 5 | 0.96668 | 0.92001 | -0.046676 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | QUARRY 5 | 0.96668 | 0.92001 | -0.046676 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | QUARRY 5 | 0.96668 | 0.92001 | -0.046676 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | QUARRY 5 | 0.96668 | 0.92001 | -0.046676 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | QUARRY 5 | 0.96668 | 0.92001 | -0.046676 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | QUARRY 5 | 0.96668 | 0.92001 | -0.046676 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | QUARRY 5 | 0.96668 | 0.92001 | -0.046676 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | QUARRY 5 | 0.96668 | 0.92001 | -0.046676 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | QUARRY 5 | 0.96668 | 0.92001 | -0.046676 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | QUARRY 5 | 0.96668 | 0.92001 | -0.046676 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | QUARRY 5 | 0.96668 | 0.92001 | -0.046676 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | QUARRY 5 | 0.96668 | 0.92001 | -0.046676 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | QUARRY 5 | 0.96668 | 0.92001 | -0.046676 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | QUARRY 5 | 0.96668 | 0.92001 | -0.046676 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | QUARRY 5 | 0.96668 | 0.92001 | -0.046676 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | QUARRY 5 | 0.96668 | 0.92001 | -0.046676 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | QUARRY 5 | 0.96668 | 0.92001 | -0.046676 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | QUARRY 5 | 0.96668 | 0.92001 | -0.046676 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | QUARRY 5 | 0.96668 | 0.92001 | -0.046676 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | QUARRY 5 | 0.97876 | 0.92676 | -0.052001 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | QUARRY 5 | 0.97876 | 0.92676 | -0.052001 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | QUARRY 5 | 0.97876 | 0.92676 | -0.052001 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | QUARRY 5 | 0.97876 | 0.92676 | -0.052001 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | QUARRY 5 | 0.97876 | 0.92676 | -0.052001 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | QUARRY 5 | 0.97876 | 0.92676 | -0.052001 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | QUARRY 5 | 0.97876 | 0.92676 | -0.052001 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | QUARRY 5 | 0.97876 | 0.92676 | -0.052001 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | QUARRY 5 | 0.97876 | 0.92676 | -0.052001 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | QUARRY 5 | 0.97876 | 0.92676 | -0.052001 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | QUARRY 5 | 0.97876 | 0.92676 | -0.052001 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | QUARRY 5 | 0.97876 | 0.92676 | -0.052001 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | QUARRY 5 | 0.97876 | 0.92676 | -0.052001 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | QUARRY 5 | 0.97876 | 0.92676 | -0.052001 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | QUARRY 5 | 0.97876 | 0.92676 | -0.052001 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | QUARRY 5 | 0.97876 | 0.92676 | -0.052001 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | QUARRY 5 | 0.97876 | 0.92676 | -0.052001 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | QUARRY 5 | 0.97876 | 0.92676 | -0.052001 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | QUARRY 5 | 0.97876 | 0.92676 | -0.052001 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | QUARRY 5 | 0.97876 | 0.92676 | -0.052001 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | QUARRY 5 | 0.983 | 0.90515 | -0.077847 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | QUARRY 5 | 0.983 | 0.90515 | -0.077847 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | QUARRY 5 | 0.983 | 0.90515 | -0.077847 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | QUARRY 5 | 0.983 | 0.90515 | -0.077847 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | QUARRY 5 | 0.983 | 0.90515 | -0.077847 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | QUARRY 5 | 0.983 | 0.90515 | -0.077847 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | QUARRY 5 | 0.983 | 0.90515 | -0.077847 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | QUARRY 5 | 0.983 | 0.90515 | -0.077847 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | QUARRY 5 | 0.983 | 0.90515 | -0.077847 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | QUARRY 5 | 0.983 | 0.90515 | -0.077847 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | QUARRY 5 | 0.983 | 0.90515 | -0.077847 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | QUARRY 5 | 0.983 | 0.90515 | -0.077847 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | QUARRY 5 | 0.983 | 0.90515 | -0.077847 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | QUARRY 5 | 0.983 | 0.90515 | -0.077847 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | QUARRY 5 | 0.983 | 0.90515 | -0.077847 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | QUARRY 5 | 0.983 | 0.90515 | -0.077847 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | QUARRY 5 | 0.983 | 0.90515 | -0.077847 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | QUARRY 5 | 0.983 | 0.90515 | -0.077847 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | QUARRY 5 | 0.983 | 0.90515 | -0.077847 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | QUARRY 5 | 0.983 | 0.90515 | -0.077847 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | QUARRY 5 | 0.983 | 0.90515 | -0.077847 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | QUARRY 5 | 0.983 | 0.90515 | -0.077847 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | QUARRY 5 | 0.983 | 0.90515 | -0.077847 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | QUARRY 5 | 0.983 | 0.90515 | -0.077847 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | QUARRY 5 | 0.983 | 0.90515 | -0.077847 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | QUARRY 5 | 0.983 | 0.90515 | -0.077847 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | QUARRY 5 | 0.983 | 0.90515 | -0.077847 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | QUARRY 5 | 0.983 | 0.90515 | -0.077847 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | RANSOM 2 | 0.93755 | 0.8733 | -0.064249 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | RANSOM 2 | 0.93755 | 0.8733 | -0.064249 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | RANSOM 2 | 0.94308 | 0.8744 | -0.068679 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | RANSOM 2 | 0.94308 | 0.8744 | -0.068679 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | RANSOM 2 | 0.94308 | 0.8744 | -0.068679 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | RANSOM 2 | 0.94308 | 0.8744 | -0.068679 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | RANSOM 2 | 0.94308 | 0.8744 | -0.06868 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | RANSOM 2 | 0.94308 | 0.8744 | -0.06868 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | RANSOM 3 | 0.94008 | 0.87621 | -0.063871 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | RANSOM 3 | 0.94008 | 0.87621 | -0.063871 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | RANSOM 3 | 0.94558 | 0.8773 | -0.068277 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | RANSOM 3 | 0.94558 | 0.8773 | -0.068277 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | RANSOM 3 | 0.94558 | 0.8773 | -0.068278 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | RANSOM 3 | 0.94558 | 0.8773 | -0.068278 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | RANSOM 3 | 0.94558 | 0.8773 | -0.068278 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | RANSOM 3 | 0.94558 | 0.8773 | -0.068278 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | RAYTOWN5 | 0.99288 | 0.92937 | -0.063506 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | RAYTOWN5 | 0.99288 | 0.92937 | -0.063506 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | RAYTOWN5 | 0.99288 | 0.92937 | -0.063506 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | RAYTOWN5 | 0.99288 | 0.92937 | -0.063506 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | RAYTOWN5 | 0.99288 | 0.92937 | -0.063506 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | RAYTOWN5 | 0.99288 | 0.92937 | -0.063506 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | RAYTOWN5 | 0.99288 | 0.92937 | -0.063506 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | RAYTOWN5 | 0.99288 | 0.92937 | -0.063506 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | RAYTOWN5 | 0.99288 | 0.92937 | -0.063506 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | RAYTOWN5 | 0.99288 | 0.92937 | -0.063506 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | RAYTOWN5 | 0.99288 | 0.92937 | -0.063506 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | RAYTOWN5 | 0.99288 | 0.92937 | -0.063506 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | RAYTOWN5 | 0.99288 | 0.92937 | -0.063506 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | RAYTOWN5 | 0.99288 | 0.92937 | -0.063506 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | RAYTOWN5 | 0.99288 | 0.92937 | -0.063506 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | RAYTOWN5 | 0.99288 | 0.92937 | -0.063506 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | RAYTOWN5 | 0.99288 | 0.92937 | -0.063506 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | RAYTOWN5 | 0.99288 | 0.92937 | -0.063506 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | RAYTOWN5 | 0.99288 | 0.92937 | -0.063506 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | RAYTOWN5 | 0.99288 | 0.92937 | -0.063506 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | RAYTOWN5 | 0.99288 | 0.92937 | -0.063506 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | RAYTOWN5 | 0.99288 | 0.92937 | -0.063506 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | RAYTOWN5 | 0.99288 | 0.92937 | -0.063506 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | RAYTOWN5 | 0.99288 | 0.92937 | -0.063506 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | RAYTOWN5 | 0.99288 | 0.92937 | -0.063506 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | RAYTOWN5 | 0.99288 | 0.92937 | -0.063506 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | RAYTOWN5 | 0.99288 | 0.92937 | -0.063506 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | RAYTOWN5 | 0.99288 | 0.92937 | -0.063506 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | RCKFALLPV7 | 0.97956 | 0.91801 | -0.061555 |  | 0.92 | 1.05 | 0.094783 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | RCKFALLPV7 | 0.97956 | 0.91801 | -0.061555 |  | 0.92 | 1.05 | 0.03645 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | RCKFALLPV7 | 0.97956 | 0.91801 | -0.061555 |  | 0.92 | 1.05 | 0.04755 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | RCKFALLPV7 | 0.97956 | 0.91801 | -0.061555 |  | 0.92 | 1.05 | 0.06097 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | RCKFALLPV7 | 0.97956 | 0.91801 | -0.061555 |  | 0.92 | 1.05 | 0.061051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | RCKFALLPV7 | 0.97956 | 0.91801 | -0.061555 |  | 0.92 | 1.05 | 0.04456 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | RCKFALLPV7 | 0.97956 | 0.91801 | -0.061555 |  | 0.92 | 1.05 | 0.048811 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | RCKFALLPV7 | 0.97956 | 0.91801 | -0.061555 |  | 0.92 | 1.05 | 0.13004 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | RCKFALLPV7 | 0.97956 | 0.91801 | -0.061555 |  | 0.92 | 1.05 | 0.049018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | RCKFALLPV7 | 0.97956 | 0.91801 | -0.061555 |  | 0.92 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | RCKFALLPV7 | 0.97956 | 0.91801 | -0.061555 |  | 0.92 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | RCKFALLPV7 | 0.97956 | 0.91801 | -0.061555 |  | 0.92 | 1.05 | 0.05974 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | RCKFALLPV7 | 0.97956 | 0.91801 | -0.061555 |  | 0.92 | 1.05 | 0.076949 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | RCKFALLPV7 | 0.97956 | 0.91801 | -0.061555 |  | 0.92 | 1.05 | 0.042157 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | RCKFALLPV7 | 0.97956 | 0.91801 | -0.061555 |  | 0.92 | 1.05 | 0.040957 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | RCKFALLPV7 | 0.97956 | 0.91801 | -0.061555 |  | 0.92 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | RCKFALLPV7 | 0.97956 | 0.91801 | -0.061555 |  | 0.92 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | RCKFALLPV7 | 0.97956 | 0.91801 | -0.061555 |  | 0.92 | 1.05 | 0.054637 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | RCKFALLPV7 | 0.97956 | 0.91801 | -0.061555 |  | 0.92 | 1.05 | 0.060597 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | RCKFALLPV7 | 0.97956 | 0.91801 | -0.061555 |  | 0.92 | 1.05 | 0.044286 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | RCKFALLPV7 | 0.97956 | 0.91801 | -0.061555 |  | 0.92 | 1.05 | 0.059107 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | RCKFALLPV7 | 0.97956 | 0.91801 | -0.061555 |  | 0.92 | 1.05 | 0.052698 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | RCKFALLPV7 | 0.97956 | 0.91801 | -0.061555 |  | 0.92 | 1.05 | 0.067422 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | RCKFALLPV7 | 0.97956 | 0.91801 | -0.061555 |  | 0.92 | 1.05 | 0.053768 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | RCKFALLPV7 | 0.97956 | 0.91801 | -0.061555 |  | 0.92 | 1.05 | 0.03909 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | READING3 | 0.95104 | 0.87 | -0.081036 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | READING3 | 0.95104 | 0.87 | -0.081036 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | READING3 | 0.95104 | 0.87 | -0.081036 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | READING3 | 0.95104 | 0.87 | -0.081036 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | READING3 | 0.95104 | 0.87 | -0.081036 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | READING3 | 0.95104 | 0.87 | -0.081036 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | READING3 | 0.95104 | 0.87 | -0.081036 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | READING3 | 0.95104 | 0.87 | -0.081036 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | READING3 | 0.95104 | 0.87 | -0.081036 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | READING3 | 0.95104 | 0.87 | -0.081036 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | READING3 | 0.95104 | 0.87 | -0.081036 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | READING3 | 0.95104 | 0.87 | -0.081036 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | READING3 | 0.95104 | 0.87 | -0.081036 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | READING3 | 0.95104 | 0.87 | -0.081036 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | READING3 | 0.95104 | 0.87 | -0.081036 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | READING3 | 0.95104 | 0.87 | -0.081036 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | READING3 | 0.95104 | 0.87 | -0.081036 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | READING3 | 0.95104 | 0.87 | -0.081036 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | READING3 | 0.95104 | 0.87 | -0.081036 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | READING3 | 0.95104 | 0.87 | -0.081036 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | READING3 | 0.95104 | 0.87 | -0.081036 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | READING3 | 0.95104 | 0.87 | -0.081036 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | READING3 | 0.95104 | 0.87 | -0.081036 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | READING3 | 0.95104 | 0.87 | -0.081036 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | READING3 | 0.95104 | 0.87 | -0.081036 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | READING3 | 0.95104 | 0.87 | -0.081036 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | READING3 | 0.95104 | 0.87 | -0.081036 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | READING3 | 0.95104 | 0.87 | -0.081036 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | REDEL 5 | 0.98491 | 0.90438 | -0.080539 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | REDEL 5 | 0.98491 | 0.90438 | -0.080539 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | REDEL 5 | 0.98491 | 0.90438 | -0.080539 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | REDEL 5 | 0.98491 | 0.90438 | -0.080539 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | REDEL 5 | 0.98491 | 0.90438 | -0.080539 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | REDEL 5 | 0.98491 | 0.90438 | -0.080539 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | REDEL 5 | 0.98491 | 0.90438 | -0.080539 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | REDEL 5 | 0.98491 | 0.90438 | -0.080539 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | REDEL 5 | 0.98491 | 0.90438 | -0.080539 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | REDEL 5 | 0.98491 | 0.90438 | -0.080539 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | REDEL 5 | 0.98491 | 0.90438 | -0.080539 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | REDEL 5 | 0.98491 | 0.90438 | -0.080539 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | REDEL 5 | 0.98491 | 0.90438 | -0.080539 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | REDEL 5 | 0.98491 | 0.90438 | -0.080539 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | REDEL 5 | 0.98491 | 0.90438 | -0.080539 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | REDEL 5 | 0.98491 | 0.90438 | -0.080539 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | REDEL 5 | 0.98491 | 0.90438 | -0.080539 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | REDEL 5 | 0.98491 | 0.90438 | -0.080539 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | REDEL 5 | 0.98491 | 0.90438 | -0.080539 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | REDEL 5 | 0.98491 | 0.90438 | -0.080539 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | REDEL 5 | 0.98491 | 0.90438 | -0.080539 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | REDEL 5 | 0.98491 | 0.90438 | -0.080539 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | REDEL 5 | 0.98491 | 0.90438 | -0.080539 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | REDEL 5 | 0.98491 | 0.90438 | -0.080539 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | REDEL 5 | 0.98491 | 0.90438 | -0.080539 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | REDEL 5 | 0.98491 | 0.90438 | -0.080539 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | REDEL 5 | 0.98491 | 0.90438 | -0.080539 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | REDEL 5 | 0.98491 | 0.90438 | -0.080539 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | REEDER 5 | 0.96377 | 0.92511 | -0.038667 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | REEDER 5 | 0.96377 | 0.92511 | -0.038667 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | REEDER 5 | 0.96377 | 0.92511 | -0.038667 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | REEDER 5 | 0.96377 | 0.92511 | -0.038667 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | REEDER 5 | 0.96377 | 0.92511 | -0.038667 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | REEDER 5 | 0.96377 | 0.92511 | -0.038667 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | REEDER 5 | 0.96377 | 0.92511 | -0.038667 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | REEDER 5 | 0.96377 | 0.92511 | -0.038667 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | REEDER 5 | 0.96377 | 0.92511 | -0.038667 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | REEDER 5 | 0.96377 | 0.92511 | -0.038667 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | REEDER 5 | 0.96377 | 0.92511 | -0.038667 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | REEDER 5 | 0.96377 | 0.92511 | -0.038667 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | REEDER 5 | 0.96377 | 0.92511 | -0.038667 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | REEDER 5 | 0.96377 | 0.92511 | -0.038667 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | REEDER 5 | 0.96377 | 0.92511 | -0.038667 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | REEDER 5 | 0.96377 | 0.92511 | -0.038667 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | REEDER 5 | 0.96377 | 0.92511 | -0.038667 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | REEDER 5 | 0.96377 | 0.92511 | -0.038667 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | REEDER 5 | 0.96377 | 0.92511 | -0.038667 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | REEDER 5 | 0.96377 | 0.92511 | -0.038667 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | REEDER 5 | 0.97219 | 0.92908 | -0.043109 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | REEDER 5 | 0.97219 | 0.92908 | -0.043109 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | REEDER 5 | 0.97219 | 0.92908 | -0.043109 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | REEDER 5 | 0.97219 | 0.92908 | -0.043109 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | REEDER 5 | 0.97219 | 0.92908 | -0.043109 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | REEDER 5 | 0.97219 | 0.92908 | -0.043109 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | REEDER 5 | 0.97219 | 0.92908 | -0.043109 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | REEDER 5 | 0.97219 | 0.92908 | -0.043109 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | REEDER 5 | 0.97219 | 0.92908 | -0.043109 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | REEDER 5 | 0.97219 | 0.92908 | -0.043109 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | REEDER 5 | 0.97219 | 0.92908 | -0.043109 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | REEDER 5 | 0.97219 | 0.92908 | -0.043109 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | REEDER 5 | 0.97219 | 0.92908 | -0.043109 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | REEDER 5 | 0.97219 | 0.92908 | -0.043109 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | REEDER 5 | 0.97219 | 0.92908 | -0.043109 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | REEDER 5 | 0.97219 | 0.92908 | -0.043109 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | REEDER 5 | 0.97219 | 0.92908 | -0.043109 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | REEDER 5 | 0.97219 | 0.92908 | -0.043109 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | REEDER 5 | 0.97219 | 0.92908 | -0.043109 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | REEDER 5 | 0.97219 | 0.92908 | -0.043109 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | REEDER 5 | 0.97498 | 0.90826 | -0.066722 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | REEDER 5 | 0.97498 | 0.90826 | -0.066722 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | REEDER 5 | 0.97498 | 0.90826 | -0.066722 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | REEDER 5 | 0.97498 | 0.90826 | -0.066722 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | REEDER 5 | 0.97498 | 0.90826 | -0.066722 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | REEDER 5 | 0.97498 | 0.90826 | -0.066722 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | REEDER 5 | 0.97498 | 0.90826 | -0.066722 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | REEDER 5 | 0.97498 | 0.90826 | -0.066722 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | REEDER 5 | 0.97498 | 0.90826 | -0.066722 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | REEDER 5 | 0.97498 | 0.90826 | -0.066722 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | REEDER 5 | 0.97498 | 0.90826 | -0.066722 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | REEDER 5 | 0.97498 | 0.90826 | -0.066722 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | REEDER 5 | 0.97498 | 0.90826 | -0.066722 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | REEDER 5 | 0.97498 | 0.90826 | -0.066722 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | REEDER 5 | 0.97498 | 0.90826 | -0.066722 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | REEDER 5 | 0.97498 | 0.90826 | -0.066722 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | REEDER 5 | 0.97498 | 0.90826 | -0.066722 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | REEDER 5 | 0.97498 | 0.90826 | -0.066722 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | REEDER 5 | 0.97498 | 0.90826 | -0.066722 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | REEDER 5 | 0.97498 | 0.90826 | -0.066722 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | REEDER 5 | 0.97498 | 0.90826 | -0.066722 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | REEDER 5 | 0.97498 | 0.90826 | -0.066722 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | REEDER 5 | 0.97498 | 0.90826 | -0.066722 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | REEDER 5 | 0.97498 | 0.90826 | -0.066722 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | REEDER 5 | 0.97498 | 0.90826 | -0.066722 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | REEDER 5 | 0.97498 | 0.90826 | -0.066722 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | REEDER 5 | 0.97498 | 0.90826 | -0.066722 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | REEDER 5 | 0.97498 | 0.90826 | -0.066722 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | RENFROW7 | 0.97929 | 0.91775 | -0.061538 |  | 0.92 | 1.05 | 0.094783 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | RENFROW7 | 0.97929 | 0.91775 | -0.061538 |  | 0.92 | 1.05 | 0.03645 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | RENFROW7 | 0.97929 | 0.91775 | -0.061538 |  | 0.92 | 1.05 | 0.04755 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | RENFROW7 | 0.97929 | 0.91775 | -0.061538 |  | 0.92 | 1.05 | 0.06097 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | RENFROW7 | 0.97929 | 0.91775 | -0.061538 |  | 0.92 | 1.05 | 0.061051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | RENFROW7 | 0.97929 | 0.91775 | -0.061538 |  | 0.92 | 1.05 | 0.04456 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | RENFROW7 | 0.97929 | 0.91775 | -0.061538 |  | 0.92 | 1.05 | 0.048811 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | RENFROW7 | 0.97929 | 0.91775 | -0.061538 |  | 0.92 | 1.05 | 0.13004 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | RENFROW7 | 0.97929 | 0.91775 | -0.061538 |  | 0.92 | 1.05 | 0.049018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | RENFROW7 | 0.97929 | 0.91775 | -0.061538 |  | 0.92 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | RENFROW7 | 0.97929 | 0.91775 | -0.061538 |  | 0.92 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | RENFROW7 | 0.97929 | 0.91775 | -0.061538 |  | 0.92 | 1.05 | 0.05974 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | RENFROW7 | 0.97929 | 0.91775 | -0.061538 |  | 0.92 | 1.05 | 0.076949 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | RENFROW7 | 0.97929 | 0.91775 | -0.061538 |  | 0.92 | 1.05 | 0.042157 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | RENFROW7 | 0.97929 | 0.91775 | -0.061538 |  | 0.92 | 1.05 | 0.040957 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | RENFROW7 | 0.97929 | 0.91775 | -0.061538 |  | 0.92 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | RENFROW7 | 0.97929 | 0.91775 | -0.061538 |  | 0.92 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | RENFROW7 | 0.97929 | 0.91775 | -0.061538 |  | 0.92 | 1.05 | 0.054637 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | RENFROW7 | 0.97929 | 0.91775 | -0.061538 |  | 0.92 | 1.05 | 0.060597 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | RENFROW7 | 0.97929 | 0.91775 | -0.061538 |  | 0.92 | 1.05 | 0.044286 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | RENFROW7 | 0.97929 | 0.91775 | -0.061538 |  | 0.92 | 1.05 | 0.059107 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | RENFROW7 | 0.97929 | 0.91775 | -0.061538 |  | 0.92 | 1.05 | 0.052698 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | RENFROW7 | 0.97929 | 0.91775 | -0.061538 |  | 0.92 | 1.05 | 0.067422 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | RENFROW7 | 0.97929 | 0.91775 | -0.061538 |  | 0.92 | 1.05 | 0.053768 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | RENFROW7 | 0.97929 | 0.91775 | -0.061538 |  | 0.92 | 1.05 | 0.03909 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | RILEY 5 | 0.96538 | 0.92927 | -0.036104 |  | 0.93 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | RILEY 5 | 0.96538 | 0.92927 | -0.036104 |  | 0.93 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | RILEY 5 | 0.96538 | 0.92927 | -0.036104 |  | 0.93 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | RILEY 5 | 0.96538 | 0.92927 | -0.036104 |  | 0.93 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | RILEY 5 | 0.96538 | 0.92927 | -0.036104 |  | 0.93 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | RILEY 5 | 0.96538 | 0.92927 | -0.036104 |  | 0.93 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | RILEY 5 | 0.96538 | 0.92927 | -0.036104 |  | 0.93 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | RILEY 5 | 0.96538 | 0.92927 | -0.036104 |  | 0.93 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | RILEY 5 | 0.96538 | 0.92927 | -0.036104 |  | 0.93 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | RILEY 5 | 0.96538 | 0.92927 | -0.036104 |  | 0.93 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | RILEY 5 | 0.96538 | 0.92927 | -0.036104 |  | 0.93 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | RILEY 5 | 0.96538 | 0.92927 | -0.036104 |  | 0.93 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | RILEY 5 | 0.96538 | 0.92927 | -0.036104 |  | 0.93 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | RILEY 5 | 0.96538 | 0.92927 | -0.036104 |  | 0.93 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | RILEY 5 | 0.96538 | 0.92927 | -0.036104 |  | 0.93 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | RILEY 5 | 0.96538 | 0.92927 | -0.036104 |  | 0.93 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | RILEY 5 | 0.96538 | 0.92927 | -0.036104 |  | 0.93 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | RILEY 5 | 0.96538 | 0.92927 | -0.036104 |  | 0.93 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | RILEY 5 | 0.96538 | 0.92927 | -0.036104 |  | 0.93 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | RILEY 5 | 0.96538 | 0.92927 | -0.036104 |  | 0.93 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | RILEY 5 | 0.95988 | 0.92055 | -0.039338 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | RILEY 5 | 0.95988 | 0.92055 | -0.039338 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | RILEY 5 | 0.95988 | 0.92055 | -0.039338 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | RILEY 5 | 0.95988 | 0.92055 | -0.039338 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | RILEY 5 | 0.95988 | 0.92055 | -0.039338 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | RILEY 5 | 0.95988 | 0.92055 | -0.039338 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | RILEY 5 | 0.95988 | 0.92055 | -0.039338 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | RILEY 5 | 0.95988 | 0.92055 | -0.039338 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | RILEY 5 | 0.95988 | 0.92055 | -0.039338 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | RILEY 5 | 0.95988 | 0.92055 | -0.039338 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | RILEY 5 | 0.95988 | 0.92055 | -0.039338 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | RILEY 5 | 0.95988 | 0.92055 | -0.039338 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | RILEY 5 | 0.95988 | 0.92055 | -0.039338 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | RILEY 5 | 0.95988 | 0.92055 | -0.039338 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | RILEY 5 | 0.95988 | 0.92055 | -0.039338 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | RILEY 5 | 0.95988 | 0.92055 | -0.039338 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | RILEY 5 | 0.95988 | 0.92055 | -0.039338 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | RILEY 5 | 0.95988 | 0.92055 | -0.039338 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | RILEY 5 | 0.95988 | 0.92055 | -0.039338 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | RILEY 5 | 0.95988 | 0.92055 | -0.039338 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | RILEY 5 | 0.96854 | 0.92456 | -0.043981 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | RILEY 5 | 0.96854 | 0.92456 | -0.043981 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | RILEY 5 | 0.96854 | 0.92456 | -0.043981 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | RILEY 5 | 0.96854 | 0.92456 | -0.043981 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | RILEY 5 | 0.96854 | 0.92456 | -0.043981 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | RILEY 5 | 0.96854 | 0.92456 | -0.043981 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | RILEY 5 | 0.96854 | 0.92456 | -0.043981 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | RILEY 5 | 0.96854 | 0.92456 | -0.043981 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | RILEY 5 | 0.96854 | 0.92456 | -0.043981 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | RILEY 5 | 0.96854 | 0.92456 | -0.043981 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | RILEY 5 | 0.96854 | 0.92456 | -0.043981 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | RILEY 5 | 0.96854 | 0.92456 | -0.043981 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | RILEY 5 | 0.96854 | 0.92456 | -0.043981 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | RILEY 5 | 0.96854 | 0.92456 | -0.043981 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | RILEY 5 | 0.96854 | 0.92456 | -0.043981 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | RILEY 5 | 0.96854 | 0.92456 | -0.043981 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | RILEY 5 | 0.96854 | 0.92456 | -0.043981 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | RILEY 5 | 0.96854 | 0.92456 | -0.043981 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | RILEY 5 | 0.96854 | 0.92456 | -0.043981 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | RILEY 5 | 0.96854 | 0.92456 | -0.043981 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | RILEY 5 | 0.97089 | 0.90176 | -0.069137 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | RILEY 5 | 0.97089 | 0.90176 | -0.069137 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | RILEY 5 | 0.97089 | 0.90176 | -0.069137 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | RILEY 5 | 0.97089 | 0.90176 | -0.069137 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | RILEY 5 | 0.97089 | 0.90176 | -0.069137 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | RILEY 5 | 0.97089 | 0.90176 | -0.069137 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | RILEY 5 | 0.97089 | 0.90176 | -0.069137 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | RILEY 5 | 0.97089 | 0.90176 | -0.069137 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | RILEY 5 | 0.97089 | 0.90176 | -0.069137 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | RILEY 5 | 0.97089 | 0.90176 | -0.069137 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | RILEY 5 | 0.97089 | 0.90176 | -0.069137 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | RILEY 5 | 0.97089 | 0.90176 | -0.069137 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | RILEY 5 | 0.97089 | 0.90176 | -0.069137 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | RILEY 5 | 0.97089 | 0.90176 | -0.069137 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | RILEY 5 | 0.97089 | 0.90176 | -0.069137 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | RILEY 5 | 0.97089 | 0.90176 | -0.069137 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | RILEY 5 | 0.97089 | 0.90176 | -0.069137 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | RILEY 5 | 0.97089 | 0.90176 | -0.069137 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | RILEY 5 | 0.97089 | 0.90176 | -0.069137 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | RILEY 5 | 0.97089 | 0.90176 | -0.069137 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | RILEY 5 | 0.97089 | 0.90176 | -0.069137 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | RILEY 5 | 0.97089 | 0.90176 | -0.069137 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | RILEY 5 | 0.97089 | 0.90176 | -0.069137 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | RILEY 5 | 0.97089 | 0.90176 | -0.069137 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | RILEY 5 | 0.97089 | 0.90176 | -0.069137 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | RILEY 5 | 0.97089 | 0.90176 | -0.069137 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | RILEY 5 | 0.97089 | 0.90176 | -0.069137 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | RILEY 5 | 0.97089 | 0.90176 | -0.069137 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | RILEY 5 | 0.96467 | 0.92754 | -0.037134 |  | 0.93 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | RILEY 5 | 0.96467 | 0.92754 | -0.037134 |  | 0.93 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | RILEY 5 | 0.96467 | 0.92754 | -0.037134 |  | 0.93 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | RILEY 5 | 0.96467 | 0.92754 | -0.037134 |  | 0.93 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | RILEY 5 | 0.96467 | 0.92754 | -0.037134 |  | 0.93 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | RILEY 5 | 0.96467 | 0.92754 | -0.037134 |  | 0.93 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | RILEY 5 | 0.96467 | 0.92754 | -0.037134 |  | 0.93 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | RILEY 5 | 0.96467 | 0.92754 | -0.037134 |  | 0.93 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | RILEY 5 | 0.96467 | 0.92754 | -0.037134 |  | 0.93 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | RILEY 5 | 0.96467 | 0.92754 | -0.037134 |  | 0.93 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | RILEY 5 | 0.96467 | 0.92754 | -0.037134 |  | 0.93 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | RILEY 5 | 0.96467 | 0.92754 | -0.037134 |  | 0.93 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | RILEY 5 | 0.96467 | 0.92754 | -0.037134 |  | 0.93 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | RILEY 5 | 0.96467 | 0.92754 | -0.037134 |  | 0.93 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | RILEY 5 | 0.96467 | 0.92754 | -0.037134 |  | 0.93 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | RILEY 5 | 0.96467 | 0.92754 | -0.037134 |  | 0.93 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | RILEY 5 | 0.96467 | 0.92754 | -0.037134 |  | 0.93 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | RILEY 5 | 0.96467 | 0.92754 | -0.037134 |  | 0.93 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | RILEY 5 | 0.96467 | 0.92754 | -0.037134 |  | 0.93 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | RILEY 5 | 0.96467 | 0.92754 | -0.037134 |  | 0.93 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | RNM393 5 | 0.97327 | 0.92184 | -0.051425 |  | 0.925 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | RNM393 5 | 0.97327 | 0.92184 | -0.051425 |  | 0.925 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | RNM393 5 | 0.97327 | 0.92184 | -0.051425 |  | 0.925 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | RNM393 5 | 0.97327 | 0.92184 | -0.051425 |  | 0.925 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | RNM393 5 | 0.97327 | 0.92184 | -0.051425 |  | 0.925 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | RNM393 5 | 0.97327 | 0.92184 | -0.051425 |  | 0.925 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | RNM393 5 | 0.97327 | 0.92184 | -0.051425 |  | 0.925 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | RNM393 5 | 0.97327 | 0.92184 | -0.051425 |  | 0.925 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | RNM393 5 | 0.97327 | 0.92184 | -0.051425 |  | 0.925 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | RNM393 5 | 0.97327 | 0.92184 | -0.051425 |  | 0.925 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | RNM393 5 | 0.97327 | 0.92184 | -0.051425 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | RNM393 5 | 0.97327 | 0.92184 | -0.051425 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | RNM393 5 | 0.97327 | 0.92184 | -0.051425 |  | 0.925 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | RNM393 5 | 0.97327 | 0.92184 | -0.051425 |  | 0.925 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | RNM393 5 | 0.97327 | 0.92184 | -0.051425 |  | 0.925 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | RNM393 5 | 0.9739 | 0.92286 | -0.051044 |  | 0.925 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | RNM393 5 | 0.9739 | 0.92286 | -0.051044 |  | 0.925 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | RNM393 5 | 0.9739 | 0.92286 | -0.051044 |  | 0.925 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | RNM393 5 | 0.9739 | 0.92286 | -0.051044 |  | 0.925 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | RNM393 5 | 0.9739 | 0.92286 | -0.051044 |  | 0.925 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | RNM393 5 | 0.9739 | 0.92286 | -0.051044 |  | 0.925 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | RNM393 5 | 0.9739 | 0.92286 | -0.051044 |  | 0.925 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | RNM393 5 | 0.9739 | 0.92286 | -0.051044 |  | 0.925 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | RNM393 5 | 0.9739 | 0.92286 | -0.051044 |  | 0.925 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | RNM393 5 | 0.9739 | 0.92286 | -0.051044 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | RNM393 5 | 0.9739 | 0.92286 | -0.051044 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | RNM393 5 | 0.9739 | 0.92286 | -0.051044 |  | 0.925 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | RNM393 5 | 0.9739 | 0.92286 | -0.051044 |  | 0.925 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | RNM393 5 | 0.9739 | 0.92286 | -0.051044 |  | 0.925 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ROEPARK5 | 0.98458 | 0.92194 | -0.06264 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ROEPARK5 | 0.98458 | 0.92194 | -0.06264 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ROEPARK5 | 0.98458 | 0.92194 | -0.06264 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ROEPARK5 | 0.98458 | 0.92194 | -0.06264 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ROEPARK5 | 0.98458 | 0.92194 | -0.06264 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ROEPARK5 | 0.98458 | 0.92194 | -0.06264 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ROEPARK5 | 0.98458 | 0.92194 | -0.06264 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | ROEPARK5 | 0.98458 | 0.92194 | -0.06264 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | ROEPARK5 | 0.98458 | 0.92194 | -0.06264 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ROEPARK5 | 0.98458 | 0.92194 | -0.06264 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ROEPARK5 | 0.98458 | 0.92194 | -0.06264 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ROEPARK5 | 0.98458 | 0.92194 | -0.06264 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ROEPARK5 | 0.98458 | 0.92194 | -0.06264 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ROEPARK5 | 0.98458 | 0.92194 | -0.06264 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ROEPARK5 | 0.98458 | 0.92194 | -0.06264 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ROEPARK5 | 0.98458 | 0.92194 | -0.06264 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ROEPARK5 | 0.98458 | 0.92194 | -0.06264 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ROEPARK5 | 0.98458 | 0.92194 | -0.06264 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | ROEPARK5 | 0.98458 | 0.92194 | -0.06264 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | ROEPARK5 | 0.98458 | 0.92194 | -0.06264 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ROEPARK5 | 0.98458 | 0.92194 | -0.06264 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ROEPARK5 | 0.98458 | 0.92194 | -0.06264 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | ROEPARK5 | 0.98458 | 0.92194 | -0.06264 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ROEPARK5 | 0.98458 | 0.92194 | -0.06264 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ROEPARK5 | 0.98458 | 0.92194 | -0.06264 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ROEPARK5 | 0.98458 | 0.92194 | -0.06264 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ROEPARK5 | 0.98458 | 0.92194 | -0.06264 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | ROEPARK5 | 0.98458 | 0.92194 | -0.06264 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | S.OTTWA5 | 1.0104 | 0.92027 | -0.090133 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | S.OTTWA5 | 1.0104 | 0.92027 | -0.090133 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | S.OTTWA5 | 1.0104 | 0.92027 | -0.090133 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | S.OTTWA5 | 1.0104 | 0.92027 | -0.090133 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | S.OTTWA5 | 1.0104 | 0.92027 | -0.090133 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | S.OTTWA5 | 1.0104 | 0.92027 | -0.090133 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | S.OTTWA5 | 1.0104 | 0.92027 | -0.090133 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | S.OTTWA5 | 1.0104 | 0.92027 | -0.090133 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | S.OTTWA5 | 1.0104 | 0.92027 | -0.090133 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | S.OTTWA5 | 1.0104 | 0.92027 | -0.090133 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | S.OTTWA5 | 1.0104 | 0.92027 | -0.090133 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | S.OTTWA5 | 1.0104 | 0.92027 | -0.090133 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | S.OTTWA5 | 1.0104 | 0.92027 | -0.090133 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | S.OTTWA5 | 1.0104 | 0.92027 | -0.090133 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | S.OTTWA5 | 1.0104 | 0.92027 | -0.090133 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | S.OTTWA5 | 1.0104 | 0.92027 | -0.090133 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | S.OTTWA5 | 1.0104 | 0.92027 | -0.090133 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | S.OTTWA5 | 1.0104 | 0.92027 | -0.090133 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | S.OTTWA5 | 1.0104 | 0.92027 | -0.090133 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | S.OTTWA5 | 1.0104 | 0.92027 | -0.090133 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | S.OTTWA5 | 1.0104 | 0.92027 | -0.090133 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | S.OTTWA5 | 1.0104 | 0.92027 | -0.090133 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | S.OTTWA5 | 1.0104 | 0.92027 | -0.090133 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | S.OTTWA5 | 1.0104 | 0.92027 | -0.090133 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | S.OTTWA5 | 1.0104 | 0.92027 | -0.090133 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | S.OTTWA5 | 1.0104 | 0.92027 | -0.090133 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | S.OTTWA5 | 1.0104 | 0.92027 | -0.090133 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | S.OTTWA5 | 1.0104 | 0.92027 | -0.090133 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SCRANTN3 | 0.96254 | 0.89414 | -0.068406 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | SCRANTN3 | 0.96254 | 0.89414 | -0.068406 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SCRANTN3 | 0.96254 | 0.89414 | -0.068406 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SCRANTN3 | 0.96254 | 0.89414 | -0.068406 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SCRANTN3 | 0.96254 | 0.89414 | -0.068406 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | SCRANTN3 | 0.96254 | 0.89414 | -0.068406 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SCRANTN3 | 0.96254 | 0.89414 | -0.068406 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | SCRANTN3 | 0.96254 | 0.89414 | -0.068406 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | SCRANTN3 | 0.96254 | 0.89414 | -0.068406 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SCRANTN3 | 0.96254 | 0.89414 | -0.068406 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SCRANTN3 | 0.96254 | 0.89414 | -0.068406 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SCRANTN3 | 0.96254 | 0.89414 | -0.068406 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SCRANTN3 | 0.96254 | 0.89414 | -0.068406 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SCRANTN3 | 0.96254 | 0.89414 | -0.068406 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SCRANTN3 | 0.96254 | 0.89414 | -0.068406 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SCRANTN3 | 0.96254 | 0.89414 | -0.068406 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SCRANTN3 | 0.96254 | 0.89414 | -0.068406 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SCRANTN3 | 0.96254 | 0.89414 | -0.068406 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | SCRANTN3 | 0.96254 | 0.89414 | -0.068406 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | SCRANTN3 | 0.96254 | 0.89414 | -0.068406 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SCRANTN3 | 0.96254 | 0.89414 | -0.068406 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SCRANTN3 | 0.96254 | 0.89414 | -0.068406 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | SCRANTN3 | 0.96254 | 0.89414 | -0.068406 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SCRANTN3 | 0.96254 | 0.89414 | -0.068406 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SCRANTN3 | 0.96254 | 0.89414 | -0.068406 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SCRANTN3 | 0.96254 | 0.89414 | -0.068406 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SCRANTN3 | 0.96254 | 0.89414 | -0.068406 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | SCRANTN3 | 0.96254 | 0.89414 | -0.068406 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | SEGUIN 3 | 0.96544 | 0.89933 | -0.066107 |  | 0.9 | 1.05 | 0.041569 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SEGUIN 3 | 0.96544 | 0.89933 | -0.066107 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SEGUIN 3 | 0.96544 | 0.89933 | -0.066107 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SEGUIN 3 | 0.96544 | 0.89933 | -0.066107 |  | 0.9 | 1.05 | 0.03222 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SEGUIN 3 | 0.96544 | 0.89933 | -0.066107 |  | 0.9 | 1.05 | 0.030633 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SEGUIN 3 | 0.96544 | 0.89933 | -0.066107 |  | 0.9 | 1.05 | 0.030061 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SEGUIN 3 | 0.96544 | 0.89933 | -0.066107 |  | 0.9 | 1.05 | 0.031207 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SEOTTWA5 | 1.0104 | 0.9209 | -0.08945 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | SEOTTWA5 | 1.0104 | 0.9209 | -0.08945 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SEOTTWA5 | 1.0104 | 0.9209 | -0.08945 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SEOTTWA5 | 1.0104 | 0.9209 | -0.08945 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SEOTTWA5 | 1.0104 | 0.9209 | -0.08945 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | SEOTTWA5 | 1.0104 | 0.9209 | -0.08945 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SEOTTWA5 | 1.0104 | 0.9209 | -0.08945 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | SEOTTWA5 | 1.0104 | 0.9209 | -0.08945 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | SEOTTWA5 | 1.0104 | 0.9209 | -0.08945 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SEOTTWA5 | 1.0104 | 0.9209 | -0.08945 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SEOTTWA5 | 1.0104 | 0.9209 | -0.08945 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SEOTTWA5 | 1.0104 | 0.9209 | -0.08945 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SEOTTWA5 | 1.0104 | 0.9209 | -0.08945 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SEOTTWA5 | 1.0104 | 0.9209 | -0.08945 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SEOTTWA5 | 1.0104 | 0.9209 | -0.08945 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SEOTTWA5 | 1.0104 | 0.9209 | -0.08945 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SEOTTWA5 | 1.0104 | 0.9209 | -0.08945 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SEOTTWA5 | 1.0104 | 0.9209 | -0.08945 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | SEOTTWA5 | 1.0104 | 0.9209 | -0.08945 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | SEOTTWA5 | 1.0104 | 0.9209 | -0.08945 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SEOTTWA5 | 1.0104 | 0.9209 | -0.08945 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SEOTTWA5 | 1.0104 | 0.9209 | -0.08945 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | SEOTTWA5 | 1.0104 | 0.9209 | -0.08945 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SEOTTWA5 | 1.0104 | 0.9209 | -0.08945 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SEOTTWA5 | 1.0104 | 0.9209 | -0.08945 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SEOTTWA5 | 1.0104 | 0.9209 | -0.08945 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SEOTTWA5 | 1.0104 | 0.9209 | -0.08945 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | SEOTTWA5 | 1.0104 | 0.9209 | -0.08945 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SHALE 7 | 0.98736 | 0.94337 | -0.043984 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | SHALE 7 | 0.98736 | 0.94337 | -0.043984 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SHALE 7 | 0.98736 | 0.94337 | -0.043984 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SHALE 7 | 0.98736 | 0.94337 | -0.043984 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SHALE 7 | 0.98736 | 0.94337 | -0.043984 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | SHALE 7 | 0.98736 | 0.94337 | -0.043984 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SHALE 7 | 0.98736 | 0.94337 | -0.043984 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | SHALE 7 | 0.98736 | 0.94337 | -0.043984 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | SHALE 7 | 0.98736 | 0.94337 | -0.043984 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SHALE 7 | 0.98736 | 0.94337 | -0.043984 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SHALE 7 | 0.98736 | 0.94337 | -0.043984 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SHALE 7 | 0.98736 | 0.94337 | -0.043984 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SHALE 7 | 0.98736 | 0.94337 | -0.043984 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SHALE 7 | 0.98736 | 0.94337 | -0.043984 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SHALE 7 | 0.98736 | 0.94337 | -0.043984 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SHALE 7 | 0.98736 | 0.94337 | -0.043984 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SHALE 7 | 0.98736 | 0.94337 | -0.043984 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SHALE 7 | 0.98736 | 0.94337 | -0.043984 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | SHALE 7 | 0.98736 | 0.94337 | -0.043984 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | SHALE 7 | 0.98736 | 0.94337 | -0.043984 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SHALE 7 | 0.98736 | 0.94337 | -0.043984 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SHALE 7 | 0.98736 | 0.94337 | -0.043984 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | SHALE 7 | 0.98736 | 0.94337 | -0.043984 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SHALE 7 | 0.98736 | 0.94337 | -0.043984 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SHALE 7 | 0.98736 | 0.94337 | -0.043984 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SHALE 7 | 0.98736 | 0.94337 | -0.043984 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SHALE 7 | 0.98736 | 0.94337 | -0.043984 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | SHALE 7 | 0.98736 | 0.94337 | -0.043984 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | SHARNSP3 | 0.96302 | 0.89487 | -0.068149 |  | 0.9 | 1.05 | 0.064516 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 3.3 MVAR switched shunt at CHASE 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | SHARNSP3 | 0.92701 | 0.85918 | -0.067831 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SHARNSP3 | 0.92701 | 0.85918 | -0.067831 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | SHARNSP3 | 0.93902 | 0.86518 | -0.073834 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SHARNSP3 | 0.93902 | 0.86518 | -0.073834 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | SHARNSP3 | 0.93902 | 0.86518 | -0.073834 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SHARNSP3 | 0.93902 | 0.86518 | -0.073834 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | SHARNSP3 | 0.93902 | 0.86518 | -0.073835 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SHARNSP3 | 0.93902 | 0.86518 | -0.073835 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SHAWNEE5 | 0.98265 | 0.92268 | -0.059968 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | SHAWNEE5 | 0.98265 | 0.92268 | -0.059968 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SHAWNEE5 | 0.98265 | 0.92268 | -0.059968 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SHAWNEE5 | 0.98265 | 0.92268 | -0.059968 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SHAWNEE5 | 0.98265 | 0.92268 | -0.059968 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | SHAWNEE5 | 0.98265 | 0.92268 | -0.059968 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SHAWNEE5 | 0.98265 | 0.92268 | -0.059968 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | SHAWNEE5 | 0.98265 | 0.92268 | -0.059968 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | SHAWNEE5 | 0.98265 | 0.92268 | -0.059968 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SHAWNEE5 | 0.98265 | 0.92268 | -0.059968 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SHAWNEE5 | 0.98265 | 0.92268 | -0.059968 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SHAWNEE5 | 0.98265 | 0.92268 | -0.059968 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SHAWNEE5 | 0.98265 | 0.92268 | -0.059968 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SHAWNEE5 | 0.98265 | 0.92268 | -0.059968 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SHAWNEE5 | 0.98265 | 0.92268 | -0.059968 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SHAWNEE5 | 0.98265 | 0.92268 | -0.059968 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SHAWNEE5 | 0.98265 | 0.92268 | -0.059968 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SHAWNEE5 | 0.98265 | 0.92268 | -0.059968 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | SHAWNEE5 | 0.98265 | 0.92268 | -0.059968 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | SHAWNEE5 | 0.98265 | 0.92268 | -0.059968 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SHAWNEE5 | 0.98265 | 0.92268 | -0.059968 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SHAWNEE5 | 0.98265 | 0.92268 | -0.059968 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | SHAWNEE5 | 0.98265 | 0.92268 | -0.059968 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SHAWNEE5 | 0.98265 | 0.92268 | -0.059968 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SHAWNEE5 | 0.98265 | 0.92268 | -0.059968 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SHAWNEE5 | 0.98265 | 0.92268 | -0.059968 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SHAWNEE5 | 0.98265 | 0.92268 | -0.059968 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | SHAWNEE5 | 0.98265 | 0.92268 | -0.059968 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SHWNMSN5 | 0.98029 | 0.91809 | -0.062202 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | SHWNMSN5 | 0.98029 | 0.91809 | -0.062202 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SHWNMSN5 | 0.98029 | 0.91809 | -0.062202 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SHWNMSN5 | 0.98029 | 0.91809 | -0.062202 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SHWNMSN5 | 0.98029 | 0.91809 | -0.062202 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | SHWNMSN5 | 0.98029 | 0.91809 | -0.062202 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SHWNMSN5 | 0.98029 | 0.91809 | -0.062202 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | SHWNMSN5 | 0.98029 | 0.91809 | -0.062202 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | SHWNMSN5 | 0.98029 | 0.91809 | -0.062202 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SHWNMSN5 | 0.98029 | 0.91809 | -0.062202 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SHWNMSN5 | 0.98029 | 0.91809 | -0.062202 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SHWNMSN5 | 0.98029 | 0.91809 | -0.062202 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SHWNMSN5 | 0.98029 | 0.91809 | -0.062202 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SHWNMSN5 | 0.98029 | 0.91809 | -0.062202 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SHWNMSN5 | 0.98029 | 0.91809 | -0.062202 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SHWNMSN5 | 0.98029 | 0.91809 | -0.062202 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SHWNMSN5 | 0.98029 | 0.91809 | -0.062202 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SHWNMSN5 | 0.98029 | 0.91809 | -0.062202 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | SHWNMSN5 | 0.98029 | 0.91809 | -0.062202 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | SHWNMSN5 | 0.98029 | 0.91809 | -0.062202 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SHWNMSN5 | 0.98029 | 0.91809 | -0.062202 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SHWNMSN5 | 0.98029 | 0.91809 | -0.062202 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | SHWNMSN5 | 0.98029 | 0.91809 | -0.062202 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SHWNMSN5 | 0.98029 | 0.91809 | -0.062202 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SHWNMSN5 | 0.98029 | 0.91809 | -0.062202 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SHWNMSN5 | 0.98029 | 0.91809 | -0.062202 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SHWNMSN5 | 0.98029 | 0.91809 | -0.062202 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | SHWNMSN5 | 0.98029 | 0.91809 | -0.062202 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SIBLEYRD2 | 0.97444 | 0.9097 | -0.064743 |  | 0.925 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | SIBLEYRD2 | 0.97444 | 0.9097 | -0.064743 |  | 0.925 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SIBLEYRD2 | 0.97444 | 0.9097 | -0.064743 |  | 0.925 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SIBLEYRD2 | 0.97444 | 0.9097 | -0.064743 |  | 0.925 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SIBLEYRD2 | 0.97444 | 0.9097 | -0.064743 |  | 0.925 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SIBLEYRD2 | 0.97444 | 0.9097 | -0.064743 |  | 0.925 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SIBLEYRD2 | 0.97444 | 0.9097 | -0.064743 |  | 0.925 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SIBLEYRD2 | 0.97444 | 0.9097 | -0.064743 |  | 0.925 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SIBLEYRD2 | 0.97444 | 0.9097 | -0.064743 |  | 0.925 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SIBLEYRD2 | 0.97444 | 0.9097 | -0.064743 |  | 0.925 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | SIBLEYRD2 | 0.97444 | 0.9097 | -0.064743 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | SIBLEYRD2 | 0.97444 | 0.9097 | -0.064743 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SIBLEYRD2 | 0.97444 | 0.9097 | -0.064743 |  | 0.925 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SIBLEYRD2 | 0.97444 | 0.9097 | -0.064743 |  | 0.925 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SIBLEYRD2 | 0.97444 | 0.9097 | -0.064743 |  | 0.925 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | SIBLEYRD2 | 0.97491 | 0.91062 | -0.064294 |  | 0.925 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SIBLEYRD2 | 0.97491 | 0.91062 | -0.064294 |  | 0.925 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SIBLEYRD2 | 0.97491 | 0.91062 | -0.064294 |  | 0.925 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SIBLEYRD2 | 0.97491 | 0.91062 | -0.064294 |  | 0.925 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SIBLEYRD2 | 0.97491 | 0.91062 | -0.064294 |  | 0.925 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SIBLEYRD2 | 0.97491 | 0.91062 | -0.064294 |  | 0.925 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SIBLEYRD2 | 0.97491 | 0.91062 | -0.064294 |  | 0.925 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SIBLEYRD2 | 0.97491 | 0.91062 | -0.064294 |  | 0.925 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SIBLEYRD2 | 0.97491 | 0.91062 | -0.064294 |  | 0.925 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | SIBLEYRD2 | 0.97491 | 0.91062 | -0.064294 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | SIBLEYRD2 | 0.97491 | 0.91062 | -0.064294 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SIBLEYRD2 | 0.97491 | 0.91062 | -0.064294 |  | 0.925 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SIBLEYRD2 | 0.97491 | 0.91062 | -0.064294 |  | 0.925 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SIBLEYRD2 | 0.97491 | 0.91062 | -0.064294 |  | 0.925 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SIBLEYRD2 | 0.97509 | 0.91434 | -0.060753 |  | 0.925 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | SIBLEYRD2 | 0.97509 | 0.91434 | -0.060753 |  | 0.925 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SIBLEYRD2 | 0.97509 | 0.91434 | -0.060753 |  | 0.925 | 1.05 | 0.055405 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SIBLEYRD2 | 0.97509 | 0.91434 | -0.060753 |  | 0.925 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SIBLEYRD2 | 0.97509 | 0.91434 | -0.060753 |  | 0.925 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SIBLEYRD2 | 0.97509 | 0.91434 | -0.060753 |  | 0.925 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SIBLEYRD2 | 0.97509 | 0.91434 | -0.060753 |  | 0.925 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SIBLEYRD2 | 0.97509 | 0.91434 | -0.060753 |  | 0.925 | 1.05 | 0.082012 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SIBLEYRD2 | 0.97509 | 0.91434 | -0.060753 |  | 0.925 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SIBLEYRD2 | 0.97509 | 0.91434 | -0.060753 |  | 0.925 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | SIBLEYRD2 | 0.97509 | 0.91434 | -0.060753 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | SIBLEYRD2 | 0.97509 | 0.91434 | -0.060753 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SIBLEYRD2 | 0.97509 | 0.91434 | -0.060753 |  | 0.925 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SIBLEYRD2 | 0.97509 | 0.91434 | -0.060753 |  | 0.925 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SIBLEYRD2 | 0.97509 | 0.91434 | -0.060753 |  | 0.925 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SIBLEYRD5 | 0.97519 | 0.91062 | -0.064571 |  | 0.925 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | SIBLEYRD5 | 0.97519 | 0.91062 | -0.064571 |  | 0.925 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SIBLEYRD5 | 0.97519 | 0.91062 | -0.064571 |  | 0.925 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SIBLEYRD5 | 0.97519 | 0.91062 | -0.064571 |  | 0.925 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SIBLEYRD5 | 0.97519 | 0.91062 | -0.064571 |  | 0.925 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SIBLEYRD5 | 0.97519 | 0.91062 | -0.064571 |  | 0.925 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SIBLEYRD5 | 0.97519 | 0.91062 | -0.064571 |  | 0.925 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SIBLEYRD5 | 0.97519 | 0.91062 | -0.064571 |  | 0.925 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SIBLEYRD5 | 0.97519 | 0.91062 | -0.064571 |  | 0.925 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SIBLEYRD5 | 0.97519 | 0.91062 | -0.064571 |  | 0.925 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | SIBLEYRD5 | 0.97519 | 0.91062 | -0.064571 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | SIBLEYRD5 | 0.97519 | 0.91062 | -0.064571 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SIBLEYRD5 | 0.97519 | 0.91062 | -0.064571 |  | 0.925 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SIBLEYRD5 | 0.97519 | 0.91062 | -0.064571 |  | 0.925 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SIBLEYRD5 | 0.97519 | 0.91062 | -0.064571 |  | 0.925 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | SIBLEYRD5 | 0.97567 | 0.91154 | -0.064123 |  | 0.925 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SIBLEYRD5 | 0.97567 | 0.91154 | -0.064123 |  | 0.925 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SIBLEYRD5 | 0.97567 | 0.91154 | -0.064123 |  | 0.925 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SIBLEYRD5 | 0.97567 | 0.91154 | -0.064123 |  | 0.925 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SIBLEYRD5 | 0.97567 | 0.91154 | -0.064123 |  | 0.925 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SIBLEYRD5 | 0.97567 | 0.91154 | -0.064123 |  | 0.925 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SIBLEYRD5 | 0.97567 | 0.91154 | -0.064123 |  | 0.925 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SIBLEYRD5 | 0.97567 | 0.91154 | -0.064123 |  | 0.925 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SIBLEYRD5 | 0.97567 | 0.91154 | -0.064123 |  | 0.925 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | SIBLEYRD5 | 0.97567 | 0.91154 | -0.064123 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | SIBLEYRD5 | 0.97567 | 0.91154 | -0.064123 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SIBLEYRD5 | 0.97567 | 0.91154 | -0.064123 |  | 0.925 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SIBLEYRD5 | 0.97567 | 0.91154 | -0.064123 |  | 0.925 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SIBLEYRD5 | 0.97567 | 0.91154 | -0.064123 |  | 0.925 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SIBLEYRD5 | 0.97584 | 0.91525 | -0.060593 |  | 0.925 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | SIBLEYRD5 | 0.97584 | 0.91525 | -0.060593 |  | 0.925 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SIBLEYRD5 | 0.97584 | 0.91525 | -0.060593 |  | 0.925 | 1.05 | 0.055405 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SIBLEYRD5 | 0.97584 | 0.91525 | -0.060593 |  | 0.925 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SIBLEYRD5 | 0.97584 | 0.91525 | -0.060593 |  | 0.925 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SIBLEYRD5 | 0.97584 | 0.91525 | -0.060593 |  | 0.925 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SIBLEYRD5 | 0.97584 | 0.91525 | -0.060593 |  | 0.925 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SIBLEYRD5 | 0.97584 | 0.91525 | -0.060593 |  | 0.925 | 1.05 | 0.082012 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SIBLEYRD5 | 0.97584 | 0.91525 | -0.060593 |  | 0.925 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SIBLEYRD5 | 0.97584 | 0.91525 | -0.060593 |  | 0.925 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | SIBLEYRD5 | 0.97584 | 0.91525 | -0.060593 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | SIBLEYRD5 | 0.97584 | 0.91525 | -0.060593 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SIBLEYRD5 | 0.97584 | 0.91525 | -0.060593 |  | 0.925 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SIBLEYRD5 | 0.97584 | 0.91525 | -0.060593 |  | 0.925 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SIBLEYRD5 | 0.97584 | 0.91525 | -0.060593 |  | 0.925 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SOUTHTN3 | 0.96251 | 0.91897 | -0.04354 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SOUTHTN3 | 0.96251 | 0.91897 | -0.04354 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SOUTHTN3 | 0.96251 | 0.91897 | -0.04354 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SOUTHTN3 | 0.96251 | 0.91897 | -0.04354 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SOUTHTN3 | 0.96251 | 0.91897 | -0.04354 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SOUTHTN3 | 0.96251 | 0.91897 | -0.04354 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SOUTHTN3 | 0.96251 | 0.91897 | -0.04354 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SOUTHTN3 | 0.96251 | 0.91897 | -0.04354 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SOUTHTN3 | 0.96251 | 0.91897 | -0.04354 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SOUTHTN3 | 0.96251 | 0.91897 | -0.04354 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SOUTHTN3 | 0.96251 | 0.91897 | -0.04354 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SOUTHTN3 | 0.96251 | 0.91897 | -0.04354 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SOUTHTN3 | 0.96251 | 0.91897 | -0.04354 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SOUTHTN3 | 0.96251 | 0.91897 | -0.04354 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SOUTHTN3 | 0.96251 | 0.91897 | -0.04354 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SOUTHTN3 | 0.96251 | 0.91897 | -0.04354 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SOUTHTN3 | 0.96251 | 0.91897 | -0.04354 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SOUTHTN3 | 0.96251 | 0.91897 | -0.04354 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SOUTHTN3 | 0.96251 | 0.91897 | -0.04354 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SOUTHTN3 | 0.96251 | 0.91897 | -0.04354 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SOUTHTN3 | 0.97318 | 0.92541 | -0.047768 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SOUTHTN3 | 0.97318 | 0.92541 | -0.047768 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SOUTHTN3 | 0.97318 | 0.92541 | -0.047768 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SOUTHTN3 | 0.97318 | 0.92541 | -0.047768 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SOUTHTN3 | 0.97318 | 0.92541 | -0.047768 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SOUTHTN3 | 0.97318 | 0.92541 | -0.047768 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SOUTHTN3 | 0.97318 | 0.92541 | -0.047768 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SOUTHTN3 | 0.97318 | 0.92541 | -0.047768 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SOUTHTN3 | 0.97318 | 0.92541 | -0.047768 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SOUTHTN3 | 0.97318 | 0.92541 | -0.047768 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SOUTHTN3 | 0.97318 | 0.92541 | -0.047768 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SOUTHTN3 | 0.97318 | 0.92541 | -0.047768 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SOUTHTN3 | 0.97318 | 0.92541 | -0.047768 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SOUTHTN3 | 0.97318 | 0.92541 | -0.047768 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SOUTHTN3 | 0.97318 | 0.92541 | -0.047768 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SOUTHTN3 | 0.97318 | 0.92541 | -0.047768 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SOUTHTN3 | 0.97318 | 0.92541 | -0.047768 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SOUTHTN3 | 0.97318 | 0.92541 | -0.047768 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SOUTHTN3 | 0.97318 | 0.92541 | -0.047768 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SOUTHTN3 | 0.97318 | 0.92541 | -0.047768 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SOUTHTN3 | 0.97828 | 0.90719 | -0.071093 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | SOUTHTN3 | 0.97828 | 0.90719 | -0.071093 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SOUTHTN3 | 0.97828 | 0.90719 | -0.071093 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SOUTHTN3 | 0.97828 | 0.90719 | -0.071093 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SOUTHTN3 | 0.97828 | 0.90719 | -0.071093 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | SOUTHTN3 | 0.97828 | 0.90719 | -0.071093 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SOUTHTN3 | 0.97828 | 0.90719 | -0.071093 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | SOUTHTN3 | 0.97828 | 0.90719 | -0.071093 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | SOUTHTN3 | 0.97828 | 0.90719 | -0.071093 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SOUTHTN3 | 0.97828 | 0.90719 | -0.071093 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SOUTHTN3 | 0.97828 | 0.90719 | -0.071093 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SOUTHTN3 | 0.97828 | 0.90719 | -0.071093 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SOUTHTN3 | 0.97828 | 0.90719 | -0.071093 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SOUTHTN3 | 0.97828 | 0.90719 | -0.071093 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SOUTHTN3 | 0.97828 | 0.90719 | -0.071093 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SOUTHTN3 | 0.97828 | 0.90719 | -0.071093 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SOUTHTN3 | 0.97828 | 0.90719 | -0.071093 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SOUTHTN3 | 0.97828 | 0.90719 | -0.071093 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | SOUTHTN3 | 0.97828 | 0.90719 | -0.071093 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | SOUTHTN3 | 0.97828 | 0.90719 | -0.071093 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SOUTHTN3 | 0.97828 | 0.90719 | -0.071093 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SOUTHTN3 | 0.97828 | 0.90719 | -0.071093 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | SOUTHTN3 | 0.97828 | 0.90719 | -0.071093 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SOUTHTN3 | 0.97828 | 0.90719 | -0.071093 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SOUTHTN3 | 0.97828 | 0.90719 | -0.071093 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SOUTHTN3 | 0.97828 | 0.90719 | -0.071093 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SOUTHTN3 | 0.97828 | 0.90719 | -0.071093 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | SOUTHTN3 | 0.97828 | 0.90719 | -0.071093 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SOUTHTN3 | 0.96865 | 0.92901 | -0.039638 |  | 0.93 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SOUTHTN3 | 0.96865 | 0.92901 | -0.039638 |  | 0.93 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SOUTHTN3 | 0.96865 | 0.92901 | -0.039638 |  | 0.93 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SOUTHTN3 | 0.96865 | 0.92901 | -0.039638 |  | 0.93 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SOUTHTN3 | 0.96865 | 0.92901 | -0.039638 |  | 0.93 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SOUTHTN3 | 0.96865 | 0.92901 | -0.039638 |  | 0.93 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SOUTHTN3 | 0.96865 | 0.92901 | -0.039638 |  | 0.93 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SOUTHTN3 | 0.96865 | 0.92901 | -0.039638 |  | 0.93 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SOUTHTN3 | 0.96865 | 0.92901 | -0.039638 |  | 0.93 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SOUTHTN3 | 0.96865 | 0.92901 | -0.039638 |  | 0.93 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SOUTHTN3 | 0.96865 | 0.92901 | -0.039638 |  | 0.93 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SOUTHTN3 | 0.96865 | 0.92901 | -0.039638 |  | 0.93 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SOUTHTN3 | 0.96865 | 0.92901 | -0.039638 |  | 0.93 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SOUTHTN3 | 0.96865 | 0.92901 | -0.039638 |  | 0.93 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SOUTHTN3 | 0.96865 | 0.92901 | -0.039638 |  | 0.93 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SOUTHTN3 | 0.96865 | 0.92901 | -0.039638 |  | 0.93 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SOUTHTN3 | 0.96865 | 0.92901 | -0.039638 |  | 0.93 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SOUTHTN3 | 0.96865 | 0.92901 | -0.039638 |  | 0.93 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SOUTHTN3 | 0.96865 | 0.92901 | -0.039638 |  | 0.93 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SOUTHTN3 | 0.96865 | 0.92901 | -0.039638 |  | 0.93 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SPRGHL 5 | 0.96915 | 0.92423 | -0.044919 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SPRGHL 5 | 0.96915 | 0.92423 | -0.044919 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SPRGHL 5 | 0.96915 | 0.92423 | -0.044919 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SPRGHL 5 | 0.96915 | 0.92423 | -0.044919 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SPRGHL 5 | 0.96915 | 0.92423 | -0.044919 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SPRGHL 5 | 0.96915 | 0.92423 | -0.044919 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SPRGHL 5 | 0.96915 | 0.92423 | -0.044919 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SPRGHL 5 | 0.96915 | 0.92423 | -0.044919 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SPRGHL 5 | 0.96915 | 0.92423 | -0.044919 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SPRGHL 5 | 0.96915 | 0.92423 | -0.044919 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SPRGHL 5 | 0.96915 | 0.92423 | -0.044919 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SPRGHL 5 | 0.96915 | 0.92423 | -0.044919 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SPRGHL 5 | 0.96915 | 0.92423 | -0.044919 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SPRGHL 5 | 0.96915 | 0.92423 | -0.044919 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SPRGHL 5 | 0.96915 | 0.92423 | -0.044919 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SPRGHL 5 | 0.96915 | 0.92423 | -0.044919 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SPRGHL 5 | 0.96915 | 0.92423 | -0.044919 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SPRGHL 5 | 0.96915 | 0.92423 | -0.044919 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SPRGHL 5 | 0.96915 | 0.92423 | -0.044919 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SPRGHL 5 | 0.96915 | 0.92423 | -0.044919 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SPRGHL 5 | 0.98216 | 0.90104 | -0.081119 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | SPRGHL 5 | 0.98216 | 0.90104 | -0.081119 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SPRGHL 5 | 0.98216 | 0.90104 | -0.081119 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SPRGHL 5 | 0.98216 | 0.90104 | -0.081119 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SPRGHL 5 | 0.98216 | 0.90104 | -0.081119 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | SPRGHL 5 | 0.98216 | 0.90104 | -0.081119 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SPRGHL 5 | 0.98216 | 0.90104 | -0.081119 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | SPRGHL 5 | 0.98216 | 0.90104 | -0.081119 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | SPRGHL 5 | 0.98216 | 0.90104 | -0.081119 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SPRGHL 5 | 0.98216 | 0.90104 | -0.081119 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SPRGHL 5 | 0.98216 | 0.90104 | -0.081119 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SPRGHL 5 | 0.98216 | 0.90104 | -0.081119 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SPRGHL 5 | 0.98216 | 0.90104 | -0.081119 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SPRGHL 5 | 0.98216 | 0.90104 | -0.081119 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SPRGHL 5 | 0.98216 | 0.90104 | -0.081119 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SPRGHL 5 | 0.98216 | 0.90104 | -0.081119 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SPRGHL 5 | 0.98216 | 0.90104 | -0.081119 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SPRGHL 5 | 0.98216 | 0.90104 | -0.081119 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | SPRGHL 5 | 0.98216 | 0.90104 | -0.081119 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | SPRGHL 5 | 0.98216 | 0.90104 | -0.081119 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SPRGHL 5 | 0.98216 | 0.90104 | -0.081119 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SPRGHL 5 | 0.98216 | 0.90104 | -0.081119 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | SPRGHL 5 | 0.98216 | 0.90104 | -0.081119 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SPRGHL 5 | 0.98216 | 0.90104 | -0.081119 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SPRGHL 5 | 0.98216 | 0.90104 | -0.081119 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SPRGHL 5 | 0.98216 | 0.90104 | -0.081119 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SPRGHL 5 | 0.98216 | 0.90104 | -0.081119 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | SPRGHL 5 | 0.98216 | 0.90104 | -0.081119 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SPRINT15 | 0.96097 | 0.92195 | -0.039015 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SPRINT15 | 0.96097 | 0.92195 | -0.039015 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SPRINT15 | 0.96097 | 0.92195 | -0.039015 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SPRINT15 | 0.96097 | 0.92195 | -0.039015 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SPRINT15 | 0.96097 | 0.92195 | -0.039015 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SPRINT15 | 0.96097 | 0.92195 | -0.039015 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SPRINT15 | 0.96097 | 0.92195 | -0.039015 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SPRINT15 | 0.96097 | 0.92195 | -0.039015 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SPRINT15 | 0.96097 | 0.92195 | -0.039015 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SPRINT15 | 0.96097 | 0.92195 | -0.039015 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SPRINT15 | 0.96097 | 0.92195 | -0.039015 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SPRINT15 | 0.96097 | 0.92195 | -0.039015 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SPRINT15 | 0.96097 | 0.92195 | -0.039015 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SPRINT15 | 0.96097 | 0.92195 | -0.039015 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SPRINT15 | 0.96097 | 0.92195 | -0.039015 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SPRINT15 | 0.96097 | 0.92195 | -0.039015 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SPRINT15 | 0.96097 | 0.92195 | -0.039015 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SPRINT15 | 0.96097 | 0.92195 | -0.039015 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SPRINT15 | 0.96097 | 0.92195 | -0.039015 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SPRINT15 | 0.96097 | 0.92195 | -0.039015 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SPRINT15 | 0.96945 | 0.92577 | -0.043684 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SPRINT15 | 0.96945 | 0.92577 | -0.043684 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SPRINT15 | 0.96945 | 0.92577 | -0.043684 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SPRINT15 | 0.96945 | 0.92577 | -0.043684 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SPRINT15 | 0.96945 | 0.92577 | -0.043684 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SPRINT15 | 0.96945 | 0.92577 | -0.043684 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SPRINT15 | 0.96945 | 0.92577 | -0.043684 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SPRINT15 | 0.96945 | 0.92577 | -0.043684 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SPRINT15 | 0.96945 | 0.92577 | -0.043684 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SPRINT15 | 0.96945 | 0.92577 | -0.043684 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SPRINT15 | 0.96945 | 0.92577 | -0.043684 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SPRINT15 | 0.96945 | 0.92577 | -0.043684 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SPRINT15 | 0.96945 | 0.92577 | -0.043684 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SPRINT15 | 0.96945 | 0.92577 | -0.043684 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SPRINT15 | 0.96945 | 0.92577 | -0.043684 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SPRINT15 | 0.96945 | 0.92577 | -0.043684 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SPRINT15 | 0.96945 | 0.92577 | -0.043684 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SPRINT15 | 0.96945 | 0.92577 | -0.043684 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SPRINT15 | 0.96945 | 0.92577 | -0.043684 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SPRINT15 | 0.96945 | 0.92577 | -0.043684 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SPRINT15 | 0.97173 | 0.90287 | -0.068862 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | SPRINT15 | 0.97173 | 0.90287 | -0.068862 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SPRINT15 | 0.97173 | 0.90287 | -0.068862 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SPRINT15 | 0.97173 | 0.90287 | -0.068862 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SPRINT15 | 0.97173 | 0.90287 | -0.068862 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | SPRINT15 | 0.97173 | 0.90287 | -0.068862 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SPRINT15 | 0.97173 | 0.90287 | -0.068862 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | SPRINT15 | 0.97173 | 0.90287 | -0.068862 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | SPRINT15 | 0.97173 | 0.90287 | -0.068862 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SPRINT15 | 0.97173 | 0.90287 | -0.068862 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SPRINT15 | 0.97173 | 0.90287 | -0.068862 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SPRINT15 | 0.97173 | 0.90287 | -0.068862 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SPRINT15 | 0.97173 | 0.90287 | -0.068862 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SPRINT15 | 0.97173 | 0.90287 | -0.068862 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SPRINT15 | 0.97173 | 0.90287 | -0.068862 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SPRINT15 | 0.97173 | 0.90287 | -0.068862 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SPRINT15 | 0.97173 | 0.90287 | -0.068862 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SPRINT15 | 0.97173 | 0.90287 | -0.068862 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | SPRINT15 | 0.97173 | 0.90287 | -0.068862 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | SPRINT15 | 0.97173 | 0.90287 | -0.068862 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SPRINT15 | 0.97173 | 0.90287 | -0.068862 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SPRINT15 | 0.97173 | 0.90287 | -0.068862 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | SPRINT15 | 0.97173 | 0.90287 | -0.068862 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SPRINT15 | 0.97173 | 0.90287 | -0.068862 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SPRINT15 | 0.97173 | 0.90287 | -0.068862 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SPRINT15 | 0.97173 | 0.90287 | -0.068862 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SPRINT15 | 0.97173 | 0.90287 | -0.068862 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | SPRINT15 | 0.97173 | 0.90287 | -0.068862 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SPRINT15 | 0.96564 | 0.92872 | -0.036919 |  | 0.93 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SPRINT15 | 0.96564 | 0.92872 | -0.036919 |  | 0.93 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SPRINT15 | 0.96564 | 0.92872 | -0.036919 |  | 0.93 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SPRINT15 | 0.96564 | 0.92872 | -0.036919 |  | 0.93 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SPRINT15 | 0.96564 | 0.92872 | -0.036919 |  | 0.93 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SPRINT15 | 0.96564 | 0.92872 | -0.036919 |  | 0.93 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SPRINT15 | 0.96564 | 0.92872 | -0.036919 |  | 0.93 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SPRINT15 | 0.96564 | 0.92872 | -0.036919 |  | 0.93 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SPRINT15 | 0.96564 | 0.92872 | -0.036919 |  | 0.93 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SPRINT15 | 0.96564 | 0.92872 | -0.036919 |  | 0.93 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SPRINT15 | 0.96564 | 0.92872 | -0.036919 |  | 0.93 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SPRINT15 | 0.96564 | 0.92872 | -0.036919 |  | 0.93 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SPRINT15 | 0.96564 | 0.92872 | -0.036919 |  | 0.93 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SPRINT15 | 0.96564 | 0.92872 | -0.036919 |  | 0.93 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SPRINT15 | 0.96564 | 0.92872 | -0.036919 |  | 0.93 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SPRINT15 | 0.96564 | 0.92872 | -0.036919 |  | 0.93 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SPRINT15 | 0.96564 | 0.92872 | -0.036919 |  | 0.93 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SPRINT15 | 0.96564 | 0.92872 | -0.036919 |  | 0.93 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SPRINT15 | 0.96564 | 0.92872 | -0.036919 |  | 0.93 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SPRINT15 | 0.96564 | 0.92872 | -0.036919 |  | 0.93 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SPRINT25 | 0.96092 | 0.9219 | -0.039027 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SPRINT25 | 0.96092 | 0.9219 | -0.039027 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SPRINT25 | 0.96092 | 0.9219 | -0.039027 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SPRINT25 | 0.96092 | 0.9219 | -0.039027 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SPRINT25 | 0.96092 | 0.9219 | -0.039027 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SPRINT25 | 0.96092 | 0.9219 | -0.039027 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SPRINT25 | 0.96092 | 0.9219 | -0.039027 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SPRINT25 | 0.96092 | 0.9219 | -0.039027 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SPRINT25 | 0.96092 | 0.9219 | -0.039027 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SPRINT25 | 0.96092 | 0.9219 | -0.039027 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SPRINT25 | 0.96092 | 0.9219 | -0.039027 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SPRINT25 | 0.96092 | 0.9219 | -0.039027 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SPRINT25 | 0.96092 | 0.9219 | -0.039027 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SPRINT25 | 0.96092 | 0.9219 | -0.039027 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SPRINT25 | 0.96092 | 0.9219 | -0.039027 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SPRINT25 | 0.96092 | 0.9219 | -0.039027 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SPRINT25 | 0.96092 | 0.9219 | -0.039027 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SPRINT25 | 0.96092 | 0.9219 | -0.039027 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SPRINT25 | 0.96092 | 0.9219 | -0.039027 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SPRINT25 | 0.96092 | 0.9219 | -0.039027 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SPRINT25 | 0.96941 | 0.92572 | -0.043696 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SPRINT25 | 0.96941 | 0.92572 | -0.043696 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SPRINT25 | 0.96941 | 0.92572 | -0.043696 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SPRINT25 | 0.96941 | 0.92572 | -0.043696 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SPRINT25 | 0.96941 | 0.92572 | -0.043696 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SPRINT25 | 0.96941 | 0.92572 | -0.043696 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SPRINT25 | 0.96941 | 0.92572 | -0.043696 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SPRINT25 | 0.96941 | 0.92572 | -0.043696 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SPRINT25 | 0.96941 | 0.92572 | -0.043696 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SPRINT25 | 0.96941 | 0.92572 | -0.043696 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SPRINT25 | 0.96941 | 0.92572 | -0.043696 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SPRINT25 | 0.96941 | 0.92572 | -0.043696 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SPRINT25 | 0.96941 | 0.92572 | -0.043696 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SPRINT25 | 0.96941 | 0.92572 | -0.043696 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SPRINT25 | 0.96941 | 0.92572 | -0.043696 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SPRINT25 | 0.96941 | 0.92572 | -0.043696 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SPRINT25 | 0.96941 | 0.92572 | -0.043696 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SPRINT25 | 0.96941 | 0.92572 | -0.043696 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SPRINT25 | 0.96941 | 0.92572 | -0.043696 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SPRINT25 | 0.96941 | 0.92572 | -0.043696 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SPRINT25 | 0.9717 | 0.90282 | -0.068873 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | SPRINT25 | 0.9717 | 0.90282 | -0.068873 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SPRINT25 | 0.9717 | 0.90282 | -0.068873 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SPRINT25 | 0.9717 | 0.90282 | -0.068873 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SPRINT25 | 0.9717 | 0.90282 | -0.068873 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | SPRINT25 | 0.9717 | 0.90282 | -0.068873 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SPRINT25 | 0.9717 | 0.90282 | -0.068873 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | SPRINT25 | 0.9717 | 0.90282 | -0.068873 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | SPRINT25 | 0.9717 | 0.90282 | -0.068873 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SPRINT25 | 0.9717 | 0.90282 | -0.068873 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SPRINT25 | 0.9717 | 0.90282 | -0.068873 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SPRINT25 | 0.9717 | 0.90282 | -0.068873 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SPRINT25 | 0.9717 | 0.90282 | -0.068873 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SPRINT25 | 0.9717 | 0.90282 | -0.068873 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SPRINT25 | 0.9717 | 0.90282 | -0.068873 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SPRINT25 | 0.9717 | 0.90282 | -0.068873 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SPRINT25 | 0.9717 | 0.90282 | -0.068873 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SPRINT25 | 0.9717 | 0.90282 | -0.068873 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | SPRINT25 | 0.9717 | 0.90282 | -0.068873 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | SPRINT25 | 0.9717 | 0.90282 | -0.068873 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SPRINT25 | 0.9717 | 0.90282 | -0.068873 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SPRINT25 | 0.9717 | 0.90282 | -0.068873 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | SPRINT25 | 0.9717 | 0.90282 | -0.068873 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SPRINT25 | 0.9717 | 0.90282 | -0.068873 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SPRINT25 | 0.9717 | 0.90282 | -0.068873 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SPRINT25 | 0.9717 | 0.90282 | -0.068873 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SPRINT25 | 0.9717 | 0.90282 | -0.068873 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | SPRINT25 | 0.9717 | 0.90282 | -0.068873 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SPRINT25 | 0.9656 | 0.92867 | -0.036927 |  | 0.93 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SPRINT25 | 0.9656 | 0.92867 | -0.036927 |  | 0.93 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SPRINT25 | 0.9656 | 0.92867 | -0.036927 |  | 0.93 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SPRINT25 | 0.9656 | 0.92867 | -0.036927 |  | 0.93 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SPRINT25 | 0.9656 | 0.92867 | -0.036927 |  | 0.93 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SPRINT25 | 0.9656 | 0.92867 | -0.036927 |  | 0.93 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SPRINT25 | 0.9656 | 0.92867 | -0.036927 |  | 0.93 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SPRINT25 | 0.9656 | 0.92867 | -0.036927 |  | 0.93 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SPRINT25 | 0.9656 | 0.92867 | -0.036927 |  | 0.93 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SPRINT25 | 0.9656 | 0.92867 | -0.036927 |  | 0.93 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SPRINT25 | 0.9656 | 0.92867 | -0.036927 |  | 0.93 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SPRINT25 | 0.9656 | 0.92867 | -0.036927 |  | 0.93 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SPRINT25 | 0.9656 | 0.92867 | -0.036927 |  | 0.93 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SPRINT25 | 0.9656 | 0.92867 | -0.036927 |  | 0.93 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SPRINT25 | 0.9656 | 0.92867 | -0.036927 |  | 0.93 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SPRINT25 | 0.9656 | 0.92867 | -0.036927 |  | 0.93 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SPRINT25 | 0.9656 | 0.92867 | -0.036927 |  | 0.93 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SPRINT25 | 0.9656 | 0.92867 | -0.036927 |  | 0.93 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SPRINT25 | 0.9656 | 0.92867 | -0.036927 |  | 0.93 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SPRINT25 | 0.9656 | 0.92867 | -0.036927 |  | 0.93 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | STFRAN 3 | 0.95873 | 0.8897 | -0.069029 |  | 0.9 | 1.05 | 0.041569 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | STFRAN 3 | 0.95873 | 0.8897 | -0.069029 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | STFRAN 3 | 0.95873 | 0.8897 | -0.069029 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | STFRAN 3 | 0.95873 | 0.8897 | -0.069029 |  | 0.9 | 1.05 | 0.03222 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | STFRAN 3 | 0.95873 | 0.8897 | -0.069029 |  | 0.9 | 1.05 | 0.030633 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | STFRAN 3 | 0.95873 | 0.8897 | -0.069029 |  | 0.9 | 1.05 | 0.030061 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | STFRAN 3 | 0.95873 | 0.8897 | -0.069029 |  | 0.9 | 1.05 | 0.031207 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | STFRAN 3 | 0.94844 | 0.87616 | -0.072283 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | STFRAN 3 | 0.94844 | 0.87616 | -0.072283 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | STFRAN 3 | 0.9482 | 0.86863 | -0.079566 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | STFRAN 3 | 0.9482 | 0.86863 | -0.079566 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | STFRAN 3 | 0.9482 | 0.86863 | -0.079566 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | STFRAN 3 | 0.9482 | 0.86863 | -0.079566 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | STFRAN 3 | 0.9482 | 0.86863 | -0.079567 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | STFRAN 3 | 0.9482 | 0.86863 | -0.079567 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | STFRANT3 | 0.95907 | 0.88989 | -0.069177 |  | 0.9 | 1.05 | 0.041569 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | STFRANT3 | 0.95907 | 0.88989 | -0.069177 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | STFRANT3 | 0.95907 | 0.88989 | -0.069177 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | STFRANT3 | 0.95907 | 0.88989 | -0.069177 |  | 0.9 | 1.05 | 0.03222 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | STFRANT3 | 0.95907 | 0.88989 | -0.069177 |  | 0.9 | 1.05 | 0.030633 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | STFRANT3 | 0.95907 | 0.88989 | -0.069177 |  | 0.9 | 1.05 | 0.030061 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | STFRANT3 | 0.95907 | 0.88989 | -0.069177 |  | 0.9 | 1.05 | 0.031207 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | STFRANT3 | 0.94773 | 0.87498 | -0.072753 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | STFRANT3 | 0.94773 | 0.87498 | -0.072753 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | STFRANT3 | 0.94746 | 0.86726 | -0.080198 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | STFRANT3 | 0.94746 | 0.86726 | -0.080198 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | STFRANT3 | 0.94746 | 0.86726 | -0.080198 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | STFRANT3 | 0.94746 | 0.86726 | -0.080198 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | STFRANT3 | 0.94746 | 0.86726 | -0.080199 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | STFRANT3 | 0.94746 | 0.86726 | -0.080199 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | STHTOWN5 | 0.98444 | 0.91669 | -0.067752 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | STHTOWN5 | 0.98444 | 0.91669 | -0.067752 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | STHTOWN5 | 0.98444 | 0.91669 | -0.067752 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | STHTOWN5 | 0.98444 | 0.91669 | -0.067752 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | STHTOWN5 | 0.98444 | 0.91669 | -0.067752 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | STHTOWN5 | 0.98444 | 0.91669 | -0.067752 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | STHTOWN5 | 0.98444 | 0.91669 | -0.067752 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | STHTOWN5 | 0.98444 | 0.91669 | -0.067752 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | STHTOWN5 | 0.98444 | 0.91669 | -0.067752 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | STHTOWN5 | 0.98444 | 0.91669 | -0.067752 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | STHTOWN5 | 0.98444 | 0.91669 | -0.067752 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | STHTOWN5 | 0.98444 | 0.91669 | -0.067752 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | STHTOWN5 | 0.98444 | 0.91669 | -0.067752 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | STHTOWN5 | 0.98444 | 0.91669 | -0.067752 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | STHTOWN5 | 0.98444 | 0.91669 | -0.067752 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | STHTOWN5 | 0.98444 | 0.91669 | -0.067752 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | STHTOWN5 | 0.98444 | 0.91669 | -0.067752 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | STHTOWN5 | 0.98444 | 0.91669 | -0.067752 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | STHTOWN5 | 0.98444 | 0.91669 | -0.067752 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | STHTOWN5 | 0.98444 | 0.91669 | -0.067752 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | STHTOWN5 | 0.98444 | 0.91669 | -0.067752 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | STHTOWN5 | 0.98444 | 0.91669 | -0.067752 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | STHTOWN5 | 0.98444 | 0.91669 | -0.067752 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | STHTOWN5 | 0.98444 | 0.91669 | -0.067752 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | STHTOWN5 | 0.98444 | 0.91669 | -0.067752 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | STHTOWN5 | 0.98444 | 0.91669 | -0.067752 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | STHTOWN5 | 0.98444 | 0.91669 | -0.067752 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | STHTOWN5 | 0.98444 | 0.91669 | -0.067752 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | STHTOWN_CAP5 | 0.98557 | 0.91774 | -0.06783 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | STHTOWN_CAP5 | 0.98557 | 0.91774 | -0.06783 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | STHTOWN_CAP5 | 0.98557 | 0.91774 | -0.06783 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | STHTOWN_CAP5 | 0.98557 | 0.91774 | -0.06783 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | STHTOWN_CAP5 | 0.98557 | 0.91774 | -0.06783 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | STHTOWN_CAP5 | 0.98557 | 0.91774 | -0.06783 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | STHTOWN_CAP5 | 0.98557 | 0.91774 | -0.06783 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | STHTOWN_CAP5 | 0.98557 | 0.91774 | -0.06783 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | STHTOWN_CAP5 | 0.98557 | 0.91774 | -0.06783 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | STHTOWN_CAP5 | 0.98557 | 0.91774 | -0.06783 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | STHTOWN_CAP5 | 0.98557 | 0.91774 | -0.06783 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | STHTOWN_CAP5 | 0.98557 | 0.91774 | -0.06783 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | STHTOWN_CAP5 | 0.98557 | 0.91774 | -0.06783 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | STHTOWN_CAP5 | 0.98557 | 0.91774 | -0.06783 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | STHTOWN_CAP5 | 0.98557 | 0.91774 | -0.06783 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | STHTOWN_CAP5 | 0.98557 | 0.91774 | -0.06783 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | STHTOWN_CAP5 | 0.98557 | 0.91774 | -0.06783 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | STHTOWN_CAP5 | 0.98557 | 0.91774 | -0.06783 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | STHTOWN_CAP5 | 0.98557 | 0.91774 | -0.06783 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | STHTOWN_CAP5 | 0.98557 | 0.91774 | -0.06783 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | STHTOWN_CAP5 | 0.98557 | 0.91774 | -0.06783 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | STHTOWN_CAP5 | 0.98557 | 0.91774 | -0.06783 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | STHTOWN_CAP5 | 0.98557 | 0.91774 | -0.06783 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | STHTOWN_CAP5 | 0.98557 | 0.91774 | -0.06783 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | STHTOWN_CAP5 | 0.98557 | 0.91774 | -0.06783 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | STHTOWN_CAP5 | 0.98557 | 0.91774 | -0.06783 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | STHTOWN_CAP5 | 0.98557 | 0.91774 | -0.06783 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | STHTOWN_CAP5 | 0.98557 | 0.91774 | -0.06783 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | STILWEL5 | 0.97405 | 0.92904 | -0.045009 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | STILWEL5 | 0.97405 | 0.92904 | -0.045009 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | STILWEL5 | 0.97405 | 0.92904 | -0.045009 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | STILWEL5 | 0.97405 | 0.92904 | -0.045009 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | STILWEL5 | 0.97405 | 0.92904 | -0.045009 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | STILWEL5 | 0.97405 | 0.92904 | -0.045009 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | STILWEL5 | 0.97405 | 0.92904 | -0.045009 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | STILWEL5 | 0.97405 | 0.92904 | -0.045009 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | STILWEL5 | 0.97405 | 0.92904 | -0.045009 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | STILWEL5 | 0.97405 | 0.92904 | -0.045009 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | STILWEL5 | 0.97405 | 0.92904 | -0.045009 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | STILWEL5 | 0.97405 | 0.92904 | -0.045009 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | STILWEL5 | 0.97405 | 0.92904 | -0.045009 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | STILWEL5 | 0.97405 | 0.92904 | -0.045009 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | STILWEL5 | 0.97405 | 0.92904 | -0.045009 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | STILWEL5 | 0.97405 | 0.92904 | -0.045009 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | STILWEL5 | 0.97405 | 0.92904 | -0.045009 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | STILWEL5 | 0.97405 | 0.92904 | -0.045009 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | STILWEL5 | 0.97405 | 0.92904 | -0.045009 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | STILWEL5 | 0.97405 | 0.92904 | -0.045009 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | STILWEL5 | 0.98715 | 0.90395 | -0.083202 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | STILWEL5 | 0.98715 | 0.90395 | -0.083202 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | STILWEL5 | 0.98715 | 0.90395 | -0.083202 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | STILWEL5 | 0.98715 | 0.90395 | -0.083202 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | STILWEL5 | 0.98715 | 0.90395 | -0.083202 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | STILWEL5 | 0.98715 | 0.90395 | -0.083202 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | STILWEL5 | 0.98715 | 0.90395 | -0.083202 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | STILWEL5 | 0.98715 | 0.90395 | -0.083202 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | STILWEL5 | 0.98715 | 0.90395 | -0.083202 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | STILWEL5 | 0.98715 | 0.90395 | -0.083202 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | STILWEL5 | 0.98715 | 0.90395 | -0.083202 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | STILWEL5 | 0.98715 | 0.90395 | -0.083202 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | STILWEL5 | 0.98715 | 0.90395 | -0.083202 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | STILWEL5 | 0.98715 | 0.90395 | -0.083202 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | STILWEL5 | 0.98715 | 0.90395 | -0.083202 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | STILWEL5 | 0.98715 | 0.90395 | -0.083202 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | STILWEL5 | 0.98715 | 0.90395 | -0.083202 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | STILWEL5 | 0.98715 | 0.90395 | -0.083202 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | STILWEL5 | 0.98715 | 0.90395 | -0.083202 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | STILWEL5 | 0.98715 | 0.90395 | -0.083202 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | STILWEL5 | 0.98715 | 0.90395 | -0.083202 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | STILWEL5 | 0.98715 | 0.90395 | -0.083202 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | STILWEL5 | 0.98715 | 0.90395 | -0.083202 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | STILWEL5 | 0.98715 | 0.90395 | -0.083202 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | STILWEL5 | 0.98715 | 0.90395 | -0.083202 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | STILWEL5 | 0.98715 | 0.90395 | -0.083202 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | STILWEL5 | 0.98715 | 0.90395 | -0.083202 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | STILWEL5 | 0.98715 | 0.90395 | -0.083202 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | STILWEL7 | 0.9602 | 0.91852 | -0.041676 |  | 0.95 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | STILWEL7 | 0.9602 | 0.91852 | -0.041676 |  | 0.95 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | STILWEL7 | 0.9602 | 0.91852 | -0.041676 |  | 0.95 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | STILWEL7 | 0.9602 | 0.91852 | -0.041676 |  | 0.95 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | STILWEL7 | 0.9602 | 0.91852 | -0.041676 |  | 0.95 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | STILWEL7 | 0.9602 | 0.91852 | -0.041676 |  | 0.95 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | STILWEL7 | 0.9602 | 0.91852 | -0.041676 |  | 0.95 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | STILWEL7 | 0.9602 | 0.91852 | -0.041676 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | STILWEL7 | 0.9602 | 0.91852 | -0.041676 |  | 0.95 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | STILWEL7 | 0.9602 | 0.91852 | -0.041676 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | STILWEL7 | 0.9602 | 0.91852 | -0.041676 |  | 0.95 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | STILWEL7 | 0.9602 | 0.91852 | -0.041676 |  | 0.95 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | STILWEL7 | 0.9602 | 0.91852 | -0.041676 |  | 0.95 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | STILWEL7 | 0.9602 | 0.91852 | -0.041676 |  | 0.95 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | STILWEL7 | 0.9602 | 0.91852 | -0.041676 |  | 0.95 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | STILWEL7 | 0.9602 | 0.91852 | -0.041676 |  | 0.95 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | STILWEL7 | 0.9602 | 0.91852 | -0.041676 |  | 0.95 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | STILWEL7 | 0.9602 | 0.91852 | -0.041676 |  | 0.95 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | STILWEL7 | 0.9602 | 0.91852 | -0.041676 |  | 0.95 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | STILWEL7 | 0.9602 | 0.91852 | -0.041676 |  | 0.95 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | STILWEL7 | 0.94313 | 0.89348 | -0.049654 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | STILWEL7 | 0.94313 | 0.89348 | -0.049654 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | STILWEL7 | 0.94313 | 0.89348 | -0.049654 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | STILWEL7 | 0.94313 | 0.89348 | -0.049654 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | STILWEL7 | 0.94313 | 0.89348 | -0.049654 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | STILWEL7 | 0.94313 | 0.89348 | -0.049654 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | STILWEL7 | 0.94313 | 0.89348 | -0.049654 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | STILWEL7 | 0.94313 | 0.89348 | -0.049654 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | STILWEL7 | 0.94313 | 0.89348 | -0.049654 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | STILWEL7 | 0.94313 | 0.89348 | -0.049654 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | STILWEL7 | 0.94313 | 0.89348 | -0.049654 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | STILWEL7 | 0.94313 | 0.89348 | -0.049654 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | STILWEL7 | 0.94313 | 0.89348 | -0.049654 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | STILWEL7 | 0.94313 | 0.89348 | -0.049654 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | STILWEL7 | 0.94313 | 0.89348 | -0.049654 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | STILWEL7 | 0.94313 | 0.89348 | -0.049654 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | STILWEL7 | 0.94313 | 0.89348 | -0.049654 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | STILWEL7 | 0.94313 | 0.89348 | -0.049654 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | STILWEL7 | 0.94313 | 0.89348 | -0.049654 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | STILWEL7 | 0.94313 | 0.89348 | -0.049654 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | STILWEL7 | 0.96455 | 0.91314 | -0.051415 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | STILWEL7 | 0.96455 | 0.91314 | -0.051415 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | STILWEL7 | 0.96455 | 0.91314 | -0.051415 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | STILWEL7 | 0.96455 | 0.91314 | -0.051415 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | STILWEL7 | 0.96455 | 0.91314 | -0.051415 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | STILWEL7 | 0.96455 | 0.91314 | -0.051415 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | STILWEL7 | 0.96455 | 0.91314 | -0.051415 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | STILWEL7 | 0.96455 | 0.91314 | -0.051415 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | STILWEL7 | 0.96455 | 0.91314 | -0.051415 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | STILWEL7 | 0.96455 | 0.91314 | -0.051415 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | STILWEL7 | 0.96455 | 0.91314 | -0.051415 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | STILWEL7 | 0.96455 | 0.91314 | -0.051415 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | STILWEL7 | 0.96455 | 0.91314 | -0.051415 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | STILWEL7 | 0.96455 | 0.91314 | -0.051415 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | STILWEL7 | 0.96455 | 0.91314 | -0.051415 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | STILWEL7 | 0.96455 | 0.91314 | -0.051415 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | STILWEL7 | 0.96455 | 0.91314 | -0.051415 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | STILWEL7 | 0.96455 | 0.91314 | -0.051415 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | STILWEL7 | 0.96455 | 0.91314 | -0.051415 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | STILWEL7 | 0.96455 | 0.91314 | -0.051415 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | STILWEL7 | 0.96534 | 0.87557 | -0.08977 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | STILWEL7 | 0.96534 | 0.87557 | -0.08977 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | STILWEL7 | 0.96534 | 0.87557 | -0.08977 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | STILWEL7 | 0.96534 | 0.87557 | -0.08977 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | STILWEL7 | 0.96534 | 0.87557 | -0.08977 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | STILWEL7 | 0.96534 | 0.87557 | -0.08977 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | STILWEL7 | 0.96534 | 0.87557 | -0.08977 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | STILWEL7 | 0.96534 | 0.87557 | -0.08977 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | STILWEL7 | 0.96534 | 0.87557 | -0.08977 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | STILWEL7 | 0.96534 | 0.87557 | -0.08977 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | STILWEL7 | 0.96534 | 0.87557 | -0.08977 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | STILWEL7 | 0.96534 | 0.87557 | -0.08977 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | STILWEL7 | 0.96534 | 0.87557 | -0.08977 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | STILWEL7 | 0.96534 | 0.87557 | -0.08977 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | STILWEL7 | 0.96534 | 0.87557 | -0.08977 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | STILWEL7 | 0.96534 | 0.87557 | -0.08977 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | STILWEL7 | 0.96534 | 0.87557 | -0.08977 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | STILWEL7 | 0.96534 | 0.87557 | -0.08977 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | STILWEL7 | 0.96534 | 0.87557 | -0.08977 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | STILWEL7 | 0.96534 | 0.87557 | -0.08977 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | STILWEL7 | 0.96534 | 0.87557 | -0.08977 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | STILWEL7 | 0.96534 | 0.87557 | -0.08977 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | STILWEL7 | 0.96534 | 0.87557 | -0.08977 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | STILWEL7 | 0.96534 | 0.87557 | -0.08977 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | STILWEL7 | 0.96534 | 0.87557 | -0.08977 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | STILWEL7 | 0.96534 | 0.87557 | -0.08977 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | STILWEL7 | 0.96534 | 0.87557 | -0.08977 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | STILWEL7 | 0.96534 | 0.87557 | -0.08977 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | STILWEL7 | 0.95833 | 0.9159 | -0.042433 |  | 0.95 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | STILWEL7 | 0.95833 | 0.9159 | -0.042433 |  | 0.95 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | STILWEL7 | 0.95833 | 0.9159 | -0.042433 |  | 0.95 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | STILWEL7 | 0.95833 | 0.9159 | -0.042433 |  | 0.95 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | STILWEL7 | 0.95833 | 0.9159 | -0.042433 |  | 0.95 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | STILWEL7 | 0.95833 | 0.9159 | -0.042433 |  | 0.95 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | STILWEL7 | 0.95833 | 0.9159 | -0.042433 |  | 0.95 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | STILWEL7 | 0.95833 | 0.9159 | -0.042433 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | STILWEL7 | 0.95833 | 0.9159 | -0.042433 |  | 0.95 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | STILWEL7 | 0.95833 | 0.9159 | -0.042433 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | STILWEL7 | 0.95833 | 0.9159 | -0.042433 |  | 0.95 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | STILWEL7 | 0.95833 | 0.9159 | -0.042433 |  | 0.95 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | STILWEL7 | 0.95833 | 0.9159 | -0.042433 |  | 0.95 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | STILWEL7 | 0.95833 | 0.9159 | -0.042433 |  | 0.95 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | STILWEL7 | 0.95833 | 0.9159 | -0.042433 |  | 0.95 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | STILWEL7 | 0.95833 | 0.9159 | -0.042433 |  | 0.95 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | STILWEL7 | 0.95833 | 0.9159 | -0.042433 |  | 0.95 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | STILWEL7 | 0.95833 | 0.9159 | -0.042433 |  | 0.95 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | STILWEL7 | 0.95833 | 0.9159 | -0.042433 |  | 0.95 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | STILWEL7 | 0.95833 | 0.9159 | -0.042433 |  | 0.95 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | STK324 2 | 0.96837 | 0.92337 | -0.044994 |  | 0.925 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | STK324 2 | 0.96837 | 0.92337 | -0.044994 |  | 0.925 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | STK324 2 | 0.96837 | 0.92337 | -0.044994 |  | 0.925 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | STK324 2 | 0.96837 | 0.92337 | -0.044994 |  | 0.925 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | STK324 2 | 0.96837 | 0.92337 | -0.044994 |  | 0.925 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | STK324 2 | 0.96837 | 0.92337 | -0.044994 |  | 0.925 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | STK324 2 | 0.96837 | 0.92337 | -0.044994 |  | 0.925 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | STK324 2 | 0.96837 | 0.92337 | -0.044994 |  | 0.925 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | STK324 2 | 0.96837 | 0.92337 | -0.044994 |  | 0.925 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | STK324 2 | 0.96837 | 0.92337 | -0.044994 |  | 0.925 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | STK324 2 | 0.96837 | 0.92337 | -0.044994 |  | 0.925 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | STK324 2 | 0.96837 | 0.92337 | -0.044994 |  | 0.925 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | STK324 2 | 0.96837 | 0.92337 | -0.044994 |  | 0.925 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | STK324 2 | 0.96837 | 0.92337 | -0.044994 |  | 0.925 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | STK324 2 | 0.96837 | 0.92337 | -0.044994 |  | 0.925 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | STK324 2 | 0.96837 | 0.92337 | -0.044994 |  | 0.925 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | STK324 2 | 0.96837 | 0.92337 | -0.044994 |  | 0.925 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | STK324 2 | 0.96837 | 0.92337 | -0.044994 |  | 0.925 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | STK324 2 | 0.96837 | 0.92337 | -0.044994 |  | 0.925 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | STK324 2 | 0.96837 | 0.92337 | -0.044994 |  | 0.925 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | STK324 2 | 0.96617 | 0.92485 | -0.041317 |  | 0.925 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | STK324 2 | 0.96617 | 0.92485 | -0.041317 |  | 0.925 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | STK324 2 | 0.96617 | 0.92485 | -0.041317 |  | 0.925 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | STK324 2 | 0.96617 | 0.92485 | -0.041317 |  | 0.925 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | STK324 2 | 0.96617 | 0.92485 | -0.041317 |  | 0.925 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | STK324 2 | 0.96617 | 0.92485 | -0.041317 |  | 0.925 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | STK324 2 | 0.96617 | 0.92485 | -0.041317 |  | 0.925 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | STK324 2 | 0.96617 | 0.92485 | -0.041317 |  | 0.925 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | STK324 2 | 0.96617 | 0.92485 | -0.041317 |  | 0.925 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | STK324 2 | 0.96617 | 0.92485 | -0.041317 |  | 0.925 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | STK324 2 | 0.96617 | 0.92485 | -0.041317 |  | 0.925 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | STK324 2 | 0.96617 | 0.92485 | -0.041317 |  | 0.925 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | STK324 2 | 0.96617 | 0.92485 | -0.041317 |  | 0.925 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | STK324 2 | 0.96617 | 0.92485 | -0.041317 |  | 0.925 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | STK324 2 | 0.96617 | 0.92485 | -0.041317 |  | 0.925 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | STK324 2 | 0.96617 | 0.92485 | -0.041317 |  | 0.925 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | STK324 2 | 0.96617 | 0.92485 | -0.041317 |  | 0.925 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | STK324 2 | 0.96617 | 0.92485 | -0.041317 |  | 0.925 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | STK324 2 | 0.96617 | 0.92485 | -0.041317 |  | 0.925 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | STK324 2 | 0.96617 | 0.92485 | -0.041317 |  | 0.925 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | STK324 2 | 0.96804 | 0.90297 | -0.065067 |  | 0.925 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | STK324 2 | 0.96804 | 0.90297 | -0.065067 |  | 0.925 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | STK324 2 | 0.96804 | 0.90297 | -0.065067 |  | 0.925 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | STK324 2 | 0.96804 | 0.90297 | -0.065067 |  | 0.925 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | STK324 2 | 0.96804 | 0.90297 | -0.065067 |  | 0.925 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | STK324 2 | 0.96804 | 0.90297 | -0.065067 |  | 0.925 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | STK324 2 | 0.96804 | 0.90297 | -0.065067 |  | 0.925 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | STK324 2 | 0.96804 | 0.90297 | -0.065067 |  | 0.925 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | STK324 2 | 0.96804 | 0.90297 | -0.065067 |  | 0.925 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | STK324 2 | 0.96804 | 0.90297 | -0.065067 |  | 0.925 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | STK324 2 | 0.96804 | 0.90297 | -0.065067 |  | 0.925 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | STK324 2 | 0.96804 | 0.90297 | -0.065067 |  | 0.925 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | STK324 2 | 0.96804 | 0.90297 | -0.065067 |  | 0.925 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | STK324 2 | 0.96804 | 0.90297 | -0.065067 |  | 0.925 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | STK324 2 | 0.96804 | 0.90297 | -0.065067 |  | 0.925 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | STK324 2 | 0.96804 | 0.90297 | -0.065067 |  | 0.925 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | STK324 2 | 0.96804 | 0.90297 | -0.065067 |  | 0.925 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | STK324 2 | 0.96804 | 0.90297 | -0.065067 |  | 0.925 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | STK324 2 | 0.96804 | 0.90297 | -0.065067 |  | 0.925 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | STK324 2 | 0.96804 | 0.90297 | -0.065067 |  | 0.925 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | STK324 2 | 0.96804 | 0.90297 | -0.065067 |  | 0.925 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | STK324 2 | 0.96804 | 0.90297 | -0.065067 |  | 0.925 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | STK324 2 | 0.96804 | 0.90297 | -0.065067 |  | 0.925 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | STK324 2 | 0.96804 | 0.90297 | -0.065067 |  | 0.925 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | STK324 2 | 0.96804 | 0.90297 | -0.065067 |  | 0.925 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | STK324 2 | 0.96804 | 0.90297 | -0.065067 |  | 0.925 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | STK324 2 | 0.96804 | 0.90297 | -0.065067 |  | 0.925 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | STK324 2 | 0.96804 | 0.90297 | -0.065067 |  | 0.925 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | STK324J2 | 0.96837 | 0.92338 | -0.044994 |  | 0.925 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | STK324J2 | 0.96837 | 0.92338 | -0.044994 |  | 0.925 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | STK324J2 | 0.96837 | 0.92338 | -0.044994 |  | 0.925 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | STK324J2 | 0.96837 | 0.92338 | -0.044994 |  | 0.925 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | STK324J2 | 0.96837 | 0.92338 | -0.044994 |  | 0.925 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | STK324J2 | 0.96837 | 0.92338 | -0.044994 |  | 0.925 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | STK324J2 | 0.96837 | 0.92338 | -0.044994 |  | 0.925 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | STK324J2 | 0.96837 | 0.92338 | -0.044994 |  | 0.925 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | STK324J2 | 0.96837 | 0.92338 | -0.044994 |  | 0.925 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | STK324J2 | 0.96837 | 0.92338 | -0.044994 |  | 0.925 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | STK324J2 | 0.96837 | 0.92338 | -0.044994 |  | 0.925 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | STK324J2 | 0.96837 | 0.92338 | -0.044994 |  | 0.925 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | STK324J2 | 0.96837 | 0.92338 | -0.044994 |  | 0.925 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | STK324J2 | 0.96837 | 0.92338 | -0.044994 |  | 0.925 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | STK324J2 | 0.96837 | 0.92338 | -0.044994 |  | 0.925 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | STK324J2 | 0.96837 | 0.92338 | -0.044994 |  | 0.925 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | STK324J2 | 0.96837 | 0.92338 | -0.044994 |  | 0.925 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | STK324J2 | 0.96837 | 0.92338 | -0.044994 |  | 0.925 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | STK324J2 | 0.96837 | 0.92338 | -0.044994 |  | 0.925 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | STK324J2 | 0.96837 | 0.92338 | -0.044994 |  | 0.925 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | STK324J2 | 0.96618 | 0.92486 | -0.041317 |  | 0.925 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | STK324J2 | 0.96618 | 0.92486 | -0.041317 |  | 0.925 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | STK324J2 | 0.96618 | 0.92486 | -0.041317 |  | 0.925 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | STK324J2 | 0.96618 | 0.92486 | -0.041317 |  | 0.925 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | STK324J2 | 0.96618 | 0.92486 | -0.041317 |  | 0.925 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | STK324J2 | 0.96618 | 0.92486 | -0.041317 |  | 0.925 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | STK324J2 | 0.96618 | 0.92486 | -0.041317 |  | 0.925 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | STK324J2 | 0.96618 | 0.92486 | -0.041317 |  | 0.925 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | STK324J2 | 0.96618 | 0.92486 | -0.041317 |  | 0.925 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | STK324J2 | 0.96618 | 0.92486 | -0.041317 |  | 0.925 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | STK324J2 | 0.96618 | 0.92486 | -0.041317 |  | 0.925 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | STK324J2 | 0.96618 | 0.92486 | -0.041317 |  | 0.925 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | STK324J2 | 0.96618 | 0.92486 | -0.041317 |  | 0.925 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | STK324J2 | 0.96618 | 0.92486 | -0.041317 |  | 0.925 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | STK324J2 | 0.96618 | 0.92486 | -0.041317 |  | 0.925 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | STK324J2 | 0.96618 | 0.92486 | -0.041317 |  | 0.925 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | STK324J2 | 0.96618 | 0.92486 | -0.041317 |  | 0.925 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | STK324J2 | 0.96618 | 0.92486 | -0.041317 |  | 0.925 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | STK324J2 | 0.96618 | 0.92486 | -0.041317 |  | 0.925 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | STK324J2 | 0.96618 | 0.92486 | -0.041317 |  | 0.925 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | STK324J2 | 0.96805 | 0.90298 | -0.065066 |  | 0.925 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | STK324J2 | 0.96805 | 0.90298 | -0.065066 |  | 0.925 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | STK324J2 | 0.96805 | 0.90298 | -0.065066 |  | 0.925 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | STK324J2 | 0.96805 | 0.90298 | -0.065066 |  | 0.925 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | STK324J2 | 0.96805 | 0.90298 | -0.065066 |  | 0.925 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | STK324J2 | 0.96805 | 0.90298 | -0.065066 |  | 0.925 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | STK324J2 | 0.96805 | 0.90298 | -0.065066 |  | 0.925 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | STK324J2 | 0.96805 | 0.90298 | -0.065066 |  | 0.925 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | STK324J2 | 0.96805 | 0.90298 | -0.065066 |  | 0.925 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | STK324J2 | 0.96805 | 0.90298 | -0.065066 |  | 0.925 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | STK324J2 | 0.96805 | 0.90298 | -0.065066 |  | 0.925 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | STK324J2 | 0.96805 | 0.90298 | -0.065066 |  | 0.925 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | STK324J2 | 0.96805 | 0.90298 | -0.065066 |  | 0.925 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | STK324J2 | 0.96805 | 0.90298 | -0.065066 |  | 0.925 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | STK324J2 | 0.96805 | 0.90298 | -0.065066 |  | 0.925 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | STK324J2 | 0.96805 | 0.90298 | -0.065066 |  | 0.925 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | STK324J2 | 0.96805 | 0.90298 | -0.065066 |  | 0.925 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | STK324J2 | 0.96805 | 0.90298 | -0.065066 |  | 0.925 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | STK324J2 | 0.96805 | 0.90298 | -0.065066 |  | 0.925 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | STK324J2 | 0.96805 | 0.90298 | -0.065066 |  | 0.925 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | STK324J2 | 0.96805 | 0.90298 | -0.065066 |  | 0.925 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | STK324J2 | 0.96805 | 0.90298 | -0.065066 |  | 0.925 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | STK324J2 | 0.96805 | 0.90298 | -0.065066 |  | 0.925 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | STK324J2 | 0.96805 | 0.90298 | -0.065066 |  | 0.925 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | STK324J2 | 0.96805 | 0.90298 | -0.065066 |  | 0.925 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | STK324J2 | 0.96805 | 0.90298 | -0.065066 |  | 0.925 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | STK324J2 | 0.96805 | 0.90298 | -0.065066 |  | 0.925 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | STK324J2 | 0.96805 | 0.90298 | -0.065066 |  | 0.925 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | STK418 2 | 0.96663 | 0.91957 | -0.047061 |  | 0.925 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | STK418 2 | 0.96663 | 0.91957 | -0.047061 |  | 0.925 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | STK418 2 | 0.96663 | 0.91957 | -0.047061 |  | 0.925 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | STK418 2 | 0.96663 | 0.91957 | -0.047061 |  | 0.925 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | STK418 2 | 0.96663 | 0.91957 | -0.047061 |  | 0.925 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | STK418 2 | 0.96663 | 0.91957 | -0.047061 |  | 0.925 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | STK418 2 | 0.96663 | 0.91957 | -0.047061 |  | 0.925 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | STK418 2 | 0.96663 | 0.91957 | -0.047061 |  | 0.925 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | STK418 2 | 0.96663 | 0.91957 | -0.047061 |  | 0.925 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | STK418 2 | 0.96663 | 0.91957 | -0.047061 |  | 0.925 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | STK418 2 | 0.96663 | 0.91957 | -0.047061 |  | 0.925 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | STK418 2 | 0.96663 | 0.91957 | -0.047061 |  | 0.925 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | STK418 2 | 0.96663 | 0.91957 | -0.047061 |  | 0.925 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | STK418 2 | 0.96663 | 0.91957 | -0.047061 |  | 0.925 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | STK418 2 | 0.96663 | 0.91957 | -0.047061 |  | 0.925 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | STK418 2 | 0.96663 | 0.91957 | -0.047061 |  | 0.925 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | STK418 2 | 0.96663 | 0.91957 | -0.047061 |  | 0.925 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | STK418 2 | 0.96663 | 0.91957 | -0.047061 |  | 0.925 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | STK418 2 | 0.96663 | 0.91957 | -0.047061 |  | 0.925 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | STK418 2 | 0.96663 | 0.91957 | -0.047061 |  | 0.925 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | STK418 2 | 0.9643 | 0.92104 | -0.043263 |  | 0.925 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | STK418 2 | 0.9643 | 0.92104 | -0.043263 |  | 0.925 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | STK418 2 | 0.9643 | 0.92104 | -0.043263 |  | 0.925 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | STK418 2 | 0.9643 | 0.92104 | -0.043263 |  | 0.925 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | STK418 2 | 0.9643 | 0.92104 | -0.043263 |  | 0.925 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | STK418 2 | 0.9643 | 0.92104 | -0.043263 |  | 0.925 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | STK418 2 | 0.9643 | 0.92104 | -0.043263 |  | 0.925 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | STK418 2 | 0.9643 | 0.92104 | -0.043263 |  | 0.925 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | STK418 2 | 0.9643 | 0.92104 | -0.043263 |  | 0.925 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | STK418 2 | 0.9643 | 0.92104 | -0.043263 |  | 0.925 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | STK418 2 | 0.9643 | 0.92104 | -0.043263 |  | 0.925 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | STK418 2 | 0.9643 | 0.92104 | -0.043263 |  | 0.925 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | STK418 2 | 0.9643 | 0.92104 | -0.043263 |  | 0.925 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | STK418 2 | 0.9643 | 0.92104 | -0.043263 |  | 0.925 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | STK418 2 | 0.9643 | 0.92104 | -0.043263 |  | 0.925 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | STK418 2 | 0.9643 | 0.92104 | -0.043263 |  | 0.925 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | STK418 2 | 0.9643 | 0.92104 | -0.043263 |  | 0.925 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | STK418 2 | 0.9643 | 0.92104 | -0.043263 |  | 0.925 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | STK418 2 | 0.9643 | 0.92104 | -0.043263 |  | 0.925 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | STK418 2 | 0.9643 | 0.92104 | -0.043263 |  | 0.925 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | STK418 2 | 0.96971 | 0.92127 | -0.048431 |  | 0.925 | 1.05 | 0.030773 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | STK418 2 | 0.96971 | 0.92127 | -0.048431 |  | 0.925 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | STK418 2 | 0.96971 | 0.92127 | -0.048431 |  | 0.925 | 1.05 | 0.046711 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | STK418 2 | 0.96971 | 0.92127 | -0.048431 |  | 0.925 | 1.05 | 0.032369 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | STK418 2 | 0.96971 | 0.92127 | -0.048431 |  | 0.925 | 1.05 | 0.030466 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | STK418 2 | 0.96971 | 0.92127 | -0.048431 |  | 0.925 | 1.05 | 0.04987 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | STK418 2 | 0.96971 | 0.92127 | -0.048431 |  | 0.925 | 1.05 | 0.099365 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | STK418 2 | 0.96971 | 0.92127 | -0.048431 |  | 0.925 | 1.05 | 0.071132 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | STK418 2 | 0.96971 | 0.92127 | -0.048431 |  | 0.925 | 1.05 | 0.043927 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | STK418 2 | 0.96971 | 0.92127 | -0.048431 |  | 0.925 | 1.05 | 0.030565 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | STK418 2 | 0.96971 | 0.92127 | -0.048431 |  | 0.925 | 1.05 | 0.072847 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | STK418 2 | 0.96971 | 0.92127 | -0.048431 |  | 0.925 | 1.05 | 0.041148 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | STK418 2 | 0.96971 | 0.92127 | -0.048431 |  | 0.925 | 1.05 | 0.042015 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | STK418 2 | 0.96971 | 0.92127 | -0.048431 |  | 0.925 | 1.05 | 0.030318 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | STK418 2 | 0.96971 | 0.92127 | -0.048431 |  | 0.925 | 1.05 | 0.054104 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | STK418 2 | 0.96971 | 0.92127 | -0.048431 |  | 0.925 | 1.05 | 0.047089 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | STK418 2 | 0.96971 | 0.92127 | -0.048431 |  | 0.925 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | STK418 2 | 0.96971 | 0.92127 | -0.048431 |  | 0.925 | 1.05 | 0.13688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | STK418 2 | 0.96971 | 0.92127 | -0.048431 |  | 0.925 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | STK418 2 | 0.96971 | 0.92127 | -0.048431 |  | 0.925 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | STK418 2 | 0.96971 | 0.92127 | -0.048431 |  | 0.925 | 1.05 | 0.039752 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | STK418 2 | 0.96971 | 0.92127 | -0.048431 |  | 0.925 | 1.05 | 0.041972 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | STK418 2 | 0.96971 | 0.92127 | -0.048431 |  | 0.925 | 1.05 | 0.054397 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | STK418 2 | 0.96971 | 0.92127 | -0.048431 |  | 0.925 | 1.05 | 0.073688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | STK418 2 | 0.96971 | 0.92127 | -0.048431 |  | 0.925 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | STK418 2 | 0.96971 | 0.92127 | -0.048431 |  | 0.925 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | STK418 2 | 0.96971 | 0.92127 | -0.048431 |  | 0.925 | 1.05 | 0.072188 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | STK418 2 | 0.96971 | 0.92127 | -0.048431 |  | 0.925 | 1.05 | 0.042186 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | STK418 2 | 0.96971 | 0.92127 | -0.048431 |  | 0.925 | 1.05 | 0.041423 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | STK418 2 | 0.96971 | 0.92127 | -0.048431 |  | 0.925 | 1.05 | 0.050171 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | STK418 2 | 0.96971 | 0.92127 | -0.048431 |  | 0.925 | 1.05 | 0.04386 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | STK418 2 | 0.96971 | 0.92127 | -0.048431 |  | 0.925 | 1.05 | 0.050218 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | STK418 2 | 0.96971 | 0.92127 | -0.048431 |  | 0.925 | 1.05 | 0.040041 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | STK418 2 | 0.96971 | 0.92127 | -0.048431 |  | 0.925 | 1.05 | 0.038784 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | STK418 2 | 0.96719 | 0.92482 | -0.042369 |  | 0.925 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | STK418 2 | 0.96719 | 0.92482 | -0.042369 |  | 0.925 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | STK418 2 | 0.96719 | 0.92482 | -0.042369 |  | 0.925 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | STK418 2 | 0.96719 | 0.92482 | -0.042369 |  | 0.925 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | STK418 2 | 0.96719 | 0.92482 | -0.042369 |  | 0.925 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | STK418 2 | 0.96719 | 0.92482 | -0.042369 |  | 0.925 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | STK418 2 | 0.96719 | 0.92482 | -0.042369 |  | 0.925 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | STK418 2 | 0.96719 | 0.92482 | -0.042369 |  | 0.925 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | STK418 2 | 0.96719 | 0.92482 | -0.042369 |  | 0.925 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | STK418 2 | 0.96719 | 0.92482 | -0.042369 |  | 0.925 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | STK418 2 | 0.96719 | 0.92482 | -0.042369 |  | 0.925 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | STK418 2 | 0.96719 | 0.92482 | -0.042369 |  | 0.925 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | STK418 2 | 0.96719 | 0.92482 | -0.042369 |  | 0.925 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | STK418 2 | 0.96719 | 0.92482 | -0.042369 |  | 0.925 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | STK418 2 | 0.96719 | 0.92482 | -0.042369 |  | 0.925 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | STK418 2 | 0.96719 | 0.92482 | -0.042369 |  | 0.925 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | STK418 2 | 0.96719 | 0.92482 | -0.042369 |  | 0.925 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | STK418 2 | 0.96719 | 0.92482 | -0.042369 |  | 0.925 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | STK418 2 | 0.96719 | 0.92482 | -0.042369 |  | 0.925 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | STK418 2 | 0.96719 | 0.92482 | -0.042369 |  | 0.925 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | STK418 2 | 0.9663 | 0.89867 | -0.067635 |  | 0.925 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | STK418 2 | 0.9663 | 0.89867 | -0.067635 |  | 0.925 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | STK418 2 | 0.9663 | 0.89867 | -0.067635 |  | 0.925 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | STK418 2 | 0.9663 | 0.89867 | -0.067635 |  | 0.925 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | STK418 2 | 0.9663 | 0.89867 | -0.067635 |  | 0.925 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | STK418 2 | 0.9663 | 0.89867 | -0.067635 |  | 0.925 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | STK418 2 | 0.9663 | 0.89867 | -0.067635 |  | 0.925 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | STK418 2 | 0.9663 | 0.89867 | -0.067635 |  | 0.925 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | STK418 2 | 0.9663 | 0.89867 | -0.067635 |  | 0.925 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | STK418 2 | 0.9663 | 0.89867 | -0.067635 |  | 0.925 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | STK418 2 | 0.9663 | 0.89867 | -0.067635 |  | 0.925 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | STK418 2 | 0.9663 | 0.89867 | -0.067635 |  | 0.925 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | STK418 2 | 0.9663 | 0.89867 | -0.067635 |  | 0.925 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | STK418 2 | 0.9663 | 0.89867 | -0.067635 |  | 0.925 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | STK418 2 | 0.9663 | 0.89867 | -0.067635 |  | 0.925 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | STK418 2 | 0.9663 | 0.89867 | -0.067635 |  | 0.925 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | STK418 2 | 0.9663 | 0.89867 | -0.067635 |  | 0.925 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | STK418 2 | 0.9663 | 0.89867 | -0.067635 |  | 0.925 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | STK418 2 | 0.9663 | 0.89867 | -0.067635 |  | 0.925 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | STK418 2 | 0.9663 | 0.89867 | -0.067635 |  | 0.925 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | STK418 2 | 0.9663 | 0.89867 | -0.067635 |  | 0.925 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | STK418 2 | 0.9663 | 0.89867 | -0.067635 |  | 0.925 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | STK418 2 | 0.9663 | 0.89867 | -0.067635 |  | 0.925 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | STK418 2 | 0.9663 | 0.89867 | -0.067635 |  | 0.925 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | STK418 2 | 0.9663 | 0.89867 | -0.067635 |  | 0.925 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | STK418 2 | 0.9663 | 0.89867 | -0.067635 |  | 0.925 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | STK418 2 | 0.9663 | 0.89867 | -0.067635 |  | 0.925 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | STK418 2 | 0.9663 | 0.89867 | -0.067635 |  | 0.925 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SUMMIT 6 | 0.98368 | 0.94098 | -0.042695 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | SUMMIT 6 | 0.98368 | 0.94098 | -0.042695 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SUMMIT 6 | 0.98368 | 0.94098 | -0.042695 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SUMMIT 6 | 0.98368 | 0.94098 | -0.042695 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SUMMIT 6 | 0.98368 | 0.94098 | -0.042695 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | SUMMIT 6 | 0.98368 | 0.94098 | -0.042695 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SUMMIT 6 | 0.98368 | 0.94098 | -0.042695 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | SUMMIT 6 | 0.98368 | 0.94098 | -0.042695 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | SUMMIT 6 | 0.98368 | 0.94098 | -0.042695 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SUMMIT 6 | 0.98368 | 0.94098 | -0.042695 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SUMMIT 6 | 0.98368 | 0.94098 | -0.042695 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SUMMIT 6 | 0.98368 | 0.94098 | -0.042695 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SUMMIT 6 | 0.98368 | 0.94098 | -0.042695 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SUMMIT 6 | 0.98368 | 0.94098 | -0.042695 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SUMMIT 6 | 0.98368 | 0.94098 | -0.042695 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SUMMIT 6 | 0.98368 | 0.94098 | -0.042695 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SUMMIT 6 | 0.98368 | 0.94098 | -0.042695 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SUMMIT 6 | 0.98368 | 0.94098 | -0.042695 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | SUMMIT 6 | 0.98368 | 0.94098 | -0.042695 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | SUMMIT 6 | 0.98368 | 0.94098 | -0.042695 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SUMMIT 6 | 0.98368 | 0.94098 | -0.042695 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SUMMIT 6 | 0.98368 | 0.94098 | -0.042695 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | SUMMIT 6 | 0.98368 | 0.94098 | -0.042695 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SUMMIT 6 | 0.98368 | 0.94098 | -0.042695 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SUMMIT 6 | 0.98368 | 0.94098 | -0.042695 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SUMMIT 6 | 0.98368 | 0.94098 | -0.042695 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SUMMIT 6 | 0.98368 | 0.94098 | -0.042695 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | SUMMIT 6 | 0.98368 | 0.94098 | -0.042695 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | SUMMIT 7 | 0.9777 | 0.94071 | -0.036994 |  | 0.95 | 1.05 | 0.064516 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SUMMIT 7 | 0.97455 | 0.94349 | -0.031052 |  | 0.95 | 1.05 | 0.03965 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SUMMIT 7 | 0.97455 | 0.94349 | -0.031052 |  | 0.95 | 1.05 | 0.042938 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SUMMIT 7 | 0.97455 | 0.94349 | -0.031052 |  | 0.95 | 1.05 | 0.032864 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SUMMIT 7 | 0.97455 | 0.94349 | -0.031052 |  | 0.95 | 1.05 | 0.034629 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | SUMMIT 7 | 0.97455 | 0.94349 | -0.031052 |  | 0.95 | 1.05 | 0.036988 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SUMMIT 7 | 0.97455 | 0.94349 | -0.031052 |  | 0.95 | 1.05 | 0.03396 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | SUMMIT 7 | 0.97455 | 0.94349 | -0.031052 |  | 0.95 | 1.05 | 0.030296 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SUMMIT 7 | 0.97455 | 0.94349 | -0.031052 |  | 0.95 | 1.05 | 0.037836 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SUMMIT 7 | 0.97455 | 0.94349 | -0.031052 |  | 0.95 | 1.05 | 0.036214 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SUMMIT 7 | 0.97455 | 0.94349 | -0.031052 |  | 0.95 | 1.05 | 0.055483 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SUMMIT 7 | 0.97455 | 0.94349 | -0.031052 |  | 0.95 | 1.05 | 0.036214 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SUMMIT 7 | 0.97455 | 0.94349 | -0.031052 |  | 0.95 | 1.05 | 0.037031 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SUMMIT 7 | 0.97455 | 0.94349 | -0.031052 |  | 0.95 | 1.05 | 0.03728 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SUMMIT 7 | 0.97455 | 0.94349 | -0.031052 |  | 0.95 | 1.05 | 0.034689 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SUMMIT 7 | 0.97455 | 0.94349 | -0.031052 |  | 0.95 | 1.05 | 0.033481 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SUMMIT 7 | 0.97455 | 0.94349 | -0.031052 |  | 0.95 | 1.05 | 0.035246 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SUMMIT 7 | 0.97455 | 0.94349 | -0.031052 |  | 0.95 | 1.05 | 0.03235 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SUMMIT 7 | 0.97455 | 0.94349 | -0.031052 |  | 0.95 | 1.05 | 0.031498 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SUMMIT 7 | 0.97455 | 0.94349 | -0.031052 |  | 0.95 | 1.05 | 0.033388 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SUMMIT 7 | 0.97455 | 0.94349 | -0.031052 |  | 0.95 | 1.05 | 0.034867 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SUMMIT 7 | 0.97341 | 0.94144 | -0.031961 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SUMMIT 7 | 0.97341 | 0.94144 | -0.031961 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SUMMIT 7 | 0.97341 | 0.94144 | -0.031961 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SUMMIT 7 | 0.97341 | 0.94144 | -0.031961 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SUMMIT 7 | 0.97341 | 0.94144 | -0.031961 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SUMMIT 7 | 0.97341 | 0.94144 | -0.031961 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SUMMIT 7 | 0.97341 | 0.94144 | -0.031961 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SUMMIT 7 | 0.97341 | 0.94144 | -0.031961 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SUMMIT 7 | 0.97341 | 0.94144 | -0.031961 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SUMMIT 7 | 0.97341 | 0.94144 | -0.031961 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SUMMIT 7 | 0.97341 | 0.94144 | -0.031961 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SUMMIT 7 | 0.97341 | 0.94144 | -0.031961 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SUMMIT 7 | 0.97341 | 0.94144 | -0.031961 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SUMMIT 7 | 0.97341 | 0.94144 | -0.031961 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SUMMIT 7 | 0.97341 | 0.94144 | -0.031961 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SUMMIT 7 | 0.97341 | 0.94144 | -0.031961 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SUMMIT 7 | 0.97341 | 0.94144 | -0.031961 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SUMMIT 7 | 0.97341 | 0.94144 | -0.031961 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SUMMIT 7 | 0.97341 | 0.94144 | -0.031961 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SUMMIT 7 | 0.97341 | 0.94144 | -0.031961 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SUMMIT 7 | 0.97784 | 0.94204 | -0.035799 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SUMMIT 7 | 0.97784 | 0.94204 | -0.035799 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SUMMIT 7 | 0.97784 | 0.94204 | -0.035799 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SUMMIT 7 | 0.97784 | 0.94204 | -0.035799 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SUMMIT 7 | 0.97784 | 0.94204 | -0.035799 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SUMMIT 7 | 0.97784 | 0.94204 | -0.035799 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SUMMIT 7 | 0.97784 | 0.94204 | -0.035799 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SUMMIT 7 | 0.97784 | 0.94204 | -0.035799 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SUMMIT 7 | 0.97784 | 0.94204 | -0.035799 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SUMMIT 7 | 0.97784 | 0.94204 | -0.035799 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SUMMIT 7 | 0.97784 | 0.94204 | -0.035799 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SUMMIT 7 | 0.97784 | 0.94204 | -0.035799 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SUMMIT 7 | 0.97784 | 0.94204 | -0.035799 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SUMMIT 7 | 0.97784 | 0.94204 | -0.035799 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SUMMIT 7 | 0.97784 | 0.94204 | -0.035799 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SUMMIT 7 | 0.97784 | 0.94204 | -0.035799 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SUMMIT 7 | 0.97784 | 0.94204 | -0.035799 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SUMMIT 7 | 0.97784 | 0.94204 | -0.035799 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SUMMIT 7 | 0.97784 | 0.94204 | -0.035799 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SUMMIT 7 | 0.97784 | 0.94204 | -0.035799 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SUMMIT 7 | 0.97356 | 0.91208 | -0.061484 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | SUMMIT 7 | 0.97356 | 0.91208 | -0.061484 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SUMMIT 7 | 0.97356 | 0.91208 | -0.061484 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SUMMIT 7 | 0.97356 | 0.91208 | -0.061484 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SUMMIT 7 | 0.97356 | 0.91208 | -0.061484 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | SUMMIT 7 | 0.97356 | 0.91208 | -0.061484 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SUMMIT 7 | 0.97356 | 0.91208 | -0.061484 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | SUMMIT 7 | 0.97356 | 0.91208 | -0.061484 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | SUMMIT 7 | 0.97356 | 0.91208 | -0.061484 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SUMMIT 7 | 0.97356 | 0.91208 | -0.061484 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SUMMIT 7 | 0.97356 | 0.91208 | -0.061484 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SUMMIT 7 | 0.97356 | 0.91208 | -0.061484 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SUMMIT 7 | 0.97356 | 0.91208 | -0.061484 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SUMMIT 7 | 0.97356 | 0.91208 | -0.061484 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SUMMIT 7 | 0.97356 | 0.91208 | -0.061484 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SUMMIT 7 | 0.97356 | 0.91208 | -0.061484 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SUMMIT 7 | 0.97356 | 0.91208 | -0.061484 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SUMMIT 7 | 0.97356 | 0.91208 | -0.061484 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | SUMMIT 7 | 0.97356 | 0.91208 | -0.061484 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | SUMMIT 7 | 0.97356 | 0.91208 | -0.061484 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SUMMIT 7 | 0.97356 | 0.91208 | -0.061484 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SUMMIT 7 | 0.97356 | 0.91208 | -0.061484 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | SUMMIT 7 | 0.97356 | 0.91208 | -0.061484 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SUMMIT 7 | 0.97356 | 0.91208 | -0.061484 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SUMMIT 7 | 0.97356 | 0.91208 | -0.061484 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SUMMIT 7 | 0.97356 | 0.91208 | -0.061484 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SUMMIT 7 | 0.97356 | 0.91208 | -0.061484 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | SUMMIT 7 | 0.97356 | 0.91208 | -0.061484 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SUNSHINE5 | 0.98823 | 0.9183 | -0.069932 |  | 0.92 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | SUNSHINE5 | 0.98823 | 0.9183 | -0.069932 |  | 0.92 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SUNSHINE5 | 0.98823 | 0.9183 | -0.069932 |  | 0.92 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SUNSHINE5 | 0.98823 | 0.9183 | -0.069932 |  | 0.92 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SUNSHINE5 | 0.98823 | 0.9183 | -0.069932 |  | 0.92 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SUNSHINE5 | 0.98823 | 0.9183 | -0.069932 |  | 0.92 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SUNSHINE5 | 0.98823 | 0.9183 | -0.069932 |  | 0.92 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SUNSHINE5 | 0.98823 | 0.9183 | -0.069932 |  | 0.92 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SUNSHINE5 | 0.98823 | 0.9183 | -0.069932 |  | 0.92 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SUNSHINE5 | 0.98823 | 0.9183 | -0.069932 |  | 0.92 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | SUNSHINE5 | 0.98823 | 0.9183 | -0.069932 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | SUNSHINE5 | 0.98823 | 0.9183 | -0.069932 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SUNSHINE5 | 0.98823 | 0.9183 | -0.069932 |  | 0.92 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SUNSHINE5 | 0.98823 | 0.9183 | -0.069932 |  | 0.92 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SUNSHINE5 | 0.98823 | 0.9183 | -0.069932 |  | 0.92 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | SUNSHINE5 | 0.9888 | 0.91925 | -0.069553 |  | 0.92 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SUNSHINE5 | 0.9888 | 0.91925 | -0.069553 |  | 0.92 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SUNSHINE5 | 0.9888 | 0.91925 | -0.069553 |  | 0.92 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SUNSHINE5 | 0.9888 | 0.91925 | -0.069553 |  | 0.92 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SUNSHINE5 | 0.9888 | 0.91925 | -0.069553 |  | 0.92 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SUNSHINE5 | 0.9888 | 0.91925 | -0.069553 |  | 0.92 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SUNSHINE5 | 0.9888 | 0.91925 | -0.069553 |  | 0.92 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SUNSHINE5 | 0.9888 | 0.91925 | -0.069553 |  | 0.92 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SUNSHINE5 | 0.9888 | 0.91925 | -0.069553 |  | 0.92 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | SUNSHINE5 | 0.9888 | 0.91925 | -0.069553 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | SUNSHINE5 | 0.9888 | 0.91925 | -0.069553 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SUNSHINE5 | 0.9888 | 0.91925 | -0.069553 |  | 0.92 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SUNSHINE5 | 0.9888 | 0.91925 | -0.069553 |  | 0.92 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SUNSHINE5 | 0.9888 | 0.91925 | -0.069553 |  | 0.92 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SWISVAL6 | 0.96898 | 0.92783 | -0.041151 |  | 0.95 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SWISVAL6 | 0.96898 | 0.92783 | -0.041151 |  | 0.95 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SWISVAL6 | 0.96898 | 0.92783 | -0.041151 |  | 0.95 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SWISVAL6 | 0.96898 | 0.92783 | -0.041151 |  | 0.95 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SWISVAL6 | 0.96898 | 0.92783 | -0.041151 |  | 0.95 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SWISVAL6 | 0.96898 | 0.92783 | -0.041151 |  | 0.95 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SWISVAL6 | 0.96898 | 0.92783 | -0.041151 |  | 0.95 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SWISVAL6 | 0.96898 | 0.92783 | -0.041151 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SWISVAL6 | 0.96898 | 0.92783 | -0.041151 |  | 0.95 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SWISVAL6 | 0.96898 | 0.92783 | -0.041151 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SWISVAL6 | 0.96898 | 0.92783 | -0.041151 |  | 0.95 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SWISVAL6 | 0.96898 | 0.92783 | -0.041151 |  | 0.95 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SWISVAL6 | 0.96898 | 0.92783 | -0.041151 |  | 0.95 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SWISVAL6 | 0.96898 | 0.92783 | -0.041151 |  | 0.95 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SWISVAL6 | 0.96898 | 0.92783 | -0.041151 |  | 0.95 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SWISVAL6 | 0.96898 | 0.92783 | -0.041151 |  | 0.95 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SWISVAL6 | 0.96898 | 0.92783 | -0.041151 |  | 0.95 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SWISVAL6 | 0.96898 | 0.92783 | -0.041151 |  | 0.95 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SWISVAL6 | 0.96898 | 0.92783 | -0.041151 |  | 0.95 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SWISVAL6 | 0.96898 | 0.92783 | -0.041151 |  | 0.95 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SWISVAL6 | 0.96554 | 0.91973 | -0.045814 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SWISVAL6 | 0.96554 | 0.91973 | -0.045814 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SWISVAL6 | 0.96554 | 0.91973 | -0.045814 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SWISVAL6 | 0.96554 | 0.91973 | -0.045814 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SWISVAL6 | 0.96554 | 0.91973 | -0.045814 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SWISVAL6 | 0.96554 | 0.91973 | -0.045814 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SWISVAL6 | 0.96554 | 0.91973 | -0.045814 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SWISVAL6 | 0.96554 | 0.91973 | -0.045814 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SWISVAL6 | 0.96554 | 0.91973 | -0.045814 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SWISVAL6 | 0.96554 | 0.91973 | -0.045814 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SWISVAL6 | 0.96554 | 0.91973 | -0.045814 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SWISVAL6 | 0.96554 | 0.91973 | -0.045814 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SWISVAL6 | 0.96554 | 0.91973 | -0.045814 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SWISVAL6 | 0.96554 | 0.91973 | -0.045814 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SWISVAL6 | 0.96554 | 0.91973 | -0.045814 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SWISVAL6 | 0.96554 | 0.91973 | -0.045814 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SWISVAL6 | 0.96554 | 0.91973 | -0.045814 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SWISVAL6 | 0.96554 | 0.91973 | -0.045814 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SWISVAL6 | 0.96554 | 0.91973 | -0.045814 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SWISVAL6 | 0.96554 | 0.91973 | -0.045814 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SWISVAL6 | 0.9716 | 0.92 | -0.051595 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SWISVAL6 | 0.9716 | 0.92 | -0.051595 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SWISVAL6 | 0.9716 | 0.92 | -0.051595 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SWISVAL6 | 0.9716 | 0.92 | -0.051595 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SWISVAL6 | 0.9716 | 0.92 | -0.051595 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SWISVAL6 | 0.9716 | 0.92 | -0.051595 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SWISVAL6 | 0.9716 | 0.92 | -0.051595 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SWISVAL6 | 0.9716 | 0.92 | -0.051595 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SWISVAL6 | 0.9716 | 0.92 | -0.051595 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SWISVAL6 | 0.9716 | 0.92 | -0.051595 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SWISVAL6 | 0.9716 | 0.92 | -0.051595 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SWISVAL6 | 0.9716 | 0.92 | -0.051595 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SWISVAL6 | 0.9716 | 0.92 | -0.051595 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SWISVAL6 | 0.9716 | 0.92 | -0.051595 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SWISVAL6 | 0.9716 | 0.92 | -0.051595 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SWISVAL6 | 0.9716 | 0.92 | -0.051595 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SWISVAL6 | 0.9716 | 0.92 | -0.051595 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SWISVAL6 | 0.9716 | 0.92 | -0.051595 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SWISVAL6 | 0.9716 | 0.92 | -0.051595 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SWISVAL6 | 0.9716 | 0.92 | -0.051595 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SWISVAL6 | 0.97461 | 0.91673 | -0.057886 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | SWISVAL6 | 0.97461 | 0.91673 | -0.057886 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SWISVAL6 | 0.97461 | 0.91673 | -0.057886 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SWISVAL6 | 0.97461 | 0.91673 | -0.057886 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SWISVAL6 | 0.97461 | 0.91673 | -0.057886 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | SWISVAL6 | 0.97461 | 0.91673 | -0.057886 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SWISVAL6 | 0.97461 | 0.91673 | -0.057886 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | SWISVAL6 | 0.97461 | 0.91673 | -0.057886 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | SWISVAL6 | 0.97461 | 0.91673 | -0.057886 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SWISVAL6 | 0.97461 | 0.91673 | -0.057886 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SWISVAL6 | 0.97461 | 0.91673 | -0.057886 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SWISVAL6 | 0.97461 | 0.91673 | -0.057886 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SWISVAL6 | 0.97461 | 0.91673 | -0.057886 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SWISVAL6 | 0.97461 | 0.91673 | -0.057886 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SWISVAL6 | 0.97461 | 0.91673 | -0.057886 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SWISVAL6 | 0.97461 | 0.91673 | -0.057886 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SWISVAL6 | 0.97461 | 0.91673 | -0.057886 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SWISVAL6 | 0.97461 | 0.91673 | -0.057886 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | SWISVAL6 | 0.97461 | 0.91673 | -0.057886 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | SWISVAL6 | 0.97461 | 0.91673 | -0.057886 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SWISVAL6 | 0.97461 | 0.91673 | -0.057886 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SWISVAL6 | 0.97461 | 0.91673 | -0.057886 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | SWISVAL6 | 0.97461 | 0.91673 | -0.057886 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SWISVAL6 | 0.97461 | 0.91673 | -0.057886 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SWISVAL6 | 0.97461 | 0.91673 | -0.057886 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SWISVAL6 | 0.97461 | 0.91673 | -0.057886 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SWISVAL6 | 0.97461 | 0.91673 | -0.057886 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | SWISVAL6 | 0.97461 | 0.91673 | -0.057886 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SWISVAL6 | 0.96854 | 0.92651 | -0.042033 |  | 0.95 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SWISVAL6 | 0.96854 | 0.92651 | -0.042033 |  | 0.95 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SWISVAL6 | 0.96854 | 0.92651 | -0.042033 |  | 0.95 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SWISVAL6 | 0.96854 | 0.92651 | -0.042033 |  | 0.95 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SWISVAL6 | 0.96854 | 0.92651 | -0.042033 |  | 0.95 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SWISVAL6 | 0.96854 | 0.92651 | -0.042033 |  | 0.95 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SWISVAL6 | 0.96854 | 0.92651 | -0.042033 |  | 0.95 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SWISVAL6 | 0.96854 | 0.92651 | -0.042033 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SWISVAL6 | 0.96854 | 0.92651 | -0.042033 |  | 0.95 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SWISVAL6 | 0.96854 | 0.92651 | -0.042033 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SWISVAL6 | 0.96854 | 0.92651 | -0.042033 |  | 0.95 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SWISVAL6 | 0.96854 | 0.92651 | -0.042033 |  | 0.95 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SWISVAL6 | 0.96854 | 0.92651 | -0.042033 |  | 0.95 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SWISVAL6 | 0.96854 | 0.92651 | -0.042033 |  | 0.95 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SWISVAL6 | 0.96854 | 0.92651 | -0.042033 |  | 0.95 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SWISVAL6 | 0.96854 | 0.92651 | -0.042033 |  | 0.95 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SWISVAL6 | 0.96854 | 0.92651 | -0.042033 |  | 0.95 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SWISVAL6 | 0.96854 | 0.92651 | -0.042033 |  | 0.95 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SWISVAL6 | 0.96854 | 0.92651 | -0.042033 |  | 0.95 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SWISVAL6 | 0.96854 | 0.92651 | -0.042033 |  | 0.95 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SWISVAL7 | 0.96662 | 0.91848 | -0.048144 |  | 0.95 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SWISVAL7 | 0.96662 | 0.91848 | -0.048144 |  | 0.95 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SWISVAL7 | 0.96662 | 0.91848 | -0.048144 |  | 0.95 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SWISVAL7 | 0.96662 | 0.91848 | -0.048144 |  | 0.95 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SWISVAL7 | 0.96662 | 0.91848 | -0.048144 |  | 0.95 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SWISVAL7 | 0.96662 | 0.91848 | -0.048144 |  | 0.95 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SWISVAL7 | 0.96662 | 0.91848 | -0.048144 |  | 0.95 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SWISVAL7 | 0.96662 | 0.91848 | -0.048144 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SWISVAL7 | 0.96662 | 0.91848 | -0.048144 |  | 0.95 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SWISVAL7 | 0.96662 | 0.91848 | -0.048144 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SWISVAL7 | 0.96662 | 0.91848 | -0.048144 |  | 0.95 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SWISVAL7 | 0.96662 | 0.91848 | -0.048144 |  | 0.95 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SWISVAL7 | 0.96662 | 0.91848 | -0.048144 |  | 0.95 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SWISVAL7 | 0.96662 | 0.91848 | -0.048144 |  | 0.95 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SWISVAL7 | 0.96662 | 0.91848 | -0.048144 |  | 0.95 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SWISVAL7 | 0.96662 | 0.91848 | -0.048144 |  | 0.95 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SWISVAL7 | 0.96662 | 0.91848 | -0.048144 |  | 0.95 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SWISVAL7 | 0.96662 | 0.91848 | -0.048144 |  | 0.95 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SWISVAL7 | 0.96662 | 0.91848 | -0.048144 |  | 0.95 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SWISVAL7 | 0.96662 | 0.91848 | -0.048144 |  | 0.95 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SWISVAL7 | 0.96243 | 0.90956 | -0.052877 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SWISVAL7 | 0.96243 | 0.90956 | -0.052877 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SWISVAL7 | 0.96243 | 0.90956 | -0.052877 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SWISVAL7 | 0.96243 | 0.90956 | -0.052877 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SWISVAL7 | 0.96243 | 0.90956 | -0.052877 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SWISVAL7 | 0.96243 | 0.90956 | -0.052877 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SWISVAL7 | 0.96243 | 0.90956 | -0.052877 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SWISVAL7 | 0.96243 | 0.90956 | -0.052877 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SWISVAL7 | 0.96243 | 0.90956 | -0.052877 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SWISVAL7 | 0.96243 | 0.90956 | -0.052877 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SWISVAL7 | 0.96243 | 0.90956 | -0.052877 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SWISVAL7 | 0.96243 | 0.90956 | -0.052877 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SWISVAL7 | 0.96243 | 0.90956 | -0.052877 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SWISVAL7 | 0.96243 | 0.90956 | -0.052877 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SWISVAL7 | 0.96243 | 0.90956 | -0.052877 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SWISVAL7 | 0.96243 | 0.90956 | -0.052877 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SWISVAL7 | 0.96243 | 0.90956 | -0.052877 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SWISVAL7 | 0.96243 | 0.90956 | -0.052877 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SWISVAL7 | 0.96243 | 0.90956 | -0.052877 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SWISVAL7 | 0.96243 | 0.90956 | -0.052877 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SWISVAL7 | 0.96974 | 0.90925 | -0.060493 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SWISVAL7 | 0.96974 | 0.90925 | -0.060493 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SWISVAL7 | 0.96974 | 0.90925 | -0.060493 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SWISVAL7 | 0.96974 | 0.90925 | -0.060493 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SWISVAL7 | 0.96974 | 0.90925 | -0.060493 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SWISVAL7 | 0.96974 | 0.90925 | -0.060493 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SWISVAL7 | 0.96974 | 0.90925 | -0.060493 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SWISVAL7 | 0.96974 | 0.90925 | -0.060493 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SWISVAL7 | 0.96974 | 0.90925 | -0.060493 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SWISVAL7 | 0.96974 | 0.90925 | -0.060493 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SWISVAL7 | 0.96974 | 0.90925 | -0.060493 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SWISVAL7 | 0.96974 | 0.90925 | -0.060493 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SWISVAL7 | 0.96974 | 0.90925 | -0.060493 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SWISVAL7 | 0.96974 | 0.90925 | -0.060493 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SWISVAL7 | 0.96974 | 0.90925 | -0.060493 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SWISVAL7 | 0.96974 | 0.90925 | -0.060493 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SWISVAL7 | 0.96974 | 0.90925 | -0.060493 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SWISVAL7 | 0.96974 | 0.90925 | -0.060493 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SWISVAL7 | 0.96974 | 0.90925 | -0.060493 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SWISVAL7 | 0.96974 | 0.90925 | -0.060493 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SWISVAL7 | 0.97402 | 0.90507 | -0.068955 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | SWISVAL7 | 0.97402 | 0.90507 | -0.068955 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SWISVAL7 | 0.97402 | 0.90507 | -0.068955 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SWISVAL7 | 0.97402 | 0.90507 | -0.068955 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SWISVAL7 | 0.97402 | 0.90507 | -0.068955 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | SWISVAL7 | 0.97402 | 0.90507 | -0.068955 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SWISVAL7 | 0.97402 | 0.90507 | -0.068955 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | SWISVAL7 | 0.97402 | 0.90507 | -0.068955 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | SWISVAL7 | 0.97402 | 0.90507 | -0.068955 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SWISVAL7 | 0.97402 | 0.90507 | -0.068955 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SWISVAL7 | 0.97402 | 0.90507 | -0.068955 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SWISVAL7 | 0.97402 | 0.90507 | -0.068955 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SWISVAL7 | 0.97402 | 0.90507 | -0.068955 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SWISVAL7 | 0.97402 | 0.90507 | -0.068955 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SWISVAL7 | 0.97402 | 0.90507 | -0.068955 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SWISVAL7 | 0.97402 | 0.90507 | -0.068955 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SWISVAL7 | 0.97402 | 0.90507 | -0.068955 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SWISVAL7 | 0.97402 | 0.90507 | -0.068955 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | SWISVAL7 | 0.97402 | 0.90507 | -0.068955 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | SWISVAL7 | 0.97402 | 0.90507 | -0.068955 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SWISVAL7 | 0.97402 | 0.90507 | -0.068955 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SWISVAL7 | 0.97402 | 0.90507 | -0.068955 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | SWISVAL7 | 0.97402 | 0.90507 | -0.068955 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SWISVAL7 | 0.97402 | 0.90507 | -0.068955 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SWISVAL7 | 0.97402 | 0.90507 | -0.068955 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SWISVAL7 | 0.97402 | 0.90507 | -0.068955 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SWISVAL7 | 0.97402 | 0.90507 | -0.068955 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | SWISVAL7 | 0.97402 | 0.90507 | -0.068955 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SWISVAL7 | 0.96608 | 0.91709 | -0.048985 |  | 0.95 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SWISVAL7 | 0.96608 | 0.91709 | -0.048985 |  | 0.95 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SWISVAL7 | 0.96608 | 0.91709 | -0.048985 |  | 0.95 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SWISVAL7 | 0.96608 | 0.91709 | -0.048985 |  | 0.95 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SWISVAL7 | 0.96608 | 0.91709 | -0.048985 |  | 0.95 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SWISVAL7 | 0.96608 | 0.91709 | -0.048985 |  | 0.95 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SWISVAL7 | 0.96608 | 0.91709 | -0.048985 |  | 0.95 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SWISVAL7 | 0.96608 | 0.91709 | -0.048985 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SWISVAL7 | 0.96608 | 0.91709 | -0.048985 |  | 0.95 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SWISVAL7 | 0.96608 | 0.91709 | -0.048985 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SWISVAL7 | 0.96608 | 0.91709 | -0.048985 |  | 0.95 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SWISVAL7 | 0.96608 | 0.91709 | -0.048985 |  | 0.95 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SWISVAL7 | 0.96608 | 0.91709 | -0.048985 |  | 0.95 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SWISVAL7 | 0.96608 | 0.91709 | -0.048985 |  | 0.95 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SWISVAL7 | 0.96608 | 0.91709 | -0.048985 |  | 0.95 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SWISVAL7 | 0.96608 | 0.91709 | -0.048985 |  | 0.95 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SWISVAL7 | 0.96608 | 0.91709 | -0.048985 |  | 0.95 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SWISVAL7 | 0.96608 | 0.91709 | -0.048985 |  | 0.95 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SWISVAL7 | 0.96608 | 0.91709 | -0.048985 |  | 0.95 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SWISVAL7 | 0.96608 | 0.91709 | -0.048985 |  | 0.95 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SWITZER5 | 0.96467 | 0.92736 | -0.03731 |  | 0.93 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SWITZER5 | 0.96467 | 0.92736 | -0.03731 |  | 0.93 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SWITZER5 | 0.96467 | 0.92736 | -0.03731 |  | 0.93 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SWITZER5 | 0.96467 | 0.92736 | -0.03731 |  | 0.93 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SWITZER5 | 0.96467 | 0.92736 | -0.03731 |  | 0.93 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SWITZER5 | 0.96467 | 0.92736 | -0.03731 |  | 0.93 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SWITZER5 | 0.96467 | 0.92736 | -0.03731 |  | 0.93 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SWITZER5 | 0.96467 | 0.92736 | -0.03731 |  | 0.93 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SWITZER5 | 0.96467 | 0.92736 | -0.03731 |  | 0.93 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SWITZER5 | 0.96467 | 0.92736 | -0.03731 |  | 0.93 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SWITZER5 | 0.96467 | 0.92736 | -0.03731 |  | 0.93 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SWITZER5 | 0.96467 | 0.92736 | -0.03731 |  | 0.93 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SWITZER5 | 0.96467 | 0.92736 | -0.03731 |  | 0.93 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SWITZER5 | 0.96467 | 0.92736 | -0.03731 |  | 0.93 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SWITZER5 | 0.96467 | 0.92736 | -0.03731 |  | 0.93 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SWITZER5 | 0.96467 | 0.92736 | -0.03731 |  | 0.93 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SWITZER5 | 0.96467 | 0.92736 | -0.03731 |  | 0.93 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SWITZER5 | 0.96467 | 0.92736 | -0.03731 |  | 0.93 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SWITZER5 | 0.96467 | 0.92736 | -0.03731 |  | 0.93 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SWITZER5 | 0.96467 | 0.92736 | -0.03731 |  | 0.93 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SWITZER5 | 0.95854 | 0.91764 | -0.040897 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SWITZER5 | 0.95854 | 0.91764 | -0.040897 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SWITZER5 | 0.95854 | 0.91764 | -0.040897 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SWITZER5 | 0.95854 | 0.91764 | -0.040897 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SWITZER5 | 0.95854 | 0.91764 | -0.040897 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SWITZER5 | 0.95854 | 0.91764 | -0.040897 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SWITZER5 | 0.95854 | 0.91764 | -0.040897 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SWITZER5 | 0.95854 | 0.91764 | -0.040897 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SWITZER5 | 0.95854 | 0.91764 | -0.040897 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SWITZER5 | 0.95854 | 0.91764 | -0.040897 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SWITZER5 | 0.95854 | 0.91764 | -0.040897 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SWITZER5 | 0.95854 | 0.91764 | -0.040897 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SWITZER5 | 0.95854 | 0.91764 | -0.040897 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SWITZER5 | 0.95854 | 0.91764 | -0.040897 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SWITZER5 | 0.95854 | 0.91764 | -0.040897 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SWITZER5 | 0.95854 | 0.91764 | -0.040897 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SWITZER5 | 0.95854 | 0.91764 | -0.040897 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SWITZER5 | 0.95854 | 0.91764 | -0.040897 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SWITZER5 | 0.95854 | 0.91764 | -0.040897 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SWITZER5 | 0.95854 | 0.91764 | -0.040897 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SWITZER5 | 0.96806 | 0.92253 | -0.045529 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SWITZER5 | 0.96806 | 0.92253 | -0.045529 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SWITZER5 | 0.96806 | 0.92253 | -0.045529 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SWITZER5 | 0.96806 | 0.92253 | -0.045529 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SWITZER5 | 0.96806 | 0.92253 | -0.045529 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SWITZER5 | 0.96806 | 0.92253 | -0.045529 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SWITZER5 | 0.96806 | 0.92253 | -0.045529 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SWITZER5 | 0.96806 | 0.92253 | -0.045529 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SWITZER5 | 0.96806 | 0.92253 | -0.045529 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SWITZER5 | 0.96806 | 0.92253 | -0.045529 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SWITZER5 | 0.96806 | 0.92253 | -0.045529 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SWITZER5 | 0.96806 | 0.92253 | -0.045529 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SWITZER5 | 0.96806 | 0.92253 | -0.045529 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SWITZER5 | 0.96806 | 0.92253 | -0.045529 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SWITZER5 | 0.96806 | 0.92253 | -0.045529 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SWITZER5 | 0.96806 | 0.92253 | -0.045529 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SWITZER5 | 0.96806 | 0.92253 | -0.045529 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SWITZER5 | 0.96806 | 0.92253 | -0.045529 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SWITZER5 | 0.96806 | 0.92253 | -0.045529 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SWITZER5 | 0.96806 | 0.92253 | -0.045529 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SWITZER5 | 0.97055 | 0.89938 | -0.071166 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | SWITZER5 | 0.97055 | 0.89938 | -0.071166 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SWITZER5 | 0.97055 | 0.89938 | -0.071166 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SWITZER5 | 0.97055 | 0.89938 | -0.071166 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SWITZER5 | 0.97055 | 0.89938 | -0.071166 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | SWITZER5 | 0.97055 | 0.89938 | -0.071166 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SWITZER5 | 0.97055 | 0.89938 | -0.071166 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | SWITZER5 | 0.97055 | 0.89938 | -0.071166 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | SWITZER5 | 0.97055 | 0.89938 | -0.071166 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SWITZER5 | 0.97055 | 0.89938 | -0.071166 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SWITZER5 | 0.97055 | 0.89938 | -0.071166 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SWITZER5 | 0.97055 | 0.89938 | -0.071166 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SWITZER5 | 0.97055 | 0.89938 | -0.071166 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SWITZER5 | 0.97055 | 0.89938 | -0.071166 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SWITZER5 | 0.97055 | 0.89938 | -0.071166 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SWITZER5 | 0.97055 | 0.89938 | -0.071166 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SWITZER5 | 0.97055 | 0.89938 | -0.071166 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SWITZER5 | 0.97055 | 0.89938 | -0.071166 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | SWITZER5 | 0.97055 | 0.89938 | -0.071166 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | SWITZER5 | 0.97055 | 0.89938 | -0.071166 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SWITZER5 | 0.97055 | 0.89938 | -0.071166 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SWITZER5 | 0.97055 | 0.89938 | -0.071166 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | SWITZER5 | 0.97055 | 0.89938 | -0.071166 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SWITZER5 | 0.97055 | 0.89938 | -0.071166 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SWITZER5 | 0.97055 | 0.89938 | -0.071166 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SWITZER5 | 0.97055 | 0.89938 | -0.071166 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SWITZER5 | 0.97055 | 0.89938 | -0.071166 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | SWITZER5 | 0.97055 | 0.89938 | -0.071166 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SWITZER5 | 0.96392 | 0.92561 | -0.038313 |  | 0.93 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SWITZER5 | 0.96392 | 0.92561 | -0.038313 |  | 0.93 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SWITZER5 | 0.96392 | 0.92561 | -0.038313 |  | 0.93 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SWITZER5 | 0.96392 | 0.92561 | -0.038313 |  | 0.93 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SWITZER5 | 0.96392 | 0.92561 | -0.038313 |  | 0.93 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SWITZER5 | 0.96392 | 0.92561 | -0.038313 |  | 0.93 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SWITZER5 | 0.96392 | 0.92561 | -0.038313 |  | 0.93 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SWITZER5 | 0.96392 | 0.92561 | -0.038313 |  | 0.93 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SWITZER5 | 0.96392 | 0.92561 | -0.038313 |  | 0.93 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SWITZER5 | 0.96392 | 0.92561 | -0.038313 |  | 0.93 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SWITZER5 | 0.96392 | 0.92561 | -0.038313 |  | 0.93 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SWITZER5 | 0.96392 | 0.92561 | -0.038313 |  | 0.93 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SWITZER5 | 0.96392 | 0.92561 | -0.038313 |  | 0.93 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SWITZER5 | 0.96392 | 0.92561 | -0.038313 |  | 0.93 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SWITZER5 | 0.96392 | 0.92561 | -0.038313 |  | 0.93 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SWITZER5 | 0.96392 | 0.92561 | -0.038313 |  | 0.93 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SWITZER5 | 0.96392 | 0.92561 | -0.038313 |  | 0.93 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SWITZER5 | 0.96392 | 0.92561 | -0.038313 |  | 0.93 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SWITZER5 | 0.96392 | 0.92561 | -0.038313 |  | 0.93 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SWITZER5 | 0.96392 | 0.92561 | -0.038313 |  | 0.93 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SWLWRNC3 | 0.96637 | 0.92591 | -0.040462 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SWLWRNC3 | 0.96637 | 0.92591 | -0.040462 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SWLWRNC3 | 0.96637 | 0.92591 | -0.040462 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SWLWRNC3 | 0.96637 | 0.92591 | -0.040462 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SWLWRNC3 | 0.96637 | 0.92591 | -0.040462 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SWLWRNC3 | 0.96637 | 0.92591 | -0.040462 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SWLWRNC3 | 0.96637 | 0.92591 | -0.040462 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SWLWRNC3 | 0.96637 | 0.92591 | -0.040462 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SWLWRNC3 | 0.96637 | 0.92591 | -0.040462 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SWLWRNC3 | 0.96637 | 0.92591 | -0.040462 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SWLWRNC3 | 0.96637 | 0.92591 | -0.040462 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SWLWRNC3 | 0.96637 | 0.92591 | -0.040462 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SWLWRNC3 | 0.96637 | 0.92591 | -0.040462 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SWLWRNC3 | 0.96637 | 0.92591 | -0.040462 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SWLWRNC3 | 0.96637 | 0.92591 | -0.040462 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SWLWRNC3 | 0.96637 | 0.92591 | -0.040462 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SWLWRNC3 | 0.96637 | 0.92591 | -0.040462 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SWLWRNC3 | 0.96637 | 0.92591 | -0.040462 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SWLWRNC3 | 0.96637 | 0.92591 | -0.040462 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SWLWRNC3 | 0.96637 | 0.92591 | -0.040462 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SWLWRNC3 | 0.97221 | 0.92884 | -0.043367 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SWLWRNC3 | 0.97221 | 0.92884 | -0.043367 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SWLWRNC3 | 0.97221 | 0.92884 | -0.043367 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SWLWRNC3 | 0.97221 | 0.92884 | -0.043367 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SWLWRNC3 | 0.97221 | 0.92884 | -0.043367 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SWLWRNC3 | 0.97221 | 0.92884 | -0.043367 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SWLWRNC3 | 0.97221 | 0.92884 | -0.043367 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SWLWRNC3 | 0.97221 | 0.92884 | -0.043367 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SWLWRNC3 | 0.97221 | 0.92884 | -0.043367 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SWLWRNC3 | 0.97221 | 0.92884 | -0.043367 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SWLWRNC3 | 0.97221 | 0.92884 | -0.043367 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SWLWRNC3 | 0.97221 | 0.92884 | -0.043367 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SWLWRNC3 | 0.97221 | 0.92884 | -0.043367 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SWLWRNC3 | 0.97221 | 0.92884 | -0.043367 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SWLWRNC3 | 0.97221 | 0.92884 | -0.043367 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SWLWRNC3 | 0.97221 | 0.92884 | -0.043367 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SWLWRNC3 | 0.97221 | 0.92884 | -0.043367 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SWLWRNC3 | 0.97221 | 0.92884 | -0.043367 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SWLWRNC3 | 0.97221 | 0.92884 | -0.043367 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SWLWRNC3 | 0.97221 | 0.92884 | -0.043367 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SWLWRNC3 | 0.97784 | 0.92677 | -0.051071 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | SWLWRNC3 | 0.97784 | 0.92677 | -0.051071 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SWLWRNC3 | 0.97784 | 0.92677 | -0.051071 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SWLWRNC3 | 0.97784 | 0.92677 | -0.051071 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SWLWRNC3 | 0.97784 | 0.92677 | -0.051071 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | SWLWRNC3 | 0.97784 | 0.92677 | -0.051071 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SWLWRNC3 | 0.97784 | 0.92677 | -0.051071 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | SWLWRNC3 | 0.97784 | 0.92677 | -0.051071 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | SWLWRNC3 | 0.97784 | 0.92677 | -0.051071 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SWLWRNC3 | 0.97784 | 0.92677 | -0.051071 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SWLWRNC3 | 0.97784 | 0.92677 | -0.051071 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SWLWRNC3 | 0.97784 | 0.92677 | -0.051071 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SWLWRNC3 | 0.97784 | 0.92677 | -0.051071 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SWLWRNC3 | 0.97784 | 0.92677 | -0.051071 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SWLWRNC3 | 0.97784 | 0.92677 | -0.051071 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SWLWRNC3 | 0.97784 | 0.92677 | -0.051071 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SWLWRNC3 | 0.97784 | 0.92677 | -0.051071 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SWLWRNC3 | 0.97784 | 0.92677 | -0.051071 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | SWLWRNC3 | 0.97784 | 0.92677 | -0.051071 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | SWLWRNC3 | 0.97784 | 0.92677 | -0.051071 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SWLWRNC3 | 0.97784 | 0.92677 | -0.051071 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SWLWRNC3 | 0.97784 | 0.92677 | -0.051071 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | SWLWRNC3 | 0.97784 | 0.92677 | -0.051071 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SWLWRNC3 | 0.97784 | 0.92677 | -0.051071 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SWLWRNC3 | 0.97784 | 0.92677 | -0.051071 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SWLWRNC3 | 0.97784 | 0.92677 | -0.051071 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SWLWRNC3 | 0.97784 | 0.92677 | -0.051071 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | SWLWRNC3 | 0.97784 | 0.92677 | -0.051071 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | SWOPE S5 | 0.99181 | 0.92931 | -0.062496 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | SWOPE S5 | 0.99181 | 0.92931 | -0.062496 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | SWOPE S5 | 0.99181 | 0.92931 | -0.062496 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | SWOPE S5 | 0.99181 | 0.92931 | -0.062496 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | SWOPE S5 | 0.99181 | 0.92931 | -0.062496 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | SWOPE S5 | 0.99181 | 0.92931 | -0.062496 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | SWOPE S5 | 0.99181 | 0.92931 | -0.062496 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | SWOPE S5 | 0.99181 | 0.92931 | -0.062496 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | SWOPE S5 | 0.99181 | 0.92931 | -0.062496 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | SWOPE S5 | 0.99181 | 0.92931 | -0.062496 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | SWOPE S5 | 0.99181 | 0.92931 | -0.062496 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | SWOPE S5 | 0.99181 | 0.92931 | -0.062496 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | SWOPE S5 | 0.99181 | 0.92931 | -0.062496 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | SWOPE S5 | 0.99181 | 0.92931 | -0.062496 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | SWOPE S5 | 0.99181 | 0.92931 | -0.062496 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | SWOPE S5 | 0.99181 | 0.92931 | -0.062496 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | SWOPE S5 | 0.99181 | 0.92931 | -0.062496 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | SWOPE S5 | 0.99181 | 0.92931 | -0.062496 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | SWOPE S5 | 0.99181 | 0.92931 | -0.062496 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | SWOPE S5 | 0.99181 | 0.92931 | -0.062496 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | SWOPE S5 | 0.99181 | 0.92931 | -0.062496 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | SWOPE S5 | 0.99181 | 0.92931 | -0.062496 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | SWOPE S5 | 0.99181 | 0.92931 | -0.062496 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | SWOPE S5 | 0.99181 | 0.92931 | -0.062496 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | SWOPE S5 | 0.99181 | 0.92931 | -0.062496 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | SWOPE S5 | 0.99181 | 0.92931 | -0.062496 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | SWOPE S5 | 0.99181 | 0.92931 | -0.062496 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | SWOPE S5 | 0.99181 | 0.92931 | -0.062496 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | TAYLOR 4 | 0.96668 | 0.9296 | -0.037088 |  | 0.93 | 1.05 | 0.040027 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | TAYLOR 4 | 0.96668 | 0.9296 | -0.037088 |  | 0.93 | 1.05 | 0.090773 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | TAYLOR 4 | 0.96668 | 0.9296 | -0.037088 |  | 0.93 | 1.05 | 0.034521 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | TAYLOR 4 | 0.96668 | 0.9296 | -0.037088 |  | 0.93 | 1.05 | 0.038035 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | TAYLOR 4 | 0.96668 | 0.9296 | -0.037088 |  | 0.93 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | TAYLOR 4 | 0.96668 | 0.9296 | -0.037088 |  | 0.93 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | TAYLOR 4 | 0.96668 | 0.9296 | -0.037088 |  | 0.93 | 1.05 | 0.050618 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | TAYLOR 4 | 0.96668 | 0.9296 | -0.037088 |  | 0.93 | 1.05 | 0.04163 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | TAYLOR 4 | 0.96668 | 0.9296 | -0.037088 |  | 0.93 | 1.05 | 0.043776 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | TAYLOR 4 | 0.96668 | 0.9296 | -0.037088 |  | 0.93 | 1.05 | 0.034868 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | TAYLOR 4 | 0.96668 | 0.9296 | -0.037088 |  | 0.93 | 1.05 | 0.031975 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | TAYLOR 4 | 0.96668 | 0.9296 | -0.037088 |  | 0.93 | 1.05 | 0.037422 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | TAYLOR 4 | 0.96668 | 0.9296 | -0.037088 |  | 0.93 | 1.05 | 0.050095 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | TAYLOR 4 | 0.96151 | 0.922 | -0.039517 |  | 0.93 | 1.05 | 0.094783 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | TAYLOR 4 | 0.96151 | 0.922 | -0.039517 |  | 0.93 | 1.05 | 0.03645 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | TAYLOR 4 | 0.96151 | 0.922 | -0.039517 |  | 0.93 | 1.05 | 0.04755 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | TAYLOR 4 | 0.96151 | 0.922 | -0.039517 |  | 0.93 | 1.05 | 0.06097 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | TAYLOR 4 | 0.96151 | 0.922 | -0.039517 |  | 0.93 | 1.05 | 0.061051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | TAYLOR 4 | 0.96151 | 0.922 | -0.039517 |  | 0.93 | 1.05 | 0.04456 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | TAYLOR 4 | 0.96151 | 0.922 | -0.039517 |  | 0.93 | 1.05 | 0.048811 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | TAYLOR 4 | 0.96151 | 0.922 | -0.039517 |  | 0.93 | 1.05 | 0.13004 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | TAYLOR 4 | 0.96151 | 0.922 | -0.039517 |  | 0.93 | 1.05 | 0.049018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | TAYLOR 4 | 0.96151 | 0.922 | -0.039517 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | TAYLOR 4 | 0.96151 | 0.922 | -0.039517 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | TAYLOR 4 | 0.96151 | 0.922 | -0.039517 |  | 0.93 | 1.05 | 0.05974 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | TAYLOR 4 | 0.96151 | 0.922 | -0.039517 |  | 0.93 | 1.05 | 0.076949 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | TAYLOR 4 | 0.96151 | 0.922 | -0.039517 |  | 0.93 | 1.05 | 0.042157 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | TAYLOR 4 | 0.96151 | 0.922 | -0.039517 |  | 0.93 | 1.05 | 0.040957 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | TAYLOR 4 | 0.96151 | 0.922 | -0.039517 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | TAYLOR 4 | 0.96151 | 0.922 | -0.039517 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | TAYLOR 4 | 0.96151 | 0.922 | -0.039517 |  | 0.93 | 1.05 | 0.054637 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | TAYLOR 4 | 0.96151 | 0.922 | -0.039517 |  | 0.93 | 1.05 | 0.060597 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | TAYLOR 4 | 0.96151 | 0.922 | -0.039517 |  | 0.93 | 1.05 | 0.044286 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | TAYLOR 4 | 0.96151 | 0.922 | -0.039517 |  | 0.93 | 1.05 | 0.059107 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | TAYLOR 4 | 0.96151 | 0.922 | -0.039517 |  | 0.93 | 1.05 | 0.052698 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | TAYLOR 4 | 0.96151 | 0.922 | -0.039517 |  | 0.93 | 1.05 | 0.067422 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | TAYLOR 4 | 0.96151 | 0.922 | -0.039517 |  | 0.93 | 1.05 | 0.053768 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | TAYLOR 4 | 0.96151 | 0.922 | -0.039517 |  | 0.93 | 1.05 | 0.03909 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | TAYLOR 4 | 0.96069 | 0.92568 | -0.035014 |  | 0.93 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | TAYLOR 4 | 0.96069 | 0.92568 | -0.035014 |  | 0.93 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | TAYLOR 4 | 0.96069 | 0.92568 | -0.035014 |  | 0.93 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | TAYLOR 4 | 0.96069 | 0.92568 | -0.035014 |  | 0.93 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | TAYLOR 4 | 0.96069 | 0.92568 | -0.035014 |  | 0.93 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | TAYLOR 4 | 0.96069 | 0.92568 | -0.035014 |  | 0.93 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | TAYLOR 4 | 0.96069 | 0.92568 | -0.035014 |  | 0.93 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | TAYLOR 4 | 0.96069 | 0.92568 | -0.035014 |  | 0.93 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | TAYLOR 4 | 0.96069 | 0.92568 | -0.035014 |  | 0.93 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | TAYLOR 4 | 0.96069 | 0.92568 | -0.035014 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | TAYLOR 4 | 0.96069 | 0.92568 | -0.035014 |  | 0.93 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | TAYLOR 4 | 0.96069 | 0.92568 | -0.035014 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | TAYLOR 4 | 0.96069 | 0.92568 | -0.035014 |  | 0.93 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | TAYLOR 4 | 0.96069 | 0.92568 | -0.035014 |  | 0.93 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | TAYLOR 4 | 0.96069 | 0.92568 | -0.035014 |  | 0.93 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | TAYLOR 4 | 0.96069 | 0.92568 | -0.035014 |  | 0.93 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | TAYLOR 4 | 0.96069 | 0.92568 | -0.035014 |  | 0.93 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | TAYLOR 4 | 0.96069 | 0.92568 | -0.035014 |  | 0.93 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | TAYLOR 4 | 0.96069 | 0.92568 | -0.035014 |  | 0.93 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | TAYLOR 4 | 0.96069 | 0.92568 | -0.035014 |  | 0.93 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | TAYLOR 4 | 0.96069 | 0.92568 | -0.035014 |  | 0.93 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | TAYLOR 4 | 0.96069 | 0.92568 | -0.035014 |  | 0.93 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | TAYLOR 4 | 0.96353 | 0.9167 | -0.046822 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | TAYLOR 4 | 0.96353 | 0.9167 | -0.046822 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | TAYLOR 4 | 0.96353 | 0.9167 | -0.046822 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | TAYLOR 4 | 0.96353 | 0.9167 | -0.046822 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | TAYLOR 4 | 0.96353 | 0.9167 | -0.046822 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | TAYLOR 4 | 0.96353 | 0.9167 | -0.046822 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | TAYLOR 4 | 0.96353 | 0.9167 | -0.046822 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | TAYLOR 4 | 0.96353 | 0.9167 | -0.046822 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | TAYLOR 4 | 0.96353 | 0.9167 | -0.046822 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | TAYLOR 4 | 0.96353 | 0.9167 | -0.046822 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | TAYLOR 4 | 0.96353 | 0.9167 | -0.046822 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | TAYLOR 4 | 0.96353 | 0.9167 | -0.046822 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | TAYLOR 4 | 0.96353 | 0.9167 | -0.046822 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | TAYLOR 4 | 0.96353 | 0.9167 | -0.046822 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | TAYLOR 4 | 0.96353 | 0.9167 | -0.046822 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | TAYLOR 4 | 0.96353 | 0.9167 | -0.046822 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | TAYLOR 4 | 0.96353 | 0.9167 | -0.046822 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | TAYLOR 4 | 0.96353 | 0.9167 | -0.046822 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | TAYLOR 4 | 0.96353 | 0.9167 | -0.046822 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | TAYLOR 4 | 0.96353 | 0.9167 | -0.046822 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | TAYLOR 4 | 0.96353 | 0.9167 | -0.046822 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | TAYLOR 4 | 0.96353 | 0.9167 | -0.046822 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | TAYLOR 4 | 0.96353 | 0.9167 | -0.046822 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | TAYLOR 4 | 0.96353 | 0.9167 | -0.046822 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | TAYLOR 4 | 0.96353 | 0.9167 | -0.046822 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | TAYLOR 4 | 0.96353 | 0.9167 | -0.046822 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | TAYLOR 4 | 0.96353 | 0.9167 | -0.046822 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | TAYLOR 4 | 0.96353 | 0.9167 | -0.046822 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | TECHILL6 | 0.95944 | 0.92489 | -0.034554 |  | 0.95 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | TECHILL6 | 0.95944 | 0.92489 | -0.034554 |  | 0.95 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | TECHILL6 | 0.95944 | 0.92489 | -0.034554 |  | 0.95 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | TECHILL6 | 0.95944 | 0.92489 | -0.034554 |  | 0.95 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | TECHILL6 | 0.95944 | 0.92489 | -0.034554 |  | 0.95 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | TECHILL6 | 0.95944 | 0.92489 | -0.034554 |  | 0.95 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | TECHILL6 | 0.95944 | 0.92489 | -0.034554 |  | 0.95 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | TECHILL6 | 0.95944 | 0.92489 | -0.034554 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | TECHILL6 | 0.95944 | 0.92489 | -0.034554 |  | 0.95 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | TECHILL6 | 0.95944 | 0.92489 | -0.034554 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | TECHILL6 | 0.95944 | 0.92489 | -0.034554 |  | 0.95 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | TECHILL6 | 0.95944 | 0.92489 | -0.034554 |  | 0.95 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | TECHILL6 | 0.95944 | 0.92489 | -0.034554 |  | 0.95 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | TECHILL6 | 0.95944 | 0.92489 | -0.034554 |  | 0.95 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | TECHILL6 | 0.95944 | 0.92489 | -0.034554 |  | 0.95 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | TECHILL6 | 0.95944 | 0.92489 | -0.034554 |  | 0.95 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | TECHILL6 | 0.95944 | 0.92489 | -0.034554 |  | 0.95 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | TECHILL6 | 0.95944 | 0.92489 | -0.034554 |  | 0.95 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | TECHILL6 | 0.95944 | 0.92489 | -0.034554 |  | 0.95 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | TECHILL6 | 0.95944 | 0.92489 | -0.034554 |  | 0.95 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | TECHILL6 | 0.95628 | 0.91708 | -0.039199 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | TECHILL6 | 0.95628 | 0.91708 | -0.039199 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | TECHILL6 | 0.95628 | 0.91708 | -0.039199 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | TECHILL6 | 0.95628 | 0.91708 | -0.039199 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | TECHILL6 | 0.95628 | 0.91708 | -0.039199 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | TECHILL6 | 0.95628 | 0.91708 | -0.039199 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | TECHILL6 | 0.95628 | 0.91708 | -0.039199 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | TECHILL6 | 0.95628 | 0.91708 | -0.039199 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | TECHILL6 | 0.95628 | 0.91708 | -0.039199 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | TECHILL6 | 0.95628 | 0.91708 | -0.039199 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | TECHILL6 | 0.95628 | 0.91708 | -0.039199 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | TECHILL6 | 0.95628 | 0.91708 | -0.039199 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | TECHILL6 | 0.95628 | 0.91708 | -0.039199 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | TECHILL6 | 0.95628 | 0.91708 | -0.039199 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | TECHILL6 | 0.95628 | 0.91708 | -0.039199 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | TECHILL6 | 0.95628 | 0.91708 | -0.039199 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | TECHILL6 | 0.95628 | 0.91708 | -0.039199 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | TECHILL6 | 0.95628 | 0.91708 | -0.039199 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | TECHILL6 | 0.95628 | 0.91708 | -0.039199 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | TECHILL6 | 0.95628 | 0.91708 | -0.039199 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | TECHILL6 | 0.96211 | 0.91836 | -0.043751 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | TECHILL6 | 0.96211 | 0.91836 | -0.043751 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | TECHILL6 | 0.96211 | 0.91836 | -0.043751 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | TECHILL6 | 0.96211 | 0.91836 | -0.043751 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | TECHILL6 | 0.96211 | 0.91836 | -0.043751 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | TECHILL6 | 0.96211 | 0.91836 | -0.043751 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | TECHILL6 | 0.96211 | 0.91836 | -0.043751 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | TECHILL6 | 0.96211 | 0.91836 | -0.043751 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | TECHILL6 | 0.96211 | 0.91836 | -0.043751 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | TECHILL6 | 0.96211 | 0.91836 | -0.043751 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | TECHILL6 | 0.96211 | 0.91836 | -0.043751 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | TECHILL6 | 0.96211 | 0.91836 | -0.043751 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | TECHILL6 | 0.96211 | 0.91836 | -0.043751 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | TECHILL6 | 0.96211 | 0.91836 | -0.043751 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | TECHILL6 | 0.96211 | 0.91836 | -0.043751 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | TECHILL6 | 0.96211 | 0.91836 | -0.043751 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | TECHILL6 | 0.96211 | 0.91836 | -0.043751 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | TECHILL6 | 0.96211 | 0.91836 | -0.043751 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | TECHILL6 | 0.96211 | 0.91836 | -0.043751 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | TECHILL6 | 0.96211 | 0.91836 | -0.043751 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | TECHILL6 | 0.96633 | 0.91773 | -0.048592 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | TECHILL6 | 0.96633 | 0.91773 | -0.048592 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | TECHILL6 | 0.96633 | 0.91773 | -0.048592 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | TECHILL6 | 0.96633 | 0.91773 | -0.048592 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | TECHILL6 | 0.96633 | 0.91773 | -0.048592 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | TECHILL6 | 0.96633 | 0.91773 | -0.048592 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | TECHILL6 | 0.96633 | 0.91773 | -0.048592 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | TECHILL6 | 0.96633 | 0.91773 | -0.048592 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | TECHILL6 | 0.96633 | 0.91773 | -0.048592 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | TECHILL6 | 0.96633 | 0.91773 | -0.048592 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | TECHILL6 | 0.96633 | 0.91773 | -0.048592 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | TECHILL6 | 0.96633 | 0.91773 | -0.048592 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | TECHILL6 | 0.96633 | 0.91773 | -0.048592 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | TECHILL6 | 0.96633 | 0.91773 | -0.048592 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | TECHILL6 | 0.96633 | 0.91773 | -0.048592 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | TECHILL6 | 0.96633 | 0.91773 | -0.048592 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | TECHILL6 | 0.96633 | 0.91773 | -0.048592 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | TECHILL6 | 0.96633 | 0.91773 | -0.048592 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | TECHILL6 | 0.96633 | 0.91773 | -0.048592 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | TECHILL6 | 0.96633 | 0.91773 | -0.048592 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | TECHILL6 | 0.96633 | 0.91773 | -0.048592 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | TECHILL6 | 0.96633 | 0.91773 | -0.048592 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | TECHILL6 | 0.96633 | 0.91773 | -0.048592 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | TECHILL6 | 0.96633 | 0.91773 | -0.048592 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | TECHILL6 | 0.96633 | 0.91773 | -0.048592 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | TECHILL6 | 0.96633 | 0.91773 | -0.048592 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | TECHILL6 | 0.96633 | 0.91773 | -0.048592 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | TECHILL6 | 0.96633 | 0.91773 | -0.048592 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | TECHILL6 | 0.95904 | 0.92357 | -0.035471 |  | 0.95 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | TECHILL6 | 0.95904 | 0.92357 | -0.035471 |  | 0.95 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | TECHILL6 | 0.95904 | 0.92357 | -0.035471 |  | 0.95 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | TECHILL6 | 0.95904 | 0.92357 | -0.035471 |  | 0.95 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | TECHILL6 | 0.95904 | 0.92357 | -0.035471 |  | 0.95 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | TECHILL6 | 0.95904 | 0.92357 | -0.035471 |  | 0.95 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | TECHILL6 | 0.95904 | 0.92357 | -0.035471 |  | 0.95 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | TECHILL6 | 0.95904 | 0.92357 | -0.035471 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | TECHILL6 | 0.95904 | 0.92357 | -0.035471 |  | 0.95 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | TECHILL6 | 0.95904 | 0.92357 | -0.035471 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | TECHILL6 | 0.95904 | 0.92357 | -0.035471 |  | 0.95 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | TECHILL6 | 0.95904 | 0.92357 | -0.035471 |  | 0.95 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | TECHILL6 | 0.95904 | 0.92357 | -0.035471 |  | 0.95 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | TECHILL6 | 0.95904 | 0.92357 | -0.035471 |  | 0.95 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | TECHILL6 | 0.95904 | 0.92357 | -0.035471 |  | 0.95 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | TECHILL6 | 0.95904 | 0.92357 | -0.035471 |  | 0.95 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | TECHILL6 | 0.95904 | 0.92357 | -0.035471 |  | 0.95 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | TECHILL6 | 0.95904 | 0.92357 | -0.035471 |  | 0.95 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | TECHILL6 | 0.95904 | 0.92357 | -0.035471 |  | 0.95 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | TECHILL6 | 0.95904 | 0.92357 | -0.035471 |  | 0.95 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | TIOGA 4 | 0.95703 | 0.91935 | -0.037685 |  | 0.93 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | TIOGA 4 | 0.95703 | 0.91935 | -0.037685 |  | 0.93 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | TIOGA 4 | 0.95703 | 0.91935 | -0.037685 |  | 0.93 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | TIOGA 4 | 0.95703 | 0.91935 | -0.037685 |  | 0.93 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | TIOGA 4 | 0.95703 | 0.91935 | -0.037685 |  | 0.93 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | TIOGA 4 | 0.95703 | 0.91935 | -0.037685 |  | 0.93 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | TIOGA 4 | 0.95703 | 0.91935 | -0.037685 |  | 0.93 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | TIOGA 4 | 0.95703 | 0.91935 | -0.037685 |  | 0.93 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | TIOGA 4 | 0.95703 | 0.91935 | -0.037685 |  | 0.93 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | TIOGA 4 | 0.95703 | 0.91935 | -0.037685 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | TIOGA 4 | 0.95703 | 0.91935 | -0.037685 |  | 0.93 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | TIOGA 4 | 0.95703 | 0.91935 | -0.037685 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | TIOGA 4 | 0.95703 | 0.91935 | -0.037685 |  | 0.93 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | TIOGA 4 | 0.95703 | 0.91935 | -0.037685 |  | 0.93 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | TIOGA 4 | 0.95703 | 0.91935 | -0.037685 |  | 0.93 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | TIOGA 4 | 0.95703 | 0.91935 | -0.037685 |  | 0.93 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | TIOGA 4 | 0.95703 | 0.91935 | -0.037685 |  | 0.93 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | TIOGA 4 | 0.95703 | 0.91935 | -0.037685 |  | 0.93 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | TIOGA 4 | 0.95703 | 0.91935 | -0.037685 |  | 0.93 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | TIOGA 4 | 0.95703 | 0.91935 | -0.037685 |  | 0.93 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | TIOGA 4 | 0.95703 | 0.91935 | -0.037685 |  | 0.93 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | TIOGA 4 | 0.95703 | 0.91935 | -0.037685 |  | 0.93 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | TIOGA 4 | 0.97126 | 0.90821 | -0.063051 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | TIOGA 4 | 0.97126 | 0.90821 | -0.063051 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | TIOGA 4 | 0.97126 | 0.90821 | -0.063051 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | TIOGA 4 | 0.97126 | 0.90821 | -0.063051 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | TIOGA 4 | 0.97126 | 0.90821 | -0.063051 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | TIOGA 4 | 0.97126 | 0.90821 | -0.063051 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | TIOGA 4 | 0.97126 | 0.90821 | -0.063051 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | TIOGA 4 | 0.97126 | 0.90821 | -0.063051 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | TIOGA 4 | 0.97126 | 0.90821 | -0.063051 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | TIOGA 4 | 0.97126 | 0.90821 | -0.063051 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | TIOGA 4 | 0.97126 | 0.90821 | -0.063051 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | TIOGA 4 | 0.97126 | 0.90821 | -0.063051 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | TIOGA 4 | 0.97126 | 0.90821 | -0.063051 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | TIOGA 4 | 0.97126 | 0.90821 | -0.063051 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | TIOGA 4 | 0.97126 | 0.90821 | -0.063051 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | TIOGA 4 | 0.97126 | 0.90821 | -0.063051 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | TIOGA 4 | 0.97126 | 0.90821 | -0.063051 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | TIOGA 4 | 0.97126 | 0.90821 | -0.063051 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | TIOGA 4 | 0.97126 | 0.90821 | -0.063051 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | TIOGA 4 | 0.97126 | 0.90821 | -0.063051 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | TIOGA 4 | 0.97126 | 0.90821 | -0.063051 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | TIOGA 4 | 0.97126 | 0.90821 | -0.063051 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | TIOGA 4 | 0.97126 | 0.90821 | -0.063051 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | TIOGA 4 | 0.97126 | 0.90821 | -0.063051 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | TIOGA 4 | 0.97126 | 0.90821 | -0.063051 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | TIOGA 4 | 0.97126 | 0.90821 | -0.063051 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | TIOGA 4 | 0.97126 | 0.90821 | -0.063051 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | TIOGA 4 | 0.97126 | 0.90821 | -0.063051 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | TIP292 5 | 0.97415 | 0.92354 | -0.050611 |  | 0.925 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | TIP292 5 | 0.97415 | 0.92354 | -0.050611 |  | 0.925 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | TIP292 5 | 0.97415 | 0.92354 | -0.050611 |  | 0.925 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | TIP292 5 | 0.97415 | 0.92354 | -0.050611 |  | 0.925 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | TIP292 5 | 0.97415 | 0.92354 | -0.050611 |  | 0.925 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | TIP292 5 | 0.97415 | 0.92354 | -0.050611 |  | 0.925 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | TIP292 5 | 0.97415 | 0.92354 | -0.050611 |  | 0.925 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | TIP292 5 | 0.97415 | 0.92354 | -0.050611 |  | 0.925 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | TIP292 5 | 0.97415 | 0.92354 | -0.050611 |  | 0.925 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | TIP292 5 | 0.97415 | 0.92354 | -0.050611 |  | 0.925 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | TIP292 5 | 0.97415 | 0.92354 | -0.050611 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | TIP292 5 | 0.97415 | 0.92354 | -0.050611 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | TIP292 5 | 0.97415 | 0.92354 | -0.050611 |  | 0.925 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | TIP292 5 | 0.97415 | 0.92354 | -0.050611 |  | 0.925 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | TIP292 5 | 0.97415 | 0.92354 | -0.050611 |  | 0.925 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | TIP292 5 | 0.97483 | 0.92462 | -0.050213 |  | 0.925 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | TIP292 5 | 0.97483 | 0.92462 | -0.050213 |  | 0.925 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | TIP292 5 | 0.97483 | 0.92462 | -0.050213 |  | 0.925 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | TIP292 5 | 0.97483 | 0.92462 | -0.050213 |  | 0.925 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | TIP292 5 | 0.97483 | 0.92462 | -0.050213 |  | 0.925 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | TIP292 5 | 0.97483 | 0.92462 | -0.050213 |  | 0.925 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | TIP292 5 | 0.97483 | 0.92462 | -0.050213 |  | 0.925 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | TIP292 5 | 0.97483 | 0.92462 | -0.050213 |  | 0.925 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | TIP292 5 | 0.97483 | 0.92462 | -0.050213 |  | 0.925 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | TIP292 5 | 0.97483 | 0.92462 | -0.050213 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | TIP292 5 | 0.97483 | 0.92462 | -0.050213 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | TIP292 5 | 0.97483 | 0.92462 | -0.050213 |  | 0.925 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | TIP292 5 | 0.97483 | 0.92462 | -0.050213 |  | 0.925 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | TIP292 5 | 0.97483 | 0.92462 | -0.050213 |  | 0.925 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | TOMHAWK5 | 0.9777 | 0.90968 | -0.068016 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | TOMHAWK5 | 0.9777 | 0.90968 | -0.068016 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | TOMHAWK5 | 0.9777 | 0.90968 | -0.068016 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | TOMHAWK5 | 0.9777 | 0.90968 | -0.068016 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | TOMHAWK5 | 0.9777 | 0.90968 | -0.068016 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | TOMHAWK5 | 0.9777 | 0.90968 | -0.068016 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | TOMHAWK5 | 0.9777 | 0.90968 | -0.068016 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | TOMHAWK5 | 0.9777 | 0.90968 | -0.068016 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | TOMHAWK5 | 0.9777 | 0.90968 | -0.068016 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | TOMHAWK5 | 0.9777 | 0.90968 | -0.068016 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | TOMHAWK5 | 0.9777 | 0.90968 | -0.068016 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | TOMHAWK5 | 0.9777 | 0.90968 | -0.068016 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | TOMHAWK5 | 0.9777 | 0.90968 | -0.068016 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | TOMHAWK5 | 0.9777 | 0.90968 | -0.068016 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | TOMHAWK5 | 0.9777 | 0.90968 | -0.068016 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | TOMHAWK5 | 0.9777 | 0.90968 | -0.068016 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | TOMHAWK5 | 0.9777 | 0.90968 | -0.068016 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | TOMHAWK5 | 0.9777 | 0.90968 | -0.068016 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | TOMHAWK5 | 0.9777 | 0.90968 | -0.068016 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | TOMHAWK5 | 0.9777 | 0.90968 | -0.068016 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | TOMHAWK5 | 0.9777 | 0.90968 | -0.068016 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | TOMHAWK5 | 0.9777 | 0.90968 | -0.068016 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | TOMHAWK5 | 0.9777 | 0.90968 | -0.068016 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | TOMHAWK5 | 0.9777 | 0.90968 | -0.068016 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | TOMHAWK5 | 0.9777 | 0.90968 | -0.068016 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | TOMHAWK5 | 0.9777 | 0.90968 | -0.068016 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | TOMHAWK5 | 0.9777 | 0.90968 | -0.068016 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | TOMHAWK5 | 0.9777 | 0.90968 | -0.068016 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | TONTITN7 | 0.97914 | 0.91525 | -0.063891 |  | 0.92 | 1.05 | 0.030712 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | TONTITN7 | 0.97914 | 0.91525 | -0.063891 |  | 0.92 | 1.05 | 0.038311 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | TONTITN7 | 0.97914 | 0.91525 | -0.063891 |  | 0.92 | 1.05 | 0.061498 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | TONTITN7 | 0.97914 | 0.91525 | -0.063891 |  | 0.92 | 1.05 | 0.070613 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | TONTITN7 | 0.97914 | 0.91525 | -0.063891 |  | 0.92 | 1.05 | 0.037457 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | TONTITN7 | 0.97914 | 0.91525 | -0.063891 |  | 0.92 | 1.05 | 0.15352 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | TONTITN7 | 0.97914 | 0.91525 | -0.063891 |  | 0.92 | 1.05 | 0.062033 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | TONTITN7 | 0.97996 | 0.9172 | -0.062756 |  | 0.92 | 1.05 | 0.038311 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | TONTITN7 | 0.97996 | 0.9172 | -0.062756 |  | 0.92 | 1.05 | 0.058472 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | TONTITN7 | 0.97996 | 0.9172 | -0.062756 |  | 0.92 | 1.05 | 0.070613 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | TONTITN7 | 0.97996 | 0.9172 | -0.062756 |  | 0.92 | 1.05 | 0.036297 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | TONTITN7 | 0.97996 | 0.9172 | -0.062756 |  | 0.92 | 1.05 | 0.15352 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | TONTITN7 | 0.97996 | 0.9172 | -0.062756 |  | 0.92 | 1.05 | 0.060874 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | TRIB SW3 | 0.9463 | 0.89889 | -0.047415 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | TRIB SW3 | 0.9463 | 0.89889 | -0.047415 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | TURNER_RD5 | 0.98921 | 0.91166 | -0.077547 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | TURNER_RD5 | 0.98921 | 0.91166 | -0.077547 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | TURNER_RD5 | 0.98921 | 0.91166 | -0.077547 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | TURNER_RD5 | 0.98921 | 0.91166 | -0.077547 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | TURNER_RD5 | 0.98921 | 0.91166 | -0.077547 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | TURNER_RD5 | 0.98921 | 0.91166 | -0.077547 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | TURNER_RD5 | 0.98921 | 0.91166 | -0.077547 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | TURNER_RD5 | 0.98921 | 0.91166 | -0.077547 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | TURNER_RD5 | 0.98921 | 0.91166 | -0.077547 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | TURNER_RD5 | 0.98921 | 0.91166 | -0.077547 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | TURNER_RD5 | 0.98921 | 0.91166 | -0.077547 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | TURNER_RD5 | 0.98921 | 0.91166 | -0.077547 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | TURNER_RD5 | 0.98921 | 0.91166 | -0.077547 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | TURNER_RD5 | 0.98921 | 0.91166 | -0.077547 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | TURNER_RD5 | 0.98921 | 0.91166 | -0.077547 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | TURNER_RD5 | 0.98921 | 0.91166 | -0.077547 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | TURNER_RD5 | 0.98921 | 0.91166 | -0.077547 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | TURNER_RD5 | 0.98921 | 0.91166 | -0.077547 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | TURNER_RD5 | 0.98921 | 0.91166 | -0.077547 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | TURNER_RD5 | 0.98921 | 0.91166 | -0.077547 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | TURNER_RD5 | 0.98921 | 0.91166 | -0.077547 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | TURNER_RD5 | 0.98921 | 0.91166 | -0.077547 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | TURNER_RD5 | 0.98921 | 0.91166 | -0.077547 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | TURNER_RD5 | 0.98921 | 0.91166 | -0.077547 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | TURNER_RD5 | 0.98921 | 0.91166 | -0.077547 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | TURNER_RD5 | 0.98921 | 0.91166 | -0.077547 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | TURNER_RD5 | 0.98921 | 0.91166 | -0.077547 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | TURNER_RD5 | 0.98921 | 0.91166 | -0.077547 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | TV1MNDV4 | 0.95731 | 0.91823 | -0.039082 |  | 0.93 | 1.05 | 0.030148 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | TV1MNDV4 | 0.95731 | 0.91823 | -0.039082 |  | 0.93 | 1.05 | 0.049467 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | TV1MNDV4 | 0.95731 | 0.91823 | -0.039082 |  | 0.93 | 1.05 | 0.058621 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | TV1MNDV4 | 0.95731 | 0.91823 | -0.039082 |  | 0.93 | 1.05 | 0.082177 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | TV1MNDV4 | 0.95731 | 0.91823 | -0.039082 |  | 0.93 | 1.05 | 0.087314 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | TV1MNDV4 | 0.95731 | 0.91823 | -0.039082 |  | 0.93 | 1.05 | 0.048683 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | TV1MNDV4 | 0.95731 | 0.91823 | -0.039082 |  | 0.93 | 1.05 | 0.11232 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | TV1MNDV4 | 0.95731 | 0.91823 | -0.039082 |  | 0.93 | 1.05 | 0.044109 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | TV1MNDV4 | 0.95731 | 0.91823 | -0.039082 |  | 0.93 | 1.05 | 0.045565 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | TV1MNDV4 | 0.95731 | 0.91823 | -0.039082 |  | 0.93 | 1.05 | 0.066779 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | TV1MNDV4 | 0.95731 | 0.91823 | -0.039082 |  | 0.93 | 1.05 | 0.05473 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | TV1MNDV4 | 0.95731 | 0.91823 | -0.039082 |  | 0.93 | 1.05 | 0.041831 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | TV1MNDV4 | 0.95731 | 0.91823 | -0.039082 |  | 0.93 | 1.05 | 0.46658 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | TV1MNDV4 | 0.95731 | 0.91823 | -0.039082 |  | 0.93 | 1.05 | 0.030148 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | TV1MNDV4 | 0.95731 | 0.91823 | -0.039082 |  | 0.93 | 1.05 | 0.041831 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | TV1MNDV4 | 0.95731 | 0.91823 | -0.039082 |  | 0.93 | 1.05 | 0.040658 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | TV1MNDV4 | 0.95731 | 0.91823 | -0.039082 |  | 0.93 | 1.05 | 0.043997 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | TV1MNDV4 | 0.95731 | 0.91823 | -0.039082 |  | 0.93 | 1.05 | 0.068133 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | TV1MNDV4 | 0.95731 | 0.91823 | -0.039082 |  | 0.93 | 1.05 | 0.068393 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | TV1MNDV4 | 0.95731 | 0.91823 | -0.039082 |  | 0.93 | 1.05 | 0.05813 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | TV1MNDV4 | 0.95731 | 0.91823 | -0.039082 |  | 0.93 | 1.05 | 0.05813 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | TV1MNDV4 | 0.95731 | 0.91823 | -0.039082 |  | 0.93 | 1.05 | 0.098736 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | TV1MNDV4 | 0.95731 | 0.91823 | -0.039082 |  | 0.93 | 1.05 | 0.045332 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | TV1MNDV4 | 0.95731 | 0.91823 | -0.039082 |  | 0.93 | 1.05 | 0.044706 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | TV1MNDV4 | 0.95731 | 0.91823 | -0.039082 |  | 0.93 | 1.05 | 0.063507 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | TV1MNDV4 | 0.95731 | 0.91823 | -0.039082 |  | 0.93 | 1.05 | 0.048755 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | TV1MNDV4 | 0.95731 | 0.91823 | -0.039082 |  | 0.93 | 1.05 | 0.060242 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | TV1MNDV4 | 0.95731 | 0.91823 | -0.039082 |  | 0.93 | 1.05 | 0.041736 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | TV1MNDV4 | 0.95731 | 0.91823 | -0.039082 |  | 0.93 | 1.05 | 0.040069 | P23:345:WERE:N345-345-20:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | TV1MNDV4 | 0.95854 | 0.92008 | -0.038465 |  | 0.93 | 1.05 | 0.040027 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | TV1MNDV4 | 0.95854 | 0.92008 | -0.038465 |  | 0.93 | 1.05 | 0.090773 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | TV1MNDV4 | 0.95854 | 0.92008 | -0.038465 |  | 0.93 | 1.05 | 0.034521 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | TV1MNDV4 | 0.95854 | 0.92008 | -0.038465 |  | 0.93 | 1.05 | 0.038035 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | TV1MNDV4 | 0.95854 | 0.92008 | -0.038465 |  | 0.93 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | TV1MNDV4 | 0.95854 | 0.92008 | -0.038465 |  | 0.93 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | TV1MNDV4 | 0.95854 | 0.92008 | -0.038465 |  | 0.93 | 1.05 | 0.050618 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | TV1MNDV4 | 0.95854 | 0.92008 | -0.038465 |  | 0.93 | 1.05 | 0.04163 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | TV1MNDV4 | 0.95854 | 0.92008 | -0.038465 |  | 0.93 | 1.05 | 0.043776 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | TV1MNDV4 | 0.95854 | 0.92008 | -0.038465 |  | 0.93 | 1.05 | 0.034868 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | TV1MNDV4 | 0.95854 | 0.92008 | -0.038465 |  | 0.93 | 1.05 | 0.031975 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | TV1MNDV4 | 0.95854 | 0.92008 | -0.038465 |  | 0.93 | 1.05 | 0.037422 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | TV1MNDV4 | 0.95854 | 0.92008 | -0.038465 |  | 0.93 | 1.05 | 0.050095 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | TV1MNDV4 | 0.95496 | 0.91279 | -0.042162 |  | 0.93 | 1.05 | 0.094783 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | TV1MNDV4 | 0.95496 | 0.91279 | -0.042162 |  | 0.93 | 1.05 | 0.03645 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | TV1MNDV4 | 0.95496 | 0.91279 | -0.042162 |  | 0.93 | 1.05 | 0.04755 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | TV1MNDV4 | 0.95496 | 0.91279 | -0.042162 |  | 0.93 | 1.05 | 0.06097 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | TV1MNDV4 | 0.95496 | 0.91279 | -0.042162 |  | 0.93 | 1.05 | 0.061051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | TV1MNDV4 | 0.95496 | 0.91279 | -0.042162 |  | 0.93 | 1.05 | 0.04456 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | TV1MNDV4 | 0.95496 | 0.91279 | -0.042162 |  | 0.93 | 1.05 | 0.048811 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | TV1MNDV4 | 0.95496 | 0.91279 | -0.042162 |  | 0.93 | 1.05 | 0.13004 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | TV1MNDV4 | 0.95496 | 0.91279 | -0.042162 |  | 0.93 | 1.05 | 0.049018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | TV1MNDV4 | 0.95496 | 0.91279 | -0.042162 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | TV1MNDV4 | 0.95496 | 0.91279 | -0.042162 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | TV1MNDV4 | 0.95496 | 0.91279 | -0.042162 |  | 0.93 | 1.05 | 0.05974 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | TV1MNDV4 | 0.95496 | 0.91279 | -0.042162 |  | 0.93 | 1.05 | 0.076949 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | TV1MNDV4 | 0.95496 | 0.91279 | -0.042162 |  | 0.93 | 1.05 | 0.042157 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | TV1MNDV4 | 0.95496 | 0.91279 | -0.042162 |  | 0.93 | 1.05 | 0.040957 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | TV1MNDV4 | 0.95496 | 0.91279 | -0.042162 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | TV1MNDV4 | 0.95496 | 0.91279 | -0.042162 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | TV1MNDV4 | 0.95496 | 0.91279 | -0.042162 |  | 0.93 | 1.05 | 0.054637 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | TV1MNDV4 | 0.95496 | 0.91279 | -0.042162 |  | 0.93 | 1.05 | 0.060597 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | TV1MNDV4 | 0.95496 | 0.91279 | -0.042162 |  | 0.93 | 1.05 | 0.044286 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | TV1MNDV4 | 0.95496 | 0.91279 | -0.042162 |  | 0.93 | 1.05 | 0.059107 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | TV1MNDV4 | 0.95496 | 0.91279 | -0.042162 |  | 0.93 | 1.05 | 0.052698 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | TV1MNDV4 | 0.95496 | 0.91279 | -0.042162 |  | 0.93 | 1.05 | 0.067422 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | TV1MNDV4 | 0.95496 | 0.91279 | -0.042162 |  | 0.93 | 1.05 | 0.053768 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | TV1MNDV4 | 0.95496 | 0.91279 | -0.042162 |  | 0.93 | 1.05 | 0.03909 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | TV1MNDV4 | 0.96658 | 0.94357 | -0.023008 |  | 0.95 | 1.05 | 0.14625 | System Intact | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | TV1MNDV4 | 0.95513 | 0.91679 | -0.038344 |  | 0.93 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | TV1MNDV4 | 0.95513 | 0.91679 | -0.038344 |  | 0.93 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | TV1MNDV4 | 0.95513 | 0.91679 | -0.038344 |  | 0.93 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | TV1MNDV4 | 0.95513 | 0.91679 | -0.038344 |  | 0.93 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | TV1MNDV4 | 0.95513 | 0.91679 | -0.038344 |  | 0.93 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | TV1MNDV4 | 0.95513 | 0.91679 | -0.038344 |  | 0.93 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | TV1MNDV4 | 0.95513 | 0.91679 | -0.038344 |  | 0.93 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | TV1MNDV4 | 0.95513 | 0.91679 | -0.038344 |  | 0.93 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | TV1MNDV4 | 0.95513 | 0.91679 | -0.038344 |  | 0.93 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | TV1MNDV4 | 0.95513 | 0.91679 | -0.038344 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | TV1MNDV4 | 0.95513 | 0.91679 | -0.038344 |  | 0.93 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | TV1MNDV4 | 0.95513 | 0.91679 | -0.038344 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | TV1MNDV4 | 0.95513 | 0.91679 | -0.038344 |  | 0.93 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | TV1MNDV4 | 0.95513 | 0.91679 | -0.038344 |  | 0.93 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | TV1MNDV4 | 0.95513 | 0.91679 | -0.038344 |  | 0.93 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | TV1MNDV4 | 0.95513 | 0.91679 | -0.038344 |  | 0.93 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | TV1MNDV4 | 0.95513 | 0.91679 | -0.038344 |  | 0.93 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | TV1MNDV4 | 0.95513 | 0.91679 | -0.038344 |  | 0.93 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | TV1MNDV4 | 0.95513 | 0.91679 | -0.038344 |  | 0.93 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | TV1MNDV4 | 0.95513 | 0.91679 | -0.038344 |  | 0.93 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | TV1MNDV4 | 0.95513 | 0.91679 | -0.038344 |  | 0.93 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | TV1MNDV4 | 0.95513 | 0.91679 | -0.038344 |  | 0.93 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | TV1MNDV4 | 0.95711 | 0.90665 | -0.050462 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | TV1MNDV4 | 0.95711 | 0.90665 | -0.050462 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | TV1MNDV4 | 0.95711 | 0.90665 | -0.050462 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | TV1MNDV4 | 0.95711 | 0.90665 | -0.050462 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | TV1MNDV4 | 0.95711 | 0.90665 | -0.050462 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | TV1MNDV4 | 0.95711 | 0.90665 | -0.050462 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | TV1MNDV4 | 0.95711 | 0.90665 | -0.050462 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | TV1MNDV4 | 0.95711 | 0.90665 | -0.050462 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | TV1MNDV4 | 0.95711 | 0.90665 | -0.050462 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | TV1MNDV4 | 0.95711 | 0.90665 | -0.050462 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | TV1MNDV4 | 0.95711 | 0.90665 | -0.050462 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | TV1MNDV4 | 0.95711 | 0.90665 | -0.050462 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | TV1MNDV4 | 0.95711 | 0.90665 | -0.050462 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | TV1MNDV4 | 0.95711 | 0.90665 | -0.050462 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | TV1MNDV4 | 0.95711 | 0.90665 | -0.050462 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | TV1MNDV4 | 0.95711 | 0.90665 | -0.050462 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | TV1MNDV4 | 0.95711 | 0.90665 | -0.050462 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | TV1MNDV4 | 0.95711 | 0.90665 | -0.050462 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | TV1MNDV4 | 0.95711 | 0.90665 | -0.050462 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | TV1MNDV4 | 0.95711 | 0.90665 | -0.050462 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | TV1MNDV4 | 0.95711 | 0.90665 | -0.050462 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | TV1MNDV4 | 0.95711 | 0.90665 | -0.050462 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | TV1MNDV4 | 0.95711 | 0.90665 | -0.050462 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | TV1MNDV4 | 0.95711 | 0.90665 | -0.050462 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | TV1MNDV4 | 0.95711 | 0.90665 | -0.050462 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | TV1MNDV4 | 0.95711 | 0.90665 | -0.050462 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | TV1MNDV4 | 0.95711 | 0.90665 | -0.050462 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | TV1MNDV4 | 0.95711 | 0.90665 | -0.050462 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | W.GRDNR7 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | W.GRDNR7 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | W.GRDNR7 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | W.GRDNR7 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | W.GRDNR7 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | W.GRDNR7 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | W.GRDNR7 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | W.GRDNR7 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | W.GRDNR7 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | W.GRDNR7 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | W.GRDNR7 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | W.GRDNR7 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | W.GRDNR7 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | W.GRDNR7 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | W.GRDNR7 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | W.GRDNR7 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | W.GRDNR7 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | W.GRDNR7 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | W.GRDNR7 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | W.GRDNR7 | 0.9575 | 0.91071 | -0.046786 |  | 0.95 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | W.GRDNR7 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | W.GRDNR7 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | W.GRDNR7 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | W.GRDNR7 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | W.GRDNR7 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | W.GRDNR7 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | W.GRDNR7 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | W.GRDNR7 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | W.GRDNR7 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | W.GRDNR7 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | W.GRDNR7 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | W.GRDNR7 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | W.GRDNR7 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | W.GRDNR7 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | W.GRDNR7 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | W.GRDNR7 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | W.GRDNR7 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | W.GRDNR7 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | W.GRDNR7 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | W.GRDNR7 | 0.94913 | 0.89636 | -0.052769 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | W.GRDNR7 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | W.GRDNR7 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | W.GRDNR7 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | W.GRDNR7 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | W.GRDNR7 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | W.GRDNR7 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | W.GRDNR7 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | W.GRDNR7 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | W.GRDNR7 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | W.GRDNR7 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | W.GRDNR7 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | W.GRDNR7 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | W.GRDNR7 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | W.GRDNR7 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | W.GRDNR7 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | W.GRDNR7 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | W.GRDNR7 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | W.GRDNR7 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | W.GRDNR7 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | W.GRDNR7 | 0.96298 | 0.90217 | -0.060808 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | W.GRDNR7 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | W.GRDNR7 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | W.GRDNR7 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | W.GRDNR7 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | W.GRDNR7 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | W.GRDNR7 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | W.GRDNR7 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | W.GRDNR7 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | W.GRDNR7 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | W.GRDNR7 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | W.GRDNR7 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | W.GRDNR7 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | W.GRDNR7 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | W.GRDNR7 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | W.GRDNR7 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | W.GRDNR7 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | W.GRDNR7 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | W.GRDNR7 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | W.GRDNR7 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | W.GRDNR7 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | W.GRDNR7 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | W.GRDNR7 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | W.GRDNR7 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | W.GRDNR7 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | W.GRDNR7 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | W.GRDNR7 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | W.GRDNR7 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | W.GRDNR7 | 0.96936 | 0.88276 | -0.086602 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | W.GRDNR7 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | W.GRDNR7 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | W.GRDNR7 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | W.GRDNR7 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | W.GRDNR7 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | W.GRDNR7 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | W.GRDNR7 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | W.GRDNR7 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | W.GRDNR7 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | W.GRDNR7 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | W.GRDNR7 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | W.GRDNR7 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | W.GRDNR7 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | W.GRDNR7 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | W.GRDNR7 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | W.GRDNR7 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | W.GRDNR7 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | W.GRDNR7 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | W.GRDNR7 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | W.GRDNR7 | 0.95653 | 0.90885 | -0.047679 |  | 0.95 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | WAGSTAF5 | 0.99551 | 0.90857 | -0.086938 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | WAGSTAF5 | 0.99551 | 0.90857 | -0.086938 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | WAGSTAF5 | 0.99551 | 0.90857 | -0.086938 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | WAGSTAF5 | 0.99551 | 0.90857 | -0.086938 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | WAGSTAF5 | 0.99551 | 0.90857 | -0.086938 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | WAGSTAF5 | 0.99551 | 0.90857 | -0.086938 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | WAGSTAF5 | 0.99551 | 0.90857 | -0.086938 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | WAGSTAF5 | 0.99551 | 0.90857 | -0.086938 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | WAGSTAF5 | 0.99551 | 0.90857 | -0.086938 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | WAGSTAF5 | 0.99551 | 0.90857 | -0.086938 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | WAGSTAF5 | 0.99551 | 0.90857 | -0.086938 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | WAGSTAF5 | 0.99551 | 0.90857 | -0.086938 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | WAGSTAF5 | 0.99551 | 0.90857 | -0.086938 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | WAGSTAF5 | 0.99551 | 0.90857 | -0.086938 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | WAGSTAF5 | 0.99551 | 0.90857 | -0.086938 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | WAGSTAF5 | 0.99551 | 0.90857 | -0.086938 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | WAGSTAF5 | 0.99551 | 0.90857 | -0.086938 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | WAGSTAF5 | 0.99551 | 0.90857 | -0.086938 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | WAGSTAF5 | 0.99551 | 0.90857 | -0.086938 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | WAGSTAF5 | 0.99551 | 0.90857 | -0.086938 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | WAGSTAF5 | 0.99551 | 0.90857 | -0.086938 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | WAGSTAF5 | 0.99551 | 0.90857 | -0.086938 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | WAGSTAF5 | 0.99551 | 0.90857 | -0.086938 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | WAGSTAF5 | 0.99551 | 0.90857 | -0.086938 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | WAGSTAF5 | 0.99551 | 0.90857 | -0.086938 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | WAGSTAF5 | 0.99551 | 0.90857 | -0.086938 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | WAGSTAF5 | 0.99551 | 0.90857 | -0.086938 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | WAGSTAF5 | 0.99551 | 0.90857 | -0.086938 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | WASHBURN5 | 0.98254 | 0.91862 | -0.063925 |  | 0.92 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | WASHBURN5 | 0.98254 | 0.91862 | -0.063925 |  | 0.92 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | WASHBURN5 | 0.98254 | 0.91862 | -0.063925 |  | 0.92 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | WASHBURN5 | 0.98254 | 0.91862 | -0.063925 |  | 0.92 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | WASHBURN5 | 0.98254 | 0.91862 | -0.063925 |  | 0.92 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | WASHBURN5 | 0.98254 | 0.91862 | -0.063925 |  | 0.92 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | WASHBURN5 | 0.98254 | 0.91862 | -0.063925 |  | 0.92 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | WASHBURN5 | 0.98254 | 0.91862 | -0.063925 |  | 0.92 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | WASHBURN5 | 0.98254 | 0.91862 | -0.063925 |  | 0.92 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | WASHBURN5 | 0.98254 | 0.91862 | -0.063925 |  | 0.92 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | WASHBURN5 | 0.98254 | 0.91862 | -0.063925 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | WASHBURN5 | 0.98254 | 0.91862 | -0.063925 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | WASHBURN5 | 0.98254 | 0.91862 | -0.063925 |  | 0.92 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | WASHBURN5 | 0.98254 | 0.91862 | -0.063925 |  | 0.92 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | WASHBURN5 | 0.98254 | 0.91862 | -0.063925 |  | 0.92 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | WAVERLY3 | 0.96425 | 0.92085 | -0.043394 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | WAVERLY3 | 0.96425 | 0.92085 | -0.043394 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | WAVERLY3 | 0.96425 | 0.92085 | -0.043394 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | WAVERLY3 | 0.96425 | 0.92085 | -0.043394 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | WAVERLY3 | 0.96425 | 0.92085 | -0.043394 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | WAVERLY3 | 0.96425 | 0.92085 | -0.043394 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | WAVERLY3 | 0.96425 | 0.92085 | -0.043394 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | WAVERLY3 | 0.96425 | 0.92085 | -0.043394 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | WAVERLY3 | 0.96425 | 0.92085 | -0.043394 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | WAVERLY3 | 0.96425 | 0.92085 | -0.043394 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | WAVERLY3 | 0.96425 | 0.92085 | -0.043394 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | WAVERLY3 | 0.96425 | 0.92085 | -0.043394 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | WAVERLY3 | 0.96425 | 0.92085 | -0.043394 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | WAVERLY3 | 0.96425 | 0.92085 | -0.043394 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | WAVERLY3 | 0.96425 | 0.92085 | -0.043394 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | WAVERLY3 | 0.96425 | 0.92085 | -0.043394 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | WAVERLY3 | 0.96425 | 0.92085 | -0.043394 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | WAVERLY3 | 0.96425 | 0.92085 | -0.043394 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | WAVERLY3 | 0.96425 | 0.92085 | -0.043394 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | WAVERLY3 | 0.96425 | 0.92085 | -0.043394 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | WAVERLY3 | 0.97446 | 0.92673 | -0.047731 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | WAVERLY3 | 0.97446 | 0.92673 | -0.047731 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | WAVERLY3 | 0.97446 | 0.92673 | -0.047731 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | WAVERLY3 | 0.97446 | 0.92673 | -0.047731 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | WAVERLY3 | 0.97446 | 0.92673 | -0.047731 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | WAVERLY3 | 0.97446 | 0.92673 | -0.047731 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | WAVERLY3 | 0.97446 | 0.92673 | -0.047731 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | WAVERLY3 | 0.97446 | 0.92673 | -0.047731 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | WAVERLY3 | 0.97446 | 0.92673 | -0.047731 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | WAVERLY3 | 0.97446 | 0.92673 | -0.047731 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | WAVERLY3 | 0.97446 | 0.92673 | -0.047731 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | WAVERLY3 | 0.97446 | 0.92673 | -0.047731 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | WAVERLY3 | 0.97446 | 0.92673 | -0.047731 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | WAVERLY3 | 0.97446 | 0.92673 | -0.047731 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | WAVERLY3 | 0.97446 | 0.92673 | -0.047731 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | WAVERLY3 | 0.97446 | 0.92673 | -0.047731 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | WAVERLY3 | 0.97446 | 0.92673 | -0.047731 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | WAVERLY3 | 0.97446 | 0.92673 | -0.047731 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | WAVERLY3 | 0.97446 | 0.92673 | -0.047731 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | WAVERLY3 | 0.97446 | 0.92673 | -0.047731 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | WAVERLY3 | 0.98013 | 0.91264 | -0.067491 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | WAVERLY3 | 0.98013 | 0.91264 | -0.067491 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | WAVERLY3 | 0.98013 | 0.91264 | -0.067491 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | WAVERLY3 | 0.98013 | 0.91264 | -0.067491 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | WAVERLY3 | 0.98013 | 0.91264 | -0.067491 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | WAVERLY3 | 0.98013 | 0.91264 | -0.067491 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | WAVERLY3 | 0.98013 | 0.91264 | -0.067491 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | WAVERLY3 | 0.98013 | 0.91264 | -0.067491 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | WAVERLY3 | 0.98013 | 0.91264 | -0.067491 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | WAVERLY3 | 0.98013 | 0.91264 | -0.067491 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | WAVERLY3 | 0.98013 | 0.91264 | -0.067491 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | WAVERLY3 | 0.98013 | 0.91264 | -0.067491 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | WAVERLY3 | 0.98013 | 0.91264 | -0.067491 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | WAVERLY3 | 0.98013 | 0.91264 | -0.067491 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | WAVERLY3 | 0.98013 | 0.91264 | -0.067491 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | WAVERLY3 | 0.98013 | 0.91264 | -0.067491 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | WAVERLY3 | 0.98013 | 0.91264 | -0.067491 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | WAVERLY3 | 0.98013 | 0.91264 | -0.067491 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | WAVERLY3 | 0.98013 | 0.91264 | -0.067491 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | WAVERLY3 | 0.98013 | 0.91264 | -0.067491 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | WAVERLY3 | 0.98013 | 0.91264 | -0.067491 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | WAVERLY3 | 0.98013 | 0.91264 | -0.067491 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | WAVERLY3 | 0.98013 | 0.91264 | -0.067491 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | WAVERLY3 | 0.98013 | 0.91264 | -0.067491 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | WAVERLY3 | 0.98013 | 0.91264 | -0.067491 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | WAVERLY3 | 0.98013 | 0.91264 | -0.067491 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | WAVERLY3 | 0.98013 | 0.91264 | -0.067491 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | WAVERLY3 | 0.98013 | 0.91264 | -0.067491 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | WGARDNR5 | 1.0059 | 0.92479 | -0.081146 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | WGARDNR5 | 1.0059 | 0.92479 | -0.081146 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | WGARDNR5 | 1.0059 | 0.92479 | -0.081146 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | WGARDNR5 | 1.0059 | 0.92479 | -0.081146 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | WGARDNR5 | 1.0059 | 0.92479 | -0.081146 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | WGARDNR5 | 1.0059 | 0.92479 | -0.081146 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | WGARDNR5 | 1.0059 | 0.92479 | -0.081146 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | WGARDNR5 | 1.0059 | 0.92479 | -0.081146 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | WGARDNR5 | 1.0059 | 0.92479 | -0.081146 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | WGARDNR5 | 1.0059 | 0.92479 | -0.081146 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | WGARDNR5 | 1.0059 | 0.92479 | -0.081146 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | WGARDNR5 | 1.0059 | 0.92479 | -0.081146 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | WGARDNR5 | 1.0059 | 0.92479 | -0.081146 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | WGARDNR5 | 1.0059 | 0.92479 | -0.081146 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | WGARDNR5 | 1.0059 | 0.92479 | -0.081146 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | WGARDNR5 | 1.0059 | 0.92479 | -0.081146 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | WGARDNR5 | 1.0059 | 0.92479 | -0.081146 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | WGARDNR5 | 1.0059 | 0.92479 | -0.081146 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | WGARDNR5 | 1.0059 | 0.92479 | -0.081146 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | WGARDNR5 | 1.0059 | 0.92479 | -0.081146 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | WGARDNR5 | 1.0059 | 0.92479 | -0.081146 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | WGARDNR5 | 1.0059 | 0.92479 | -0.081146 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | WGARDNR5 | 1.0059 | 0.92479 | -0.081146 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | WGARDNR5 | 1.0059 | 0.92479 | -0.081146 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | WGARDNR5 | 1.0059 | 0.92479 | -0.081146 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | WGARDNR5 | 1.0059 | 0.92479 | -0.081146 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | WGARDNR5 | 1.0059 | 0.92479 | -0.081146 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | WGARDNR5 | 1.0059 | 0.92479 | -0.081146 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | WHARV4 | 0.94016 | 0.90134 | -0.038821 |  | 0.93 | 1.05 | 0.055416 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | WHARV4 | 0.94016 | 0.90134 | -0.038821 |  | 0.93 | 1.05 | 0.031006 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | WHARV4 | 0.94016 | 0.90134 | -0.038821 |  | 0.93 | 1.05 | 0.065094 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | WHARV4 | 0.94016 | 0.90134 | -0.038821 |  | 0.93 | 1.05 | 0.044621 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | WHARV4 | 0.94016 | 0.90134 | -0.038821 |  | 0.93 | 1.05 | 0.048914 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | WHARV4 | 0.94016 | 0.90134 | -0.038821 |  | 0.93 | 1.05 | 0.048508 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | WHARV4 | 0.94016 | 0.90134 | -0.038821 |  | 0.93 | 1.05 | 0.047017 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | WHARV4 | 0.94016 | 0.90134 | -0.038821 |  | 0.93 | 1.05 | 0.040068 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | WHARV4 | 0.94016 | 0.90134 | -0.038821 |  | 0.93 | 1.05 | 0.043101 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | WHARV4 | 0.94016 | 0.90134 | -0.038821 |  | 0.93 | 1.05 | 0.051186 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | WHARV4 | 0.94016 | 0.90134 | -0.038821 |  | 0.93 | 1.05 | 0.041545 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | WHARV4 | 0.94016 | 0.90134 | -0.038821 |  | 0.93 | 1.05 | 0.050897 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | WHARV4 | 0.94016 | 0.90134 | -0.038821 |  | 0.93 | 1.05 | 0.07159 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | WHARV4 | 0.94016 | 0.90134 | -0.038821 |  | 0.93 | 1.05 | 0.050897 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | WHARV4 | 0.94016 | 0.90134 | -0.038821 |  | 0.93 | 1.05 | 0.052178 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | WHARV4 | 0.94016 | 0.90134 | -0.038821 |  | 0.93 | 1.05 | 0.0519 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | WHARV4 | 0.94016 | 0.90134 | -0.038821 |  | 0.93 | 1.05 | 0.034974 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | WHARV4 | 0.94016 | 0.90134 | -0.038821 |  | 0.93 | 1.05 | 0.050152 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | WHARV4 | 0.94016 | 0.90134 | -0.038821 |  | 0.93 | 1.05 | 0.037496 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | WHARV4 | 0.94016 | 0.90134 | -0.038821 |  | 0.93 | 1.05 | 0.037496 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | WHARV4 | 0.94016 | 0.90134 | -0.038821 |  | 0.93 | 1.05 | 0.045947 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | WHARV4 | 0.94016 | 0.90134 | -0.038821 |  | 0.93 | 1.05 | 0.049649 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | WHARV4 | 0.94016 | 0.90134 | -0.038821 |  | 0.93 | 1.05 | 0.040149 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | WHARV4 | 0.94016 | 0.90134 | -0.038821 |  | 0.93 | 1.05 | 0.046162 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | WHARV4 | 0.94016 | 0.90134 | -0.038821 |  | 0.93 | 1.05 | 0.044763 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | WHARV4 | 0.94016 | 0.90134 | -0.038821 |  | 0.93 | 1.05 | 0.047325 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | WHARV4 | 0.94016 | 0.90134 | -0.038821 |  | 0.93 | 1.05 | 0.048761 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | WHARV4 | 0.94016 | 0.90134 | -0.038821 |  | 0.93 | 1.05 | 0.035454 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | WHARV4 | 0.94058 | 0.90166 | -0.03892 |  | 0.93 | 1.05 | 0.055416 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | WHARV4 | 0.94058 | 0.90166 | -0.03892 |  | 0.93 | 1.05 | 0.031006 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | WHARV4 | 0.94058 | 0.90166 | -0.03892 |  | 0.93 | 1.05 | 0.036106 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | WHARV4 | 0.94058 | 0.90166 | -0.03892 |  | 0.93 | 1.05 | 0.037647 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | WHARV4 | 0.94058 | 0.90166 | -0.03892 |  | 0.93 | 1.05 | 0.048914 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | WHARV4 | 0.94058 | 0.90166 | -0.03892 |  | 0.93 | 1.05 | 0.048508 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | WHARV4 | 0.94058 | 0.90166 | -0.03892 |  | 0.93 | 1.05 | 0.040159 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | WHARV4 | 0.94058 | 0.90166 | -0.03892 |  | 0.93 | 1.05 | 0.040068 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | WHARV4 | 0.94058 | 0.90166 | -0.03892 |  | 0.93 | 1.05 | 0.043101 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | WHARV4 | 0.94058 | 0.90166 | -0.03892 |  | 0.93 | 1.05 | 0.051186 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | WHARV4 | 0.94058 | 0.90166 | -0.03892 |  | 0.93 | 1.05 | 0.041545 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | WHARV4 | 0.94058 | 0.90166 | -0.03892 |  | 0.93 | 1.05 | 0.050897 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | WHARV4 | 0.94058 | 0.90166 | -0.03892 |  | 0.93 | 1.05 | 0.032959 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | WHARV4 | 0.94058 | 0.90166 | -0.03892 |  | 0.93 | 1.05 | 0.050897 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | WHARV4 | 0.94058 | 0.90166 | -0.03892 |  | 0.93 | 1.05 | 0.052178 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | WHARV4 | 0.94058 | 0.90166 | -0.03892 |  | 0.93 | 1.05 | 0.0519 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | WHARV4 | 0.94058 | 0.90166 | -0.03892 |  | 0.93 | 1.05 | 0.034974 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | WHARV4 | 0.94058 | 0.90166 | -0.03892 |  | 0.93 | 1.05 | 0.035428 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | WHARV4 | 0.94058 | 0.90166 | -0.03892 |  | 0.93 | 1.05 | 0.037496 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | WHARV4 | 0.94058 | 0.90166 | -0.03892 |  | 0.93 | 1.05 | 0.037496 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | WHARV4 | 0.94058 | 0.90166 | -0.03892 |  | 0.93 | 1.05 | 0.039177 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | WHARV4 | 0.94058 | 0.90166 | -0.03892 |  | 0.93 | 1.05 | 0.049649 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | WHARV4 | 0.94058 | 0.90166 | -0.03892 |  | 0.93 | 1.05 | 0.040149 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | WHARV4 | 0.94058 | 0.90166 | -0.03892 |  | 0.93 | 1.05 | 0.046162 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | WHARV4 | 0.94058 | 0.90166 | -0.03892 |  | 0.93 | 1.05 | 0.044763 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | WHARV4 | 0.94058 | 0.90166 | -0.03892 |  | 0.93 | 1.05 | 0.047325 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | WHARV4 | 0.94058 | 0.90166 | -0.03892 |  | 0.93 | 1.05 | 0.048761 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | WHARV4 | 0.94058 | 0.90166 | -0.03892 |  | 0.93 | 1.05 | 0.035454 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | WHARV4 | 0.97128 | 0.89782 | -0.073453 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | WHARV4 | 0.97128 | 0.89782 | -0.073453 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | WHARV4 | 0.97128 | 0.89782 | -0.073453 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | WHARV4 | 0.97128 | 0.89782 | -0.073453 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | WHARV4 | 0.97128 | 0.89782 | -0.073453 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | WHARV4 | 0.97128 | 0.89782 | -0.073453 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | WHARV4 | 0.97128 | 0.89782 | -0.073453 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | WHARV4 | 0.97128 | 0.89782 | -0.073453 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | WHARV4 | 0.97128 | 0.89782 | -0.073453 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | WHARV4 | 0.97128 | 0.89782 | -0.073453 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | WHARV4 | 0.97128 | 0.89782 | -0.073453 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | WHARV4 | 0.97128 | 0.89782 | -0.073453 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | WHARV4 | 0.97128 | 0.89782 | -0.073453 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | WHARV4 | 0.97128 | 0.89782 | -0.073453 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | WHARV4 | 0.97128 | 0.89782 | -0.073453 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | WHARV4 | 0.97128 | 0.89782 | -0.073453 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | WHARV4 | 0.97128 | 0.89782 | -0.073453 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | WHARV4 | 0.97128 | 0.89782 | -0.073453 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | WHARV4 | 0.97128 | 0.89782 | -0.073453 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | WHARV4 | 0.97128 | 0.89782 | -0.073453 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | WHARV4 | 0.97128 | 0.89782 | -0.073453 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | WHARV4 | 0.97128 | 0.89782 | -0.073453 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | WHARV4 | 0.97128 | 0.89782 | -0.073453 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | WHARV4 | 0.97128 | 0.89782 | -0.073453 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | WHARV4 | 0.97128 | 0.89782 | -0.073453 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | WHARV4 | 0.97128 | 0.89782 | -0.073453 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | WHARV4 | 0.97128 | 0.89782 | -0.073453 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | WHARV4 | 0.97128 | 0.89782 | -0.073453 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | WICHITA7 | 0.98349 | 0.94369 | -0.039804 |  | 0.95 | 1.05 | 0.077434 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | WICHITA7 | 0.98349 | 0.94369 | -0.039804 |  | 0.95 | 1.05 | 0.032924 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | WICHITA7 | 0.98349 | 0.94369 | -0.039804 |  | 0.95 | 1.05 | 0.032924 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | WICHITA7 | 0.98349 | 0.94369 | -0.039804 |  | 0.95 | 1.05 | 0.032685 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | WICHITA7 | 0.98349 | 0.94369 | -0.039804 |  | 0.95 | 1.05 | 0.030104 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | WICHITA7 | 0.98349 | 0.94369 | -0.039804 |  | 0.95 | 1.05 | 0.036404 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | WICHITA7 | 0.98404 | 0.94392 | -0.040118 |  | 0.95 | 1.05 | 0.030773 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | WICHITA7 | 0.98404 | 0.94392 | -0.040118 |  | 0.95 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | WICHITA7 | 0.98404 | 0.94392 | -0.040118 |  | 0.95 | 1.05 | 0.046711 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | WICHITA7 | 0.98404 | 0.94392 | -0.040118 |  | 0.95 | 1.05 | 0.032369 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | WICHITA7 | 0.98404 | 0.94392 | -0.040118 |  | 0.95 | 1.05 | 0.030466 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | WICHITA7 | 0.98404 | 0.94392 | -0.040118 |  | 0.95 | 1.05 | 0.04987 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | WICHITA7 | 0.98404 | 0.94392 | -0.040118 |  | 0.95 | 1.05 | 0.099365 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | WICHITA7 | 0.98404 | 0.94392 | -0.040118 |  | 0.95 | 1.05 | 0.071132 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | WICHITA7 | 0.98404 | 0.94392 | -0.040118 |  | 0.95 | 1.05 | 0.043927 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | WICHITA7 | 0.98404 | 0.94392 | -0.040118 |  | 0.95 | 1.05 | 0.030565 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | WICHITA7 | 0.98404 | 0.94392 | -0.040118 |  | 0.95 | 1.05 | 0.072847 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | WICHITA7 | 0.98404 | 0.94392 | -0.040118 |  | 0.95 | 1.05 | 0.041148 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | WICHITA7 | 0.98404 | 0.94392 | -0.040118 |  | 0.95 | 1.05 | 0.042015 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | WICHITA7 | 0.98404 | 0.94392 | -0.040118 |  | 0.95 | 1.05 | 0.030318 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | WICHITA7 | 0.98404 | 0.94392 | -0.040118 |  | 0.95 | 1.05 | 0.054104 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | WICHITA7 | 0.98404 | 0.94392 | -0.040118 |  | 0.95 | 1.05 | 0.047089 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | WICHITA7 | 0.98404 | 0.94392 | -0.040118 |  | 0.95 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | WICHITA7 | 0.98404 | 0.94392 | -0.040118 |  | 0.95 | 1.05 | 0.13688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | WICHITA7 | 0.98404 | 0.94392 | -0.040118 |  | 0.95 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | WICHITA7 | 0.98404 | 0.94392 | -0.040118 |  | 0.95 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | WICHITA7 | 0.98404 | 0.94392 | -0.040118 |  | 0.95 | 1.05 | 0.039752 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | WICHITA7 | 0.98404 | 0.94392 | -0.040118 |  | 0.95 | 1.05 | 0.041972 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | WICHITA7 | 0.98404 | 0.94392 | -0.040118 |  | 0.95 | 1.05 | 0.054397 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | WICHITA7 | 0.98404 | 0.94392 | -0.040118 |  | 0.95 | 1.05 | 0.073688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | WICHITA7 | 0.98404 | 0.94392 | -0.040118 |  | 0.95 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | WICHITA7 | 0.98404 | 0.94392 | -0.040118 |  | 0.95 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | WICHITA7 | 0.98404 | 0.94392 | -0.040118 |  | 0.95 | 1.05 | 0.072188 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | WICHITA7 | 0.98404 | 0.94392 | -0.040118 |  | 0.95 | 1.05 | 0.042186 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | WICHITA7 | 0.98404 | 0.94392 | -0.040118 |  | 0.95 | 1.05 | 0.041423 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | WICHITA7 | 0.98404 | 0.94392 | -0.040118 |  | 0.95 | 1.05 | 0.050171 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | WICHITA7 | 0.98404 | 0.94392 | -0.040118 |  | 0.95 | 1.05 | 0.04386 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | WICHITA7 | 0.98404 | 0.94392 | -0.040118 |  | 0.95 | 1.05 | 0.050218 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | WICHITA7 | 0.98404 | 0.94392 | -0.040118 |  | 0.95 | 1.05 | 0.040041 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | WICHITA7 | 0.98404 | 0.94392 | -0.040118 |  | 0.95 | 1.05 | 0.038784 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | WICHITA7 | 0.97996 | 0.94154 | -0.038418 |  | 0.95 | 1.05 | 0.040027 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | WICHITA7 | 0.97996 | 0.94154 | -0.038418 |  | 0.95 | 1.05 | 0.090773 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | WICHITA7 | 0.97996 | 0.94154 | -0.038418 |  | 0.95 | 1.05 | 0.034521 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | WICHITA7 | 0.97996 | 0.94154 | -0.038418 |  | 0.95 | 1.05 | 0.038035 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | WICHITA7 | 0.97996 | 0.94154 | -0.038418 |  | 0.95 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | WICHITA7 | 0.97996 | 0.94154 | -0.038418 |  | 0.95 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | WICHITA7 | 0.97996 | 0.94154 | -0.038418 |  | 0.95 | 1.05 | 0.050618 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | WICHITA7 | 0.97996 | 0.94154 | -0.038418 |  | 0.95 | 1.05 | 0.04163 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | WICHITA7 | 0.97996 | 0.94154 | -0.038418 |  | 0.95 | 1.05 | 0.043776 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | WICHITA7 | 0.97996 | 0.94154 | -0.038418 |  | 0.95 | 1.05 | 0.034868 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | WICHITA7 | 0.97996 | 0.94154 | -0.038418 |  | 0.95 | 1.05 | 0.031975 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | WICHITA7 | 0.97996 | 0.94154 | -0.038418 |  | 0.95 | 1.05 | 0.037422 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | WICHITA7 | 0.97996 | 0.94154 | -0.038418 |  | 0.95 | 1.05 | 0.050095 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | WICHITA7 | 0.97974 | 0.92969 | -0.050051 |  | 0.95 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | WICHITA7 | 0.97974 | 0.92969 | -0.050051 |  | 0.95 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | WICHITA7 | 0.97974 | 0.92969 | -0.050051 |  | 0.95 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | WICHITA7 | 0.97974 | 0.92969 | -0.050051 |  | 0.95 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | WICHITA7 | 0.97974 | 0.92969 | -0.050051 |  | 0.95 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | WICHITA7 | 0.97974 | 0.92969 | -0.050051 |  | 0.95 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | WICHITA7 | 0.97974 | 0.92969 | -0.050051 |  | 0.95 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | WICHITA7 | 0.97974 | 0.92969 | -0.050051 |  | 0.95 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | WICHITA7 | 0.97974 | 0.92969 | -0.050051 |  | 0.95 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | WICHITA7 | 0.97974 | 0.92969 | -0.050051 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | WICHITA7 | 0.97974 | 0.92969 | -0.050051 |  | 0.95 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | WICHITA7 | 0.97974 | 0.92969 | -0.050051 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | WICHITA7 | 0.97974 | 0.92969 | -0.050051 |  | 0.95 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | WICHITA7 | 0.97974 | 0.92969 | -0.050051 |  | 0.95 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | WICHITA7 | 0.97974 | 0.92969 | -0.050051 |  | 0.95 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | WICHITA7 | 0.97974 | 0.92969 | -0.050051 |  | 0.95 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | WICHITA7 | 0.97974 | 0.92969 | -0.050051 |  | 0.95 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | WICHITA7 | 0.97974 | 0.92969 | -0.050051 |  | 0.95 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | WICHITA7 | 0.97974 | 0.92969 | -0.050051 |  | 0.95 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | WICHITA7 | 0.97974 | 0.92969 | -0.050051 |  | 0.95 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | WICHITA7 | 0.97974 | 0.92969 | -0.050051 |  | 0.95 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | WICHITA7 | 0.97974 | 0.92969 | -0.050051 |  | 0.95 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | WICHITA7 | 0.98203 | 0.93199 | -0.050039 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | WICHITA7 | 0.98203 | 0.93199 | -0.050039 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | WICHITA7 | 0.98203 | 0.93199 | -0.050039 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | WICHITA7 | 0.98203 | 0.93199 | -0.050039 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | WICHITA7 | 0.98203 | 0.93199 | -0.050039 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | WICHITA7 | 0.98203 | 0.93199 | -0.050039 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | WICHITA7 | 0.98203 | 0.93199 | -0.050039 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | WICHITA7 | 0.98203 | 0.93199 | -0.050039 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | WICHITA7 | 0.98203 | 0.93199 | -0.050039 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | WICHITA7 | 0.98203 | 0.93199 | -0.050039 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | WICHITA7 | 0.98203 | 0.93199 | -0.050039 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | WICHITA7 | 0.98203 | 0.93199 | -0.050039 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | WICHITA7 | 0.98203 | 0.93199 | -0.050039 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | WICHITA7 | 0.98203 | 0.93199 | -0.050039 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | WICHITA7 | 0.98203 | 0.93199 | -0.050039 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | WICHITA7 | 0.98203 | 0.93199 | -0.050039 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | WICHITA7 | 0.98203 | 0.93199 | -0.050039 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | WICHITA7 | 0.98203 | 0.93199 | -0.050039 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | WICHITA7 | 0.98203 | 0.93199 | -0.050039 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | WICHITA7 | 0.98203 | 0.93199 | -0.050039 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | WICHITA7 | 0.98203 | 0.93199 | -0.050039 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | WICHITA7 | 0.98203 | 0.93199 | -0.050039 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | WICHITA7 | 0.98203 | 0.93199 | -0.050039 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | WICHITA7 | 0.98203 | 0.93199 | -0.050039 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | WICHITA7 | 0.98203 | 0.93199 | -0.050039 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | WICHITA7 | 0.98203 | 0.93199 | -0.050039 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | WICHITA7 | 0.98203 | 0.93199 | -0.050039 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | WICHITA7 | 0.98203 | 0.93199 | -0.050039 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | WINDSR 5 | 0.98591 | 0.91908 | -0.066826 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | WINDSR 5 | 0.98591 | 0.91908 | -0.066826 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | WINDSR 5 | 0.98591 | 0.91908 | -0.066826 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | WINDSR 5 | 0.98591 | 0.91908 | -0.066826 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | WINDSR 5 | 0.98591 | 0.91908 | -0.066826 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | WINDSR 5 | 0.98591 | 0.91908 | -0.066826 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | WINDSR 5 | 0.98591 | 0.91908 | -0.066826 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | WINDSR 5 | 0.98591 | 0.91908 | -0.066826 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | WINDSR 5 | 0.98591 | 0.91908 | -0.066826 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | WINDSR 5 | 0.98591 | 0.91908 | -0.066826 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | WINDSR 5 | 0.98591 | 0.91908 | -0.066826 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | WINDSR 5 | 0.98591 | 0.91908 | -0.066826 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | WINDSR 5 | 0.98591 | 0.91908 | -0.066826 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | WINDSR 5 | 0.98591 | 0.91908 | -0.066826 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | WINDSR 5 | 0.98591 | 0.91908 | -0.066826 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | WINDSR 5 | 0.98591 | 0.91908 | -0.066826 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | WINDSR 5 | 0.98591 | 0.91908 | -0.066826 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | WINDSR 5 | 0.98591 | 0.91908 | -0.066826 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | WINDSR 5 | 0.98591 | 0.91908 | -0.066826 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | WINDSR 5 | 0.98591 | 0.91908 | -0.066826 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | WINDSR 5 | 0.98591 | 0.91908 | -0.066826 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | WINDSR 5 | 0.98591 | 0.91908 | -0.066826 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | WINDSR 5 | 0.98591 | 0.91908 | -0.066826 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | WINDSR 5 | 0.98591 | 0.91908 | -0.066826 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | WINDSR 5 | 0.98591 | 0.91908 | -0.066826 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | WINDSR 5 | 0.98591 | 0.91908 | -0.066826 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | WINDSR 5 | 0.98591 | 0.91908 | -0.066826 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | WINDSR 5 | 0.98591 | 0.91908 | -0.066826 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | WINJT S5 | 0.99183 | 0.92934 | -0.062494 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | WINJT S5 | 0.99183 | 0.92934 | -0.062494 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | WINJT S5 | 0.99183 | 0.92934 | -0.062494 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | WINJT S5 | 0.99183 | 0.92934 | -0.062494 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | WINJT S5 | 0.99183 | 0.92934 | -0.062494 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | WINJT S5 | 0.99183 | 0.92934 | -0.062494 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | WINJT S5 | 0.99183 | 0.92934 | -0.062494 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | WINJT S5 | 0.99183 | 0.92934 | -0.062494 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | WINJT S5 | 0.99183 | 0.92934 | -0.062494 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | WINJT S5 | 0.99183 | 0.92934 | -0.062494 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | WINJT S5 | 0.99183 | 0.92934 | -0.062494 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | WINJT S5 | 0.99183 | 0.92934 | -0.062494 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | WINJT S5 | 0.99183 | 0.92934 | -0.062494 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | WINJT S5 | 0.99183 | 0.92934 | -0.062494 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | WINJT S5 | 0.99183 | 0.92934 | -0.062494 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | WINJT S5 | 0.99183 | 0.92934 | -0.062494 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | WINJT S5 | 0.99183 | 0.92934 | -0.062494 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | WINJT S5 | 0.99183 | 0.92934 | -0.062494 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | WINJT S5 | 0.99183 | 0.92934 | -0.062494 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | WINJT S5 | 0.99183 | 0.92934 | -0.062494 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | WINJT S5 | 0.99183 | 0.92934 | -0.062494 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | WINJT S5 | 0.99183 | 0.92934 | -0.062494 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | WINJT S5 | 0.99183 | 0.92934 | -0.062494 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | WINJT S5 | 0.99183 | 0.92934 | -0.062494 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | WINJT S5 | 0.99183 | 0.92934 | -0.062494 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | WINJT S5 | 0.99183 | 0.92934 | -0.062494 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | WINJT S5 | 0.99183 | 0.92934 | -0.062494 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | WINJT S5 | 0.99183 | 0.92934 | -0.062494 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | WMBROS 3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | WMBROS 3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | WMBROS 3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | WMBROS 3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | WMBROS 3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | WMBROS 3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | WMBROS 3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | WMBROS 3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | WMBROS 3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | WMBROS 3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | WMBROS 3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | WMBROS 3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | WMBROS 3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | WMBROS 3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | WMBROS 3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | WMBROS 3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | WMBROS 3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | WMBROS 3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | WMBROS 3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | WMBROS 3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | WMBROS 3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | WMBROS 3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | WMBROS 3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | WMBROS 3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | WMBROS 3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | WMBROS 3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | WMBROS 3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | WMBROS 3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | WMBROSJ3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | WMBROSJ3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | WMBROSJ3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | WMBROSJ3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | WMBROSJ3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | WMBROSJ3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | WMBROSJ3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | WMBROSJ3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | WMBROSJ3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | WMBROSJ3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | WMBROSJ3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | WMBROSJ3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | WMBROSJ3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | WMBROSJ3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | WMBROSJ3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | WMBROSJ3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | WMBROSJ3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | WMBROSJ3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | WMBROSJ3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | WMBROSJ3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | WMBROSJ3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | WMBROSJ3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | WMBROSJ3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | WMBROSJ3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | WMBROSJ3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | WMBROSJ3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | WMBROSJ3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | WMBROSJ3 | 0.95122 | 0.86333 | -0.087894 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | WOODLND5 | 0.96814 | 0.9281 | -0.040039 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | WOODLND5 | 0.96814 | 0.9281 | -0.040039 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | WOODLND5 | 0.96814 | 0.9281 | -0.040039 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | WOODLND5 | 0.96814 | 0.9281 | -0.040039 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | WOODLND5 | 0.96814 | 0.9281 | -0.040039 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | WOODLND5 | 0.96814 | 0.9281 | -0.040039 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | WOODLND5 | 0.96814 | 0.9281 | -0.040039 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | WOODLND5 | 0.96814 | 0.9281 | -0.040039 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | WOODLND5 | 0.96814 | 0.9281 | -0.040039 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | WOODLND5 | 0.96814 | 0.9281 | -0.040039 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | WOODLND5 | 0.96814 | 0.9281 | -0.040039 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | WOODLND5 | 0.96814 | 0.9281 | -0.040039 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | WOODLND5 | 0.96814 | 0.9281 | -0.040039 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | WOODLND5 | 0.96814 | 0.9281 | -0.040039 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | WOODLND5 | 0.96814 | 0.9281 | -0.040039 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | WOODLND5 | 0.96814 | 0.9281 | -0.040039 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | WOODLND5 | 0.96814 | 0.9281 | -0.040039 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | WOODLND5 | 0.96814 | 0.9281 | -0.040039 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | WOODLND5 | 0.96814 | 0.9281 | -0.040039 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | WOODLND5 | 0.96814 | 0.9281 | -0.040039 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | WOODLND5 | 0.9811 | 0.91439 | -0.066711 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | WOODLND5 | 0.9811 | 0.91439 | -0.066711 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | WOODLND5 | 0.9811 | 0.91439 | -0.066711 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | WOODLND5 | 0.9811 | 0.91439 | -0.066711 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | WOODLND5 | 0.9811 | 0.91439 | -0.066711 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | WOODLND5 | 0.9811 | 0.91439 | -0.066711 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | WOODLND5 | 0.9811 | 0.91439 | -0.066711 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | WOODLND5 | 0.9811 | 0.91439 | -0.066711 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | WOODLND5 | 0.9811 | 0.91439 | -0.066711 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | WOODLND5 | 0.9811 | 0.91439 | -0.066711 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | WOODLND5 | 0.9811 | 0.91439 | -0.066711 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | WOODLND5 | 0.9811 | 0.91439 | -0.066711 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | WOODLND5 | 0.9811 | 0.91439 | -0.066711 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | WOODLND5 | 0.9811 | 0.91439 | -0.066711 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | WOODLND5 | 0.9811 | 0.91439 | -0.066711 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | WOODLND5 | 0.9811 | 0.91439 | -0.066711 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | WOODLND5 | 0.9811 | 0.91439 | -0.066711 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | WOODLND5 | 0.9811 | 0.91439 | -0.066711 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | WOODLND5 | 0.9811 | 0.91439 | -0.066711 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | WOODLND5 | 0.9811 | 0.91439 | -0.066711 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | WOODLND5 | 0.9811 | 0.91439 | -0.066711 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | WOODLND5 | 0.9811 | 0.91439 | -0.066711 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | WOODLND5 | 0.9811 | 0.91439 | -0.066711 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | WOODLND5 | 0.9811 | 0.91439 | -0.066711 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | WOODLND5 | 0.9811 | 0.91439 | -0.066711 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | WOODLND5 | 0.9811 | 0.91439 | -0.066711 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | WOODLND5 | 0.9811 | 0.91439 | -0.066711 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | WOODLND5 | 0.9811 | 0.91439 | -0.066711 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | WREN 3 | 0.96624 | 0.92566 | -0.040579 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | WREN 3 | 0.96624 | 0.92566 | -0.040579 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | WREN 3 | 0.96624 | 0.92566 | -0.040579 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | WREN 3 | 0.96624 | 0.92566 | -0.040579 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | WREN 3 | 0.96624 | 0.92566 | -0.040579 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | WREN 3 | 0.96624 | 0.92566 | -0.040579 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | WREN 3 | 0.96624 | 0.92566 | -0.040579 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | WREN 3 | 0.96624 | 0.92566 | -0.040579 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | WREN 3 | 0.96624 | 0.92566 | -0.040579 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | WREN 3 | 0.96624 | 0.92566 | -0.040579 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | WREN 3 | 0.96624 | 0.92566 | -0.040579 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | WREN 3 | 0.96624 | 0.92566 | -0.040579 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | WREN 3 | 0.96624 | 0.92566 | -0.040579 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | WREN 3 | 0.96624 | 0.92566 | -0.040579 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | WREN 3 | 0.96624 | 0.92566 | -0.040579 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | WREN 3 | 0.96624 | 0.92566 | -0.040579 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | WREN 3 | 0.96624 | 0.92566 | -0.040579 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | WREN 3 | 0.96624 | 0.92566 | -0.040579 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | WREN 3 | 0.96624 | 0.92566 | -0.040579 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | WREN 3 | 0.96624 | 0.92566 | -0.040579 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | WREN 3 | 0.97205 | 0.92863 | -0.043417 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | WREN 3 | 0.97205 | 0.92863 | -0.043417 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | WREN 3 | 0.97205 | 0.92863 | -0.043417 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | WREN 3 | 0.97205 | 0.92863 | -0.043417 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | WREN 3 | 0.97205 | 0.92863 | -0.043417 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | WREN 3 | 0.97205 | 0.92863 | -0.043417 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | WREN 3 | 0.97205 | 0.92863 | -0.043417 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | WREN 3 | 0.97205 | 0.92863 | -0.043417 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | WREN 3 | 0.97205 | 0.92863 | -0.043417 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | WREN 3 | 0.97205 | 0.92863 | -0.043417 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | WREN 3 | 0.97205 | 0.92863 | -0.043417 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | WREN 3 | 0.97205 | 0.92863 | -0.043417 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | WREN 3 | 0.97205 | 0.92863 | -0.043417 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | WREN 3 | 0.97205 | 0.92863 | -0.043417 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | WREN 3 | 0.97205 | 0.92863 | -0.043417 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | WREN 3 | 0.97205 | 0.92863 | -0.043417 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | WREN 3 | 0.97205 | 0.92863 | -0.043417 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | WREN 3 | 0.97205 | 0.92863 | -0.043417 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | WREN 3 | 0.97205 | 0.92863 | -0.043417 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | WREN 3 | 0.97205 | 0.92863 | -0.043417 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | WREN 3 | 0.97786 | 0.9268 | -0.051052 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | WREN 3 | 0.97786 | 0.9268 | -0.051052 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | WREN 3 | 0.97786 | 0.9268 | -0.051052 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | WREN 3 | 0.97786 | 0.9268 | -0.051052 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | WREN 3 | 0.97786 | 0.9268 | -0.051052 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | WREN 3 | 0.97786 | 0.9268 | -0.051052 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | WREN 3 | 0.97786 | 0.9268 | -0.051052 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | WREN 3 | 0.97786 | 0.9268 | -0.051052 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | WREN 3 | 0.97786 | 0.9268 | -0.051052 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | WREN 3 | 0.97786 | 0.9268 | -0.051052 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | WREN 3 | 0.97786 | 0.9268 | -0.051052 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | WREN 3 | 0.97786 | 0.9268 | -0.051052 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | WREN 3 | 0.97786 | 0.9268 | -0.051052 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | WREN 3 | 0.97786 | 0.9268 | -0.051052 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | WREN 3 | 0.97786 | 0.9268 | -0.051052 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | WREN 3 | 0.97786 | 0.9268 | -0.051052 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | WREN 3 | 0.97786 | 0.9268 | -0.051052 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | WREN 3 | 0.97786 | 0.9268 | -0.051052 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | WREN 3 | 0.97786 | 0.9268 | -0.051052 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | WREN 3 | 0.97786 | 0.9268 | -0.051052 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | WREN 3 | 0.97786 | 0.9268 | -0.051052 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | WREN 3 | 0.97786 | 0.9268 | -0.051052 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | WREN 3 | 0.97786 | 0.9268 | -0.051052 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | WREN 3 | 0.97786 | 0.9268 | -0.051052 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | WREN 3 | 0.97786 | 0.9268 | -0.051052 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | WREN 3 | 0.97786 | 0.9268 | -0.051052 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | WREN 3 | 0.97786 | 0.9268 | -0.051052 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | WREN 3 | 0.97786 | 0.9268 | -0.051052 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | WROGERS 5 | 0.98868 | 0.91844 | -0.070236 |  | 0.92 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | WROGERS 5 | 0.98868 | 0.91844 | -0.070236 |  | 0.92 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | WROGERS 5 | 0.98868 | 0.91844 | -0.070236 |  | 0.92 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | WROGERS 5 | 0.98868 | 0.91844 | -0.070236 |  | 0.92 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | WROGERS 5 | 0.98868 | 0.91844 | -0.070236 |  | 0.92 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | WROGERS 5 | 0.98868 | 0.91844 | -0.070236 |  | 0.92 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | WROGERS 5 | 0.98868 | 0.91844 | -0.070236 |  | 0.92 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | WROGERS 5 | 0.98868 | 0.91844 | -0.070236 |  | 0.92 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | WROGERS 5 | 0.98868 | 0.91844 | -0.070236 |  | 0.92 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | WROGERS 5 | 0.98868 | 0.91844 | -0.070236 |  | 0.92 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | WROGERS 5 | 0.98868 | 0.91844 | -0.070236 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | WROGERS 5 | 0.98868 | 0.91844 | -0.070236 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | WROGERS 5 | 0.98868 | 0.91844 | -0.070236 |  | 0.92 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | WROGERS 5 | 0.98868 | 0.91844 | -0.070236 |  | 0.92 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | WROGERS 5 | 0.98868 | 0.91844 | -0.070236 |  | 0.92 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | WROGERS 5 | 0.98925 | 0.9194 | -0.069854 |  | 0.92 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | WROGERS 5 | 0.98925 | 0.9194 | -0.069854 |  | 0.92 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | WROGERS 5 | 0.98925 | 0.9194 | -0.069854 |  | 0.92 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | WROGERS 5 | 0.98925 | 0.9194 | -0.069854 |  | 0.92 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | WROGERS 5 | 0.98925 | 0.9194 | -0.069854 |  | 0.92 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | WROGERS 5 | 0.98925 | 0.9194 | -0.069854 |  | 0.92 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | WROGERS 5 | 0.98925 | 0.9194 | -0.069854 |  | 0.92 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | WROGERS 5 | 0.98925 | 0.9194 | -0.069854 |  | 0.92 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | WROGERS 5 | 0.98925 | 0.9194 | -0.069854 |  | 0.92 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | WROGERS 5 | 0.98925 | 0.9194 | -0.069854 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | WROGERS 5 | 0.98925 | 0.9194 | -0.069854 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | WROGERS 5 | 0.98925 | 0.9194 | -0.069854 |  | 0.92 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | WROGERS 5 | 0.98925 | 0.9194 | -0.069854 |  | 0.92 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | WROGERS 5 | 0.98925 | 0.9194 | -0.069854 |  | 0.92 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | WSTELEC5 | 0.99797 | 0.92966 | -0.068311 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | WSTELEC5 | 0.99797 | 0.92966 | -0.068311 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | WSTELEC5 | 0.99797 | 0.92966 | -0.068311 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | WSTELEC5 | 0.99797 | 0.92966 | -0.068311 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | WSTELEC5 | 0.99797 | 0.92966 | -0.068311 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | WSTELEC5 | 0.99797 | 0.92966 | -0.068311 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | WSTELEC5 | 0.99797 | 0.92966 | -0.068311 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | WSTELEC5 | 0.99797 | 0.92966 | -0.068311 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | WSTELEC5 | 0.99797 | 0.92966 | -0.068311 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | WSTELEC5 | 0.99797 | 0.92966 | -0.068311 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | WSTELEC5 | 0.99797 | 0.92966 | -0.068311 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | WSTELEC5 | 0.99797 | 0.92966 | -0.068311 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | WSTELEC5 | 0.99797 | 0.92966 | -0.068311 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | WSTELEC5 | 0.99797 | 0.92966 | -0.068311 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | WSTELEC5 | 0.99797 | 0.92966 | -0.068311 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | WSTELEC5 | 0.99797 | 0.92966 | -0.068311 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | WSTELEC5 | 0.99797 | 0.92966 | -0.068311 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | WSTELEC5 | 0.99797 | 0.92966 | -0.068311 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | WSTELEC5 | 0.99797 | 0.92966 | -0.068311 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | WSTELEC5 | 0.99797 | 0.92966 | -0.068311 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | WSTELEC5 | 0.99797 | 0.92966 | -0.068311 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | WSTELEC5 | 0.99797 | 0.92966 | -0.068311 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | WSTELEC5 | 0.99797 | 0.92966 | -0.068311 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | WSTELEC5 | 0.99797 | 0.92966 | -0.068311 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | WSTELEC5 | 0.99797 | 0.92966 | -0.068311 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | WSTELEC5 | 0.99797 | 0.92966 | -0.068311 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | WSTELEC5 | 0.99797 | 0.92966 | -0.068311 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | WSTELEC5 | 0.99797 | 0.92966 | -0.068311 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | WTCLF 3 | 0.92839 | 0.85396 | -0.074433 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | WTCLF 3 | 0.92839 | 0.85396 | -0.074433 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | WTCLF 3 | 0.93532 | 0.85292 | -0.082404 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | WTCLF 3 | 0.93532 | 0.85292 | -0.082404 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | WTCLF 3 | 0.93532 | 0.85292 | -0.082404 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | WTCLF 3 | 0.93532 | 0.85292 | -0.082404 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | WTCLF 3 | 0.93532 | 0.85292 | -0.082404 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | WTCLF 3 | 0.93532 | 0.85292 | -0.082404 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | WWUPLNT4 | 0.9846 | 0.92893 | -0.055668 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | WWUPLNT4 | 0.9846 | 0.92893 | -0.055668 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | WWUPLNT4 | 0.9846 | 0.92893 | -0.055668 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | WWUPLNT4 | 0.9846 | 0.92893 | -0.055668 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | WWUPLNT4 | 0.9846 | 0.92893 | -0.055668 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | WWUPLNT4 | 0.9846 | 0.92893 | -0.055668 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | WWUPLNT4 | 0.9846 | 0.92893 | -0.055668 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | WWUPLNT4 | 0.9846 | 0.92893 | -0.055668 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | WWUPLNT4 | 0.9846 | 0.92893 | -0.055668 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | WWUPLNT4 | 0.9846 | 0.92893 | -0.055668 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | WWUPLNT4 | 0.9846 | 0.92893 | -0.055668 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | WWUPLNT4 | 0.9846 | 0.92893 | -0.055668 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | WWUPLNT4 | 0.9846 | 0.92893 | -0.055668 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | WWUPLNT4 | 0.9846 | 0.92893 | -0.055668 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | WWUPLNT4 | 0.9846 | 0.92893 | -0.055668 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | WWUPLNT4 | 0.9846 | 0.92893 | -0.055668 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | WWUPLNT4 | 0.9846 | 0.92893 | -0.055668 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | WWUPLNT4 | 0.9846 | 0.92893 | -0.055668 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | WWUPLNT4 | 0.9846 | 0.92893 | -0.055668 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | WWUPLNT4 | 0.9846 | 0.92893 | -0.055668 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | WWUPLNT4 | 0.9846 | 0.92893 | -0.055668 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | WWUPLNT4 | 0.9846 | 0.92893 | -0.055668 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | WWUPLNT4 | 0.9846 | 0.92893 | -0.055668 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | WWUPLNT4 | 0.9846 | 0.92893 | -0.055668 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | WWUPLNT4 | 0.9846 | 0.92893 | -0.055668 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | WWUPLNT4 | 0.9846 | 0.92893 | -0.055668 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | WWUPLNT4 | 0.9846 | 0.92893 | -0.055668 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | WWUPLNT4 | 0.9846 | 0.92893 | -0.055668 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | BLACKRIVER 3 | 0.89454 | 0.84688 | -0.047661 |  | 0.9 | 1.05 | 0.12999 | Single 528182 NORTH_LOVNG3 115 528193 BLACKRIVER3 115 1 | Add 69 MVAR switched shunt at SENDERO +3 115 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | BLACKRIVER 3 | 0.89934 | 0.84877 | -0.050573 |  | 0.9 | 1.05 | 1 | P12:115:SPS:U27.1.NLVNG.MLGBND:::HV: | Add 69 MVAR switched shunt at SENDERO +3 115 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | BLACKRIVER 3 | 0.89934 | 0.84877 | -0.050573 |  | 0.9 | 1.05 | 0.044108 | P12:115:SPS:U27.1.NLVNG.MLGBND:::HV: | Add 69 MVAR switched shunt at SENDERO +3 115 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | BLACKRIVER 3 | 0.89934 | 0.84877 | -0.050573 |  | 0.9 | 1.05 | 0.044108 | P12:115:SPS:U27.1.NLVNG.MLGBND:::HV: | Add 69 MVAR switched shunt at SENDERO +3 115 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | G23-015-TAP | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.15431 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | G23-015-TAP | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.10783 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | G23-015-TAP | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.099827 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | G23-015-TAP | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.099827 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | G23-015-TAP | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.11115 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | G23-015-TAP | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.11188 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | G23-015-TAP | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.11151 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | G23-015-TAP | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.1314 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | G23-015-TAP | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.1314 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | G23-015-TAP | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.11061 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | G23-015-TAP | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.11062 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | G23-015-TAP | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.10856 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | G23-015-TAP | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.1085 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | G23-015-TAP | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.10905 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | G23-015-TAP | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.10892 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | G23-015-TAP | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.10871 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | G23-015-TAP | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.1111 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | G23-015-TAP | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.1111 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | G23-015-TAP | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.10955 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | G23-015-TAP | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.10955 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | G23-015-TAP | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.079031 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | G23-015-TAP | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.10818 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | GB-SHAMROCK | 0.93145 | 0.89741 | -0.034041 |  | 0.92 | 1.05 | 0.079811 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | GB-SHAMROCK | 0.93145 | 0.89741 | -0.034041 |  | 0.92 | 1.05 | 0.19454 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | GB-SHAMROCK | 0.93145 | 0.89741 | -0.034041 |  | 0.92 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | GB-SHAMROCK | 0.93145 | 0.89741 | -0.034041 |  | 0.92 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | GB-SHAMROCK | 0.93145 | 0.89741 | -0.034041 |  | 0.92 | 1.05 | 0.17748 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | GB-SHAMROCK | 0.93145 | 0.89741 | -0.034041 |  | 0.92 | 1.05 | 0.1726 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | GB-SHAMROCK | 0.93145 | 0.89741 | -0.034041 |  | 0.92 | 1.05 | 0.17544 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | GB-SHAMROCK | 0.93145 | 0.89741 | -0.034041 |  | 0.92 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | GB-SHAMROCK | 0.93145 | 0.89741 | -0.034041 |  | 0.92 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | GB-SHAMROCK | 0.93145 | 0.89741 | -0.034041 |  | 0.92 | 1.05 | 0.17987 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | GB-SHAMROCK | 0.93145 | 0.89741 | -0.034041 |  | 0.92 | 1.05 | 0.18025 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | GB-SHAMROCK | 0.93145 | 0.89741 | -0.034041 |  | 0.92 | 1.05 | 0.19087 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | GB-SHAMROCK | 0.93145 | 0.89741 | -0.034041 |  | 0.92 | 1.05 | 0.19118 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | GB-SHAMROCK | 0.93145 | 0.89741 | -0.034041 |  | 0.92 | 1.05 | 0.18842 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | GB-SHAMROCK | 0.93145 | 0.89741 | -0.034041 |  | 0.92 | 1.05 | 0.18906 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | GB-SHAMROCK | 0.93145 | 0.89741 | -0.034041 |  | 0.92 | 1.05 | 0.19024 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | GB-SHAMROCK | 0.93145 | 0.89741 | -0.034041 |  | 0.92 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | GB-SHAMROCK | 0.93145 | 0.89741 | -0.034041 |  | 0.92 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | GB-SHAMROCK | 0.93145 | 0.89741 | -0.034041 |  | 0.92 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | GB-SHAMROCK | 0.93145 | 0.89741 | -0.034041 |  | 0.92 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | GB-SHAMROCK | 0.93145 | 0.89741 | -0.034041 |  | 0.92 | 1.05 | 0.49024 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | GB-SHAMROCK | 0.93145 | 0.89741 | -0.034041 |  | 0.92 | 1.05 | 0.19283 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | GB-SHAMROCK | 0.93602 | 0.90621 | -0.02981 |  | 0.92 | 1.05 | 0.079811 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | GB-SHAMROCK | 0.93602 | 0.90621 | -0.02981 |  | 0.92 | 1.05 | 0.19454 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | GB-SHAMROCK | 0.93602 | 0.90621 | -0.02981 |  | 0.92 | 1.05 | 0.23657 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | GB-SHAMROCK | 0.93602 | 0.90621 | -0.02981 |  | 0.92 | 1.05 | 0.23657 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | GB-SHAMROCK | 0.93602 | 0.90621 | -0.02981 |  | 0.92 | 1.05 | 0.17748 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | GB-SHAMROCK | 0.93602 | 0.90621 | -0.02981 |  | 0.92 | 1.05 | 0.1726 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | GB-SHAMROCK | 0.93602 | 0.90621 | -0.02981 |  | 0.92 | 1.05 | 0.17544 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | GB-SHAMROCK | 0.93602 | 0.90621 | -0.02981 |  | 0.92 | 1.05 | 0.12267 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | GB-SHAMROCK | 0.93602 | 0.90621 | -0.02981 |  | 0.92 | 1.05 | 0.12267 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | GB-SHAMROCK | 0.93602 | 0.90621 | -0.02981 |  | 0.92 | 1.05 | 0.17987 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | GB-SHAMROCK | 0.93602 | 0.90621 | -0.02981 |  | 0.92 | 1.05 | 0.18025 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | GB-SHAMROCK | 0.93602 | 0.90621 | -0.02981 |  | 0.92 | 1.05 | 0.19087 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | GB-SHAMROCK | 0.93602 | 0.90621 | -0.02981 |  | 0.92 | 1.05 | 0.19118 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | GB-SHAMROCK | 0.93602 | 0.90621 | -0.02981 |  | 0.92 | 1.05 | 0.18842 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | GB-SHAMROCK | 0.93602 | 0.90621 | -0.02981 |  | 0.92 | 1.05 | 0.18906 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | GB-SHAMROCK | 0.93602 | 0.90621 | -0.02981 |  | 0.92 | 1.05 | 0.19024 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | GB-SHAMROCK | 0.93602 | 0.90621 | -0.02981 |  | 0.92 | 1.05 | 0.17773 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | GB-SHAMROCK | 0.93602 | 0.90621 | -0.02981 |  | 0.92 | 1.05 | 0.17773 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | GB-SHAMROCK | 0.93602 | 0.90621 | -0.02981 |  | 0.92 | 1.05 | 0.18569 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | GB-SHAMROCK | 0.93602 | 0.90621 | -0.02981 |  | 0.92 | 1.05 | 0.18569 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | GB-SHAMROCK | 0.93602 | 0.90621 | -0.02981 |  | 0.92 | 1.05 | 0.49024 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | GB-SHAMROCK | 0.93602 | 0.90621 | -0.02981 |  | 0.92 | 1.05 | 0.19283 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | GB-SHAMROCK | 0.93682 | 0.90768 | -0.029136 |  | 0.92 | 1.05 | 0.079811 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | GB-SHAMROCK | 0.93682 | 0.90768 | -0.029136 |  | 0.92 | 1.05 | 0.19454 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | GB-SHAMROCK | 0.93682 | 0.90768 | -0.029136 |  | 0.92 | 1.05 | 0.23657 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | GB-SHAMROCK | 0.93682 | 0.90768 | -0.029136 |  | 0.92 | 1.05 | 0.23657 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | GB-SHAMROCK | 0.93682 | 0.90768 | -0.029136 |  | 0.92 | 1.05 | 0.17748 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | GB-SHAMROCK | 0.93682 | 0.90768 | -0.029136 |  | 0.92 | 1.05 | 0.1726 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | GB-SHAMROCK | 0.93682 | 0.90768 | -0.029136 |  | 0.92 | 1.05 | 0.17544 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | GB-SHAMROCK | 0.93682 | 0.90768 | -0.029136 |  | 0.92 | 1.05 | 0.12267 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | GB-SHAMROCK | 0.93682 | 0.90768 | -0.029136 |  | 0.92 | 1.05 | 0.12267 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | GB-SHAMROCK | 0.93682 | 0.90768 | -0.029136 |  | 0.92 | 1.05 | 0.17987 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | GB-SHAMROCK | 0.93682 | 0.90768 | -0.029136 |  | 0.92 | 1.05 | 0.18025 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | GB-SHAMROCK | 0.93682 | 0.90768 | -0.029136 |  | 0.92 | 1.05 | 0.19087 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | GB-SHAMROCK | 0.93682 | 0.90768 | -0.029136 |  | 0.92 | 1.05 | 0.19118 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | GB-SHAMROCK | 0.93682 | 0.90768 | -0.029136 |  | 0.92 | 1.05 | 0.18842 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | GB-SHAMROCK | 0.93682 | 0.90768 | -0.029136 |  | 0.92 | 1.05 | 0.18906 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | GB-SHAMROCK | 0.93682 | 0.90768 | -0.029136 |  | 0.92 | 1.05 | 0.19024 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | GB-SHAMROCK | 0.93682 | 0.90768 | -0.029136 |  | 0.92 | 1.05 | 0.17773 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | GB-SHAMROCK | 0.93682 | 0.90768 | -0.029136 |  | 0.92 | 1.05 | 0.17773 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | GB-SHAMROCK | 0.93682 | 0.90768 | -0.029136 |  | 0.92 | 1.05 | 0.18569 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | GB-SHAMROCK | 0.93682 | 0.90768 | -0.029136 |  | 0.92 | 1.05 | 0.18569 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | GB-SHAMROCK | 0.93682 | 0.90768 | -0.029136 |  | 0.92 | 1.05 | 0.49024 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | GB-SHAMROCK | 0.93682 | 0.90768 | -0.029136 |  | 0.92 | 1.05 | 0.19283 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | GB-SHAMROCK | 0.93757 | 0.90932 | -0.02825 |  | 0.92 | 1.05 | 0.079811 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | GB-SHAMROCK | 0.93757 | 0.90932 | -0.02825 |  | 0.92 | 1.05 | 0.19454 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | GB-SHAMROCK | 0.93757 | 0.90932 | -0.02825 |  | 0.92 | 1.05 | 0.23657 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | GB-SHAMROCK | 0.93757 | 0.90932 | -0.02825 |  | 0.92 | 1.05 | 0.23657 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | GB-SHAMROCK | 0.93757 | 0.90932 | -0.02825 |  | 0.92 | 1.05 | 0.17748 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | GB-SHAMROCK | 0.93757 | 0.90932 | -0.02825 |  | 0.92 | 1.05 | 0.1726 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | GB-SHAMROCK | 0.93757 | 0.90932 | -0.02825 |  | 0.92 | 1.05 | 0.17544 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | GB-SHAMROCK | 0.93757 | 0.90932 | -0.02825 |  | 0.92 | 1.05 | 0.12267 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | GB-SHAMROCK | 0.93757 | 0.90932 | -0.02825 |  | 0.92 | 1.05 | 0.12267 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | GB-SHAMROCK | 0.93757 | 0.90932 | -0.02825 |  | 0.92 | 1.05 | 0.17987 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | GB-SHAMROCK | 0.93757 | 0.90932 | -0.02825 |  | 0.92 | 1.05 | 0.18025 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | GB-SHAMROCK | 0.93757 | 0.90932 | -0.02825 |  | 0.92 | 1.05 | 0.19087 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | GB-SHAMROCK | 0.93757 | 0.90932 | -0.02825 |  | 0.92 | 1.05 | 0.19118 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | GB-SHAMROCK | 0.93757 | 0.90932 | -0.02825 |  | 0.92 | 1.05 | 0.18842 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | GB-SHAMROCK | 0.93757 | 0.90932 | -0.02825 |  | 0.92 | 1.05 | 0.18906 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | GB-SHAMROCK | 0.93757 | 0.90932 | -0.02825 |  | 0.92 | 1.05 | 0.19024 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | GB-SHAMROCK | 0.93757 | 0.90932 | -0.02825 |  | 0.92 | 1.05 | 0.17773 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | GB-SHAMROCK | 0.93757 | 0.90932 | -0.02825 |  | 0.92 | 1.05 | 0.17773 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | GB-SHAMROCK | 0.93757 | 0.90932 | -0.02825 |  | 0.92 | 1.05 | 0.18569 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | GB-SHAMROCK | 0.93757 | 0.90932 | -0.02825 |  | 0.92 | 1.05 | 0.18569 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | GB-SHAMROCK | 0.93757 | 0.90932 | -0.02825 |  | 0.92 | 1.05 | 0.49024 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | GB-SHAMROCK | 0.93757 | 0.90932 | -0.02825 |  | 0.92 | 1.05 | 0.19283 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | GB-SHAMROCK | 0.9379 | 0.9096 | -0.0283 |  | 0.92 | 1.05 | 0.079811 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | GB-SHAMROCK | 0.9379 | 0.9096 | -0.0283 |  | 0.92 | 1.05 | 0.19454 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | GB-SHAMROCK | 0.9379 | 0.9096 | -0.0283 |  | 0.92 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | GB-SHAMROCK | 0.9379 | 0.9096 | -0.0283 |  | 0.92 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | GB-SHAMROCK | 0.9379 | 0.9096 | -0.0283 |  | 0.92 | 1.05 | 0.17748 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | GB-SHAMROCK | 0.9379 | 0.9096 | -0.0283 |  | 0.92 | 1.05 | 0.1726 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | GB-SHAMROCK | 0.9379 | 0.9096 | -0.0283 |  | 0.92 | 1.05 | 0.17544 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | GB-SHAMROCK | 0.9379 | 0.9096 | -0.0283 |  | 0.92 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | GB-SHAMROCK | 0.9379 | 0.9096 | -0.0283 |  | 0.92 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | GB-SHAMROCK | 0.9379 | 0.9096 | -0.0283 |  | 0.92 | 1.05 | 0.17987 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | GB-SHAMROCK | 0.9379 | 0.9096 | -0.0283 |  | 0.92 | 1.05 | 0.18025 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | GB-SHAMROCK | 0.9379 | 0.9096 | -0.0283 |  | 0.92 | 1.05 | 0.19087 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | GB-SHAMROCK | 0.9379 | 0.9096 | -0.0283 |  | 0.92 | 1.05 | 0.19118 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | GB-SHAMROCK | 0.9379 | 0.9096 | -0.0283 |  | 0.92 | 1.05 | 0.18842 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | GB-SHAMROCK | 0.9379 | 0.9096 | -0.0283 |  | 0.92 | 1.05 | 0.18906 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | GB-SHAMROCK | 0.9379 | 0.9096 | -0.0283 |  | 0.92 | 1.05 | 0.19024 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | GB-SHAMROCK | 0.9379 | 0.9096 | -0.0283 |  | 0.92 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | GB-SHAMROCK | 0.9379 | 0.9096 | -0.0283 |  | 0.92 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | GB-SHAMROCK | 0.9379 | 0.9096 | -0.0283 |  | 0.92 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | GB-SHAMROCK | 0.9379 | 0.9096 | -0.0283 |  | 0.92 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | GB-SHAMROCK | 0.9379 | 0.9096 | -0.0283 |  | 0.92 | 1.05 | 0.49024 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | GB-SHAMROCK | 0.9379 | 0.9096 | -0.0283 |  | 0.92 | 1.05 | 0.19283 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | GEN-2023-015 | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.15431 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | GEN-2023-015 | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.10783 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | GEN-2023-015 | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.099827 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | GEN-2023-015 | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.099827 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | GEN-2023-015 | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.11115 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | GEN-2023-015 | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.11188 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | GEN-2023-015 | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.11151 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | GEN-2023-015 | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.1314 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | GEN-2023-015 | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.1314 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | GEN-2023-015 | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.11061 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | GEN-2023-015 | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.11062 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | GEN-2023-015 | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.10856 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | GEN-2023-015 | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.1085 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | GEN-2023-015 | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.10905 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | GEN-2023-015 | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.10892 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | GEN-2023-015 | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.10871 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | GEN-2023-015 | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.1111 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | GEN-2023-015 | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.1111 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | GEN-2023-015 | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.10955 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | GEN-2023-015 | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.10955 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | GEN-2023-015 | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.079031 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | GEN-2023-015 | 1.03 | 1.0527 | 0.022728 |  | 0.9 | 1.05 | 0.10818 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | HI_BNKS1_WF7 | 1.0449 | 1.0699 | 0.024987 |  | 0.95 | 1.05 | 0.074516 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | HI_BNKS1_WF7 | 1.0449 | 1.0699 | 0.024987 |  | 0.95 | 1.05 | 0.086222 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | HI_BNKS1_WF7 | 1.0449 | 1.0699 | 0.024987 |  | 0.95 | 1.05 | 0.085199 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | HI_BNKS1_WF7 | 1.0449 | 1.0699 | 0.024987 |  | 0.95 | 1.05 | 0.085199 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | HI_BNKS1_WF7 | 1.0449 | 1.0699 | 0.024987 |  | 0.95 | 1.05 | 0.086696 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | HI_BNKS1_WF7 | 1.0449 | 1.0699 | 0.024987 |  | 0.95 | 1.05 | 0.086596 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | HI_BNKS1_WF7 | 1.0449 | 1.0699 | 0.024987 |  | 0.95 | 1.05 | 0.086715 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | HI_BNKS1_WF7 | 1.0449 | 1.0699 | 0.024987 |  | 0.95 | 1.05 | 0.086394 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | HI_BNKS1_WF7 | 1.0449 | 1.0699 | 0.024987 |  | 0.95 | 1.05 | 0.086394 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | HI_BNKS1_WF7 | 1.0449 | 1.0699 | 0.024987 |  | 0.95 | 1.05 | 0.086552 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | HI_BNKS1_WF7 | 1.0449 | 1.0699 | 0.024987 |  | 0.95 | 1.05 | 0.086628 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | HI_BNKS1_WF7 | 1.0449 | 1.0699 | 0.024987 |  | 0.95 | 1.05 | 0.08634 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | HI_BNKS1_WF7 | 1.0449 | 1.0699 | 0.024987 |  | 0.95 | 1.05 | 0.086331 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | HI_BNKS1_WF7 | 1.0449 | 1.0699 | 0.024987 |  | 0.95 | 1.05 | 0.086416 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | HI_BNKS1_WF7 | 1.0449 | 1.0699 | 0.024987 |  | 0.95 | 1.05 | 0.086398 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | HI_BNKS1_WF7 | 1.0449 | 1.0699 | 0.024987 |  | 0.95 | 1.05 | 0.086378 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | HI_BNKS1_WF7 | 1.0449 | 1.0699 | 0.024987 |  | 0.95 | 1.05 | 0.086694 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | HI_BNKS1_WF7 | 1.0449 | 1.0699 | 0.024987 |  | 0.95 | 1.05 | 0.086694 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | HI_BNKS1_WF7 | 1.0449 | 1.0699 | 0.024987 |  | 0.95 | 1.05 | 0.086466 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | HI_BNKS1_WF7 | 1.0449 | 1.0699 | 0.024987 |  | 0.95 | 1.05 | 0.086466 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | HI_BNKS1_WF7 | 1.0449 | 1.0699 | 0.024987 |  | 0.95 | 1.05 | 0.075562 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | HI_BNKS1_WF7 | 1.0449 | 1.0699 | 0.024987 |  | 0.95 | 1.05 | 0.086282 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | HI_BNKS1_WF7 | 1.0449 | 1.0698 | 0.024937 |  | 0.95 | 1.05 | 0.083755 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | HI_BNKS1_WF7 | 1.0449 | 1.0698 | 0.024937 |  | 0.95 | 1.05 | 0.090616 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | HI_BNKS1_WF7 | 1.0449 | 1.0698 | 0.024937 |  | 0.95 | 1.05 | 0.088888 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | HI_BNKS1_WF7 | 1.0449 | 1.0698 | 0.024937 |  | 0.95 | 1.05 | 0.088888 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | HI_BNKS1_WF7 | 1.0449 | 1.0698 | 0.024937 |  | 0.95 | 1.05 | 0.091397 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | HI_BNKS1_WF7 | 1.0449 | 1.0698 | 0.024937 |  | 0.95 | 1.05 | 0.091306 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | HI_BNKS1_WF7 | 1.0449 | 1.0698 | 0.024937 |  | 0.95 | 1.05 | 0.09144 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | HI_BNKS1_WF7 | 1.0449 | 1.0698 | 0.024937 |  | 0.95 | 1.05 | 0.092749 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | HI_BNKS1_WF7 | 1.0449 | 1.0698 | 0.024937 |  | 0.95 | 1.05 | 0.092749 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | HI_BNKS1_WF7 | 1.0449 | 1.0698 | 0.024937 |  | 0.95 | 1.05 | 0.091183 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | HI_BNKS1_WF7 | 1.0449 | 1.0698 | 0.024937 |  | 0.95 | 1.05 | 0.091282 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | HI_BNKS1_WF7 | 1.0449 | 1.0698 | 0.024937 |  | 0.95 | 1.05 | 0.090805 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | HI_BNKS1_WF7 | 1.0449 | 1.0698 | 0.024937 |  | 0.95 | 1.05 | 0.09079 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | HI_BNKS1_WF7 | 1.0449 | 1.0698 | 0.024937 |  | 0.95 | 1.05 | 0.090927 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | HI_BNKS1_WF7 | 1.0449 | 1.0698 | 0.024937 |  | 0.95 | 1.05 | 0.090898 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | HI_BNKS1_WF7 | 1.0449 | 1.0698 | 0.024937 |  | 0.95 | 1.05 | 0.090861 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | HI_BNKS1_WF7 | 1.0449 | 1.0698 | 0.024937 |  | 0.95 | 1.05 | 0.091391 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | HI_BNKS1_WF7 | 1.0449 | 1.0698 | 0.024937 |  | 0.95 | 1.05 | 0.091391 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | HI_BNKS1_WF7 | 1.0449 | 1.0698 | 0.024937 |  | 0.95 | 1.05 | 0.091018 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | HI_BNKS1_WF7 | 1.0449 | 1.0698 | 0.024937 |  | 0.95 | 1.05 | 0.091018 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | HI_BNKS1_WF7 | 1.0449 | 1.0698 | 0.024937 |  | 0.95 | 1.05 | 0.076682 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | HI_BNKS1_WF7 | 1.0449 | 1.0698 | 0.024937 |  | 0.95 | 1.05 | 0.090711 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | HI_BNKS1_WF7 | 1.0451 | 1.0699 | 0.024852 |  | 0.95 | 1.05 | 0.03855 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | HI_BNKS1_WF7 | 1.0451 | 1.0699 | 0.024852 |  | 0.95 | 1.05 | 0.038885 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | HI_BNKS1_WF7 | 1.0451 | 1.0699 | 0.024852 |  | 0.95 | 1.05 | 0.038747 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | HI_BNKS1_WF7 | 1.0451 | 1.0699 | 0.024852 |  | 0.95 | 1.05 | 0.038747 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | HI_BNKS1_WF7 | 1.0451 | 1.0699 | 0.024852 |  | 0.95 | 1.05 | 0.038945 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | HI_BNKS1_WF7 | 1.0451 | 1.0699 | 0.024852 |  | 0.95 | 1.05 | 0.038948 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | HI_BNKS1_WF7 | 1.0451 | 1.0699 | 0.024852 |  | 0.95 | 1.05 | 0.03895 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | HI_BNKS1_WF7 | 1.0451 | 1.0699 | 0.024852 |  | 0.95 | 1.05 | 0.039037 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | HI_BNKS1_WF7 | 1.0451 | 1.0699 | 0.024852 |  | 0.95 | 1.05 | 0.039037 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | HI_BNKS1_WF7 | 1.0451 | 1.0699 | 0.024852 |  | 0.95 | 1.05 | 0.038932 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | HI_BNKS1_WF7 | 1.0451 | 1.0699 | 0.024852 |  | 0.95 | 1.05 | 0.038936 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | HI_BNKS1_WF7 | 1.0451 | 1.0699 | 0.024852 |  | 0.95 | 1.05 | 0.038899 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | HI_BNKS1_WF7 | 1.0451 | 1.0699 | 0.024852 |  | 0.95 | 1.05 | 0.038898 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | HI_BNKS1_WF7 | 1.0451 | 1.0699 | 0.024852 |  | 0.95 | 1.05 | 0.038908 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | HI_BNKS1_WF7 | 1.0451 | 1.0699 | 0.024852 |  | 0.95 | 1.05 | 0.038906 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | HI_BNKS1_WF7 | 1.0451 | 1.0699 | 0.024852 |  | 0.95 | 1.05 | 0.038903 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | HI_BNKS1_WF7 | 1.0451 | 1.0699 | 0.024852 |  | 0.95 | 1.05 | 0.038945 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | HI_BNKS1_WF7 | 1.0451 | 1.0699 | 0.024852 |  | 0.95 | 1.05 | 0.038945 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | HI_BNKS1_WF7 | 1.0451 | 1.0699 | 0.024852 |  | 0.95 | 1.05 | 0.038916 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | HI_BNKS1_WF7 | 1.0451 | 1.0699 | 0.024852 |  | 0.95 | 1.05 | 0.038916 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | HI_BNKS1_WF7 | 1.0451 | 1.0699 | 0.024852 |  | 0.95 | 1.05 | 0.037706 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | HI_BNKS1_WF7 | 1.0451 | 1.0699 | 0.024852 |  | 0.95 | 1.05 | 0.038892 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | HI_BNKS1_WF7 | 1.0448 | 1.07 | 0.025182 |  | 0.95 | 1.05 | 0.050401 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | HI_BNKS1_WF7 | 1.0448 | 1.07 | 0.025182 |  | 0.95 | 1.05 | 0.048176 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | HI_BNKS1_WF7 | 1.0448 | 1.07 | 0.025182 |  | 0.95 | 1.05 | 0.047547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | HI_BNKS1_WF7 | 1.0448 | 1.07 | 0.025182 |  | 0.95 | 1.05 | 0.047547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | HI_BNKS1_WF7 | 1.0448 | 1.07 | 0.025182 |  | 0.95 | 1.05 | 0.04844 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | HI_BNKS1_WF7 | 1.0448 | 1.07 | 0.025182 |  | 0.95 | 1.05 | 0.048482 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | HI_BNKS1_WF7 | 1.0448 | 1.07 | 0.025182 |  | 0.95 | 1.05 | 0.048466 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | HI_BNKS1_WF7 | 1.0448 | 1.07 | 0.025182 |  | 0.95 | 1.05 | 0.049497 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | HI_BNKS1_WF7 | 1.0448 | 1.07 | 0.025182 |  | 0.95 | 1.05 | 0.049497 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | HI_BNKS1_WF7 | 1.0448 | 1.07 | 0.025182 |  | 0.95 | 1.05 | 0.048392 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | HI_BNKS1_WF7 | 1.0448 | 1.07 | 0.025182 |  | 0.95 | 1.05 | 0.048398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | HI_BNKS1_WF7 | 1.0448 | 1.07 | 0.025182 |  | 0.95 | 1.05 | 0.048235 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | HI_BNKS1_WF7 | 1.0448 | 1.07 | 0.025182 |  | 0.95 | 1.05 | 0.04823 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | HI_BNKS1_WF7 | 1.0448 | 1.07 | 0.025182 |  | 0.95 | 1.05 | 0.048274 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | HI_BNKS1_WF7 | 1.0448 | 1.07 | 0.025182 |  | 0.95 | 1.05 | 0.048264 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | HI_BNKS1_WF7 | 1.0448 | 1.07 | 0.025182 |  | 0.95 | 1.05 | 0.048248 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | HI_BNKS1_WF7 | 1.0448 | 1.07 | 0.025182 |  | 0.95 | 1.05 | 0.048436 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | HI_BNKS1_WF7 | 1.0448 | 1.07 | 0.025182 |  | 0.95 | 1.05 | 0.048436 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | HI_BNKS1_WF7 | 1.0448 | 1.07 | 0.025182 |  | 0.95 | 1.05 | 0.048312 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | HI_BNKS1_WF7 | 1.0448 | 1.07 | 0.025182 |  | 0.95 | 1.05 | 0.048312 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | HI_BNKS1_WF7 | 1.0448 | 1.07 | 0.025182 |  | 0.95 | 1.05 | 0.044355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | HI_BNKS1_WF7 | 1.0448 | 1.07 | 0.025182 |  | 0.95 | 1.05 | 0.048204 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | HI_BNKS1_WF7 | 1.045 | 1.0698 | 0.024873 |  | 0.95 | 1.05 | 0.043643 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | HI_BNKS1_WF7 | 1.045 | 1.0698 | 0.024873 |  | 0.95 | 1.05 | 0.045977 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | HI_BNKS1_WF7 | 1.045 | 1.0698 | 0.024873 |  | 0.95 | 1.05 | 0.045928 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | HI_BNKS1_WF7 | 1.045 | 1.0698 | 0.024873 |  | 0.95 | 1.05 | 0.045928 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | HI_BNKS1_WF7 | 1.045 | 1.0698 | 0.024873 |  | 0.95 | 1.05 | 0.046004 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | HI_BNKS1_WF7 | 1.045 | 1.0698 | 0.024873 |  | 0.95 | 1.05 | 0.045984 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | HI_BNKS1_WF7 | 1.045 | 1.0698 | 0.024873 |  | 0.95 | 1.05 | 0.046003 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | HI_BNKS1_WF7 | 1.045 | 1.0698 | 0.024873 |  | 0.95 | 1.05 | 0.045685 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | HI_BNKS1_WF7 | 1.045 | 1.0698 | 0.024873 |  | 0.95 | 1.05 | 0.045685 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | HI_BNKS1_WF7 | 1.045 | 1.0698 | 0.024873 |  | 0.95 | 1.05 | 0.045991 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | HI_BNKS1_WF7 | 1.045 | 1.0698 | 0.024873 |  | 0.95 | 1.05 | 0.046001 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | HI_BNKS1_WF7 | 1.045 | 1.0698 | 0.024873 |  | 0.95 | 1.05 | 0.045985 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | HI_BNKS1_WF7 | 1.045 | 1.0698 | 0.024873 |  | 0.95 | 1.05 | 0.045984 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | HI_BNKS1_WF7 | 1.045 | 1.0698 | 0.024873 |  | 0.95 | 1.05 | 0.045989 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | HI_BNKS1_WF7 | 1.045 | 1.0698 | 0.024873 |  | 0.95 | 1.05 | 0.045988 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | HI_BNKS1_WF7 | 1.045 | 1.0698 | 0.024873 |  | 0.95 | 1.05 | 0.045988 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | HI_BNKS1_WF7 | 1.045 | 1.0698 | 0.024873 |  | 0.95 | 1.05 | 0.046004 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | HI_BNKS1_WF7 | 1.045 | 1.0698 | 0.024873 |  | 0.95 | 1.05 | 0.046004 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | HI_BNKS1_WF7 | 1.045 | 1.0698 | 0.024873 |  | 0.95 | 1.05 | 0.045991 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | HI_BNKS1_WF7 | 1.045 | 1.0698 | 0.024873 |  | 0.95 | 1.05 | 0.045991 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | HI_BNKS1_WF7 | 1.045 | 1.0698 | 0.024873 |  | 0.95 | 1.05 | 0.044728 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | HI_BNKS1_WF7 | 1.045 | 1.0698 | 0.024873 |  | 0.95 | 1.05 | 0.045981 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | HI_BNKS2_WF7 | 1.0496 | 1.0747 | 0.02504 |  | 0.95 | 1.05 | 0.074516 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | HI_BNKS2_WF7 | 1.0496 | 1.0747 | 0.02504 |  | 0.95 | 1.05 | 0.086222 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | HI_BNKS2_WF7 | 1.0496 | 1.0747 | 0.02504 |  | 0.95 | 1.05 | 0.085199 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | HI_BNKS2_WF7 | 1.0496 | 1.0747 | 0.02504 |  | 0.95 | 1.05 | 0.085199 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | HI_BNKS2_WF7 | 1.0496 | 1.0747 | 0.02504 |  | 0.95 | 1.05 | 0.086696 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | HI_BNKS2_WF7 | 1.0496 | 1.0747 | 0.02504 |  | 0.95 | 1.05 | 0.086596 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | HI_BNKS2_WF7 | 1.0496 | 1.0747 | 0.02504 |  | 0.95 | 1.05 | 0.086715 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | HI_BNKS2_WF7 | 1.0496 | 1.0747 | 0.02504 |  | 0.95 | 1.05 | 0.086394 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | HI_BNKS2_WF7 | 1.0496 | 1.0747 | 0.02504 |  | 0.95 | 1.05 | 0.086394 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | HI_BNKS2_WF7 | 1.0496 | 1.0747 | 0.02504 |  | 0.95 | 1.05 | 0.086552 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | HI_BNKS2_WF7 | 1.0496 | 1.0747 | 0.02504 |  | 0.95 | 1.05 | 0.086628 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | HI_BNKS2_WF7 | 1.0496 | 1.0747 | 0.02504 |  | 0.95 | 1.05 | 0.08634 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | HI_BNKS2_WF7 | 1.0496 | 1.0747 | 0.02504 |  | 0.95 | 1.05 | 0.086331 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | HI_BNKS2_WF7 | 1.0496 | 1.0747 | 0.02504 |  | 0.95 | 1.05 | 0.086416 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | HI_BNKS2_WF7 | 1.0496 | 1.0747 | 0.02504 |  | 0.95 | 1.05 | 0.086398 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | HI_BNKS2_WF7 | 1.0496 | 1.0747 | 0.02504 |  | 0.95 | 1.05 | 0.086378 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | HI_BNKS2_WF7 | 1.0496 | 1.0747 | 0.02504 |  | 0.95 | 1.05 | 0.086694 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | HI_BNKS2_WF7 | 1.0496 | 1.0747 | 0.02504 |  | 0.95 | 1.05 | 0.086694 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | HI_BNKS2_WF7 | 1.0496 | 1.0747 | 0.02504 |  | 0.95 | 1.05 | 0.086466 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | HI_BNKS2_WF7 | 1.0496 | 1.0747 | 0.02504 |  | 0.95 | 1.05 | 0.086466 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | HI_BNKS2_WF7 | 1.0496 | 1.0747 | 0.02504 |  | 0.95 | 1.05 | 0.075562 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | HI_BNKS2_WF7 | 1.0496 | 1.0747 | 0.02504 |  | 0.95 | 1.05 | 0.086282 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | HI_BNKS2_WF7 | 1.0496 | 1.0746 | 0.02499 |  | 0.95 | 1.05 | 0.083755 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | HI_BNKS2_WF7 | 1.0496 | 1.0746 | 0.02499 |  | 0.95 | 1.05 | 0.090616 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | HI_BNKS2_WF7 | 1.0496 | 1.0746 | 0.02499 |  | 0.95 | 1.05 | 0.088888 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | HI_BNKS2_WF7 | 1.0496 | 1.0746 | 0.02499 |  | 0.95 | 1.05 | 0.088888 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | HI_BNKS2_WF7 | 1.0496 | 1.0746 | 0.02499 |  | 0.95 | 1.05 | 0.091397 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | HI_BNKS2_WF7 | 1.0496 | 1.0746 | 0.02499 |  | 0.95 | 1.05 | 0.091306 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | HI_BNKS2_WF7 | 1.0496 | 1.0746 | 0.02499 |  | 0.95 | 1.05 | 0.09144 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | HI_BNKS2_WF7 | 1.0496 | 1.0746 | 0.02499 |  | 0.95 | 1.05 | 0.092749 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | HI_BNKS2_WF7 | 1.0496 | 1.0746 | 0.02499 |  | 0.95 | 1.05 | 0.092749 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | HI_BNKS2_WF7 | 1.0496 | 1.0746 | 0.02499 |  | 0.95 | 1.05 | 0.091183 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | HI_BNKS2_WF7 | 1.0496 | 1.0746 | 0.02499 |  | 0.95 | 1.05 | 0.091282 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | HI_BNKS2_WF7 | 1.0496 | 1.0746 | 0.02499 |  | 0.95 | 1.05 | 0.090805 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | HI_BNKS2_WF7 | 1.0496 | 1.0746 | 0.02499 |  | 0.95 | 1.05 | 0.09079 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | HI_BNKS2_WF7 | 1.0496 | 1.0746 | 0.02499 |  | 0.95 | 1.05 | 0.090927 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | HI_BNKS2_WF7 | 1.0496 | 1.0746 | 0.02499 |  | 0.95 | 1.05 | 0.090898 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | HI_BNKS2_WF7 | 1.0496 | 1.0746 | 0.02499 |  | 0.95 | 1.05 | 0.090861 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | HI_BNKS2_WF7 | 1.0496 | 1.0746 | 0.02499 |  | 0.95 | 1.05 | 0.091391 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | HI_BNKS2_WF7 | 1.0496 | 1.0746 | 0.02499 |  | 0.95 | 1.05 | 0.091391 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | HI_BNKS2_WF7 | 1.0496 | 1.0746 | 0.02499 |  | 0.95 | 1.05 | 0.091018 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | HI_BNKS2_WF7 | 1.0496 | 1.0746 | 0.02499 |  | 0.95 | 1.05 | 0.091018 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | HI_BNKS2_WF7 | 1.0496 | 1.0746 | 0.02499 |  | 0.95 | 1.05 | 0.076682 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | HI_BNKS2_WF7 | 1.0496 | 1.0746 | 0.02499 |  | 0.95 | 1.05 | 0.090711 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | HI_BNKS2_WF7 | 1.0498 | 1.0748 | 0.024904 |  | 0.95 | 1.05 | 0.03855 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | HI_BNKS2_WF7 | 1.0498 | 1.0748 | 0.024904 |  | 0.95 | 1.05 | 0.038885 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | HI_BNKS2_WF7 | 1.0498 | 1.0748 | 0.024904 |  | 0.95 | 1.05 | 0.038747 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | HI_BNKS2_WF7 | 1.0498 | 1.0748 | 0.024904 |  | 0.95 | 1.05 | 0.038747 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | HI_BNKS2_WF7 | 1.0498 | 1.0748 | 0.024904 |  | 0.95 | 1.05 | 0.038945 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | HI_BNKS2_WF7 | 1.0498 | 1.0748 | 0.024904 |  | 0.95 | 1.05 | 0.038948 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | HI_BNKS2_WF7 | 1.0498 | 1.0748 | 0.024904 |  | 0.95 | 1.05 | 0.03895 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | HI_BNKS2_WF7 | 1.0498 | 1.0748 | 0.024904 |  | 0.95 | 1.05 | 0.039037 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | HI_BNKS2_WF7 | 1.0498 | 1.0748 | 0.024904 |  | 0.95 | 1.05 | 0.039037 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | HI_BNKS2_WF7 | 1.0498 | 1.0748 | 0.024904 |  | 0.95 | 1.05 | 0.038932 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | HI_BNKS2_WF7 | 1.0498 | 1.0748 | 0.024904 |  | 0.95 | 1.05 | 0.038936 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | HI_BNKS2_WF7 | 1.0498 | 1.0748 | 0.024904 |  | 0.95 | 1.05 | 0.038899 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | HI_BNKS2_WF7 | 1.0498 | 1.0748 | 0.024904 |  | 0.95 | 1.05 | 0.038898 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | HI_BNKS2_WF7 | 1.0498 | 1.0748 | 0.024904 |  | 0.95 | 1.05 | 0.038908 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | HI_BNKS2_WF7 | 1.0498 | 1.0748 | 0.024904 |  | 0.95 | 1.05 | 0.038906 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | HI_BNKS2_WF7 | 1.0498 | 1.0748 | 0.024904 |  | 0.95 | 1.05 | 0.038903 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | HI_BNKS2_WF7 | 1.0498 | 1.0748 | 0.024904 |  | 0.95 | 1.05 | 0.038945 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | HI_BNKS2_WF7 | 1.0498 | 1.0748 | 0.024904 |  | 0.95 | 1.05 | 0.038945 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | HI_BNKS2_WF7 | 1.0498 | 1.0748 | 0.024904 |  | 0.95 | 1.05 | 0.038916 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | HI_BNKS2_WF7 | 1.0498 | 1.0748 | 0.024904 |  | 0.95 | 1.05 | 0.038916 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | HI_BNKS2_WF7 | 1.0498 | 1.0748 | 0.024904 |  | 0.95 | 1.05 | 0.037706 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | HI_BNKS2_WF7 | 1.0498 | 1.0748 | 0.024904 |  | 0.95 | 1.05 | 0.038892 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | HI_BNKS2_WF7 | 1.0496 | 1.0748 | 0.025236 |  | 0.95 | 1.05 | 0.050401 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | HI_BNKS2_WF7 | 1.0496 | 1.0748 | 0.025236 |  | 0.95 | 1.05 | 0.048176 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | HI_BNKS2_WF7 | 1.0496 | 1.0748 | 0.025236 |  | 0.95 | 1.05 | 0.047547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | HI_BNKS2_WF7 | 1.0496 | 1.0748 | 0.025236 |  | 0.95 | 1.05 | 0.047547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | HI_BNKS2_WF7 | 1.0496 | 1.0748 | 0.025236 |  | 0.95 | 1.05 | 0.04844 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | HI_BNKS2_WF7 | 1.0496 | 1.0748 | 0.025236 |  | 0.95 | 1.05 | 0.048482 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | HI_BNKS2_WF7 | 1.0496 | 1.0748 | 0.025236 |  | 0.95 | 1.05 | 0.048466 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | HI_BNKS2_WF7 | 1.0496 | 1.0748 | 0.025236 |  | 0.95 | 1.05 | 0.049497 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | HI_BNKS2_WF7 | 1.0496 | 1.0748 | 0.025236 |  | 0.95 | 1.05 | 0.049497 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | HI_BNKS2_WF7 | 1.0496 | 1.0748 | 0.025236 |  | 0.95 | 1.05 | 0.048392 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | HI_BNKS2_WF7 | 1.0496 | 1.0748 | 0.025236 |  | 0.95 | 1.05 | 0.048398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | HI_BNKS2_WF7 | 1.0496 | 1.0748 | 0.025236 |  | 0.95 | 1.05 | 0.048235 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | HI_BNKS2_WF7 | 1.0496 | 1.0748 | 0.025236 |  | 0.95 | 1.05 | 0.04823 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | HI_BNKS2_WF7 | 1.0496 | 1.0748 | 0.025236 |  | 0.95 | 1.05 | 0.048274 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | HI_BNKS2_WF7 | 1.0496 | 1.0748 | 0.025236 |  | 0.95 | 1.05 | 0.048264 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | HI_BNKS2_WF7 | 1.0496 | 1.0748 | 0.025236 |  | 0.95 | 1.05 | 0.048248 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | HI_BNKS2_WF7 | 1.0496 | 1.0748 | 0.025236 |  | 0.95 | 1.05 | 0.048436 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | HI_BNKS2_WF7 | 1.0496 | 1.0748 | 0.025236 |  | 0.95 | 1.05 | 0.048436 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | HI_BNKS2_WF7 | 1.0496 | 1.0748 | 0.025236 |  | 0.95 | 1.05 | 0.048312 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | HI_BNKS2_WF7 | 1.0496 | 1.0748 | 0.025236 |  | 0.95 | 1.05 | 0.048312 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | HI_BNKS2_WF7 | 1.0496 | 1.0748 | 0.025236 |  | 0.95 | 1.05 | 0.044355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | HI_BNKS2_WF7 | 1.0496 | 1.0748 | 0.025236 |  | 0.95 | 1.05 | 0.048204 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | HI_BNKS2_WF7 | 1.0497 | 1.0747 | 0.024926 |  | 0.95 | 1.05 | 0.043643 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | HI_BNKS2_WF7 | 1.0497 | 1.0747 | 0.024926 |  | 0.95 | 1.05 | 0.045977 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | HI_BNKS2_WF7 | 1.0497 | 1.0747 | 0.024926 |  | 0.95 | 1.05 | 0.045928 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | HI_BNKS2_WF7 | 1.0497 | 1.0747 | 0.024926 |  | 0.95 | 1.05 | 0.045928 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | HI_BNKS2_WF7 | 1.0497 | 1.0747 | 0.024926 |  | 0.95 | 1.05 | 0.046004 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | HI_BNKS2_WF7 | 1.0497 | 1.0747 | 0.024926 |  | 0.95 | 1.05 | 0.045984 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | HI_BNKS2_WF7 | 1.0497 | 1.0747 | 0.024926 |  | 0.95 | 1.05 | 0.046003 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | HI_BNKS2_WF7 | 1.0497 | 1.0747 | 0.024926 |  | 0.95 | 1.05 | 0.045685 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | HI_BNKS2_WF7 | 1.0497 | 1.0747 | 0.024926 |  | 0.95 | 1.05 | 0.045685 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | HI_BNKS2_WF7 | 1.0497 | 1.0747 | 0.024926 |  | 0.95 | 1.05 | 0.045991 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | HI_BNKS2_WF7 | 1.0497 | 1.0747 | 0.024926 |  | 0.95 | 1.05 | 0.046001 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | HI_BNKS2_WF7 | 1.0497 | 1.0747 | 0.024926 |  | 0.95 | 1.05 | 0.045985 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | HI_BNKS2_WF7 | 1.0497 | 1.0747 | 0.024926 |  | 0.95 | 1.05 | 0.045984 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | HI_BNKS2_WF7 | 1.0497 | 1.0747 | 0.024926 |  | 0.95 | 1.05 | 0.045989 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | HI_BNKS2_WF7 | 1.0497 | 1.0747 | 0.024926 |  | 0.95 | 1.05 | 0.045988 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | HI_BNKS2_WF7 | 1.0497 | 1.0747 | 0.024926 |  | 0.95 | 1.05 | 0.045988 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | HI_BNKS2_WF7 | 1.0497 | 1.0747 | 0.024926 |  | 0.95 | 1.05 | 0.046004 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | HI_BNKS2_WF7 | 1.0497 | 1.0747 | 0.024926 |  | 0.95 | 1.05 | 0.046004 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | HI_BNKS2_WF7 | 1.0497 | 1.0747 | 0.024926 |  | 0.95 | 1.05 | 0.045991 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | HI_BNKS2_WF7 | 1.0497 | 1.0747 | 0.024926 |  | 0.95 | 1.05 | 0.045991 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | HI_BNKS2_WF7 | 1.0497 | 1.0747 | 0.024926 |  | 0.95 | 1.05 | 0.044728 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | HI_BNKS2_WF7 | 1.0497 | 1.0747 | 0.024926 |  | 0.95 | 1.05 | 0.045981 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-BOOKER 2 | 0.91693 | 0.89759 | -0.019335 |  | 0.9 | 1.05 | 0.079811 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-BOOKER 2 | 0.91693 | 0.89759 | -0.019335 |  | 0.9 | 1.05 | 0.19454 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-BOOKER 2 | 0.91693 | 0.89759 | -0.019335 |  | 0.9 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-BOOKER 2 | 0.91693 | 0.89759 | -0.019335 |  | 0.9 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-BOOKER 2 | 0.91693 | 0.89759 | -0.019335 |  | 0.9 | 1.05 | 0.17748 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-BOOKER 2 | 0.91693 | 0.89759 | -0.019335 |  | 0.9 | 1.05 | 0.1726 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-BOOKER 2 | 0.91693 | 0.89759 | -0.019335 |  | 0.9 | 1.05 | 0.17544 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-BOOKER 2 | 0.91693 | 0.89759 | -0.019335 |  | 0.9 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-BOOKER 2 | 0.91693 | 0.89759 | -0.019335 |  | 0.9 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-BOOKER 2 | 0.91693 | 0.89759 | -0.019335 |  | 0.9 | 1.05 | 0.17987 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-BOOKER 2 | 0.91693 | 0.89759 | -0.019335 |  | 0.9 | 1.05 | 0.18025 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-BOOKER 2 | 0.91693 | 0.89759 | -0.019335 |  | 0.9 | 1.05 | 0.19087 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-BOOKER 2 | 0.91693 | 0.89759 | -0.019335 |  | 0.9 | 1.05 | 0.19118 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-BOOKER 2 | 0.91693 | 0.89759 | -0.019335 |  | 0.9 | 1.05 | 0.18842 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-BOOKER 2 | 0.91693 | 0.89759 | -0.019335 |  | 0.9 | 1.05 | 0.18906 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-BOOKER 2 | 0.91693 | 0.89759 | -0.019335 |  | 0.9 | 1.05 | 0.19024 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-BOOKER 2 | 0.91693 | 0.89759 | -0.019335 |  | 0.9 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-BOOKER 2 | 0.91693 | 0.89759 | -0.019335 |  | 0.9 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-BOOKER 2 | 0.91693 | 0.89759 | -0.019335 |  | 0.9 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-BOOKER 2 | 0.91693 | 0.89759 | -0.019335 |  | 0.9 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-BOOKER 2 | 0.91693 | 0.89759 | -0.019335 |  | 0.9 | 1.05 | 0.49024 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-BOOKER 2 | 0.91693 | 0.89759 | -0.019335 |  | 0.9 | 1.05 | 0.19283 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-GLAZIR_G2 | 0.69081 | 0.66463 | -0.026188 |  | 0.9 | 1.05 | 0.079811 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-GLAZIR_G2 | 0.69081 | 0.66463 | -0.026188 |  | 0.9 | 1.05 | 0.19454 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-GLAZIR_G2 | 0.69081 | 0.66463 | -0.026188 |  | 0.9 | 1.05 | 0.23657 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-GLAZIR_G2 | 0.69081 | 0.66463 | -0.026188 |  | 0.9 | 1.05 | 0.23657 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-GLAZIR_G2 | 0.69081 | 0.66463 | -0.026188 |  | 0.9 | 1.05 | 0.17748 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-GLAZIR_G2 | 0.69081 | 0.66463 | -0.026188 |  | 0.9 | 1.05 | 0.1726 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-GLAZIR_G2 | 0.69081 | 0.66463 | -0.026188 |  | 0.9 | 1.05 | 0.17544 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-GLAZIR_G2 | 0.69081 | 0.66463 | -0.026188 |  | 0.9 | 1.05 | 0.12267 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-GLAZIR_G2 | 0.69081 | 0.66463 | -0.026188 |  | 0.9 | 1.05 | 0.12267 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-GLAZIR_G2 | 0.69081 | 0.66463 | -0.026188 |  | 0.9 | 1.05 | 0.17987 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-GLAZIR_G2 | 0.69081 | 0.66463 | -0.026188 |  | 0.9 | 1.05 | 0.18025 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-GLAZIR_G2 | 0.69081 | 0.66463 | -0.026188 |  | 0.9 | 1.05 | 0.19087 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-GLAZIR_G2 | 0.69081 | 0.66463 | -0.026188 |  | 0.9 | 1.05 | 0.19118 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-GLAZIR_G2 | 0.69081 | 0.66463 | -0.026188 |  | 0.9 | 1.05 | 0.18842 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-GLAZIR_G2 | 0.69081 | 0.66463 | -0.026188 |  | 0.9 | 1.05 | 0.18906 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-GLAZIR_G2 | 0.69081 | 0.66463 | -0.026188 |  | 0.9 | 1.05 | 0.19024 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-GLAZIR_G2 | 0.69081 | 0.66463 | -0.026188 |  | 0.9 | 1.05 | 0.17773 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-GLAZIR_G2 | 0.69081 | 0.66463 | -0.026188 |  | 0.9 | 1.05 | 0.17773 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-GLAZIR_G2 | 0.69081 | 0.66463 | -0.026188 |  | 0.9 | 1.05 | 0.18569 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-GLAZIR_G2 | 0.69081 | 0.66463 | -0.026188 |  | 0.9 | 1.05 | 0.18569 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-GLAZIR_G2 | 0.69081 | 0.66463 | -0.026188 |  | 0.9 | 1.05 | 0.49024 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-GLAZIR_G2 | 0.69081 | 0.66463 | -0.026188 |  | 0.9 | 1.05 | 0.19283 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-GLAZIR_G2 | 0.68774 | 0.65842 | -0.02932 |  | 0.9 | 1.05 | 0.079811 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-GLAZIR_G2 | 0.68774 | 0.65842 | -0.02932 |  | 0.9 | 1.05 | 0.19454 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-GLAZIR_G2 | 0.68774 | 0.65842 | -0.02932 |  | 0.9 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-GLAZIR_G2 | 0.68774 | 0.65842 | -0.02932 |  | 0.9 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-GLAZIR_G2 | 0.68774 | 0.65842 | -0.02932 |  | 0.9 | 1.05 | 0.17748 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-GLAZIR_G2 | 0.68774 | 0.65842 | -0.02932 |  | 0.9 | 1.05 | 0.1726 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-GLAZIR_G2 | 0.68774 | 0.65842 | -0.02932 |  | 0.9 | 1.05 | 0.17544 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-GLAZIR_G2 | 0.68774 | 0.65842 | -0.02932 |  | 0.9 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-GLAZIR_G2 | 0.68774 | 0.65842 | -0.02932 |  | 0.9 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-GLAZIR_G2 | 0.68774 | 0.65842 | -0.02932 |  | 0.9 | 1.05 | 0.17987 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-GLAZIR_G2 | 0.68774 | 0.65842 | -0.02932 |  | 0.9 | 1.05 | 0.18025 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-GLAZIR_G2 | 0.68774 | 0.65842 | -0.02932 |  | 0.9 | 1.05 | 0.19087 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-GLAZIR_G2 | 0.68774 | 0.65842 | -0.02932 |  | 0.9 | 1.05 | 0.19118 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-GLAZIR_G2 | 0.68774 | 0.65842 | -0.02932 |  | 0.9 | 1.05 | 0.18842 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-GLAZIR_G2 | 0.68774 | 0.65842 | -0.02932 |  | 0.9 | 1.05 | 0.18906 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-GLAZIR_G2 | 0.68774 | 0.65842 | -0.02932 |  | 0.9 | 1.05 | 0.19024 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-GLAZIR_G2 | 0.68774 | 0.65842 | -0.02932 |  | 0.9 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-GLAZIR_G2 | 0.68774 | 0.65842 | -0.02932 |  | 0.9 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-GLAZIR_G2 | 0.68774 | 0.65842 | -0.02932 |  | 0.9 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-GLAZIR_G2 | 0.68774 | 0.65842 | -0.02932 |  | 0.9 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-GLAZIR_G2 | 0.68774 | 0.65842 | -0.02932 |  | 0.9 | 1.05 | 0.49024 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-GLAZIR_G2 | 0.68774 | 0.65842 | -0.02932 |  | 0.9 | 1.05 | 0.19283 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-GLAZIR_G2 | 0.69048 | 0.66424 | -0.026244 |  | 0.9 | 1.05 | 0.079811 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-GLAZIR_G2 | 0.69048 | 0.66424 | -0.026244 |  | 0.9 | 1.05 | 0.19454 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-GLAZIR_G2 | 0.69048 | 0.66424 | -0.026244 |  | 0.9 | 1.05 | 0.23657 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-GLAZIR_G2 | 0.69048 | 0.66424 | -0.026244 |  | 0.9 | 1.05 | 0.23657 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-GLAZIR_G2 | 0.69048 | 0.66424 | -0.026244 |  | 0.9 | 1.05 | 0.17748 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-GLAZIR_G2 | 0.69048 | 0.66424 | -0.026244 |  | 0.9 | 1.05 | 0.1726 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-GLAZIR_G2 | 0.69048 | 0.66424 | -0.026244 |  | 0.9 | 1.05 | 0.17544 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-GLAZIR_G2 | 0.69048 | 0.66424 | -0.026244 |  | 0.9 | 1.05 | 0.12267 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-GLAZIR_G2 | 0.69048 | 0.66424 | -0.026244 |  | 0.9 | 1.05 | 0.12267 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-GLAZIR_G2 | 0.69048 | 0.66424 | -0.026244 |  | 0.9 | 1.05 | 0.17987 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-GLAZIR_G2 | 0.69048 | 0.66424 | -0.026244 |  | 0.9 | 1.05 | 0.18025 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-GLAZIR_G2 | 0.69048 | 0.66424 | -0.026244 |  | 0.9 | 1.05 | 0.19087 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-GLAZIR_G2 | 0.69048 | 0.66424 | -0.026244 |  | 0.9 | 1.05 | 0.19118 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-GLAZIR_G2 | 0.69048 | 0.66424 | -0.026244 |  | 0.9 | 1.05 | 0.18842 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-GLAZIR_G2 | 0.69048 | 0.66424 | -0.026244 |  | 0.9 | 1.05 | 0.18906 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-GLAZIR_G2 | 0.69048 | 0.66424 | -0.026244 |  | 0.9 | 1.05 | 0.19024 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-GLAZIR_G2 | 0.69048 | 0.66424 | -0.026244 |  | 0.9 | 1.05 | 0.17773 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-GLAZIR_G2 | 0.69048 | 0.66424 | -0.026244 |  | 0.9 | 1.05 | 0.17773 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-GLAZIR_G2 | 0.69048 | 0.66424 | -0.026244 |  | 0.9 | 1.05 | 0.18569 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-GLAZIR_G2 | 0.69048 | 0.66424 | -0.026244 |  | 0.9 | 1.05 | 0.18569 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-GLAZIR_G2 | 0.69048 | 0.66424 | -0.026244 |  | 0.9 | 1.05 | 0.49024 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-GLAZIR_G2 | 0.69048 | 0.66424 | -0.026244 |  | 0.9 | 1.05 | 0.19283 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-GLAZIR_G2 | 0.69044 | 0.66428 | -0.026158 |  | 0.9 | 1.05 | 0.079811 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-GLAZIR_G2 | 0.69044 | 0.66428 | -0.026158 |  | 0.9 | 1.05 | 0.19454 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-GLAZIR_G2 | 0.69044 | 0.66428 | -0.026158 |  | 0.9 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-GLAZIR_G2 | 0.69044 | 0.66428 | -0.026158 |  | 0.9 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-GLAZIR_G2 | 0.69044 | 0.66428 | -0.026158 |  | 0.9 | 1.05 | 0.17748 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-GLAZIR_G2 | 0.69044 | 0.66428 | -0.026158 |  | 0.9 | 1.05 | 0.1726 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-GLAZIR_G2 | 0.69044 | 0.66428 | -0.026158 |  | 0.9 | 1.05 | 0.17544 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-GLAZIR_G2 | 0.69044 | 0.66428 | -0.026158 |  | 0.9 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-GLAZIR_G2 | 0.69044 | 0.66428 | -0.026158 |  | 0.9 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-GLAZIR_G2 | 0.69044 | 0.66428 | -0.026158 |  | 0.9 | 1.05 | 0.17987 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-GLAZIR_G2 | 0.69044 | 0.66428 | -0.026158 |  | 0.9 | 1.05 | 0.18025 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-GLAZIR_G2 | 0.69044 | 0.66428 | -0.026158 |  | 0.9 | 1.05 | 0.19087 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-GLAZIR_G2 | 0.69044 | 0.66428 | -0.026158 |  | 0.9 | 1.05 | 0.19118 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-GLAZIR_G2 | 0.69044 | 0.66428 | -0.026158 |  | 0.9 | 1.05 | 0.18842 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-GLAZIR_G2 | 0.69044 | 0.66428 | -0.026158 |  | 0.9 | 1.05 | 0.18906 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-GLAZIR_G2 | 0.69044 | 0.66428 | -0.026158 |  | 0.9 | 1.05 | 0.19024 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-GLAZIR_G2 | 0.69044 | 0.66428 | -0.026158 |  | 0.9 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-GLAZIR_G2 | 0.69044 | 0.66428 | -0.026158 |  | 0.9 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-GLAZIR_G2 | 0.69044 | 0.66428 | -0.026158 |  | 0.9 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-GLAZIR_G2 | 0.69044 | 0.66428 | -0.026158 |  | 0.9 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-GLAZIR_G2 | 0.69044 | 0.66428 | -0.026158 |  | 0.9 | 1.05 | 0.49024 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-GLAZIR_G2 | 0.69044 | 0.66428 | -0.026158 |  | 0.9 | 1.05 | 0.19283 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-GLAZIR_G2 | 0.69054 | 0.66429 | -0.026249 |  | 0.9 | 1.05 | 0.079811 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-GLAZIR_G2 | 0.69054 | 0.66429 | -0.026249 |  | 0.9 | 1.05 | 0.19454 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-GLAZIR_G2 | 0.69054 | 0.66429 | -0.026249 |  | 0.9 | 1.05 | 0.23657 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-GLAZIR_G2 | 0.69054 | 0.66429 | -0.026249 |  | 0.9 | 1.05 | 0.23657 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-GLAZIR_G2 | 0.69054 | 0.66429 | -0.026249 |  | 0.9 | 1.05 | 0.17748 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-GLAZIR_G2 | 0.69054 | 0.66429 | -0.026249 |  | 0.9 | 1.05 | 0.1726 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-GLAZIR_G2 | 0.69054 | 0.66429 | -0.026249 |  | 0.9 | 1.05 | 0.17544 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-GLAZIR_G2 | 0.69054 | 0.66429 | -0.026249 |  | 0.9 | 1.05 | 0.12267 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-GLAZIR_G2 | 0.69054 | 0.66429 | -0.026249 |  | 0.9 | 1.05 | 0.12267 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-GLAZIR_G2 | 0.69054 | 0.66429 | -0.026249 |  | 0.9 | 1.05 | 0.17987 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-GLAZIR_G2 | 0.69054 | 0.66429 | -0.026249 |  | 0.9 | 1.05 | 0.18025 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-GLAZIR_G2 | 0.69054 | 0.66429 | -0.026249 |  | 0.9 | 1.05 | 0.19087 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-GLAZIR_G2 | 0.69054 | 0.66429 | -0.026249 |  | 0.9 | 1.05 | 0.19118 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-GLAZIR_G2 | 0.69054 | 0.66429 | -0.026249 |  | 0.9 | 1.05 | 0.18842 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-GLAZIR_G2 | 0.69054 | 0.66429 | -0.026249 |  | 0.9 | 1.05 | 0.18906 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-GLAZIR_G2 | 0.69054 | 0.66429 | -0.026249 |  | 0.9 | 1.05 | 0.19024 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-GLAZIR_G2 | 0.69054 | 0.66429 | -0.026249 |  | 0.9 | 1.05 | 0.17773 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-GLAZIR_G2 | 0.69054 | 0.66429 | -0.026249 |  | 0.9 | 1.05 | 0.17773 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-GLAZIR_G2 | 0.69054 | 0.66429 | -0.026249 |  | 0.9 | 1.05 | 0.18569 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-GLAZIR_G2 | 0.69054 | 0.66429 | -0.026249 |  | 0.9 | 1.05 | 0.18569 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-GLAZIR_G2 | 0.69054 | 0.66429 | -0.026249 |  | 0.9 | 1.05 | 0.49024 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-GLAZIR_G2 | 0.69054 | 0.66429 | -0.026249 |  | 0.9 | 1.05 | 0.19283 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-LIPSCOMB2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.079811 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-LIPSCOMB2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.19454 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-LIPSCOMB2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.23657 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-LIPSCOMB2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.23657 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-LIPSCOMB2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.17748 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-LIPSCOMB2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.1726 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-LIPSCOMB2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.17544 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-LIPSCOMB2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.12267 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-LIPSCOMB2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.12267 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-LIPSCOMB2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.17987 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-LIPSCOMB2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.18025 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-LIPSCOMB2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.19087 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-LIPSCOMB2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.19118 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-LIPSCOMB2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.18842 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-LIPSCOMB2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.18906 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-LIPSCOMB2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.19024 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-LIPSCOMB2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.17773 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-LIPSCOMB2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.17773 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-LIPSCOMB2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.18569 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-LIPSCOMB2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.18569 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-LIPSCOMB2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.49024 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-LIPSCOMB2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.19283 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-LIPSCOMB2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.079811 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-LIPSCOMB2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.19454 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-LIPSCOMB2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-LIPSCOMB2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-LIPSCOMB2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.17748 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-LIPSCOMB2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.1726 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-LIPSCOMB2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.17544 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-LIPSCOMB2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-LIPSCOMB2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-LIPSCOMB2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.17987 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-LIPSCOMB2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.18025 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-LIPSCOMB2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.19087 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-LIPSCOMB2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.19118 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-LIPSCOMB2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.18842 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-LIPSCOMB2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.18906 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-LIPSCOMB2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.19024 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-LIPSCOMB2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-LIPSCOMB2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-LIPSCOMB2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-LIPSCOMB2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-LIPSCOMB2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.49024 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-LIPSCOMB2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.19283 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-LIPSCOMB2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.079811 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-LIPSCOMB2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.19454 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-LIPSCOMB2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.23657 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-LIPSCOMB2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.23657 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-LIPSCOMB2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.17748 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-LIPSCOMB2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.1726 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-LIPSCOMB2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.17544 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-LIPSCOMB2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.12267 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-LIPSCOMB2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.12267 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-LIPSCOMB2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.17987 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-LIPSCOMB2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.18025 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-LIPSCOMB2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.19087 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-LIPSCOMB2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.19118 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-LIPSCOMB2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.18842 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-LIPSCOMB2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.18906 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-LIPSCOMB2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.19024 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-LIPSCOMB2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.17773 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-LIPSCOMB2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.17773 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-LIPSCOMB2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.18569 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-LIPSCOMB2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.18569 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-LIPSCOMB2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.49024 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-LIPSCOMB2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.19283 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-LIPSCOMB2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.079811 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-LIPSCOMB2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.19454 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-LIPSCOMB2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-LIPSCOMB2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-LIPSCOMB2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.17748 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-LIPSCOMB2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.1726 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-LIPSCOMB2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.17544 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-LIPSCOMB2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-LIPSCOMB2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-LIPSCOMB2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.17987 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-LIPSCOMB2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.18025 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-LIPSCOMB2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.19087 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-LIPSCOMB2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.19118 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-LIPSCOMB2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.18842 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-LIPSCOMB2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.18906 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-LIPSCOMB2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.19024 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-LIPSCOMB2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-LIPSCOMB2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-LIPSCOMB2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-LIPSCOMB2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-LIPSCOMB2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.49024 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-LIPSCOMB2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.19283 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-LIPSCOMB2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.079811 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-LIPSCOMB2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.19454 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-LIPSCOMB2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.23657 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-LIPSCOMB2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.23657 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-LIPSCOMB2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.17748 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-LIPSCOMB2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.1726 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-LIPSCOMB2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.17544 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-LIPSCOMB2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.12267 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-LIPSCOMB2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.12267 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-LIPSCOMB2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.17987 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-LIPSCOMB2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.18025 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-LIPSCOMB2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.19087 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-LIPSCOMB2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.19118 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-LIPSCOMB2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.18842 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-LIPSCOMB2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.18906 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-LIPSCOMB2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.19024 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-LIPSCOMB2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.17773 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-LIPSCOMB2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.17773 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-LIPSCOMB2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.18569 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-LIPSCOMB2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.18569 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-LIPSCOMB2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.49024 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-LIPSCOMB2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.19283 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-LIPS_SHA2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.079811 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-LIPS_SHA2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.19454 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-LIPS_SHA2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.23657 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-LIPS_SHA2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.23657 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-LIPS_SHA2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.17748 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-LIPS_SHA2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.1726 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-LIPS_SHA2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.17544 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-LIPS_SHA2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.12267 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-LIPS_SHA2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.12267 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-LIPS_SHA2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.17987 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-LIPS_SHA2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.18025 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-LIPS_SHA2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.19087 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-LIPS_SHA2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.19118 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-LIPS_SHA2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.18842 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-LIPS_SHA2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.18906 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-LIPS_SHA2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.19024 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-LIPS_SHA2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.17773 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-LIPS_SHA2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.17773 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-LIPS_SHA2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.18569 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-LIPS_SHA2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.18569 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-LIPS_SHA2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.49024 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-LIPS_SHA2 | 0.65051 | 0.62328 | -0.027224 |  | 0.9 | 1.05 | 0.19283 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-LIPS_SHA2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.079811 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-LIPS_SHA2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.19454 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-LIPS_SHA2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-LIPS_SHA2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-LIPS_SHA2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.17748 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-LIPS_SHA2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.1726 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-LIPS_SHA2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.17544 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-LIPS_SHA2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-LIPS_SHA2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-LIPS_SHA2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.17987 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-LIPS_SHA2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.18025 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-LIPS_SHA2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.19087 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-LIPS_SHA2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.19118 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-LIPS_SHA2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.18842 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-LIPS_SHA2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.18906 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-LIPS_SHA2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.19024 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-LIPS_SHA2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-LIPS_SHA2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-LIPS_SHA2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-LIPS_SHA2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-LIPS_SHA2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.49024 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-LIPS_SHA2 | 0.6473 | 0.61687 | -0.030434 |  | 0.9 | 1.05 | 0.19283 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-LIPS_SHA2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.079811 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-LIPS_SHA2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.19454 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-LIPS_SHA2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.23657 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-LIPS_SHA2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.23657 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-LIPS_SHA2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.17748 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-LIPS_SHA2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.1726 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-LIPS_SHA2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.17544 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-LIPS_SHA2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.12267 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-LIPS_SHA2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.12267 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-LIPS_SHA2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.17987 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-LIPS_SHA2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.18025 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-LIPS_SHA2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.19087 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-LIPS_SHA2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.19118 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-LIPS_SHA2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.18842 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-LIPS_SHA2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.18906 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-LIPS_SHA2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.19024 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-LIPS_SHA2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.17773 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-LIPS_SHA2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.17773 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-LIPS_SHA2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.18569 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-LIPS_SHA2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.18569 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-LIPS_SHA2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.49024 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-LIPS_SHA2 | 0.65016 | 0.62288 | -0.027279 |  | 0.9 | 1.05 | 0.19283 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-LIPS_SHA2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.079811 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-LIPS_SHA2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.19454 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-LIPS_SHA2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-LIPS_SHA2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-LIPS_SHA2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.17748 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-LIPS_SHA2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.1726 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-LIPS_SHA2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.17544 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-LIPS_SHA2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-LIPS_SHA2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-LIPS_SHA2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.17987 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-LIPS_SHA2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.18025 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-LIPS_SHA2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.19087 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-LIPS_SHA2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.19118 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-LIPS_SHA2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.18842 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-LIPS_SHA2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.18906 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-LIPS_SHA2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.19024 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-LIPS_SHA2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-LIPS_SHA2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-LIPS_SHA2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-LIPS_SHA2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-LIPS_SHA2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.49024 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-LIPS_SHA2 | 0.65011 | 0.62293 | -0.02719 |  | 0.9 | 1.05 | 0.19283 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-LIPS_SHA2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.079811 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-LIPS_SHA2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.19454 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-LIPS_SHA2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.23657 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-LIPS_SHA2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.23657 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-LIPS_SHA2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.17748 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-LIPS_SHA2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.1726 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-LIPS_SHA2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.17544 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-LIPS_SHA2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.12267 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-LIPS_SHA2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.12267 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-LIPS_SHA2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.17987 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-LIPS_SHA2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.18025 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-LIPS_SHA2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.19087 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-LIPS_SHA2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.19118 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-LIPS_SHA2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.18842 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-LIPS_SHA2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.18906 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-LIPS_SHA2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.19024 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-LIPS_SHA2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.17773 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-LIPS_SHA2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.17773 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-LIPS_SHA2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.18569 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-LIPS_SHA2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.18569 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-LIPS_SHA2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.49024 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-LIPS_SHA2 | 0.65022 | 0.62293 | -0.027285 |  | 0.9 | 1.05 | 0.19283 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-LUCKY_CR2 | 0.78505 | 0.76165 | -0.023398 |  | 0.9 | 1.05 | 0.079811 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-LUCKY_CR2 | 0.78505 | 0.76165 | -0.023398 |  | 0.9 | 1.05 | 0.19454 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-LUCKY_CR2 | 0.78505 | 0.76165 | -0.023398 |  | 0.9 | 1.05 | 0.23657 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-LUCKY_CR2 | 0.78505 | 0.76165 | -0.023398 |  | 0.9 | 1.05 | 0.23657 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-LUCKY_CR2 | 0.78505 | 0.76165 | -0.023398 |  | 0.9 | 1.05 | 0.17748 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-LUCKY_CR2 | 0.78505 | 0.76165 | -0.023398 |  | 0.9 | 1.05 | 0.1726 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-LUCKY_CR2 | 0.78505 | 0.76165 | -0.023398 |  | 0.9 | 1.05 | 0.17544 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-LUCKY_CR2 | 0.78505 | 0.76165 | -0.023398 |  | 0.9 | 1.05 | 0.12267 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-LUCKY_CR2 | 0.78505 | 0.76165 | -0.023398 |  | 0.9 | 1.05 | 0.12267 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-LUCKY_CR2 | 0.78505 | 0.76165 | -0.023398 |  | 0.9 | 1.05 | 0.17987 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-LUCKY_CR2 | 0.78505 | 0.76165 | -0.023398 |  | 0.9 | 1.05 | 0.18025 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-LUCKY_CR2 | 0.78505 | 0.76165 | -0.023398 |  | 0.9 | 1.05 | 0.19087 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-LUCKY_CR2 | 0.78505 | 0.76165 | -0.023398 |  | 0.9 | 1.05 | 0.19118 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-LUCKY_CR2 | 0.78505 | 0.76165 | -0.023398 |  | 0.9 | 1.05 | 0.18842 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-LUCKY_CR2 | 0.78505 | 0.76165 | -0.023398 |  | 0.9 | 1.05 | 0.18906 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-LUCKY_CR2 | 0.78505 | 0.76165 | -0.023398 |  | 0.9 | 1.05 | 0.19024 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-LUCKY_CR2 | 0.78505 | 0.76165 | -0.023398 |  | 0.9 | 1.05 | 0.17773 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-LUCKY_CR2 | 0.78505 | 0.76165 | -0.023398 |  | 0.9 | 1.05 | 0.17773 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-LUCKY_CR2 | 0.78505 | 0.76165 | -0.023398 |  | 0.9 | 1.05 | 0.18569 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-LUCKY_CR2 | 0.78505 | 0.76165 | -0.023398 |  | 0.9 | 1.05 | 0.18569 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-LUCKY_CR2 | 0.78505 | 0.76165 | -0.023398 |  | 0.9 | 1.05 | 0.49024 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-LUCKY_CR2 | 0.78505 | 0.76165 | -0.023398 |  | 0.9 | 1.05 | 0.19283 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-LUCKY_CR2 | 0.78233 | 0.75603 | -0.026306 |  | 0.9 | 1.05 | 0.079811 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-LUCKY_CR2 | 0.78233 | 0.75603 | -0.026306 |  | 0.9 | 1.05 | 0.19454 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-LUCKY_CR2 | 0.78233 | 0.75603 | -0.026306 |  | 0.9 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-LUCKY_CR2 | 0.78233 | 0.75603 | -0.026306 |  | 0.9 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-LUCKY_CR2 | 0.78233 | 0.75603 | -0.026306 |  | 0.9 | 1.05 | 0.17748 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-LUCKY_CR2 | 0.78233 | 0.75603 | -0.026306 |  | 0.9 | 1.05 | 0.1726 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-LUCKY_CR2 | 0.78233 | 0.75603 | -0.026306 |  | 0.9 | 1.05 | 0.17544 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-LUCKY_CR2 | 0.78233 | 0.75603 | -0.026306 |  | 0.9 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-LUCKY_CR2 | 0.78233 | 0.75603 | -0.026306 |  | 0.9 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-LUCKY_CR2 | 0.78233 | 0.75603 | -0.026306 |  | 0.9 | 1.05 | 0.17987 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-LUCKY_CR2 | 0.78233 | 0.75603 | -0.026306 |  | 0.9 | 1.05 | 0.18025 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-LUCKY_CR2 | 0.78233 | 0.75603 | -0.026306 |  | 0.9 | 1.05 | 0.19087 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-LUCKY_CR2 | 0.78233 | 0.75603 | -0.026306 |  | 0.9 | 1.05 | 0.19118 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-LUCKY_CR2 | 0.78233 | 0.75603 | -0.026306 |  | 0.9 | 1.05 | 0.18842 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-LUCKY_CR2 | 0.78233 | 0.75603 | -0.026306 |  | 0.9 | 1.05 | 0.18906 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-LUCKY_CR2 | 0.78233 | 0.75603 | -0.026306 |  | 0.9 | 1.05 | 0.19024 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-LUCKY_CR2 | 0.78233 | 0.75603 | -0.026306 |  | 0.9 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-LUCKY_CR2 | 0.78233 | 0.75603 | -0.026306 |  | 0.9 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-LUCKY_CR2 | 0.78233 | 0.75603 | -0.026306 |  | 0.9 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-LUCKY_CR2 | 0.78233 | 0.75603 | -0.026306 |  | 0.9 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-LUCKY_CR2 | 0.78233 | 0.75603 | -0.026306 |  | 0.9 | 1.05 | 0.49024 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-LUCKY_CR2 | 0.78233 | 0.75603 | -0.026306 |  | 0.9 | 1.05 | 0.19283 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-LUCKY_CR2 | 0.78475 | 0.7613 | -0.023456 |  | 0.9 | 1.05 | 0.079811 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-LUCKY_CR2 | 0.78475 | 0.7613 | -0.023456 |  | 0.9 | 1.05 | 0.19454 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-LUCKY_CR2 | 0.78475 | 0.7613 | -0.023456 |  | 0.9 | 1.05 | 0.23657 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-LUCKY_CR2 | 0.78475 | 0.7613 | -0.023456 |  | 0.9 | 1.05 | 0.23657 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-LUCKY_CR2 | 0.78475 | 0.7613 | -0.023456 |  | 0.9 | 1.05 | 0.17748 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-LUCKY_CR2 | 0.78475 | 0.7613 | -0.023456 |  | 0.9 | 1.05 | 0.1726 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-LUCKY_CR2 | 0.78475 | 0.7613 | -0.023456 |  | 0.9 | 1.05 | 0.17544 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-LUCKY_CR2 | 0.78475 | 0.7613 | -0.023456 |  | 0.9 | 1.05 | 0.12267 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-LUCKY_CR2 | 0.78475 | 0.7613 | -0.023456 |  | 0.9 | 1.05 | 0.12267 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-LUCKY_CR2 | 0.78475 | 0.7613 | -0.023456 |  | 0.9 | 1.05 | 0.17987 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-LUCKY_CR2 | 0.78475 | 0.7613 | -0.023456 |  | 0.9 | 1.05 | 0.18025 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-LUCKY_CR2 | 0.78475 | 0.7613 | -0.023456 |  | 0.9 | 1.05 | 0.19087 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-LUCKY_CR2 | 0.78475 | 0.7613 | -0.023456 |  | 0.9 | 1.05 | 0.19118 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-LUCKY_CR2 | 0.78475 | 0.7613 | -0.023456 |  | 0.9 | 1.05 | 0.18842 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-LUCKY_CR2 | 0.78475 | 0.7613 | -0.023456 |  | 0.9 | 1.05 | 0.18906 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-LUCKY_CR2 | 0.78475 | 0.7613 | -0.023456 |  | 0.9 | 1.05 | 0.19024 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-LUCKY_CR2 | 0.78475 | 0.7613 | -0.023456 |  | 0.9 | 1.05 | 0.17773 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-LUCKY_CR2 | 0.78475 | 0.7613 | -0.023456 |  | 0.9 | 1.05 | 0.17773 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-LUCKY_CR2 | 0.78475 | 0.7613 | -0.023456 |  | 0.9 | 1.05 | 0.18569 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-LUCKY_CR2 | 0.78475 | 0.7613 | -0.023456 |  | 0.9 | 1.05 | 0.18569 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-LUCKY_CR2 | 0.78475 | 0.7613 | -0.023456 |  | 0.9 | 1.05 | 0.49024 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-LUCKY_CR2 | 0.78475 | 0.7613 | -0.023456 |  | 0.9 | 1.05 | 0.19283 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-LUCKY_CR2 | 0.78472 | 0.76134 | -0.023379 |  | 0.9 | 1.05 | 0.079811 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-LUCKY_CR2 | 0.78472 | 0.76134 | -0.023379 |  | 0.9 | 1.05 | 0.19454 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-LUCKY_CR2 | 0.78472 | 0.76134 | -0.023379 |  | 0.9 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-LUCKY_CR2 | 0.78472 | 0.76134 | -0.023379 |  | 0.9 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-LUCKY_CR2 | 0.78472 | 0.76134 | -0.023379 |  | 0.9 | 1.05 | 0.17748 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-LUCKY_CR2 | 0.78472 | 0.76134 | -0.023379 |  | 0.9 | 1.05 | 0.1726 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-LUCKY_CR2 | 0.78472 | 0.76134 | -0.023379 |  | 0.9 | 1.05 | 0.17544 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-LUCKY_CR2 | 0.78472 | 0.76134 | -0.023379 |  | 0.9 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-LUCKY_CR2 | 0.78472 | 0.76134 | -0.023379 |  | 0.9 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-LUCKY_CR2 | 0.78472 | 0.76134 | -0.023379 |  | 0.9 | 1.05 | 0.17987 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-LUCKY_CR2 | 0.78472 | 0.76134 | -0.023379 |  | 0.9 | 1.05 | 0.18025 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-LUCKY_CR2 | 0.78472 | 0.76134 | -0.023379 |  | 0.9 | 1.05 | 0.19087 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-LUCKY_CR2 | 0.78472 | 0.76134 | -0.023379 |  | 0.9 | 1.05 | 0.19118 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-LUCKY_CR2 | 0.78472 | 0.76134 | -0.023379 |  | 0.9 | 1.05 | 0.18842 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-LUCKY_CR2 | 0.78472 | 0.76134 | -0.023379 |  | 0.9 | 1.05 | 0.18906 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-LUCKY_CR2 | 0.78472 | 0.76134 | -0.023379 |  | 0.9 | 1.05 | 0.19024 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-LUCKY_CR2 | 0.78472 | 0.76134 | -0.023379 |  | 0.9 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-LUCKY_CR2 | 0.78472 | 0.76134 | -0.023379 |  | 0.9 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-LUCKY_CR2 | 0.78472 | 0.76134 | -0.023379 |  | 0.9 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-LUCKY_CR2 | 0.78472 | 0.76134 | -0.023379 |  | 0.9 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-LUCKY_CR2 | 0.78472 | 0.76134 | -0.023379 |  | 0.9 | 1.05 | 0.49024 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-LUCKY_CR2 | 0.78472 | 0.76134 | -0.023379 |  | 0.9 | 1.05 | 0.19283 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-LUCKY_CR2 | 0.7848 | 0.76134 | -0.023459 |  | 0.9 | 1.05 | 0.079811 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-LUCKY_CR2 | 0.7848 | 0.76134 | -0.023459 |  | 0.9 | 1.05 | 0.19454 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-LUCKY_CR2 | 0.7848 | 0.76134 | -0.023459 |  | 0.9 | 1.05 | 0.23657 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-LUCKY_CR2 | 0.7848 | 0.76134 | -0.023459 |  | 0.9 | 1.05 | 0.23657 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-LUCKY_CR2 | 0.7848 | 0.76134 | -0.023459 |  | 0.9 | 1.05 | 0.17748 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-LUCKY_CR2 | 0.7848 | 0.76134 | -0.023459 |  | 0.9 | 1.05 | 0.1726 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-LUCKY_CR2 | 0.7848 | 0.76134 | -0.023459 |  | 0.9 | 1.05 | 0.17544 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-LUCKY_CR2 | 0.7848 | 0.76134 | -0.023459 |  | 0.9 | 1.05 | 0.12267 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-LUCKY_CR2 | 0.7848 | 0.76134 | -0.023459 |  | 0.9 | 1.05 | 0.12267 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-LUCKY_CR2 | 0.7848 | 0.76134 | -0.023459 |  | 0.9 | 1.05 | 0.17987 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-LUCKY_CR2 | 0.7848 | 0.76134 | -0.023459 |  | 0.9 | 1.05 | 0.18025 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-LUCKY_CR2 | 0.7848 | 0.76134 | -0.023459 |  | 0.9 | 1.05 | 0.19087 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-LUCKY_CR2 | 0.7848 | 0.76134 | -0.023459 |  | 0.9 | 1.05 | 0.19118 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-LUCKY_CR2 | 0.7848 | 0.76134 | -0.023459 |  | 0.9 | 1.05 | 0.18842 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-LUCKY_CR2 | 0.7848 | 0.76134 | -0.023459 |  | 0.9 | 1.05 | 0.18906 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-LUCKY_CR2 | 0.7848 | 0.76134 | -0.023459 |  | 0.9 | 1.05 | 0.19024 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-LUCKY_CR2 | 0.7848 | 0.76134 | -0.023459 |  | 0.9 | 1.05 | 0.17773 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-LUCKY_CR2 | 0.7848 | 0.76134 | -0.023459 |  | 0.9 | 1.05 | 0.17773 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-LUCKY_CR2 | 0.7848 | 0.76134 | -0.023459 |  | 0.9 | 1.05 | 0.18569 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-LUCKY_CR2 | 0.7848 | 0.76134 | -0.023459 |  | 0.9 | 1.05 | 0.18569 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-LUCKY_CR2 | 0.7848 | 0.76134 | -0.023459 |  | 0.9 | 1.05 | 0.49024 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-LUCKY_CR2 | 0.7848 | 0.76134 | -0.023459 |  | 0.9 | 1.05 | 0.19283 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-LUCKY_G 2 | 0.7852 | 0.76181 | -0.023393 |  | 0.9 | 1.05 | 0.079811 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-LUCKY_G 2 | 0.7852 | 0.76181 | -0.023393 |  | 0.9 | 1.05 | 0.19454 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-LUCKY_G 2 | 0.7852 | 0.76181 | -0.023393 |  | 0.9 | 1.05 | 0.23657 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-LUCKY_G 2 | 0.7852 | 0.76181 | -0.023393 |  | 0.9 | 1.05 | 0.23657 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-LUCKY_G 2 | 0.7852 | 0.76181 | -0.023393 |  | 0.9 | 1.05 | 0.17748 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-LUCKY_G 2 | 0.7852 | 0.76181 | -0.023393 |  | 0.9 | 1.05 | 0.1726 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-LUCKY_G 2 | 0.7852 | 0.76181 | -0.023393 |  | 0.9 | 1.05 | 0.17544 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-LUCKY_G 2 | 0.7852 | 0.76181 | -0.023393 |  | 0.9 | 1.05 | 0.12267 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-LUCKY_G 2 | 0.7852 | 0.76181 | -0.023393 |  | 0.9 | 1.05 | 0.12267 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-LUCKY_G 2 | 0.7852 | 0.76181 | -0.023393 |  | 0.9 | 1.05 | 0.17987 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-LUCKY_G 2 | 0.7852 | 0.76181 | -0.023393 |  | 0.9 | 1.05 | 0.18025 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-LUCKY_G 2 | 0.7852 | 0.76181 | -0.023393 |  | 0.9 | 1.05 | 0.19087 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-LUCKY_G 2 | 0.7852 | 0.76181 | -0.023393 |  | 0.9 | 1.05 | 0.19118 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-LUCKY_G 2 | 0.7852 | 0.76181 | -0.023393 |  | 0.9 | 1.05 | 0.18842 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-LUCKY_G 2 | 0.7852 | 0.76181 | -0.023393 |  | 0.9 | 1.05 | 0.18906 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-LUCKY_G 2 | 0.7852 | 0.76181 | -0.023393 |  | 0.9 | 1.05 | 0.19024 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-LUCKY_G 2 | 0.7852 | 0.76181 | -0.023393 |  | 0.9 | 1.05 | 0.17773 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-LUCKY_G 2 | 0.7852 | 0.76181 | -0.023393 |  | 0.9 | 1.05 | 0.17773 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-LUCKY_G 2 | 0.7852 | 0.76181 | -0.023393 |  | 0.9 | 1.05 | 0.18569 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-LUCKY_G 2 | 0.7852 | 0.76181 | -0.023393 |  | 0.9 | 1.05 | 0.18569 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-LUCKY_G 2 | 0.7852 | 0.76181 | -0.023393 |  | 0.9 | 1.05 | 0.49024 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-LUCKY_G 2 | 0.7852 | 0.76181 | -0.023393 |  | 0.9 | 1.05 | 0.19283 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-LUCKY_G 2 | 0.78248 | 0.75618 | -0.026301 |  | 0.9 | 1.05 | 0.079811 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-LUCKY_G 2 | 0.78248 | 0.75618 | -0.026301 |  | 0.9 | 1.05 | 0.19454 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-LUCKY_G 2 | 0.78248 | 0.75618 | -0.026301 |  | 0.9 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-LUCKY_G 2 | 0.78248 | 0.75618 | -0.026301 |  | 0.9 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-LUCKY_G 2 | 0.78248 | 0.75618 | -0.026301 |  | 0.9 | 1.05 | 0.17748 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-LUCKY_G 2 | 0.78248 | 0.75618 | -0.026301 |  | 0.9 | 1.05 | 0.1726 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-LUCKY_G 2 | 0.78248 | 0.75618 | -0.026301 |  | 0.9 | 1.05 | 0.17544 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-LUCKY_G 2 | 0.78248 | 0.75618 | -0.026301 |  | 0.9 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-LUCKY_G 2 | 0.78248 | 0.75618 | -0.026301 |  | 0.9 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-LUCKY_G 2 | 0.78248 | 0.75618 | -0.026301 |  | 0.9 | 1.05 | 0.17987 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-LUCKY_G 2 | 0.78248 | 0.75618 | -0.026301 |  | 0.9 | 1.05 | 0.18025 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-LUCKY_G 2 | 0.78248 | 0.75618 | -0.026301 |  | 0.9 | 1.05 | 0.19087 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-LUCKY_G 2 | 0.78248 | 0.75618 | -0.026301 |  | 0.9 | 1.05 | 0.19118 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-LUCKY_G 2 | 0.78248 | 0.75618 | -0.026301 |  | 0.9 | 1.05 | 0.18842 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-LUCKY_G 2 | 0.78248 | 0.75618 | -0.026301 |  | 0.9 | 1.05 | 0.18906 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-LUCKY_G 2 | 0.78248 | 0.75618 | -0.026301 |  | 0.9 | 1.05 | 0.19024 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-LUCKY_G 2 | 0.78248 | 0.75618 | -0.026301 |  | 0.9 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-LUCKY_G 2 | 0.78248 | 0.75618 | -0.026301 |  | 0.9 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-LUCKY_G 2 | 0.78248 | 0.75618 | -0.026301 |  | 0.9 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-LUCKY_G 2 | 0.78248 | 0.75618 | -0.026301 |  | 0.9 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-LUCKY_G 2 | 0.78248 | 0.75618 | -0.026301 |  | 0.9 | 1.05 | 0.49024 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-LUCKY_G 2 | 0.78248 | 0.75618 | -0.026301 |  | 0.9 | 1.05 | 0.19283 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-LUCKY_G 2 | 0.7849 | 0.76145 | -0.023451 |  | 0.9 | 1.05 | 0.079811 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-LUCKY_G 2 | 0.7849 | 0.76145 | -0.023451 |  | 0.9 | 1.05 | 0.19454 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-LUCKY_G 2 | 0.7849 | 0.76145 | -0.023451 |  | 0.9 | 1.05 | 0.23657 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-LUCKY_G 2 | 0.7849 | 0.76145 | -0.023451 |  | 0.9 | 1.05 | 0.23657 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-LUCKY_G 2 | 0.7849 | 0.76145 | -0.023451 |  | 0.9 | 1.05 | 0.17748 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-LUCKY_G 2 | 0.7849 | 0.76145 | -0.023451 |  | 0.9 | 1.05 | 0.1726 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-LUCKY_G 2 | 0.7849 | 0.76145 | -0.023451 |  | 0.9 | 1.05 | 0.17544 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-LUCKY_G 2 | 0.7849 | 0.76145 | -0.023451 |  | 0.9 | 1.05 | 0.12267 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-LUCKY_G 2 | 0.7849 | 0.76145 | -0.023451 |  | 0.9 | 1.05 | 0.12267 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-LUCKY_G 2 | 0.7849 | 0.76145 | -0.023451 |  | 0.9 | 1.05 | 0.17987 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-LUCKY_G 2 | 0.7849 | 0.76145 | -0.023451 |  | 0.9 | 1.05 | 0.18025 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-LUCKY_G 2 | 0.7849 | 0.76145 | -0.023451 |  | 0.9 | 1.05 | 0.19087 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-LUCKY_G 2 | 0.7849 | 0.76145 | -0.023451 |  | 0.9 | 1.05 | 0.19118 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-LUCKY_G 2 | 0.7849 | 0.76145 | -0.023451 |  | 0.9 | 1.05 | 0.18842 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-LUCKY_G 2 | 0.7849 | 0.76145 | -0.023451 |  | 0.9 | 1.05 | 0.18906 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-LUCKY_G 2 | 0.7849 | 0.76145 | -0.023451 |  | 0.9 | 1.05 | 0.19024 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-LUCKY_G 2 | 0.7849 | 0.76145 | -0.023451 |  | 0.9 | 1.05 | 0.17773 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-LUCKY_G 2 | 0.7849 | 0.76145 | -0.023451 |  | 0.9 | 1.05 | 0.17773 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-LUCKY_G 2 | 0.7849 | 0.76145 | -0.023451 |  | 0.9 | 1.05 | 0.18569 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-LUCKY_G 2 | 0.7849 | 0.76145 | -0.023451 |  | 0.9 | 1.05 | 0.18569 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-LUCKY_G 2 | 0.7849 | 0.76145 | -0.023451 |  | 0.9 | 1.05 | 0.49024 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-LUCKY_G 2 | 0.7849 | 0.76145 | -0.023451 |  | 0.9 | 1.05 | 0.19283 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-LUCKY_G 2 | 0.78487 | 0.76149 | -0.023374 |  | 0.9 | 1.05 | 0.079811 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-LUCKY_G 2 | 0.78487 | 0.76149 | -0.023374 |  | 0.9 | 1.05 | 0.19454 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-LUCKY_G 2 | 0.78487 | 0.76149 | -0.023374 |  | 0.9 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-LUCKY_G 2 | 0.78487 | 0.76149 | -0.023374 |  | 0.9 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-LUCKY_G 2 | 0.78487 | 0.76149 | -0.023374 |  | 0.9 | 1.05 | 0.17748 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-LUCKY_G 2 | 0.78487 | 0.76149 | -0.023374 |  | 0.9 | 1.05 | 0.1726 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-LUCKY_G 2 | 0.78487 | 0.76149 | -0.023374 |  | 0.9 | 1.05 | 0.17544 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-LUCKY_G 2 | 0.78487 | 0.76149 | -0.023374 |  | 0.9 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-LUCKY_G 2 | 0.78487 | 0.76149 | -0.023374 |  | 0.9 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-LUCKY_G 2 | 0.78487 | 0.76149 | -0.023374 |  | 0.9 | 1.05 | 0.17987 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-LUCKY_G 2 | 0.78487 | 0.76149 | -0.023374 |  | 0.9 | 1.05 | 0.18025 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-LUCKY_G 2 | 0.78487 | 0.76149 | -0.023374 |  | 0.9 | 1.05 | 0.19087 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-LUCKY_G 2 | 0.78487 | 0.76149 | -0.023374 |  | 0.9 | 1.05 | 0.19118 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-LUCKY_G 2 | 0.78487 | 0.76149 | -0.023374 |  | 0.9 | 1.05 | 0.18842 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-LUCKY_G 2 | 0.78487 | 0.76149 | -0.023374 |  | 0.9 | 1.05 | 0.18906 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-LUCKY_G 2 | 0.78487 | 0.76149 | -0.023374 |  | 0.9 | 1.05 | 0.19024 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-LUCKY_G 2 | 0.78487 | 0.76149 | -0.023374 |  | 0.9 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-LUCKY_G 2 | 0.78487 | 0.76149 | -0.023374 |  | 0.9 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-LUCKY_G 2 | 0.78487 | 0.76149 | -0.023374 |  | 0.9 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-LUCKY_G 2 | 0.78487 | 0.76149 | -0.023374 |  | 0.9 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-LUCKY_G 2 | 0.78487 | 0.76149 | -0.023374 |  | 0.9 | 1.05 | 0.49024 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-LUCKY_G 2 | 0.78487 | 0.76149 | -0.023374 |  | 0.9 | 1.05 | 0.19283 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-LUCKY_G 2 | 0.78495 | 0.7615 | -0.023454 |  | 0.9 | 1.05 | 0.079811 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-LUCKY_G 2 | 0.78495 | 0.7615 | -0.023454 |  | 0.9 | 1.05 | 0.19454 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-LUCKY_G 2 | 0.78495 | 0.7615 | -0.023454 |  | 0.9 | 1.05 | 0.23657 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-LUCKY_G 2 | 0.78495 | 0.7615 | -0.023454 |  | 0.9 | 1.05 | 0.23657 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-LUCKY_G 2 | 0.78495 | 0.7615 | -0.023454 |  | 0.9 | 1.05 | 0.17748 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-LUCKY_G 2 | 0.78495 | 0.7615 | -0.023454 |  | 0.9 | 1.05 | 0.1726 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-LUCKY_G 2 | 0.78495 | 0.7615 | -0.023454 |  | 0.9 | 1.05 | 0.17544 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-LUCKY_G 2 | 0.78495 | 0.7615 | -0.023454 |  | 0.9 | 1.05 | 0.12267 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-LUCKY_G 2 | 0.78495 | 0.7615 | -0.023454 |  | 0.9 | 1.05 | 0.12267 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-LUCKY_G 2 | 0.78495 | 0.7615 | -0.023454 |  | 0.9 | 1.05 | 0.17987 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-LUCKY_G 2 | 0.78495 | 0.7615 | -0.023454 |  | 0.9 | 1.05 | 0.18025 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-LUCKY_G 2 | 0.78495 | 0.7615 | -0.023454 |  | 0.9 | 1.05 | 0.19087 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-LUCKY_G 2 | 0.78495 | 0.7615 | -0.023454 |  | 0.9 | 1.05 | 0.19118 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-LUCKY_G 2 | 0.78495 | 0.7615 | -0.023454 |  | 0.9 | 1.05 | 0.18842 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-LUCKY_G 2 | 0.78495 | 0.7615 | -0.023454 |  | 0.9 | 1.05 | 0.18906 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-LUCKY_G 2 | 0.78495 | 0.7615 | -0.023454 |  | 0.9 | 1.05 | 0.19024 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-LUCKY_G 2 | 0.78495 | 0.7615 | -0.023454 |  | 0.9 | 1.05 | 0.17773 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-LUCKY_G 2 | 0.78495 | 0.7615 | -0.023454 |  | 0.9 | 1.05 | 0.17773 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-LUCKY_G 2 | 0.78495 | 0.7615 | -0.023454 |  | 0.9 | 1.05 | 0.18569 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-LUCKY_G 2 | 0.78495 | 0.7615 | -0.023454 |  | 0.9 | 1.05 | 0.18569 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-LUCKY_G 2 | 0.78495 | 0.7615 | -0.023454 |  | 0.9 | 1.05 | 0.49024 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-LUCKY_G 2 | 0.78495 | 0.7615 | -0.023454 |  | 0.9 | 1.05 | 0.19283 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-SHATTUCK2 | 0.62806 | 0.60033 | -0.027733 |  | 0.9 | 1.05 | 0.079811 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-SHATTUCK2 | 0.62806 | 0.60033 | -0.027733 |  | 0.9 | 1.05 | 0.19454 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-SHATTUCK2 | 0.62806 | 0.60033 | -0.027733 |  | 0.9 | 1.05 | 0.23657 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-SHATTUCK2 | 0.62806 | 0.60033 | -0.027733 |  | 0.9 | 1.05 | 0.23657 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-SHATTUCK2 | 0.62806 | 0.60033 | -0.027733 |  | 0.9 | 1.05 | 0.17748 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-SHATTUCK2 | 0.62806 | 0.60033 | -0.027733 |  | 0.9 | 1.05 | 0.1726 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-SHATTUCK2 | 0.62806 | 0.60033 | -0.027733 |  | 0.9 | 1.05 | 0.17544 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-SHATTUCK2 | 0.62806 | 0.60033 | -0.027733 |  | 0.9 | 1.05 | 0.12267 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-SHATTUCK2 | 0.62806 | 0.60033 | -0.027733 |  | 0.9 | 1.05 | 0.12267 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-SHATTUCK2 | 0.62806 | 0.60033 | -0.027733 |  | 0.9 | 1.05 | 0.17987 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-SHATTUCK2 | 0.62806 | 0.60033 | -0.027733 |  | 0.9 | 1.05 | 0.18025 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-SHATTUCK2 | 0.62806 | 0.60033 | -0.027733 |  | 0.9 | 1.05 | 0.19087 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-SHATTUCK2 | 0.62806 | 0.60033 | -0.027733 |  | 0.9 | 1.05 | 0.19118 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-SHATTUCK2 | 0.62806 | 0.60033 | -0.027733 |  | 0.9 | 1.05 | 0.18842 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-SHATTUCK2 | 0.62806 | 0.60033 | -0.027733 |  | 0.9 | 1.05 | 0.18906 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-SHATTUCK2 | 0.62806 | 0.60033 | -0.027733 |  | 0.9 | 1.05 | 0.19024 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-SHATTUCK2 | 0.62806 | 0.60033 | -0.027733 |  | 0.9 | 1.05 | 0.17773 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-SHATTUCK2 | 0.62806 | 0.60033 | -0.027733 |  | 0.9 | 1.05 | 0.17773 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-SHATTUCK2 | 0.62806 | 0.60033 | -0.027733 |  | 0.9 | 1.05 | 0.18569 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-SHATTUCK2 | 0.62806 | 0.60033 | -0.027733 |  | 0.9 | 1.05 | 0.18569 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-SHATTUCK2 | 0.62806 | 0.60033 | -0.027733 |  | 0.9 | 1.05 | 0.49024 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-SHATTUCK2 | 0.62806 | 0.60033 | -0.027733 |  | 0.9 | 1.05 | 0.19283 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-SHATTUCK2 | 0.62479 | 0.59381 | -0.03098 |  | 0.9 | 1.05 | 0.079811 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-SHATTUCK2 | 0.62479 | 0.59381 | -0.03098 |  | 0.9 | 1.05 | 0.19454 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-SHATTUCK2 | 0.62479 | 0.59381 | -0.03098 |  | 0.9 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-SHATTUCK2 | 0.62479 | 0.59381 | -0.03098 |  | 0.9 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-SHATTUCK2 | 0.62479 | 0.59381 | -0.03098 |  | 0.9 | 1.05 | 0.17748 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-SHATTUCK2 | 0.62479 | 0.59381 | -0.03098 |  | 0.9 | 1.05 | 0.1726 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-SHATTUCK2 | 0.62479 | 0.59381 | -0.03098 |  | 0.9 | 1.05 | 0.17544 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-SHATTUCK2 | 0.62479 | 0.59381 | -0.03098 |  | 0.9 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-SHATTUCK2 | 0.62479 | 0.59381 | -0.03098 |  | 0.9 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-SHATTUCK2 | 0.62479 | 0.59381 | -0.03098 |  | 0.9 | 1.05 | 0.17987 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-SHATTUCK2 | 0.62479 | 0.59381 | -0.03098 |  | 0.9 | 1.05 | 0.18025 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-SHATTUCK2 | 0.62479 | 0.59381 | -0.03098 |  | 0.9 | 1.05 | 0.19087 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-SHATTUCK2 | 0.62479 | 0.59381 | -0.03098 |  | 0.9 | 1.05 | 0.19118 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-SHATTUCK2 | 0.62479 | 0.59381 | -0.03098 |  | 0.9 | 1.05 | 0.18842 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-SHATTUCK2 | 0.62479 | 0.59381 | -0.03098 |  | 0.9 | 1.05 | 0.18906 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-SHATTUCK2 | 0.62479 | 0.59381 | -0.03098 |  | 0.9 | 1.05 | 0.19024 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-SHATTUCK2 | 0.62479 | 0.59381 | -0.03098 |  | 0.9 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-SHATTUCK2 | 0.62479 | 0.59381 | -0.03098 |  | 0.9 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-SHATTUCK2 | 0.62479 | 0.59381 | -0.03098 |  | 0.9 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-SHATTUCK2 | 0.62479 | 0.59381 | -0.03098 |  | 0.9 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-SHATTUCK2 | 0.62479 | 0.59381 | -0.03098 |  | 0.9 | 1.05 | 0.49024 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-SHATTUCK2 | 0.62479 | 0.59381 | -0.03098 |  | 0.9 | 1.05 | 0.19283 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-SHATTUCK2 | 0.6277 | 0.59991 | -0.027788 |  | 0.9 | 1.05 | 0.079811 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-SHATTUCK2 | 0.6277 | 0.59991 | -0.027788 |  | 0.9 | 1.05 | 0.19454 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-SHATTUCK2 | 0.6277 | 0.59991 | -0.027788 |  | 0.9 | 1.05 | 0.23657 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-SHATTUCK2 | 0.6277 | 0.59991 | -0.027788 |  | 0.9 | 1.05 | 0.23657 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-SHATTUCK2 | 0.6277 | 0.59991 | -0.027788 |  | 0.9 | 1.05 | 0.17748 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-SHATTUCK2 | 0.6277 | 0.59991 | -0.027788 |  | 0.9 | 1.05 | 0.1726 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-SHATTUCK2 | 0.6277 | 0.59991 | -0.027788 |  | 0.9 | 1.05 | 0.17544 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-SHATTUCK2 | 0.6277 | 0.59991 | -0.027788 |  | 0.9 | 1.05 | 0.12267 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-SHATTUCK2 | 0.6277 | 0.59991 | -0.027788 |  | 0.9 | 1.05 | 0.12267 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-SHATTUCK2 | 0.6277 | 0.59991 | -0.027788 |  | 0.9 | 1.05 | 0.17987 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-SHATTUCK2 | 0.6277 | 0.59991 | -0.027788 |  | 0.9 | 1.05 | 0.18025 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-SHATTUCK2 | 0.6277 | 0.59991 | -0.027788 |  | 0.9 | 1.05 | 0.19087 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-SHATTUCK2 | 0.6277 | 0.59991 | -0.027788 |  | 0.9 | 1.05 | 0.19118 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-SHATTUCK2 | 0.6277 | 0.59991 | -0.027788 |  | 0.9 | 1.05 | 0.18842 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-SHATTUCK2 | 0.6277 | 0.59991 | -0.027788 |  | 0.9 | 1.05 | 0.18906 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-SHATTUCK2 | 0.6277 | 0.59991 | -0.027788 |  | 0.9 | 1.05 | 0.19024 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-SHATTUCK2 | 0.6277 | 0.59991 | -0.027788 |  | 0.9 | 1.05 | 0.17773 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-SHATTUCK2 | 0.6277 | 0.59991 | -0.027788 |  | 0.9 | 1.05 | 0.17773 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-SHATTUCK2 | 0.6277 | 0.59991 | -0.027788 |  | 0.9 | 1.05 | 0.18569 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-SHATTUCK2 | 0.6277 | 0.59991 | -0.027788 |  | 0.9 | 1.05 | 0.18569 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-SHATTUCK2 | 0.6277 | 0.59991 | -0.027788 |  | 0.9 | 1.05 | 0.49024 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-SHATTUCK2 | 0.6277 | 0.59991 | -0.027788 |  | 0.9 | 1.05 | 0.19283 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-SHATTUCK2 | 0.62766 | 0.59996 | -0.027697 |  | 0.9 | 1.05 | 0.079811 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-SHATTUCK2 | 0.62766 | 0.59996 | -0.027697 |  | 0.9 | 1.05 | 0.19454 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-SHATTUCK2 | 0.62766 | 0.59996 | -0.027697 |  | 0.9 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-SHATTUCK2 | 0.62766 | 0.59996 | -0.027697 |  | 0.9 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-SHATTUCK2 | 0.62766 | 0.59996 | -0.027697 |  | 0.9 | 1.05 | 0.17748 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-SHATTUCK2 | 0.62766 | 0.59996 | -0.027697 |  | 0.9 | 1.05 | 0.1726 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-SHATTUCK2 | 0.62766 | 0.59996 | -0.027697 |  | 0.9 | 1.05 | 0.17544 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-SHATTUCK2 | 0.62766 | 0.59996 | -0.027697 |  | 0.9 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-SHATTUCK2 | 0.62766 | 0.59996 | -0.027697 |  | 0.9 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-SHATTUCK2 | 0.62766 | 0.59996 | -0.027697 |  | 0.9 | 1.05 | 0.17987 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-SHATTUCK2 | 0.62766 | 0.59996 | -0.027697 |  | 0.9 | 1.05 | 0.18025 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-SHATTUCK2 | 0.62766 | 0.59996 | -0.027697 |  | 0.9 | 1.05 | 0.19087 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-SHATTUCK2 | 0.62766 | 0.59996 | -0.027697 |  | 0.9 | 1.05 | 0.19118 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-SHATTUCK2 | 0.62766 | 0.59996 | -0.027697 |  | 0.9 | 1.05 | 0.18842 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-SHATTUCK2 | 0.62766 | 0.59996 | -0.027697 |  | 0.9 | 1.05 | 0.18906 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-SHATTUCK2 | 0.62766 | 0.59996 | -0.027697 |  | 0.9 | 1.05 | 0.19024 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-SHATTUCK2 | 0.62766 | 0.59996 | -0.027697 |  | 0.9 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-SHATTUCK2 | 0.62766 | 0.59996 | -0.027697 |  | 0.9 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-SHATTUCK2 | 0.62766 | 0.59996 | -0.027697 |  | 0.9 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-SHATTUCK2 | 0.62766 | 0.59996 | -0.027697 |  | 0.9 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-SHATTUCK2 | 0.62766 | 0.59996 | -0.027697 |  | 0.9 | 1.05 | 0.49024 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-SHATTUCK2 | 0.62766 | 0.59996 | -0.027697 |  | 0.9 | 1.05 | 0.19283 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-SHATTUCK2 | 0.62776 | 0.59997 | -0.027794 |  | 0.9 | 1.05 | 0.079811 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-SHATTUCK2 | 0.62776 | 0.59997 | -0.027794 |  | 0.9 | 1.05 | 0.19454 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-SHATTUCK2 | 0.62776 | 0.59997 | -0.027794 |  | 0.9 | 1.05 | 0.23657 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-SHATTUCK2 | 0.62776 | 0.59997 | -0.027794 |  | 0.9 | 1.05 | 0.23657 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-SHATTUCK2 | 0.62776 | 0.59997 | -0.027794 |  | 0.9 | 1.05 | 0.17748 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-SHATTUCK2 | 0.62776 | 0.59997 | -0.027794 |  | 0.9 | 1.05 | 0.1726 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-SHATTUCK2 | 0.62776 | 0.59997 | -0.027794 |  | 0.9 | 1.05 | 0.17544 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-SHATTUCK2 | 0.62776 | 0.59997 | -0.027794 |  | 0.9 | 1.05 | 0.12267 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-SHATTUCK2 | 0.62776 | 0.59997 | -0.027794 |  | 0.9 | 1.05 | 0.12267 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-SHATTUCK2 | 0.62776 | 0.59997 | -0.027794 |  | 0.9 | 1.05 | 0.17987 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-SHATTUCK2 | 0.62776 | 0.59997 | -0.027794 |  | 0.9 | 1.05 | 0.18025 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-SHATTUCK2 | 0.62776 | 0.59997 | -0.027794 |  | 0.9 | 1.05 | 0.19087 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-SHATTUCK2 | 0.62776 | 0.59997 | -0.027794 |  | 0.9 | 1.05 | 0.19118 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-SHATTUCK2 | 0.62776 | 0.59997 | -0.027794 |  | 0.9 | 1.05 | 0.18842 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-SHATTUCK2 | 0.62776 | 0.59997 | -0.027794 |  | 0.9 | 1.05 | 0.18906 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-SHATTUCK2 | 0.62776 | 0.59997 | -0.027794 |  | 0.9 | 1.05 | 0.19024 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-SHATTUCK2 | 0.62776 | 0.59997 | -0.027794 |  | 0.9 | 1.05 | 0.17773 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-SHATTUCK2 | 0.62776 | 0.59997 | -0.027794 |  | 0.9 | 1.05 | 0.17773 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-SHATTUCK2 | 0.62776 | 0.59997 | -0.027794 |  | 0.9 | 1.05 | 0.18569 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-SHATTUCK2 | 0.62776 | 0.59997 | -0.027794 |  | 0.9 | 1.05 | 0.18569 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-SHATTUCK2 | 0.62776 | 0.59997 | -0.027794 |  | 0.9 | 1.05 | 0.49024 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-SHATTUCK2 | 0.62776 | 0.59997 | -0.027794 |  | 0.9 | 1.05 | 0.19283 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-SUB_A 2 | 0.85401 | 0.83284 | -0.021179 |  | 0.9 | 1.05 | 0.079811 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-SUB_A 2 | 0.85401 | 0.83284 | -0.021179 |  | 0.9 | 1.05 | 0.19454 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-SUB_A 2 | 0.85401 | 0.83284 | -0.021179 |  | 0.9 | 1.05 | 0.23657 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-SUB_A 2 | 0.85401 | 0.83284 | -0.021179 |  | 0.9 | 1.05 | 0.23657 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-SUB_A 2 | 0.85401 | 0.83284 | -0.021179 |  | 0.9 | 1.05 | 0.17748 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-SUB_A 2 | 0.85401 | 0.83284 | -0.021179 |  | 0.9 | 1.05 | 0.1726 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-SUB_A 2 | 0.85401 | 0.83284 | -0.021179 |  | 0.9 | 1.05 | 0.17544 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-SUB_A 2 | 0.85401 | 0.83284 | -0.021179 |  | 0.9 | 1.05 | 0.12267 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-SUB_A 2 | 0.85401 | 0.83284 | -0.021179 |  | 0.9 | 1.05 | 0.12267 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-SUB_A 2 | 0.85401 | 0.83284 | -0.021179 |  | 0.9 | 1.05 | 0.17987 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-SUB_A 2 | 0.85401 | 0.83284 | -0.021179 |  | 0.9 | 1.05 | 0.18025 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-SUB_A 2 | 0.85401 | 0.83284 | -0.021179 |  | 0.9 | 1.05 | 0.19087 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-SUB_A 2 | 0.85401 | 0.83284 | -0.021179 |  | 0.9 | 1.05 | 0.19118 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-SUB_A 2 | 0.85401 | 0.83284 | -0.021179 |  | 0.9 | 1.05 | 0.18842 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-SUB_A 2 | 0.85401 | 0.83284 | -0.021179 |  | 0.9 | 1.05 | 0.18906 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-SUB_A 2 | 0.85401 | 0.83284 | -0.021179 |  | 0.9 | 1.05 | 0.19024 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-SUB_A 2 | 0.85401 | 0.83284 | -0.021179 |  | 0.9 | 1.05 | 0.17773 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-SUB_A 2 | 0.85401 | 0.83284 | -0.021179 |  | 0.9 | 1.05 | 0.17773 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-SUB_A 2 | 0.85401 | 0.83284 | -0.021179 |  | 0.9 | 1.05 | 0.18569 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-SUB_A 2 | 0.85401 | 0.83284 | -0.021179 |  | 0.9 | 1.05 | 0.18569 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-SUB_A 2 | 0.85401 | 0.83284 | -0.021179 |  | 0.9 | 1.05 | 0.49024 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-SUB_A 2 | 0.85401 | 0.83284 | -0.021179 |  | 0.9 | 1.05 | 0.19283 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-SUB_A 2 | 0.85157 | 0.82771 | -0.023857 |  | 0.9 | 1.05 | 0.079811 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-SUB_A 2 | 0.85157 | 0.82771 | -0.023857 |  | 0.9 | 1.05 | 0.19454 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-SUB_A 2 | 0.85157 | 0.82771 | -0.023857 |  | 0.9 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-SUB_A 2 | 0.85157 | 0.82771 | -0.023857 |  | 0.9 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-SUB_A 2 | 0.85157 | 0.82771 | -0.023857 |  | 0.9 | 1.05 | 0.17748 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-SUB_A 2 | 0.85157 | 0.82771 | -0.023857 |  | 0.9 | 1.05 | 0.1726 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-SUB_A 2 | 0.85157 | 0.82771 | -0.023857 |  | 0.9 | 1.05 | 0.17544 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-SUB_A 2 | 0.85157 | 0.82771 | -0.023857 |  | 0.9 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-SUB_A 2 | 0.85157 | 0.82771 | -0.023857 |  | 0.9 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-SUB_A 2 | 0.85157 | 0.82771 | -0.023857 |  | 0.9 | 1.05 | 0.17987 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-SUB_A 2 | 0.85157 | 0.82771 | -0.023857 |  | 0.9 | 1.05 | 0.18025 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-SUB_A 2 | 0.85157 | 0.82771 | -0.023857 |  | 0.9 | 1.05 | 0.19087 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-SUB_A 2 | 0.85157 | 0.82771 | -0.023857 |  | 0.9 | 1.05 | 0.19118 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-SUB_A 2 | 0.85157 | 0.82771 | -0.023857 |  | 0.9 | 1.05 | 0.18842 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-SUB_A 2 | 0.85157 | 0.82771 | -0.023857 |  | 0.9 | 1.05 | 0.18906 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-SUB_A 2 | 0.85157 | 0.82771 | -0.023857 |  | 0.9 | 1.05 | 0.19024 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-SUB_A 2 | 0.85157 | 0.82771 | -0.023857 |  | 0.9 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-SUB_A 2 | 0.85157 | 0.82771 | -0.023857 |  | 0.9 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-SUB_A 2 | 0.85157 | 0.82771 | -0.023857 |  | 0.9 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-SUB_A 2 | 0.85157 | 0.82771 | -0.023857 |  | 0.9 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-SUB_A 2 | 0.85157 | 0.82771 | -0.023857 |  | 0.9 | 1.05 | 0.49024 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-SUB_A 2 | 0.85157 | 0.82771 | -0.023857 |  | 0.9 | 1.05 | 0.19283 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-SUB_A 2 | 0.85375 | 0.83251 | -0.021235 |  | 0.9 | 1.05 | 0.079811 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-SUB_A 2 | 0.85375 | 0.83251 | -0.021235 |  | 0.9 | 1.05 | 0.19454 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-SUB_A 2 | 0.85375 | 0.83251 | -0.021235 |  | 0.9 | 1.05 | 0.23657 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-SUB_A 2 | 0.85375 | 0.83251 | -0.021235 |  | 0.9 | 1.05 | 0.23657 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-SUB_A 2 | 0.85375 | 0.83251 | -0.021235 |  | 0.9 | 1.05 | 0.17748 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-SUB_A 2 | 0.85375 | 0.83251 | -0.021235 |  | 0.9 | 1.05 | 0.1726 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-SUB_A 2 | 0.85375 | 0.83251 | -0.021235 |  | 0.9 | 1.05 | 0.17544 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-SUB_A 2 | 0.85375 | 0.83251 | -0.021235 |  | 0.9 | 1.05 | 0.12267 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-SUB_A 2 | 0.85375 | 0.83251 | -0.021235 |  | 0.9 | 1.05 | 0.12267 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-SUB_A 2 | 0.85375 | 0.83251 | -0.021235 |  | 0.9 | 1.05 | 0.17987 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-SUB_A 2 | 0.85375 | 0.83251 | -0.021235 |  | 0.9 | 1.05 | 0.18025 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-SUB_A 2 | 0.85375 | 0.83251 | -0.021235 |  | 0.9 | 1.05 | 0.19087 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-SUB_A 2 | 0.85375 | 0.83251 | -0.021235 |  | 0.9 | 1.05 | 0.19118 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-SUB_A 2 | 0.85375 | 0.83251 | -0.021235 |  | 0.9 | 1.05 | 0.18842 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-SUB_A 2 | 0.85375 | 0.83251 | -0.021235 |  | 0.9 | 1.05 | 0.18906 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-SUB_A 2 | 0.85375 | 0.83251 | -0.021235 |  | 0.9 | 1.05 | 0.19024 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-SUB_A 2 | 0.85375 | 0.83251 | -0.021235 |  | 0.9 | 1.05 | 0.17773 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-SUB_A 2 | 0.85375 | 0.83251 | -0.021235 |  | 0.9 | 1.05 | 0.17773 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-SUB_A 2 | 0.85375 | 0.83251 | -0.021235 |  | 0.9 | 1.05 | 0.18569 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-SUB_A 2 | 0.85375 | 0.83251 | -0.021235 |  | 0.9 | 1.05 | 0.18569 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-SUB_A 2 | 0.85375 | 0.83251 | -0.021235 |  | 0.9 | 1.05 | 0.49024 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-SUB_A 2 | 0.85375 | 0.83251 | -0.021235 |  | 0.9 | 1.05 | 0.19283 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-SUB_A 2 | 0.85371 | 0.83255 | -0.021165 |  | 0.9 | 1.05 | 0.079811 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-SUB_A 2 | 0.85371 | 0.83255 | -0.021165 |  | 0.9 | 1.05 | 0.19454 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-SUB_A 2 | 0.85371 | 0.83255 | -0.021165 |  | 0.9 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-SUB_A 2 | 0.85371 | 0.83255 | -0.021165 |  | 0.9 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-SUB_A 2 | 0.85371 | 0.83255 | -0.021165 |  | 0.9 | 1.05 | 0.17748 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-SUB_A 2 | 0.85371 | 0.83255 | -0.021165 |  | 0.9 | 1.05 | 0.1726 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-SUB_A 2 | 0.85371 | 0.83255 | -0.021165 |  | 0.9 | 1.05 | 0.17544 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-SUB_A 2 | 0.85371 | 0.83255 | -0.021165 |  | 0.9 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-SUB_A 2 | 0.85371 | 0.83255 | -0.021165 |  | 0.9 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-SUB_A 2 | 0.85371 | 0.83255 | -0.021165 |  | 0.9 | 1.05 | 0.17987 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-SUB_A 2 | 0.85371 | 0.83255 | -0.021165 |  | 0.9 | 1.05 | 0.18025 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-SUB_A 2 | 0.85371 | 0.83255 | -0.021165 |  | 0.9 | 1.05 | 0.19087 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-SUB_A 2 | 0.85371 | 0.83255 | -0.021165 |  | 0.9 | 1.05 | 0.19118 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-SUB_A 2 | 0.85371 | 0.83255 | -0.021165 |  | 0.9 | 1.05 | 0.18842 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-SUB_A 2 | 0.85371 | 0.83255 | -0.021165 |  | 0.9 | 1.05 | 0.18906 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-SUB_A 2 | 0.85371 | 0.83255 | -0.021165 |  | 0.9 | 1.05 | 0.19024 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-SUB_A 2 | 0.85371 | 0.83255 | -0.021165 |  | 0.9 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-SUB_A 2 | 0.85371 | 0.83255 | -0.021165 |  | 0.9 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-SUB_A 2 | 0.85371 | 0.83255 | -0.021165 |  | 0.9 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-SUB_A 2 | 0.85371 | 0.83255 | -0.021165 |  | 0.9 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-SUB_A 2 | 0.85371 | 0.83255 | -0.021165 |  | 0.9 | 1.05 | 0.49024 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-SUB_A 2 | 0.85371 | 0.83255 | -0.021165 |  | 0.9 | 1.05 | 0.19283 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-SUB_A 2 | 0.85379 | 0.83256 | -0.021237 |  | 0.9 | 1.05 | 0.079811 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-SUB_A 2 | 0.85379 | 0.83256 | -0.021237 |  | 0.9 | 1.05 | 0.19454 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-SUB_A 2 | 0.85379 | 0.83256 | -0.021237 |  | 0.9 | 1.05 | 0.23657 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-SUB_A 2 | 0.85379 | 0.83256 | -0.021237 |  | 0.9 | 1.05 | 0.23657 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-SUB_A 2 | 0.85379 | 0.83256 | -0.021237 |  | 0.9 | 1.05 | 0.17748 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-SUB_A 2 | 0.85379 | 0.83256 | -0.021237 |  | 0.9 | 1.05 | 0.1726 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-SUB_A 2 | 0.85379 | 0.83256 | -0.021237 |  | 0.9 | 1.05 | 0.17544 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-SUB_A 2 | 0.85379 | 0.83256 | -0.021237 |  | 0.9 | 1.05 | 0.12267 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-SUB_A 2 | 0.85379 | 0.83256 | -0.021237 |  | 0.9 | 1.05 | 0.12267 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-SUB_A 2 | 0.85379 | 0.83256 | -0.021237 |  | 0.9 | 1.05 | 0.17987 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-SUB_A 2 | 0.85379 | 0.83256 | -0.021237 |  | 0.9 | 1.05 | 0.18025 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-SUB_A 2 | 0.85379 | 0.83256 | -0.021237 |  | 0.9 | 1.05 | 0.19087 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-SUB_A 2 | 0.85379 | 0.83256 | -0.021237 |  | 0.9 | 1.05 | 0.19118 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-SUB_A 2 | 0.85379 | 0.83256 | -0.021237 |  | 0.9 | 1.05 | 0.18842 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-SUB_A 2 | 0.85379 | 0.83256 | -0.021237 |  | 0.9 | 1.05 | 0.18906 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-SUB_A 2 | 0.85379 | 0.83256 | -0.021237 |  | 0.9 | 1.05 | 0.19024 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-SUB_A 2 | 0.85379 | 0.83256 | -0.021237 |  | 0.9 | 1.05 | 0.17773 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-SUB_A 2 | 0.85379 | 0.83256 | -0.021237 |  | 0.9 | 1.05 | 0.17773 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-SUB_A 2 | 0.85379 | 0.83256 | -0.021237 |  | 0.9 | 1.05 | 0.18569 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-SUB_A 2 | 0.85379 | 0.83256 | -0.021237 |  | 0.9 | 1.05 | 0.18569 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-SUB_A 2 | 0.85379 | 0.83256 | -0.021237 |  | 0.9 | 1.05 | 0.49024 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-SUB_A 2 | 0.85379 | 0.83256 | -0.021237 |  | 0.9 | 1.05 | 0.19283 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-VALERO_P2 | 0.65897 | 0.63195 | -0.027018 |  | 0.9 | 1.05 | 0.079811 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-VALERO_P2 | 0.65897 | 0.63195 | -0.027018 |  | 0.9 | 1.05 | 0.19454 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-VALERO_P2 | 0.65897 | 0.63195 | -0.027018 |  | 0.9 | 1.05 | 0.23657 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-VALERO_P2 | 0.65897 | 0.63195 | -0.027018 |  | 0.9 | 1.05 | 0.23657 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-VALERO_P2 | 0.65897 | 0.63195 | -0.027018 |  | 0.9 | 1.05 | 0.17748 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-VALERO_P2 | 0.65897 | 0.63195 | -0.027018 |  | 0.9 | 1.05 | 0.1726 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-VALERO_P2 | 0.65897 | 0.63195 | -0.027018 |  | 0.9 | 1.05 | 0.17544 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-VALERO_P2 | 0.65897 | 0.63195 | -0.027018 |  | 0.9 | 1.05 | 0.12267 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-VALERO_P2 | 0.65897 | 0.63195 | -0.027018 |  | 0.9 | 1.05 | 0.12267 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-VALERO_P2 | 0.65897 | 0.63195 | -0.027018 |  | 0.9 | 1.05 | 0.17987 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-VALERO_P2 | 0.65897 | 0.63195 | -0.027018 |  | 0.9 | 1.05 | 0.18025 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-VALERO_P2 | 0.65897 | 0.63195 | -0.027018 |  | 0.9 | 1.05 | 0.19087 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-VALERO_P2 | 0.65897 | 0.63195 | -0.027018 |  | 0.9 | 1.05 | 0.19118 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-VALERO_P2 | 0.65897 | 0.63195 | -0.027018 |  | 0.9 | 1.05 | 0.18842 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-VALERO_P2 | 0.65897 | 0.63195 | -0.027018 |  | 0.9 | 1.05 | 0.18906 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-VALERO_P2 | 0.65897 | 0.63195 | -0.027018 |  | 0.9 | 1.05 | 0.19024 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-VALERO_P2 | 0.65897 | 0.63195 | -0.027018 |  | 0.9 | 1.05 | 0.17773 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-VALERO_P2 | 0.65897 | 0.63195 | -0.027018 |  | 0.9 | 1.05 | 0.17773 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-VALERO_P2 | 0.65897 | 0.63195 | -0.027018 |  | 0.9 | 1.05 | 0.18569 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-VALERO_P2 | 0.65897 | 0.63195 | -0.027018 |  | 0.9 | 1.05 | 0.18569 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-VALERO_P2 | 0.65897 | 0.63195 | -0.027018 |  | 0.9 | 1.05 | 0.49024 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-VALERO_P2 | 0.65897 | 0.63195 | -0.027018 |  | 0.9 | 1.05 | 0.19283 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-VALERO_P2 | 0.65579 | 0.62558 | -0.030213 |  | 0.9 | 1.05 | 0.079811 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-VALERO_P2 | 0.65579 | 0.62558 | -0.030213 |  | 0.9 | 1.05 | 0.19454 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-VALERO_P2 | 0.65579 | 0.62558 | -0.030213 |  | 0.9 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-VALERO_P2 | 0.65579 | 0.62558 | -0.030213 |  | 0.9 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-VALERO_P2 | 0.65579 | 0.62558 | -0.030213 |  | 0.9 | 1.05 | 0.17748 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-VALERO_P2 | 0.65579 | 0.62558 | -0.030213 |  | 0.9 | 1.05 | 0.1726 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-VALERO_P2 | 0.65579 | 0.62558 | -0.030213 |  | 0.9 | 1.05 | 0.17544 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-VALERO_P2 | 0.65579 | 0.62558 | -0.030213 |  | 0.9 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-VALERO_P2 | 0.65579 | 0.62558 | -0.030213 |  | 0.9 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-VALERO_P2 | 0.65579 | 0.62558 | -0.030213 |  | 0.9 | 1.05 | 0.17987 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-VALERO_P2 | 0.65579 | 0.62558 | -0.030213 |  | 0.9 | 1.05 | 0.18025 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-VALERO_P2 | 0.65579 | 0.62558 | -0.030213 |  | 0.9 | 1.05 | 0.19087 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-VALERO_P2 | 0.65579 | 0.62558 | -0.030213 |  | 0.9 | 1.05 | 0.19118 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-VALERO_P2 | 0.65579 | 0.62558 | -0.030213 |  | 0.9 | 1.05 | 0.18842 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-VALERO_P2 | 0.65579 | 0.62558 | -0.030213 |  | 0.9 | 1.05 | 0.18906 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-VALERO_P2 | 0.65579 | 0.62558 | -0.030213 |  | 0.9 | 1.05 | 0.19024 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-VALERO_P2 | 0.65579 | 0.62558 | -0.030213 |  | 0.9 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-VALERO_P2 | 0.65579 | 0.62558 | -0.030213 |  | 0.9 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-VALERO_P2 | 0.65579 | 0.62558 | -0.030213 |  | 0.9 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-VALERO_P2 | 0.65579 | 0.62558 | -0.030213 |  | 0.9 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-VALERO_P2 | 0.65579 | 0.62558 | -0.030213 |  | 0.9 | 1.05 | 0.49024 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-VALERO_P2 | 0.65579 | 0.62558 | -0.030213 |  | 0.9 | 1.05 | 0.19283 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-VALERO_P2 | 0.65862 | 0.63155 | -0.027073 |  | 0.9 | 1.05 | 0.079811 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-VALERO_P2 | 0.65862 | 0.63155 | -0.027073 |  | 0.9 | 1.05 | 0.19454 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-VALERO_P2 | 0.65862 | 0.63155 | -0.027073 |  | 0.9 | 1.05 | 0.23657 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-VALERO_P2 | 0.65862 | 0.63155 | -0.027073 |  | 0.9 | 1.05 | 0.23657 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-VALERO_P2 | 0.65862 | 0.63155 | -0.027073 |  | 0.9 | 1.05 | 0.17748 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-VALERO_P2 | 0.65862 | 0.63155 | -0.027073 |  | 0.9 | 1.05 | 0.1726 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-VALERO_P2 | 0.65862 | 0.63155 | -0.027073 |  | 0.9 | 1.05 | 0.17544 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-VALERO_P2 | 0.65862 | 0.63155 | -0.027073 |  | 0.9 | 1.05 | 0.12267 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-VALERO_P2 | 0.65862 | 0.63155 | -0.027073 |  | 0.9 | 1.05 | 0.12267 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-VALERO_P2 | 0.65862 | 0.63155 | -0.027073 |  | 0.9 | 1.05 | 0.17987 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-VALERO_P2 | 0.65862 | 0.63155 | -0.027073 |  | 0.9 | 1.05 | 0.18025 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-VALERO_P2 | 0.65862 | 0.63155 | -0.027073 |  | 0.9 | 1.05 | 0.19087 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-VALERO_P2 | 0.65862 | 0.63155 | -0.027073 |  | 0.9 | 1.05 | 0.19118 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-VALERO_P2 | 0.65862 | 0.63155 | -0.027073 |  | 0.9 | 1.05 | 0.18842 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-VALERO_P2 | 0.65862 | 0.63155 | -0.027073 |  | 0.9 | 1.05 | 0.18906 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-VALERO_P2 | 0.65862 | 0.63155 | -0.027073 |  | 0.9 | 1.05 | 0.19024 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-VALERO_P2 | 0.65862 | 0.63155 | -0.027073 |  | 0.9 | 1.05 | 0.17773 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-VALERO_P2 | 0.65862 | 0.63155 | -0.027073 |  | 0.9 | 1.05 | 0.17773 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-VALERO_P2 | 0.65862 | 0.63155 | -0.027073 |  | 0.9 | 1.05 | 0.18569 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-VALERO_P2 | 0.65862 | 0.63155 | -0.027073 |  | 0.9 | 1.05 | 0.18569 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-VALERO_P2 | 0.65862 | 0.63155 | -0.027073 |  | 0.9 | 1.05 | 0.49024 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-VALERO_P2 | 0.65862 | 0.63155 | -0.027073 |  | 0.9 | 1.05 | 0.19283 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-VALERO_P2 | 0.65858 | 0.6316 | -0.026985 |  | 0.9 | 1.05 | 0.079811 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-VALERO_P2 | 0.65858 | 0.6316 | -0.026985 |  | 0.9 | 1.05 | 0.19454 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-VALERO_P2 | 0.65858 | 0.6316 | -0.026985 |  | 0.9 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-VALERO_P2 | 0.65858 | 0.6316 | -0.026985 |  | 0.9 | 1.05 | 0.23657 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-VALERO_P2 | 0.65858 | 0.6316 | -0.026985 |  | 0.9 | 1.05 | 0.17748 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-VALERO_P2 | 0.65858 | 0.6316 | -0.026985 |  | 0.9 | 1.05 | 0.1726 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-VALERO_P2 | 0.65858 | 0.6316 | -0.026985 |  | 0.9 | 1.05 | 0.17544 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-VALERO_P2 | 0.65858 | 0.6316 | -0.026985 |  | 0.9 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-VALERO_P2 | 0.65858 | 0.6316 | -0.026985 |  | 0.9 | 1.05 | 0.12267 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-VALERO_P2 | 0.65858 | 0.6316 | -0.026985 |  | 0.9 | 1.05 | 0.17987 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-VALERO_P2 | 0.65858 | 0.6316 | -0.026985 |  | 0.9 | 1.05 | 0.18025 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-VALERO_P2 | 0.65858 | 0.6316 | -0.026985 |  | 0.9 | 1.05 | 0.19087 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-VALERO_P2 | 0.65858 | 0.6316 | -0.026985 |  | 0.9 | 1.05 | 0.19118 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-VALERO_P2 | 0.65858 | 0.6316 | -0.026985 |  | 0.9 | 1.05 | 0.18842 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-VALERO_P2 | 0.65858 | 0.6316 | -0.026985 |  | 0.9 | 1.05 | 0.18906 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-VALERO_P2 | 0.65858 | 0.6316 | -0.026985 |  | 0.9 | 1.05 | 0.19024 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-VALERO_P2 | 0.65858 | 0.6316 | -0.026985 |  | 0.9 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-VALERO_P2 | 0.65858 | 0.6316 | -0.026985 |  | 0.9 | 1.05 | 0.17773 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-VALERO_P2 | 0.65858 | 0.6316 | -0.026985 |  | 0.9 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-VALERO_P2 | 0.65858 | 0.6316 | -0.026985 |  | 0.9 | 1.05 | 0.18569 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-VALERO_P2 | 0.65858 | 0.6316 | -0.026985 |  | 0.9 | 1.05 | 0.49024 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-VALERO_P2 | 0.65858 | 0.6316 | -0.026985 |  | 0.9 | 1.05 | 0.19283 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | ASGI-2024-002 | NP-VALERO_P2 | 0.65868 | 0.6316 | -0.027079 |  | 0.9 | 1.05 | 0.079811 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-015 | NP-VALERO_P2 | 0.65868 | 0.6316 | -0.027079 |  | 0.9 | 1.05 | 0.19454 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-041 | NP-VALERO_P2 | 0.65868 | 0.6316 | -0.027079 |  | 0.9 | 1.05 | 0.23657 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-042 | NP-VALERO_P2 | 0.65868 | 0.6316 | -0.027079 |  | 0.9 | 1.05 | 0.23657 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-043 | NP-VALERO_P2 | 0.65868 | 0.6316 | -0.027079 |  | 0.9 | 1.05 | 0.17748 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-099 | NP-VALERO_P2 | 0.65868 | 0.6316 | -0.027079 |  | 0.9 | 1.05 | 0.1726 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-109 | NP-VALERO_P2 | 0.65868 | 0.6316 | -0.027079 |  | 0.9 | 1.05 | 0.17544 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-143 | NP-VALERO_P2 | 0.65868 | 0.6316 | -0.027079 |  | 0.9 | 1.05 | 0.12267 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-145 | NP-VALERO_P2 | 0.65868 | 0.6316 | -0.027079 |  | 0.9 | 1.05 | 0.12267 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-159 | NP-VALERO_P2 | 0.65868 | 0.6316 | -0.027079 |  | 0.9 | 1.05 | 0.17987 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-221 | NP-VALERO_P2 | 0.65868 | 0.6316 | -0.027079 |  | 0.9 | 1.05 | 0.18025 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-261 | NP-VALERO_P2 | 0.65868 | 0.6316 | -0.027079 |  | 0.9 | 1.05 | 0.19087 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-265 | NP-VALERO_P2 | 0.65868 | 0.6316 | -0.027079 |  | 0.9 | 1.05 | 0.19118 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-280 | NP-VALERO_P2 | 0.65868 | 0.6316 | -0.027079 |  | 0.9 | 1.05 | 0.18842 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-281 | NP-VALERO_P2 | 0.65868 | 0.6316 | -0.027079 |  | 0.9 | 1.05 | 0.18906 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | NP-VALERO_P2 | 0.65868 | 0.6316 | -0.027079 |  | 0.9 | 1.05 | 0.19024 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-303 | NP-VALERO_P2 | 0.65868 | 0.6316 | -0.027079 |  | 0.9 | 1.05 | 0.17773 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-304 | NP-VALERO_P2 | 0.65868 | 0.6316 | -0.027079 |  | 0.9 | 1.05 | 0.17773 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | NP-VALERO_P2 | 0.65868 | 0.6316 | -0.027079 |  | 0.9 | 1.05 | 0.18569 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | NP-VALERO_P2 | 0.65868 | 0.6316 | -0.027079 |  | 0.9 | 1.05 | 0.18569 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-317 | NP-VALERO_P2 | 0.65868 | 0.6316 | -0.027079 |  | 0.9 | 1.05 | 0.49024 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-336 | NP-VALERO_P2 | 0.65868 | 0.6316 | -0.027079 |  | 0.9 | 1.05 | 0.19283 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | SENDERO +3 | 0.89506 | 0.84743 | -0.047632 |  | 0.9 | 1.05 | 0.12999 | Single 528182 NORTH_LOVNG3 115 528193 BLACKRIVER3 115 1 | Add 69 MVAR switched shunt at SENDERO +3 115 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-295 | SENDERO +3 | 0.89986 | 0.84932 | -0.050542 |  | 0.9 | 1.05 | 1 | P12:115:SPS:U27.1.NLVNG.MLGBND:::HV: | Add 69 MVAR switched shunt at SENDERO +3 115 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-310 | SENDERO +3 | 0.89986 | 0.84932 | -0.050542 |  | 0.9 | 1.05 | 0.044108 | P12:115:SPS:U27.1.NLVNG.MLGBND:::HV: | Add 69 MVAR switched shunt at SENDERO +3 115 kV
Voltage | 05ALL | 2 | 29SP | V | GEN-2024-311 | SENDERO +3 | 0.89986 | 0.84932 | -0.050542 |  | 0.9 | 1.05 | 0.044108 | P12:115:SPS:U27.1.NLVNG.MLGBND:::HV: | Add 69 MVAR switched shunt at SENDERO +3 115 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-081 | BELFELD3 | 1.0297 | 1.0508 | 0.02105 |  | 0.9 | 1.05 | 0.041139 | 259626 | None
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-082 | BELFELD3 | 1.0297 | 1.0508 | 0.02105 |  | 0.9 | 1.05 | 0.041139 | 259626 | None
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-081 | BELFELD3 | 1.03 | 1.0511 | 0.021094 |  | 0.9 | 1.05 | 0.041139 | 259690 | None
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-082 | BELFELD3 | 1.03 | 1.0511 | 0.021094 |  | 0.9 | 1.05 | 0.041139 | 259690 | None
Voltage | 00ALL | 2 | 29WP | V | ASGI-2024-001 | FINNEY 7 | 1.0747 | 1.0985 | 0.023794 |  | 0.9 | 1.05 | 0.035469 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | ASGI-2024-020 | FINNEY 7 | 1.0747 | 1.0985 | 0.023794 |  | 0.9 | 1.05 | 0.033479 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-017 | FINNEY 7 | 1.0747 | 1.0985 | 0.023794 |  | 0.9 | 1.05 | 0.045853 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-018 | FINNEY 7 | 1.0747 | 1.0985 | 0.023794 |  | 0.9 | 1.05 | 0.045939 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-019 | FINNEY 7 | 1.0747 | 1.0985 | 0.023794 |  | 0.9 | 1.05 | 0.045939 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-020 | FINNEY 7 | 1.0747 | 1.0985 | 0.023794 |  | 0.9 | 1.05 | 0.045853 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-021 | FINNEY 7 | 1.0747 | 1.0985 | 0.023794 |  | 0.9 | 1.05 | 0.045853 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-022 | FINNEY 7 | 1.0747 | 1.0985 | 0.023794 |  | 0.9 | 1.05 | 0.045939 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-023 | FINNEY 7 | 1.0747 | 1.0985 | 0.023794 |  | 0.9 | 1.05 | 0.045939 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-081 | FINNEY 7 | 1.0747 | 1.0985 | 0.023794 |  | 0.9 | 1.05 | 0.052573 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-082 | FINNEY 7 | 1.0747 | 1.0985 | 0.023794 |  | 0.9 | 1.05 | 0.052573 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-211 | FINNEY 7 | 1.0747 | 1.0985 | 0.023794 |  | 0.9 | 1.05 | 0.039907 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-212 | FINNEY 7 | 1.0747 | 1.0985 | 0.023794 |  | 0.9 | 1.05 | 0.039907 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-213 | FINNEY 7 | 1.0747 | 1.0985 | 0.023794 |  | 0.9 | 1.05 | 0.039907 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | ASGI-2024-001 | FINNEY 7 | 1.0761 | 1.0985 | 0.022414 |  | 0.9 | 1.05 | 0.035469 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | ASGI-2024-020 | FINNEY 7 | 1.0761 | 1.0985 | 0.022414 |  | 0.9 | 1.05 | 0.057103 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-017 | FINNEY 7 | 1.0761 | 1.0985 | 0.022414 |  | 0.9 | 1.05 | 0.045853 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-018 | FINNEY 7 | 1.0761 | 1.0985 | 0.022414 |  | 0.9 | 1.05 | 0.045939 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-019 | FINNEY 7 | 1.0761 | 1.0985 | 0.022414 |  | 0.9 | 1.05 | 0.045939 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-020 | FINNEY 7 | 1.0761 | 1.0985 | 0.022414 |  | 0.9 | 1.05 | 0.045853 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-021 | FINNEY 7 | 1.0761 | 1.0985 | 0.022414 |  | 0.9 | 1.05 | 0.045853 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-022 | FINNEY 7 | 1.0761 | 1.0985 | 0.022414 |  | 0.9 | 1.05 | 0.045939 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-023 | FINNEY 7 | 1.0761 | 1.0985 | 0.022414 |  | 0.9 | 1.05 | 0.045939 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-081 | FINNEY 7 | 1.0761 | 1.0985 | 0.022414 |  | 0.9 | 1.05 | 0.052573 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-082 | FINNEY 7 | 1.0761 | 1.0985 | 0.022414 |  | 0.9 | 1.05 | 0.052573 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-129 | FINNEY 7 | 1.0761 | 1.0985 | 0.022414 |  | 0.9 | 1.05 | 0.035167 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-211 | FINNEY 7 | 1.0761 | 1.0985 | 0.022414 |  | 0.9 | 1.05 | 0.039907 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-212 | FINNEY 7 | 1.0761 | 1.0985 | 0.022414 |  | 0.9 | 1.05 | 0.039907 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-213 | FINNEY 7 | 1.0761 | 1.0985 | 0.022414 |  | 0.9 | 1.05 | 0.039907 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-249 | FINNEY 7 | 1.0761 | 1.0985 | 0.022414 |  | 0.9 | 1.05 | 0.033058 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-334 | FINNEY 7 | 1.0761 | 1.0985 | 0.022414 |  | 0.9 | 1.05 | 0.034011 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | ASGI-2024-001 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.035469 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | ASGI-2024-020 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.033479 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-017 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.045853 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-018 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.045939 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-019 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.045939 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-020 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.045853 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-021 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.045853 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-022 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.045939 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-023 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.045939 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-081 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.052573 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-082 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.052573 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-211 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.039907 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-212 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.039907 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-213 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.039907 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | ASGI-2024-001 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.035469 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | ASGI-2024-020 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.033479 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-017 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.045853 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-018 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.045939 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-019 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.045939 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-020 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.045853 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-021 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.045853 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-022 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.045939 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-023 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.045939 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-081 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.052573 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-082 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.052573 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-211 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.039907 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-212 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.039907 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-213 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.039907 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | ASGI-2024-001 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.035469 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | ASGI-2024-020 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.033479 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-017 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.045853 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-018 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.045939 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-019 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.045939 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-020 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.045853 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-021 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.045853 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-022 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.045939 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-023 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.045939 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-081 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.052573 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-082 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.052573 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-211 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.039907 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-212 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.039907 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-213 | FINNEY 7 | 1.0748 | 1.0983 | 0.023484 |  | 0.9 | 1.05 | 0.039907 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | ASGI-2024-001 | G23-015-TAP | 1.0716 | 1.0953 | 0.023667 |  | 0.9 | 1.05 | 0.035469 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | ASGI-2024-020 | G23-015-TAP | 1.0716 | 1.0953 | 0.023667 |  | 0.9 | 1.05 | 0.033479 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-017 | G23-015-TAP | 1.0716 | 1.0953 | 0.023667 |  | 0.9 | 1.05 | 0.045853 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-018 | G23-015-TAP | 1.0716 | 1.0953 | 0.023667 |  | 0.9 | 1.05 | 0.045939 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-019 | G23-015-TAP | 1.0716 | 1.0953 | 0.023667 |  | 0.9 | 1.05 | 0.045939 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-020 | G23-015-TAP | 1.0716 | 1.0953 | 0.023667 |  | 0.9 | 1.05 | 0.045853 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-021 | G23-015-TAP | 1.0716 | 1.0953 | 0.023667 |  | 0.9 | 1.05 | 0.045853 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-022 | G23-015-TAP | 1.0716 | 1.0953 | 0.023667 |  | 0.9 | 1.05 | 0.045939 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-023 | G23-015-TAP | 1.0716 | 1.0953 | 0.023667 |  | 0.9 | 1.05 | 0.045939 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-081 | G23-015-TAP | 1.0716 | 1.0953 | 0.023667 |  | 0.9 | 1.05 | 0.052573 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-082 | G23-015-TAP | 1.0716 | 1.0953 | 0.023667 |  | 0.9 | 1.05 | 0.052573 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-211 | G23-015-TAP | 1.0716 | 1.0953 | 0.023667 |  | 0.9 | 1.05 | 0.039907 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-212 | G23-015-TAP | 1.0716 | 1.0953 | 0.023667 |  | 0.9 | 1.05 | 0.039907 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-213 | G23-015-TAP | 1.0716 | 1.0953 | 0.023667 |  | 0.9 | 1.05 | 0.039907 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | ASGI-2024-001 | G23-015-TAP | 1.073 | 1.0953 | 0.02229 |  | 0.9 | 1.05 | 0.035469 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | ASGI-2024-020 | G23-015-TAP | 1.073 | 1.0953 | 0.02229 |  | 0.9 | 1.05 | 0.057103 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-017 | G23-015-TAP | 1.073 | 1.0953 | 0.02229 |  | 0.9 | 1.05 | 0.045853 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-018 | G23-015-TAP | 1.073 | 1.0953 | 0.02229 |  | 0.9 | 1.05 | 0.045939 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-019 | G23-015-TAP | 1.073 | 1.0953 | 0.02229 |  | 0.9 | 1.05 | 0.045939 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-020 | G23-015-TAP | 1.073 | 1.0953 | 0.02229 |  | 0.9 | 1.05 | 0.045853 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-021 | G23-015-TAP | 1.073 | 1.0953 | 0.02229 |  | 0.9 | 1.05 | 0.045853 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-022 | G23-015-TAP | 1.073 | 1.0953 | 0.02229 |  | 0.9 | 1.05 | 0.045939 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-023 | G23-015-TAP | 1.073 | 1.0953 | 0.02229 |  | 0.9 | 1.05 | 0.045939 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-081 | G23-015-TAP | 1.073 | 1.0953 | 0.02229 |  | 0.9 | 1.05 | 0.052573 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-082 | G23-015-TAP | 1.073 | 1.0953 | 0.02229 |  | 0.9 | 1.05 | 0.052573 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-129 | G23-015-TAP | 1.073 | 1.0953 | 0.02229 |  | 0.9 | 1.05 | 0.035167 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-211 | G23-015-TAP | 1.073 | 1.0953 | 0.02229 |  | 0.9 | 1.05 | 0.039907 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-212 | G23-015-TAP | 1.073 | 1.0953 | 0.02229 |  | 0.9 | 1.05 | 0.039907 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-213 | G23-015-TAP | 1.073 | 1.0953 | 0.02229 |  | 0.9 | 1.05 | 0.039907 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-249 | G23-015-TAP | 1.073 | 1.0953 | 0.02229 |  | 0.9 | 1.05 | 0.033058 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-334 | G23-015-TAP | 1.073 | 1.0953 | 0.02229 |  | 0.9 | 1.05 | 0.034011 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | ASGI-2024-001 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.035469 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | ASGI-2024-020 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.033479 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-017 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045853 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-018 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045939 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-019 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045939 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-020 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045853 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-021 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045853 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-022 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045939 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-023 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045939 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-081 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.052573 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-082 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.052573 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-211 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.039907 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-212 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.039907 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-213 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.039907 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | ASGI-2024-001 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.035469 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | ASGI-2024-020 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.033479 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-017 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045853 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-018 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045939 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-019 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045939 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-020 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045853 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-021 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045853 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-022 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045939 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-023 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045939 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-081 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.052573 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-082 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.052573 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-211 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.039907 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-212 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.039907 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-213 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.039907 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | ASGI-2024-001 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.035469 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | ASGI-2024-020 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.033479 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-017 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045853 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-018 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045939 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-019 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045939 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-020 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045853 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-021 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045853 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-022 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045939 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-023 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045939 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-081 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.052573 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-082 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.052573 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-211 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.039907 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-212 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.039907 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-213 | G23-015-TAP | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.039907 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-081 | GEN-2017-214 | 1.025 | 1.0513 | 0.026334 |  | 0.9 | 1.05 | 0.031793 | P13:230-115.0:UMZ:# N-1 #:: 3WND LOGAN___-BE4-LOGAN___-BE7-LGN.KW1A-BE9-1 KW1A:HV: | Add 0.02 MVAR switched shunt at GEN-2017-214 230 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-082 | GEN-2017-214 | 1.025 | 1.0513 | 0.026334 |  | 0.9 | 1.05 | 0.031793 | P13:230-115.0:UMZ:# N-1 #:: 3WND LOGAN___-BE4-LOGAN___-BE7-LGN.KW1A-BE9-1 KW1A:HV: | Add 0.02 MVAR switched shunt at GEN-2017-214 230 kV
Voltage | 00ALL | 2 | 29WP | V | ASGI-2024-001 | GEN-2023-015 | 1.0716 | 1.0953 | 0.023667 |  | 0.9 | 1.05 | 0.035469 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | ASGI-2024-020 | GEN-2023-015 | 1.0716 | 1.0953 | 0.023667 |  | 0.9 | 1.05 | 0.033479 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-017 | GEN-2023-015 | 1.0716 | 1.0953 | 0.023667 |  | 0.9 | 1.05 | 0.045853 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-018 | GEN-2023-015 | 1.0716 | 1.0953 | 0.023667 |  | 0.9 | 1.05 | 0.045939 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-019 | GEN-2023-015 | 1.0716 | 1.0953 | 0.023667 |  | 0.9 | 1.05 | 0.045939 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-020 | GEN-2023-015 | 1.0716 | 1.0953 | 0.023667 |  | 0.9 | 1.05 | 0.045853 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-021 | GEN-2023-015 | 1.0716 | 1.0953 | 0.023667 |  | 0.9 | 1.05 | 0.045853 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-022 | GEN-2023-015 | 1.0716 | 1.0953 | 0.023667 |  | 0.9 | 1.05 | 0.045939 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-023 | GEN-2023-015 | 1.0716 | 1.0953 | 0.023667 |  | 0.9 | 1.05 | 0.045939 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-081 | GEN-2023-015 | 1.0716 | 1.0953 | 0.023667 |  | 0.9 | 1.05 | 0.052573 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-082 | GEN-2023-015 | 1.0716 | 1.0953 | 0.023667 |  | 0.9 | 1.05 | 0.052573 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-211 | GEN-2023-015 | 1.0716 | 1.0953 | 0.023667 |  | 0.9 | 1.05 | 0.039907 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-212 | GEN-2023-015 | 1.0716 | 1.0953 | 0.023667 |  | 0.9 | 1.05 | 0.039907 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-213 | GEN-2023-015 | 1.0716 | 1.0953 | 0.023667 |  | 0.9 | 1.05 | 0.039907 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | ASGI-2024-001 | GEN-2023-015 | 1.073 | 1.0953 | 0.02229 |  | 0.9 | 1.05 | 0.035469 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | ASGI-2024-020 | GEN-2023-015 | 1.073 | 1.0953 | 0.02229 |  | 0.9 | 1.05 | 0.057103 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-017 | GEN-2023-015 | 1.073 | 1.0953 | 0.02229 |  | 0.9 | 1.05 | 0.045853 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-018 | GEN-2023-015 | 1.073 | 1.0953 | 0.02229 |  | 0.9 | 1.05 | 0.045939 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-019 | GEN-2023-015 | 1.073 | 1.0953 | 0.02229 |  | 0.9 | 1.05 | 0.045939 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-020 | GEN-2023-015 | 1.073 | 1.0953 | 0.02229 |  | 0.9 | 1.05 | 0.045853 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-021 | GEN-2023-015 | 1.073 | 1.0953 | 0.02229 |  | 0.9 | 1.05 | 0.045853 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-022 | GEN-2023-015 | 1.073 | 1.0953 | 0.02229 |  | 0.9 | 1.05 | 0.045939 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-023 | GEN-2023-015 | 1.073 | 1.0953 | 0.02229 |  | 0.9 | 1.05 | 0.045939 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-081 | GEN-2023-015 | 1.073 | 1.0953 | 0.02229 |  | 0.9 | 1.05 | 0.052573 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-082 | GEN-2023-015 | 1.073 | 1.0953 | 0.02229 |  | 0.9 | 1.05 | 0.052573 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-129 | GEN-2023-015 | 1.073 | 1.0953 | 0.02229 |  | 0.9 | 1.05 | 0.035167 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-211 | GEN-2023-015 | 1.073 | 1.0953 | 0.02229 |  | 0.9 | 1.05 | 0.039907 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-212 | GEN-2023-015 | 1.073 | 1.0953 | 0.02229 |  | 0.9 | 1.05 | 0.039907 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-213 | GEN-2023-015 | 1.073 | 1.0953 | 0.02229 |  | 0.9 | 1.05 | 0.039907 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-249 | GEN-2023-015 | 1.073 | 1.0953 | 0.02229 |  | 0.9 | 1.05 | 0.033058 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-334 | GEN-2023-015 | 1.073 | 1.0953 | 0.02229 |  | 0.9 | 1.05 | 0.034011 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | ASGI-2024-001 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.035469 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | ASGI-2024-020 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.033479 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-017 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045853 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-018 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045939 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-019 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045939 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-020 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045853 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-021 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045853 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-022 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045939 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-023 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045939 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-081 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.052573 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-082 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.052573 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-211 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.039907 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-212 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.039907 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-213 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.039907 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | ASGI-2024-001 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.035469 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | ASGI-2024-020 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.033479 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-017 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045853 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-018 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045939 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-019 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045939 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-020 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045853 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-021 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045853 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-022 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045939 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-023 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045939 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-081 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.052573 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-082 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.052573 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-211 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.039907 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-212 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.039907 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-213 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.039907 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | ASGI-2024-001 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.035469 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | ASGI-2024-020 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.033479 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-017 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045853 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-018 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045939 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-019 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045939 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-020 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045853 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-021 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045853 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-022 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045939 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-023 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.045939 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-081 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.052573 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-082 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.052573 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-211 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.039907 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-212 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.039907 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-213 | GEN-2023-015 | 1.0717 | 1.095 | 0.023358 |  | 0.9 | 1.05 | 0.039907 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-081 | MAURINE4 | 1.0239 | 1.0608 | 0.036962 |  | 0.9 | 1.05 | 0.047176 | 259625 | None
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-082 | MAURINE4 | 1.0239 | 1.0608 | 0.036962 |  | 0.9 | 1.05 | 0.047176 | 259625 | None
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-081 | MAURINE4 | 1.0246 | 1.0617 | 0.037109 |  | 0.9 | 1.05 | 0.041139 | 259626 | None
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-082 | MAURINE4 | 1.0246 | 1.0617 | 0.037109 |  | 0.9 | 1.05 | 0.041139 | 259626 | None
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-081 | MAURINE4 | 1.024 | 1.0609 | 0.036949 |  | 0.9 | 1.05 | 0.047176 | 259689 | None
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-082 | MAURINE4 | 1.024 | 1.0609 | 0.036949 |  | 0.9 | 1.05 | 0.047176 | 259689 | None
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-081 | MAURINE4 | 1.0247 | 1.0618 | 0.037147 |  | 0.9 | 1.05 | 0.041139 | 259690 | None
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-082 | MAURINE4 | 1.0247 | 1.0618 | 0.037147 |  | 0.9 | 1.05 | 0.041139 | 259690 | None
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-081 | MAURINE4 | 1.0202 | 1.0594 | 0.039192 |  | 0.9 | 1.05 | 0.053924 | Single 672603 BDV4 230 672602 BDX4 230 2 | None
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-082 | MAURINE4 | 1.0202 | 1.0594 | 0.039192 |  | 0.9 | 1.05 | 0.053924 | Single 672603 BDV4 230 672602 BDX4 230 2 | None
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-081 | RUSHMORE-RM8 | 1.0193 | 1.0503 | 0.031027 |  | 0.9 | 1.05 | 0.041139 | 259626 | Add 0.02 MVAR switched shunt at RUSHMORE-RM8 69 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-082 | RUSHMORE-RM8 | 1.0193 | 1.0503 | 0.031027 |  | 0.9 | 1.05 | 0.041139 | 259626 | Add 0.02 MVAR switched shunt at RUSHMORE-RM8 69 kV
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-081 | RUSHMORE-RM8 | 1.0194 | 1.0504 | 0.031044 |  | 0.9 | 1.05 | 0.041139 | 259690 | None
Voltage | 00ALL | 2 | 29WP | V | GEN-2024-082 | RUSHMORE-RM8 | 1.0194 | 1.0504 | 0.031044 |  | 0.9 | 1.05 | 0.041139 | 259690 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | BBCMPRSS-MK7 | 0.9452 | 0.89956 | -0.045642 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | BBCMPRSS-MK7 | 0.9452 | 0.89956 | -0.045642 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | BBCMPRSS-MK7 | 0.9452 | 0.89956 | -0.045642 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | BBCMPRSS-MK7 | 0.9452 | 0.89956 | -0.045642 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | BBCMPRSS-MK7 | 0.9452 | 0.89956 | -0.045642 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | BBCMPRSS-MK7 | 0.9452 | 0.89956 | -0.045642 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | BBCMPRSS-MK7 | 0.9452 | 0.89956 | -0.045642 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | BBCMPRSS-MK7 | 0.9452 | 0.89956 | -0.045642 |  | 0.9 | 1.05 | 0.035579 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | BBCMPRSS-MK7 | 0.9452 | 0.89956 | -0.045642 |  | 0.9 | 1.05 | 0.03702 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | BBCMPRSS-MK7 | 0.9452 | 0.89956 | -0.045642 |  | 0.9 | 1.05 | 0.048085 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | BBCMPRSS-MK7 | 0.9452 | 0.89956 | -0.045642 |  | 0.9 | 1.05 | 0.037791 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | BBCMPRSS-MK7 | 0.9452 | 0.89956 | -0.045642 |  | 0.9 | 1.05 | 0.03831 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | BBCMPRSS-MK7 | 0.9452 | 0.89956 | -0.045642 |  | 0.9 | 1.05 | 0.036874 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | BBCMPRSS-MK7 | 0.9452 | 0.89956 | -0.045642 |  | 0.9 | 1.05 | 0.034396 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | BBCMPRSS-MK7 | 0.9452 | 0.89956 | -0.045642 |  | 0.9 | 1.05 | 0.033129 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | BERG -MK7 | 0.93688 | 0.89039 | -0.046483 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | BERG -MK7 | 0.93688 | 0.89039 | -0.046483 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | BERG -MK7 | 0.93688 | 0.89039 | -0.046483 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | BERG -MK7 | 0.93688 | 0.89039 | -0.046483 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | BERG -MK7 | 0.93688 | 0.89039 | -0.046483 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | BERG -MK7 | 0.93688 | 0.89039 | -0.046483 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | BERG -MK7 | 0.93688 | 0.89039 | -0.046483 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | BERG -MK7 | 0.93688 | 0.89039 | -0.046483 |  | 0.9 | 1.05 | 0.035579 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | BERG -MK7 | 0.93688 | 0.89039 | -0.046483 |  | 0.9 | 1.05 | 0.03702 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | BERG -MK7 | 0.93688 | 0.89039 | -0.046483 |  | 0.9 | 1.05 | 0.048085 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | BERG -MK7 | 0.93688 | 0.89039 | -0.046483 |  | 0.9 | 1.05 | 0.037791 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | BERG -MK7 | 0.93688 | 0.89039 | -0.046483 |  | 0.9 | 1.05 | 0.03831 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | BERG -MK7 | 0.93688 | 0.89039 | -0.046483 |  | 0.9 | 1.05 | 0.036874 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | BERG -MK7 | 0.93688 | 0.89039 | -0.046483 |  | 0.9 | 1.05 | 0.034396 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | BERG -MK7 | 0.93688 | 0.89039 | -0.046483 |  | 0.9 | 1.05 | 0.033129 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | BERG -MK7 | 0.94742 | 0.8992 | -0.04822 |  | 0.9 | 1.05 | 1 | Single 655902 PLSNTV_T-MW7 115 786841 GEN-2024-329 115 1 | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | BERG -MK7 | 0.94742 | 0.8992 | -0.048218 |  | 0.9 | 1.05 | 1 | Single 786841 GEN-2024-329 115 786842 G24-329XFMR1 34 786857 'G24-329TER1 ' 13 1 | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | BERG -MK7 | 0.94744 | 0.89924 | -0.048202 |  | 0.9 | 1.05 | 1 | GEN-2024-329_POI_655902_Generator_outage | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | BIGGULCH-MK7 | 0.91825 | 0.86546 | -0.052785 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | BIGGULCH-MK7 | 0.91825 | 0.86546 | -0.052785 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | BIGGULCH-MK7 | 0.91825 | 0.86546 | -0.052785 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | BIGGULCH-MK7 | 0.91825 | 0.86546 | -0.052785 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | BIGGULCH-MK7 | 0.91825 | 0.86546 | -0.052785 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | BIGGULCH-MK7 | 0.91825 | 0.86546 | -0.052785 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | BIGGULCH-MK7 | 0.91825 | 0.86546 | -0.052785 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | BIGGULCH-MK7 | 0.91825 | 0.86546 | -0.052785 |  | 0.9 | 1.05 | 0.035579 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | BIGGULCH-MK7 | 0.91825 | 0.86546 | -0.052785 |  | 0.9 | 1.05 | 0.03702 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | BIGGULCH-MK7 | 0.91825 | 0.86546 | -0.052785 |  | 0.9 | 1.05 | 0.048085 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | BIGGULCH-MK7 | 0.91825 | 0.86546 | -0.052785 |  | 0.9 | 1.05 | 0.037791 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | BIGGULCH-MK7 | 0.91825 | 0.86546 | -0.052785 |  | 0.9 | 1.05 | 0.03831 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | BIGGULCH-MK7 | 0.91825 | 0.86546 | -0.052785 |  | 0.9 | 1.05 | 0.036874 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | BIGGULCH-MK7 | 0.91825 | 0.86546 | -0.052785 |  | 0.9 | 1.05 | 0.034396 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | BIGGULCH-MK7 | 0.91825 | 0.86546 | -0.052785 |  | 0.9 | 1.05 | 0.033129 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | BIGGULCH-MK7 | 0.92316 | 0.88321 | -0.03995 |  | 0.9 | 1.05 | 0.031482 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | BIGGULCH-MK7 | 0.92316 | 0.88321 | -0.03995 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | BIGGULCH-MK7 | 0.92316 | 0.88321 | -0.03995 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | BIGGULCH-MK7 | 0.92316 | 0.88321 | -0.03995 |  | 0.9 | 1.05 | 0.031482 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | BIGGULCH-MK7 | 0.92316 | 0.88321 | -0.03995 |  | 0.9 | 1.05 | 0.031482 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | BIGGULCH-MK7 | 0.92316 | 0.88321 | -0.03995 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | BIGGULCH-MK7 | 0.92316 | 0.88321 | -0.03995 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | BIGGULCH-MK7 | 0.92316 | 0.88321 | -0.03995 |  | 0.9 | 1.05 | 0.031809 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | BIGGULCH-MK7 | 0.92316 | 0.88321 | -0.03995 |  | 0.9 | 1.05 | 0.033425 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | BIGGULCH-MK7 | 0.92316 | 0.88321 | -0.03995 |  | 0.9 | 1.05 | 0.035007 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | BIGGULCH-MK7 | 0.92316 | 0.88321 | -0.03995 |  | 0.9 | 1.05 | 0.036151 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | BIGGULCH-MK7 | 0.92316 | 0.88321 | -0.03995 |  | 0.9 | 1.05 | 0.031351 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | BIGGULCH-MK7 | 0.92316 | 0.88321 | -0.03995 |  | 0.9 | 1.05 | 0.031987 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | BIGGULCH-MK7 | 0.92316 | 0.88321 | -0.03995 |  | 0.9 | 1.05 | 0.033545 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | BIGGULCH-MK7 | 0.92316 | 0.88321 | -0.03995 |  | 0.9 | 1.05 | 0.032049 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | BIGGULCH-MK7 | 0.93043 | 0.87857 | -0.051864 |  | 0.9 | 1.05 | 1 | Single 655902 PLSNTV_T-MW7 115 786841 GEN-2024-329 115 1 | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | BIGGULCH-MK7 | 0.93043 | 0.87857 | -0.051862 |  | 0.9 | 1.05 | 1 | Single 786841 GEN-2024-329 115 786842 G24-329XFMR1 34 786857 'G24-329TER1 ' 13 1 | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | BIGGULCH-MK7 | 0.93045 | 0.87861 | -0.051844 |  | 0.9 | 1.05 | 1 | GEN-2024-329_POI_655902_Generator_outage | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | BISON___-GE4 | 0.98846 | 0.89949 | -0.088979 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | BISON___-GE4 | 0.98846 | 0.89949 | -0.088979 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | BISON___-GE4 | 0.98846 | 0.89949 | -0.088979 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | BISON___-GE4 | 0.98846 | 0.89949 | -0.088979 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | BISON___-GE4 | 0.98846 | 0.89949 | -0.088979 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | BISON___-GE4 | 0.98846 | 0.89949 | -0.088979 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | BISON___-GE4 | 0.98846 | 0.89949 | -0.088979 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | BISON___-GE4 | 0.98846 | 0.89949 | -0.088979 |  | 0.9 | 1.05 | 0.035579 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | BISON___-GE4 | 0.98846 | 0.89949 | -0.088979 |  | 0.9 | 1.05 | 0.03702 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | BISON___-GE4 | 0.98846 | 0.89949 | -0.088979 |  | 0.9 | 1.05 | 0.048085 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | BISON___-GE4 | 0.98846 | 0.89949 | -0.088979 |  | 0.9 | 1.05 | 0.037791 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | BISON___-GE4 | 0.98846 | 0.89949 | -0.088979 |  | 0.9 | 1.05 | 0.03831 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | BISON___-GE4 | 0.98846 | 0.89949 | -0.088979 |  | 0.9 | 1.05 | 0.036874 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | BISON___-GE4 | 0.98846 | 0.89949 | -0.088979 |  | 0.9 | 1.05 | 0.034396 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | BISON___-GE4 | 0.98846 | 0.89949 | -0.088979 |  | 0.9 | 1.05 | 0.033129 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | CHADRON 7 | 1.0168 | 0.89842 | -0.11836 |  | 0.9 | 1.05 | 0.17758 | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | CHARLSON-MK7 | 0.93087 | 0.88347 | -0.0474 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | CHARLSON-MK7 | 0.93087 | 0.88347 | -0.0474 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | CHARLSON-MK7 | 0.93087 | 0.88347 | -0.0474 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | CHARLSON-MK7 | 0.93087 | 0.88347 | -0.0474 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | CHARLSON-MK7 | 0.93087 | 0.88347 | -0.0474 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | CHARLSON-MK7 | 0.93087 | 0.88347 | -0.0474 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | CHARLSON-MK7 | 0.93087 | 0.88347 | -0.0474 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | CHARLSON-MK7 | 0.93087 | 0.88347 | -0.0474 |  | 0.9 | 1.05 | 0.035579 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | CHARLSON-MK7 | 0.93087 | 0.88347 | -0.0474 |  | 0.9 | 1.05 | 0.03702 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | CHARLSON-MK7 | 0.93087 | 0.88347 | -0.0474 |  | 0.9 | 1.05 | 0.048085 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | CHARLSON-MK7 | 0.93087 | 0.88347 | -0.0474 |  | 0.9 | 1.05 | 0.037791 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | CHARLSON-MK7 | 0.93087 | 0.88347 | -0.0474 |  | 0.9 | 1.05 | 0.03831 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | CHARLSON-MK7 | 0.93087 | 0.88347 | -0.0474 |  | 0.9 | 1.05 | 0.036874 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | CHARLSON-MK7 | 0.93087 | 0.88347 | -0.0474 |  | 0.9 | 1.05 | 0.034396 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | CHARLSON-MK7 | 0.93087 | 0.88347 | -0.0474 |  | 0.9 | 1.05 | 0.033129 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | CHARLSON-MK7 | 0.9416 | 0.89245 | -0.049155 |  | 0.9 | 1.05 | 1 | Single 655902 PLSNTV_T-MW7 115 786841 GEN-2024-329 115 1 | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | CHARLSON-MK7 | 0.94161 | 0.89245 | -0.049154 |  | 0.9 | 1.05 | 1 | Single 786841 GEN-2024-329 115 786842 G24-329XFMR1 34 786857 'G24-329TER1 ' 13 1 | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | CHARLSON-MK7 | 0.94163 | 0.89249 | -0.049137 |  | 0.9 | 1.05 | 1 | GEN-2024-329_POI_655902_Generator_outage | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | CHARLSON-MK7 | 0.93554 | 0.8995 | -0.036039 |  | 0.9 | 1.05 | 0.031482 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | CHARLSON-MK7 | 0.93554 | 0.8995 | -0.036039 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | CHARLSON-MK7 | 0.93554 | 0.8995 | -0.036039 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | CHARLSON-MK7 | 0.93554 | 0.8995 | -0.036039 |  | 0.9 | 1.05 | 0.031482 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | CHARLSON-MK7 | 0.93554 | 0.8995 | -0.036039 |  | 0.9 | 1.05 | 0.031482 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | CHARLSON-MK7 | 0.93554 | 0.8995 | -0.036039 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | CHARLSON-MK7 | 0.93554 | 0.8995 | -0.036039 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | CHARLSON-MK7 | 0.93554 | 0.8995 | -0.036039 |  | 0.9 | 1.05 | 0.031809 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | CHARLSON-MK7 | 0.93554 | 0.8995 | -0.036039 |  | 0.9 | 1.05 | 0.033425 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | CHARLSON-MK7 | 0.93554 | 0.8995 | -0.036039 |  | 0.9 | 1.05 | 0.035007 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | CHARLSON-MK7 | 0.93554 | 0.8995 | -0.036039 |  | 0.9 | 1.05 | 0.036151 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | CHARLSON-MK7 | 0.93554 | 0.8995 | -0.036039 |  | 0.9 | 1.05 | 0.031351 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | CHARLSON-MK7 | 0.93554 | 0.8995 | -0.036039 |  | 0.9 | 1.05 | 0.031987 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | CHARLSON-MK7 | 0.93554 | 0.8995 | -0.036039 |  | 0.9 | 1.05 | 0.033545 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | CHARLSON-MK7 | 0.93554 | 0.8995 | -0.036039 |  | 0.9 | 1.05 | 0.032049 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | DH_CS_EA-TS4 | 0.88715 | 0.84404 | -0.043109 |  | 0.9 | 1.05 | 0.12419 | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL_-MB4-1 :HV: | Add 78 MVAR switched shunt at DH_CS_EA-TS4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | DH_CS_EA-TS4 | 0.89078 | 0.84491 | -0.045871 |  | 0.9 | 1.05 | 0.12419 | P13:345-230.0:UMZ:# N-1 #:: 3WND STEGALL_-MB3-STEGALL_-MB4-STEGALL_-MB9-1 SGQ KV3A:EHV: | Add 78 MVAR switched shunt at DH_CS_EA-TS4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | DRYCREEK-BE4 | 0.97736 | 0.88469 | -0.092675 |  | 0.9 | 1.05 | 0.17758 | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | DRYCREEK-BE4 | 0.98717 | 0.88648 | -0.10069 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | DRYCREEK-BE4 | 0.98717 | 0.88648 | -0.10069 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | DRYCREEK-BE4 | 0.98717 | 0.88648 | -0.10069 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | DRYCREEK-BE4 | 0.98717 | 0.88648 | -0.10069 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | DRYCREEK-BE4 | 0.98717 | 0.88648 | -0.10069 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | DRYCREEK-BE4 | 0.98717 | 0.88648 | -0.10069 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | DRYCREEK-BE4 | 0.98717 | 0.88648 | -0.10069 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | DRYCREEK-BE4 | 0.98717 | 0.88648 | -0.10069 |  | 0.9 | 1.05 | 0.035579 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | DRYCREEK-BE4 | 0.98717 | 0.88648 | -0.10069 |  | 0.9 | 1.05 | 0.03702 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | DRYCREEK-BE4 | 0.98717 | 0.88648 | -0.10069 |  | 0.9 | 1.05 | 0.048085 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | DRYCREEK-BE4 | 0.98717 | 0.88648 | -0.10069 |  | 0.9 | 1.05 | 0.037791 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | DRYCREEK-BE4 | 0.98717 | 0.88648 | -0.10069 |  | 0.9 | 1.05 | 0.03831 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | DRYCREEK-BE4 | 0.98717 | 0.88648 | -0.10069 |  | 0.9 | 1.05 | 0.036874 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | DRYCREEK-BE4 | 0.98717 | 0.88648 | -0.10069 |  | 0.9 | 1.05 | 0.034396 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | DRYCREEK-BE4 | 0.98717 | 0.88648 | -0.10069 |  | 0.9 | 1.05 | 0.033129 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | DRYCREEK-BE7 | 0.97701 | 0.88816 | -0.088847 |  | 0.9 | 1.05 | 0.17758 | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | DRYCREEK-BE7 | 0.98651 | 0.88789 | -0.098619 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | DRYCREEK-BE7 | 0.98651 | 0.88789 | -0.098619 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | DRYCREEK-BE7 | 0.98651 | 0.88789 | -0.098619 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | DRYCREEK-BE7 | 0.98651 | 0.88789 | -0.098619 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | DRYCREEK-BE7 | 0.98651 | 0.88789 | -0.098619 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | DRYCREEK-BE7 | 0.98651 | 0.88789 | -0.098619 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | DRYCREEK-BE7 | 0.98651 | 0.88789 | -0.098619 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | DRYCREEK-BE7 | 0.98651 | 0.88789 | -0.098619 |  | 0.9 | 1.05 | 0.035579 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | DRYCREEK-BE7 | 0.98651 | 0.88789 | -0.098619 |  | 0.9 | 1.05 | 0.03702 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | DRYCREEK-BE7 | 0.98651 | 0.88789 | -0.098619 |  | 0.9 | 1.05 | 0.048085 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | DRYCREEK-BE7 | 0.98651 | 0.88789 | -0.098619 |  | 0.9 | 1.05 | 0.037791 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | DRYCREEK-BE7 | 0.98651 | 0.88789 | -0.098619 |  | 0.9 | 1.05 | 0.03831 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | DRYCREEK-BE7 | 0.98651 | 0.88789 | -0.098619 |  | 0.9 | 1.05 | 0.036874 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | DRYCREEK-BE7 | 0.98651 | 0.88789 | -0.098619 |  | 0.9 | 1.05 | 0.034396 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | DRYCREEK-BE7 | 0.98651 | 0.88789 | -0.098619 |  | 0.9 | 1.05 | 0.033129 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | DRYCREEK-BE7 | 0.98799 | 0.89937 | -0.088619 |  | 0.9 | 1.05 | 0.1484 | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | ASGI-2024-020 | EHALLTP3 | 0.99806 | 1.0569 | 0.058818 |  | 0.9 | 1.05 | 0.034173 | P12:115:SUNC:ELLSWORTH-BUSHTON:::HV: | Add 7 MVAR switched shunt at EHALLTP3 115 kV
Voltage | 00NR | 2 | 29WP | V | ASGI-2024-020 | EHALLTP3 | 0.99806 | 1.0569 | 0.058818 |  | 0.9 | 1.05 | 0.034173 | P12:115:MIDW-MKEC:ELLSWORTH-BUSHTON:::HV: | Add 7 MVAR switched shunt at EHALLTP3 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | ELKCRK 7 | 0.9813 | 0.89505 | -0.086255 |  | 0.9 | 1.05 | 0.17758 | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | ELKCRK 7 | 0.98738 | 0.88723 | -0.10015 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | ELKCRK 7 | 0.98738 | 0.88723 | -0.10015 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | ELKCRK 7 | 0.98738 | 0.88723 | -0.10015 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | ELKCRK 7 | 0.98738 | 0.88723 | -0.10015 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | ELKCRK 7 | 0.98738 | 0.88723 | -0.10015 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | ELKCRK 7 | 0.98738 | 0.88723 | -0.10015 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | ELKCRK 7 | 0.98738 | 0.88723 | -0.10015 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | ELKCRK 7 | 0.98738 | 0.88723 | -0.10015 |  | 0.9 | 1.05 | 0.035579 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | ELKCRK 7 | 0.98738 | 0.88723 | -0.10015 |  | 0.9 | 1.05 | 0.03702 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | ELKCRK 7 | 0.98738 | 0.88723 | -0.10015 |  | 0.9 | 1.05 | 0.048085 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | ELKCRK 7 | 0.98738 | 0.88723 | -0.10015 |  | 0.9 | 1.05 | 0.037791 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | ELKCRK 7 | 0.98738 | 0.88723 | -0.10015 |  | 0.9 | 1.05 | 0.03831 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | ELKCRK 7 | 0.98738 | 0.88723 | -0.10015 |  | 0.9 | 1.05 | 0.036874 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | ELKCRK 7 | 0.98738 | 0.88723 | -0.10015 |  | 0.9 | 1.05 | 0.034396 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | ELKCRK 7 | 0.98738 | 0.88723 | -0.10015 |  | 0.9 | 1.05 | 0.033129 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | ELKCRK 7 | 0.98408 | 0.88881 | -0.095275 |  | 0.9 | 1.05 | 0.1484 | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | ELSWRTH7 | 0.97004 | 0.8811 | -0.088937 |  | 0.9 | 1.05 | 0.17758 | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | ELSWRTH7 | 0.98035 | 0.88167 | -0.098683 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | ELSWRTH7 | 0.98035 | 0.88167 | -0.098683 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | ELSWRTH7 | 0.98035 | 0.88167 | -0.098683 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | ELSWRTH7 | 0.98035 | 0.88167 | -0.098683 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | ELSWRTH7 | 0.98035 | 0.88167 | -0.098683 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | ELSWRTH7 | 0.98035 | 0.88167 | -0.098683 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | ELSWRTH7 | 0.98035 | 0.88167 | -0.098683 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | ELSWRTH7 | 0.98035 | 0.88167 | -0.098683 |  | 0.9 | 1.05 | 0.035579 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | ELSWRTH7 | 0.98035 | 0.88167 | -0.098683 |  | 0.9 | 1.05 | 0.03702 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | ELSWRTH7 | 0.98035 | 0.88167 | -0.098683 |  | 0.9 | 1.05 | 0.048085 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | ELSWRTH7 | 0.98035 | 0.88167 | -0.098683 |  | 0.9 | 1.05 | 0.037791 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | ELSWRTH7 | 0.98035 | 0.88167 | -0.098683 |  | 0.9 | 1.05 | 0.03831 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | ELSWRTH7 | 0.98035 | 0.88167 | -0.098683 |  | 0.9 | 1.05 | 0.036874 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | ELSWRTH7 | 0.98035 | 0.88167 | -0.098683 |  | 0.9 | 1.05 | 0.034396 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | ELSWRTH7 | 0.98035 | 0.88167 | -0.098683 |  | 0.9 | 1.05 | 0.033129 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | ELSWRTH7 | 0.98199 | 0.89376 | -0.088232 |  | 0.9 | 1.05 | 0.1484 | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | FREEDOM7 | 0.97039 | 0.88123 | -0.089161 |  | 0.9 | 1.05 | 0.17758 | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | FREEDOM7 | 0.98092 | 0.88224 | -0.098686 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | FREEDOM7 | 0.98092 | 0.88224 | -0.098686 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | FREEDOM7 | 0.98092 | 0.88224 | -0.098686 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | FREEDOM7 | 0.98092 | 0.88224 | -0.098686 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | FREEDOM7 | 0.98092 | 0.88224 | -0.098686 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | FREEDOM7 | 0.98092 | 0.88224 | -0.098686 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | FREEDOM7 | 0.98092 | 0.88224 | -0.098686 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | FREEDOM7 | 0.98092 | 0.88224 | -0.098686 |  | 0.9 | 1.05 | 0.035579 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | FREEDOM7 | 0.98092 | 0.88224 | -0.098686 |  | 0.9 | 1.05 | 0.03702 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | FREEDOM7 | 0.98092 | 0.88224 | -0.098686 |  | 0.9 | 1.05 | 0.048085 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | FREEDOM7 | 0.98092 | 0.88224 | -0.098686 |  | 0.9 | 1.05 | 0.037791 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | FREEDOM7 | 0.98092 | 0.88224 | -0.098686 |  | 0.9 | 1.05 | 0.03831 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | FREEDOM7 | 0.98092 | 0.88224 | -0.098686 |  | 0.9 | 1.05 | 0.036874 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | FREEDOM7 | 0.98092 | 0.88224 | -0.098686 |  | 0.9 | 1.05 | 0.034396 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | FREEDOM7 | 0.98092 | 0.88224 | -0.098686 |  | 0.9 | 1.05 | 0.033129 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | FREEDOM7 | 0.9828 | 0.89484 | -0.087965 |  | 0.9 | 1.05 | 0.1484 | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | GEN-2017-097 | 0.97421 | 0.88449 | -0.089718 |  | 0.9 | 1.05 | 0.17758 | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | GEN-2017-097 | 0.97421 | 0.88449 | -0.089718 |  | 0.9 | 1.05 | 0.17758 | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | GEN-2017-097 | 0.98567 | 0.88742 | -0.098256 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | GEN-2017-097 | 0.98567 | 0.88742 | -0.098256 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | GEN-2017-097 | 0.98567 | 0.88742 | -0.098256 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | GEN-2017-097 | 0.98567 | 0.88742 | -0.098256 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | GEN-2017-097 | 0.98567 | 0.88742 | -0.098256 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | GEN-2017-097 | 0.98567 | 0.88742 | -0.098256 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | GEN-2017-097 | 0.98567 | 0.88742 | -0.098256 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | GEN-2017-097 | 0.98567 | 0.88742 | -0.098256 |  | 0.9 | 1.05 | 0.035579 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | GEN-2017-097 | 0.98567 | 0.88742 | -0.098256 |  | 0.9 | 1.05 | 0.03702 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | GEN-2017-097 | 0.98567 | 0.88742 | -0.098256 |  | 0.9 | 1.05 | 0.048085 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | GEN-2017-097 | 0.98567 | 0.88742 | -0.098256 |  | 0.9 | 1.05 | 0.037791 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | GEN-2017-097 | 0.98567 | 0.88742 | -0.098256 |  | 0.9 | 1.05 | 0.03831 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | GEN-2017-097 | 0.98567 | 0.88742 | -0.098256 |  | 0.9 | 1.05 | 0.036874 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | GEN-2017-097 | 0.98567 | 0.88742 | -0.098256 |  | 0.9 | 1.05 | 0.034396 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | GEN-2017-097 | 0.98567 | 0.88742 | -0.098256 |  | 0.9 | 1.05 | 0.033129 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | GEN-2017-097 | 0.98567 | 0.88742 | -0.098256 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | GEN-2017-097 | 0.98567 | 0.88742 | -0.098256 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | GEN-2017-097 | 0.98567 | 0.88742 | -0.098256 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | GEN-2017-097 | 0.98567 | 0.88742 | -0.098256 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | GEN-2017-097 | 0.98567 | 0.88742 | -0.098256 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | GEN-2017-097 | 0.98567 | 0.88742 | -0.098256 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | GEN-2017-097 | 0.98567 | 0.88742 | -0.098256 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | GEN-2017-097 | 0.98567 | 0.88742 | -0.098256 |  | 0.9 | 1.05 | 0.035579 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | GEN-2017-097 | 0.98567 | 0.88742 | -0.098256 |  | 0.9 | 1.05 | 0.03702 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | GEN-2017-097 | 0.98567 | 0.88742 | -0.098256 |  | 0.9 | 1.05 | 0.048085 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | GEN-2017-097 | 0.98567 | 0.88742 | -0.098256 |  | 0.9 | 1.05 | 0.037791 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | GEN-2017-097 | 0.98567 | 0.88742 | -0.098256 |  | 0.9 | 1.05 | 0.03831 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | GEN-2017-097 | 0.98567 | 0.88742 | -0.098256 |  | 0.9 | 1.05 | 0.036874 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | GEN-2017-097 | 0.98567 | 0.88742 | -0.098256 |  | 0.9 | 1.05 | 0.034396 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | GEN-2017-097 | 0.98567 | 0.88742 | -0.098256 |  | 0.9 | 1.05 | 0.033129 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | GORDON 7 | 0.99829 | 0.89124 | -0.10705 |  | 0.9 | 1.05 | 0.17758 | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | HETINGR4 | 0.97812 | 0.89961 | -0.078509 |  | 0.9 | 1.05 | 0.14392 | Single 652424 BELFELD3 345 800121 MAURINE2 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | J12_____-MK7 | 0.90838 | 0.85469 | -0.05369 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | J12_____-MK7 | 0.90838 | 0.85469 | -0.05369 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | J12_____-MK7 | 0.90838 | 0.85469 | -0.05369 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | J12_____-MK7 | 0.90838 | 0.85469 | -0.05369 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | J12_____-MK7 | 0.90838 | 0.85469 | -0.05369 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | J12_____-MK7 | 0.90838 | 0.85469 | -0.05369 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | J12_____-MK7 | 0.90838 | 0.85469 | -0.05369 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | J12_____-MK7 | 0.90838 | 0.85469 | -0.05369 |  | 0.9 | 1.05 | 0.035579 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | J12_____-MK7 | 0.90838 | 0.85469 | -0.05369 |  | 0.9 | 1.05 | 0.03702 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | J12_____-MK7 | 0.90838 | 0.85469 | -0.05369 |  | 0.9 | 1.05 | 0.048085 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | J12_____-MK7 | 0.90838 | 0.85469 | -0.05369 |  | 0.9 | 1.05 | 0.037791 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | J12_____-MK7 | 0.90838 | 0.85469 | -0.05369 |  | 0.9 | 1.05 | 0.03831 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | J12_____-MK7 | 0.90838 | 0.85469 | -0.05369 |  | 0.9 | 1.05 | 0.036874 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | J12_____-MK7 | 0.90838 | 0.85469 | -0.05369 |  | 0.9 | 1.05 | 0.034396 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | J12_____-MK7 | 0.90838 | 0.85469 | -0.05369 |  | 0.9 | 1.05 | 0.033129 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | J12_____-MK7 | 0.91337 | 0.87276 | -0.040612 |  | 0.9 | 1.05 | 0.031482 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | J12_____-MK7 | 0.91337 | 0.87276 | -0.040612 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | J12_____-MK7 | 0.91337 | 0.87276 | -0.040612 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | J12_____-MK7 | 0.91337 | 0.87276 | -0.040612 |  | 0.9 | 1.05 | 0.031482 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | J12_____-MK7 | 0.91337 | 0.87276 | -0.040612 |  | 0.9 | 1.05 | 0.031482 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | J12_____-MK7 | 0.91337 | 0.87276 | -0.040612 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | J12_____-MK7 | 0.91337 | 0.87276 | -0.040612 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | J12_____-MK7 | 0.91337 | 0.87276 | -0.040612 |  | 0.9 | 1.05 | 0.031809 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | J12_____-MK7 | 0.91337 | 0.87276 | -0.040612 |  | 0.9 | 1.05 | 0.033425 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | J12_____-MK7 | 0.91337 | 0.87276 | -0.040612 |  | 0.9 | 1.05 | 0.035007 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | J12_____-MK7 | 0.91337 | 0.87276 | -0.040612 |  | 0.9 | 1.05 | 0.036151 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | J12_____-MK7 | 0.91337 | 0.87276 | -0.040612 |  | 0.9 | 1.05 | 0.031351 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | J12_____-MK7 | 0.91337 | 0.87276 | -0.040612 |  | 0.9 | 1.05 | 0.031987 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | J12_____-MK7 | 0.91337 | 0.87276 | -0.040612 |  | 0.9 | 1.05 | 0.033545 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | J12_____-MK7 | 0.91337 | 0.87276 | -0.040612 |  | 0.9 | 1.05 | 0.032049 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | J12_____-MK7 | 0.92076 | 0.86803 | -0.052721 |  | 0.9 | 1.05 | 1 | Single 655902 PLSNTV_T-MW7 115 786841 GEN-2024-329 115 1 | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | J12_____-MK7 | 0.92076 | 0.86804 | -0.05272 |  | 0.9 | 1.05 | 1 | Single 786841 GEN-2024-329 115 786842 G24-329XFMR1 34 786857 'G24-329TER1 ' 13 1 | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | J12_____-MK7 | 0.92077 | 0.86807 | -0.052701 |  | 0.9 | 1.05 | 1 | GEN-2024-329_POI_655902_Generator_outage | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | KEENE -MK7 | 0.93355 | 0.88688 | -0.046668 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | KEENE -MK7 | 0.93355 | 0.88688 | -0.046668 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | KEENE -MK7 | 0.93355 | 0.88688 | -0.046668 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | KEENE -MK7 | 0.93355 | 0.88688 | -0.046668 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | KEENE -MK7 | 0.93355 | 0.88688 | -0.046668 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | KEENE -MK7 | 0.93355 | 0.88688 | -0.046668 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | KEENE -MK7 | 0.93355 | 0.88688 | -0.046668 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | KEENE -MK7 | 0.93355 | 0.88688 | -0.046668 |  | 0.9 | 1.05 | 0.035579 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | KEENE -MK7 | 0.93355 | 0.88688 | -0.046668 |  | 0.9 | 1.05 | 0.03702 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | KEENE -MK7 | 0.93355 | 0.88688 | -0.046668 |  | 0.9 | 1.05 | 0.048085 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | KEENE -MK7 | 0.93355 | 0.88688 | -0.046668 |  | 0.9 | 1.05 | 0.037791 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | KEENE -MK7 | 0.93355 | 0.88688 | -0.046668 |  | 0.9 | 1.05 | 0.03831 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | KEENE -MK7 | 0.93355 | 0.88688 | -0.046668 |  | 0.9 | 1.05 | 0.036874 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | KEENE -MK7 | 0.93355 | 0.88688 | -0.046668 |  | 0.9 | 1.05 | 0.034396 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | KEENE -MK7 | 0.93355 | 0.88688 | -0.046668 |  | 0.9 | 1.05 | 0.033129 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | KEENE -MK7 | 0.94413 | 0.89572 | -0.048408 |  | 0.9 | 1.05 | 1 | Single 655902 PLSNTV_T-MW7 115 786841 GEN-2024-329 115 1 | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | KEENE -MK7 | 0.94413 | 0.89573 | -0.048407 |  | 0.9 | 1.05 | 1 | Single 786841 GEN-2024-329 115 786842 G24-329XFMR1 34 786857 'G24-329TER1 ' 13 1 | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | KEENE -MK7 | 0.94416 | 0.89577 | -0.04839 |  | 0.9 | 1.05 | 1 | GEN-2024-329_POI_655902_Generator_outage | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | KEENECRN-MK7 | 0.93012 | 0.88295 | -0.047168 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | KEENECRN-MK7 | 0.93012 | 0.88295 | -0.047168 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | KEENECRN-MK7 | 0.93012 | 0.88295 | -0.047168 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | KEENECRN-MK7 | 0.93012 | 0.88295 | -0.047168 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | KEENECRN-MK7 | 0.93012 | 0.88295 | -0.047168 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | KEENECRN-MK7 | 0.93012 | 0.88295 | -0.047168 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | KEENECRN-MK7 | 0.93012 | 0.88295 | -0.047168 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | KEENECRN-MK7 | 0.93012 | 0.88295 | -0.047168 |  | 0.9 | 1.05 | 0.035579 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | KEENECRN-MK7 | 0.93012 | 0.88295 | -0.047168 |  | 0.9 | 1.05 | 0.03702 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | KEENECRN-MK7 | 0.93012 | 0.88295 | -0.047168 |  | 0.9 | 1.05 | 0.048085 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | KEENECRN-MK7 | 0.93012 | 0.88295 | -0.047168 |  | 0.9 | 1.05 | 0.037791 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | KEENECRN-MK7 | 0.93012 | 0.88295 | -0.047168 |  | 0.9 | 1.05 | 0.03831 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | KEENECRN-MK7 | 0.93012 | 0.88295 | -0.047168 |  | 0.9 | 1.05 | 0.036874 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | KEENECRN-MK7 | 0.93012 | 0.88295 | -0.047168 |  | 0.9 | 1.05 | 0.034396 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | KEENECRN-MK7 | 0.93012 | 0.88295 | -0.047168 |  | 0.9 | 1.05 | 0.033129 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | KEENECRN-MK7 | 0.94081 | 0.89189 | -0.048918 |  | 0.9 | 1.05 | 1 | Single 655902 PLSNTV_T-MW7 115 786841 GEN-2024-329 115 1 | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | KEENECRN-MK7 | 0.94081 | 0.89189 | -0.048916 |  | 0.9 | 1.05 | 1 | Single 786841 GEN-2024-329 115 786842 G24-329XFMR1 34 786857 'G24-329TER1 ' 13 1 | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | KEENECRN-MK7 | 0.94083 | 0.89193 | -0.048899 |  | 0.9 | 1.05 | 1 | GEN-2024-329_POI_655902_Generator_outage | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | KEENECRN-MK7 | 0.93477 | 0.8989 | -0.035865 |  | 0.9 | 1.05 | 0.031482 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | KEENECRN-MK7 | 0.93477 | 0.8989 | -0.035865 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | KEENECRN-MK7 | 0.93477 | 0.8989 | -0.035865 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | KEENECRN-MK7 | 0.93477 | 0.8989 | -0.035865 |  | 0.9 | 1.05 | 0.031482 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | KEENECRN-MK7 | 0.93477 | 0.8989 | -0.035865 |  | 0.9 | 1.05 | 0.031482 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | KEENECRN-MK7 | 0.93477 | 0.8989 | -0.035865 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | KEENECRN-MK7 | 0.93477 | 0.8989 | -0.035865 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | KEENECRN-MK7 | 0.93477 | 0.8989 | -0.035865 |  | 0.9 | 1.05 | 0.031809 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | KEENECRN-MK7 | 0.93477 | 0.8989 | -0.035865 |  | 0.9 | 1.05 | 0.033425 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | KEENECRN-MK7 | 0.93477 | 0.8989 | -0.035865 |  | 0.9 | 1.05 | 0.035007 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | KEENECRN-MK7 | 0.93477 | 0.8989 | -0.035865 |  | 0.9 | 1.05 | 0.036151 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | KEENECRN-MK7 | 0.93477 | 0.8989 | -0.035865 |  | 0.9 | 1.05 | 0.031351 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | KEENECRN-MK7 | 0.93477 | 0.8989 | -0.035865 |  | 0.9 | 1.05 | 0.031987 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | KEENECRN-MK7 | 0.93477 | 0.8989 | -0.035865 |  | 0.9 | 1.05 | 0.033545 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | KEENECRN-MK7 | 0.93477 | 0.8989 | -0.035865 |  | 0.9 | 1.05 | 0.032049 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | L11_____-MK7 | 0.92097 | 0.86836 | -0.052604 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | L11_____-MK7 | 0.92097 | 0.86836 | -0.052604 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | L11_____-MK7 | 0.92097 | 0.86836 | -0.052604 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | L11_____-MK7 | 0.92097 | 0.86836 | -0.052604 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | L11_____-MK7 | 0.92097 | 0.86836 | -0.052604 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | L11_____-MK7 | 0.92097 | 0.86836 | -0.052604 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | L11_____-MK7 | 0.92097 | 0.86836 | -0.052604 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | L11_____-MK7 | 0.92097 | 0.86836 | -0.052604 |  | 0.9 | 1.05 | 0.035579 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | L11_____-MK7 | 0.92097 | 0.86836 | -0.052604 |  | 0.9 | 1.05 | 0.03702 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | L11_____-MK7 | 0.92097 | 0.86836 | -0.052604 |  | 0.9 | 1.05 | 0.048085 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | L11_____-MK7 | 0.92097 | 0.86836 | -0.052604 |  | 0.9 | 1.05 | 0.037791 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | L11_____-MK7 | 0.92097 | 0.86836 | -0.052604 |  | 0.9 | 1.05 | 0.03831 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | L11_____-MK7 | 0.92097 | 0.86836 | -0.052604 |  | 0.9 | 1.05 | 0.036874 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | L11_____-MK7 | 0.92097 | 0.86836 | -0.052604 |  | 0.9 | 1.05 | 0.034396 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | L11_____-MK7 | 0.92097 | 0.86836 | -0.052604 |  | 0.9 | 1.05 | 0.033129 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | L11_____-MK7 | 0.92587 | 0.88605 | -0.039817 |  | 0.9 | 1.05 | 0.031482 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | L11_____-MK7 | 0.92587 | 0.88605 | -0.039817 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | L11_____-MK7 | 0.92587 | 0.88605 | -0.039817 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | L11_____-MK7 | 0.92587 | 0.88605 | -0.039817 |  | 0.9 | 1.05 | 0.031482 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | L11_____-MK7 | 0.92587 | 0.88605 | -0.039817 |  | 0.9 | 1.05 | 0.031482 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | L11_____-MK7 | 0.92587 | 0.88605 | -0.039817 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | L11_____-MK7 | 0.92587 | 0.88605 | -0.039817 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | L11_____-MK7 | 0.92587 | 0.88605 | -0.039817 |  | 0.9 | 1.05 | 0.031809 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | L11_____-MK7 | 0.92587 | 0.88605 | -0.039817 |  | 0.9 | 1.05 | 0.033425 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | L11_____-MK7 | 0.92587 | 0.88605 | -0.039817 |  | 0.9 | 1.05 | 0.035007 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | L11_____-MK7 | 0.92587 | 0.88605 | -0.039817 |  | 0.9 | 1.05 | 0.036151 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | L11_____-MK7 | 0.92587 | 0.88605 | -0.039817 |  | 0.9 | 1.05 | 0.031351 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | L11_____-MK7 | 0.92587 | 0.88605 | -0.039817 |  | 0.9 | 1.05 | 0.031987 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | L11_____-MK7 | 0.92587 | 0.88605 | -0.039817 |  | 0.9 | 1.05 | 0.033545 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | L11_____-MK7 | 0.92587 | 0.88605 | -0.039817 |  | 0.9 | 1.05 | 0.032049 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | L11_____-MK7 | 0.93311 | 0.88142 | -0.051691 |  | 0.9 | 1.05 | 1 | Single 655902 PLSNTV_T-MW7 115 786841 GEN-2024-329 115 1 | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | L11_____-MK7 | 0.93312 | 0.88143 | -0.05169 |  | 0.9 | 1.05 | 1 | Single 786841 GEN-2024-329 115 786842 G24-329XFMR1 34 786857 'G24-329TER1 ' 13 1 | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | L11_____-MK7 | 0.93313 | 0.88146 | -0.051672 |  | 0.9 | 1.05 | 1 | GEN-2024-329_POI_655902_Generator_outage | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | MAURINE4 | 0.98784 | 0.87592 | -0.11192 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | MAURINE4 | 0.98784 | 0.87592 | -0.11192 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | MAURINE4 | 0.98784 | 0.87592 | -0.11192 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | MAURINE4 | 0.98784 | 0.87592 | -0.11192 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | MAURINE4 | 0.98784 | 0.87592 | -0.11192 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | MAURINE4 | 0.98784 | 0.87592 | -0.11192 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | MAURINE4 | 0.98784 | 0.87592 | -0.11192 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | MAURINE4 | 0.98784 | 0.87592 | -0.11192 |  | 0.9 | 1.05 | 0.035579 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | MAURINE4 | 0.98784 | 0.87592 | -0.11192 |  | 0.9 | 1.05 | 0.03702 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | MAURINE4 | 0.98784 | 0.87592 | -0.11192 |  | 0.9 | 1.05 | 0.048085 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | MAURINE4 | 0.98784 | 0.87592 | -0.11192 |  | 0.9 | 1.05 | 0.037791 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | MAURINE4 | 0.98784 | 0.87592 | -0.11192 |  | 0.9 | 1.05 | 0.03831 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | MAURINE4 | 0.98784 | 0.87592 | -0.11192 |  | 0.9 | 1.05 | 0.036874 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | MAURINE4 | 0.98784 | 0.87592 | -0.11192 |  | 0.9 | 1.05 | 0.034396 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | MAURINE4 | 0.98784 | 0.87592 | -0.11192 |  | 0.9 | 1.05 | 0.033129 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | MAURINE4 | 0.98791 | 0.88593 | -0.10198 |  | 0.9 | 1.05 | 0.1484 | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | MAURINE8 | 0.99323 | 0.88716 | -0.10607 |  | 0.9 | 1.05 | 0.1484 | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | MAURINE8 | 1.0016 | 0.89346 | -0.10815 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | MAURINE8 | 1.0016 | 0.89346 | -0.10815 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | MAURINE8 | 1.0016 | 0.89346 | -0.10815 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | MAURINE8 | 1.0016 | 0.89346 | -0.10815 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | MAURINE8 | 1.0016 | 0.89346 | -0.10815 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | MAURINE8 | 1.0016 | 0.89346 | -0.10815 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | MAURINE8 | 1.0016 | 0.89346 | -0.10815 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | MAURINE8 | 1.0016 | 0.89346 | -0.10815 |  | 0.9 | 1.05 | 0.035579 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | MAURINE8 | 1.0016 | 0.89346 | -0.10815 |  | 0.9 | 1.05 | 0.03702 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | MAURINE8 | 1.0016 | 0.89346 | -0.10815 |  | 0.9 | 1.05 | 0.048085 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | MAURINE8 | 1.0016 | 0.89346 | -0.10815 |  | 0.9 | 1.05 | 0.037791 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | MAURINE8 | 1.0016 | 0.89346 | -0.10815 |  | 0.9 | 1.05 | 0.03831 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | MAURINE8 | 1.0016 | 0.89346 | -0.10815 |  | 0.9 | 1.05 | 0.036874 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | MAURINE8 | 1.0016 | 0.89346 | -0.10815 |  | 0.9 | 1.05 | 0.034396 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | MAURINE8 | 1.0016 | 0.89346 | -0.10815 |  | 0.9 | 1.05 | 0.033129 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | MOCCASIN-MK7 | 0.89665 | 0.84211 | -0.054535 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | MOCCASIN-MK7 | 0.89665 | 0.84211 | -0.054535 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | MOCCASIN-MK7 | 0.89665 | 0.84211 | -0.054535 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | MOCCASIN-MK7 | 0.89665 | 0.84211 | -0.054535 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | MOCCASIN-MK7 | 0.89665 | 0.84211 | -0.054535 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | MOCCASIN-MK7 | 0.89665 | 0.84211 | -0.054535 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | MOCCASIN-MK7 | 0.89665 | 0.84211 | -0.054535 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | MOCCASIN-MK7 | 0.89665 | 0.84211 | -0.054535 |  | 0.9 | 1.05 | 0.035579 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | MOCCASIN-MK7 | 0.89665 | 0.84211 | -0.054535 |  | 0.9 | 1.05 | 0.03702 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | MOCCASIN-MK7 | 0.89665 | 0.84211 | -0.054535 |  | 0.9 | 1.05 | 0.048085 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | MOCCASIN-MK7 | 0.89665 | 0.84211 | -0.054535 |  | 0.9 | 1.05 | 0.037791 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | MOCCASIN-MK7 | 0.89665 | 0.84211 | -0.054535 |  | 0.9 | 1.05 | 0.03831 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | MOCCASIN-MK7 | 0.89665 | 0.84211 | -0.054535 |  | 0.9 | 1.05 | 0.036874 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | MOCCASIN-MK7 | 0.89665 | 0.84211 | -0.054535 |  | 0.9 | 1.05 | 0.034396 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | MOCCASIN-MK7 | 0.89665 | 0.84211 | -0.054535 |  | 0.9 | 1.05 | 0.033129 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | MOCCASIN-MK7 | 0.90171 | 0.86048 | -0.041233 |  | 0.9 | 1.05 | 0.031482 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | MOCCASIN-MK7 | 0.90171 | 0.86048 | -0.041233 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | MOCCASIN-MK7 | 0.90171 | 0.86048 | -0.041233 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | MOCCASIN-MK7 | 0.90171 | 0.86048 | -0.041233 |  | 0.9 | 1.05 | 0.031482 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | MOCCASIN-MK7 | 0.90171 | 0.86048 | -0.041233 |  | 0.9 | 1.05 | 0.031482 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | MOCCASIN-MK7 | 0.90171 | 0.86048 | -0.041233 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | MOCCASIN-MK7 | 0.90171 | 0.86048 | -0.041233 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | MOCCASIN-MK7 | 0.90171 | 0.86048 | -0.041233 |  | 0.9 | 1.05 | 0.031809 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | MOCCASIN-MK7 | 0.90171 | 0.86048 | -0.041233 |  | 0.9 | 1.05 | 0.033425 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | MOCCASIN-MK7 | 0.90171 | 0.86048 | -0.041233 |  | 0.9 | 1.05 | 0.035007 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | MOCCASIN-MK7 | 0.90171 | 0.86048 | -0.041233 |  | 0.9 | 1.05 | 0.036151 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | MOCCASIN-MK7 | 0.90171 | 0.86048 | -0.041233 |  | 0.9 | 1.05 | 0.031351 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | MOCCASIN-MK7 | 0.90171 | 0.86048 | -0.041233 |  | 0.9 | 1.05 | 0.031987 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | MOCCASIN-MK7 | 0.90171 | 0.86048 | -0.041233 |  | 0.9 | 1.05 | 0.033545 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | MOCCASIN-MK7 | 0.90171 | 0.86048 | -0.041233 |  | 0.9 | 1.05 | 0.032049 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | MOCCASIN-MK7 | 0.9092 | 0.85568 | -0.053525 |  | 0.9 | 1.05 | 1 | Single 655902 PLSNTV_T-MW7 115 786841 GEN-2024-329 115 1 | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | MOCCASIN-MK7 | 0.9092 | 0.85568 | -0.053523 |  | 0.9 | 1.05 | 1 | Single 786841 GEN-2024-329 115 786842 G24-329XFMR1 34 786857 'G24-329TER1 ' 13 1 | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | MOCCASIN-MK7 | 0.90922 | 0.85572 | -0.053504 |  | 0.9 | 1.05 | 1 | GEN-2024-329_POI_655902_Generator_outage | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | MOUNTAIN-MK7 | 0.92991 | 0.878 | -0.051901 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | MOUNTAIN-MK7 | 0.92991 | 0.878 | -0.051901 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | MOUNTAIN-MK7 | 0.92991 | 0.878 | -0.051901 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | MOUNTAIN-MK7 | 0.92991 | 0.878 | -0.051901 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | MOUNTAIN-MK7 | 0.92991 | 0.878 | -0.051901 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | MOUNTAIN-MK7 | 0.92991 | 0.878 | -0.051901 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | MOUNTAIN-MK7 | 0.92991 | 0.878 | -0.051901 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | MOUNTAIN-MK7 | 0.92991 | 0.878 | -0.051901 |  | 0.9 | 1.05 | 0.035579 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | MOUNTAIN-MK7 | 0.92991 | 0.878 | -0.051901 |  | 0.9 | 1.05 | 0.03702 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | MOUNTAIN-MK7 | 0.92991 | 0.878 | -0.051901 |  | 0.9 | 1.05 | 0.048085 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | MOUNTAIN-MK7 | 0.92991 | 0.878 | -0.051901 |  | 0.9 | 1.05 | 0.037791 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | MOUNTAIN-MK7 | 0.92991 | 0.878 | -0.051901 |  | 0.9 | 1.05 | 0.03831 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | MOUNTAIN-MK7 | 0.92991 | 0.878 | -0.051901 |  | 0.9 | 1.05 | 0.036874 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | MOUNTAIN-MK7 | 0.92991 | 0.878 | -0.051901 |  | 0.9 | 1.05 | 0.034396 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | MOUNTAIN-MK7 | 0.92991 | 0.878 | -0.051901 |  | 0.9 | 1.05 | 0.033129 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | MOUNTAIN-MK7 | 0.93475 | 0.89545 | -0.0393 |  | 0.9 | 1.05 | 0.031482 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | MOUNTAIN-MK7 | 0.93475 | 0.89545 | -0.0393 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | MOUNTAIN-MK7 | 0.93475 | 0.89545 | -0.0393 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | MOUNTAIN-MK7 | 0.93475 | 0.89545 | -0.0393 |  | 0.9 | 1.05 | 0.031482 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | MOUNTAIN-MK7 | 0.93475 | 0.89545 | -0.0393 |  | 0.9 | 1.05 | 0.031482 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | MOUNTAIN-MK7 | 0.93475 | 0.89545 | -0.0393 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | MOUNTAIN-MK7 | 0.93475 | 0.89545 | -0.0393 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | MOUNTAIN-MK7 | 0.93475 | 0.89545 | -0.0393 |  | 0.9 | 1.05 | 0.031809 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | MOUNTAIN-MK7 | 0.93475 | 0.89545 | -0.0393 |  | 0.9 | 1.05 | 0.033425 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | MOUNTAIN-MK7 | 0.93475 | 0.89545 | -0.0393 |  | 0.9 | 1.05 | 0.035007 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | MOUNTAIN-MK7 | 0.93475 | 0.89545 | -0.0393 |  | 0.9 | 1.05 | 0.036151 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | MOUNTAIN-MK7 | 0.93475 | 0.89545 | -0.0393 |  | 0.9 | 1.05 | 0.031351 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | MOUNTAIN-MK7 | 0.93475 | 0.89545 | -0.0393 |  | 0.9 | 1.05 | 0.031987 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | MOUNTAIN-MK7 | 0.93475 | 0.89545 | -0.0393 |  | 0.9 | 1.05 | 0.033545 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | MOUNTAIN-MK7 | 0.93475 | 0.89545 | -0.0393 |  | 0.9 | 1.05 | 0.032049 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | MOUNTAIN-MK7 | 0.9419 | 0.89088 | -0.051023 |  | 0.9 | 1.05 | 1 | Single 655902 PLSNTV_T-MW7 115 786841 GEN-2024-329 115 1 | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | MOUNTAIN-MK7 | 0.94191 | 0.89088 | -0.051021 |  | 0.9 | 1.05 | 1 | Single 786841 GEN-2024-329 115 786842 G24-329XFMR1 34 786857 'G24-329TER1 ' 13 1 | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | MOUNTAIN-MK7 | 0.94192 | 0.89092 | -0.051003 |  | 0.9 | 1.05 | 1 | GEN-2024-329_POI_655902_Generator_outage | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | NEWELL 7 | 0.98451 | 0.87836 | -0.10615 |  | 0.9 | 1.05 | 0.1484 | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | NEWELL 7 | 0.99371 | 0.88918 | -0.10453 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | NEWELL 7 | 0.99371 | 0.88918 | -0.10453 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | NEWELL 7 | 0.99371 | 0.88918 | -0.10453 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | NEWELL 7 | 0.99371 | 0.88918 | -0.10453 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | NEWELL 7 | 0.99371 | 0.88918 | -0.10453 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | NEWELL 7 | 0.99371 | 0.88918 | -0.10453 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | NEWELL 7 | 0.99371 | 0.88918 | -0.10453 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | NEWELL 7 | 0.99371 | 0.88918 | -0.10453 |  | 0.9 | 1.05 | 0.035579 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | NEWELL 7 | 0.99371 | 0.88918 | -0.10453 |  | 0.9 | 1.05 | 0.03702 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | NEWELL 7 | 0.99371 | 0.88918 | -0.10453 |  | 0.9 | 1.05 | 0.048085 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | NEWELL 7 | 0.99371 | 0.88918 | -0.10453 |  | 0.9 | 1.05 | 0.037791 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | NEWELL 7 | 0.99371 | 0.88918 | -0.10453 |  | 0.9 | 1.05 | 0.03831 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | NEWELL 7 | 0.99371 | 0.88918 | -0.10453 |  | 0.9 | 1.05 | 0.036874 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | NEWELL 7 | 0.99371 | 0.88918 | -0.10453 |  | 0.9 | 1.05 | 0.034396 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | NEWELL 7 | 0.99371 | 0.88918 | -0.10453 |  | 0.9 | 1.05 | 0.033129 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | NRTHFORK-MK7 | 0.93133 | 0.88454 | -0.046792 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | NRTHFORK-MK7 | 0.93133 | 0.88454 | -0.046792 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | NRTHFORK-MK7 | 0.93133 | 0.88454 | -0.046792 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | NRTHFORK-MK7 | 0.93133 | 0.88454 | -0.046792 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | NRTHFORK-MK7 | 0.93133 | 0.88454 | -0.046792 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | NRTHFORK-MK7 | 0.93133 | 0.88454 | -0.046792 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | NRTHFORK-MK7 | 0.93133 | 0.88454 | -0.046792 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | NRTHFORK-MK7 | 0.93133 | 0.88454 | -0.046792 |  | 0.9 | 1.05 | 0.035579 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | NRTHFORK-MK7 | 0.93133 | 0.88454 | -0.046792 |  | 0.9 | 1.05 | 0.03702 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | NRTHFORK-MK7 | 0.93133 | 0.88454 | -0.046792 |  | 0.9 | 1.05 | 0.048085 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | NRTHFORK-MK7 | 0.93133 | 0.88454 | -0.046792 |  | 0.9 | 1.05 | 0.037791 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | NRTHFORK-MK7 | 0.93133 | 0.88454 | -0.046792 |  | 0.9 | 1.05 | 0.03831 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | NRTHFORK-MK7 | 0.93133 | 0.88454 | -0.046792 |  | 0.9 | 1.05 | 0.036874 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | NRTHFORK-MK7 | 0.93133 | 0.88454 | -0.046792 |  | 0.9 | 1.05 | 0.034396 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | NRTHFORK-MK7 | 0.93133 | 0.88454 | -0.046792 |  | 0.9 | 1.05 | 0.033129 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | NRTHFORK-MK7 | 0.94194 | 0.8934 | -0.048533 |  | 0.9 | 1.05 | 1 | Single 655902 PLSNTV_T-MW7 115 786841 GEN-2024-329 115 1 | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | NRTHFORK-MK7 | 0.94194 | 0.89341 | -0.048532 |  | 0.9 | 1.05 | 1 | Single 786841 GEN-2024-329 115 786842 G24-329XFMR1 34 786857 'G24-329TER1 ' 13 1 | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | NRTHFORK-MK7 | 0.94196 | 0.89344 | -0.048515 |  | 0.9 | 1.05 | 1 | GEN-2024-329_POI_655902_Generator_outage | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | NUNDRWD-LNX3 | 0.97213 | 0.87933 | -0.092799 |  | 0.9 | 1.05 | 0.17758 | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | NUNDRWD-LNX3 | 0.98334 | 0.88195 | -0.10139 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | NUNDRWD-LNX3 | 0.98334 | 0.88195 | -0.10139 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | NUNDRWD-LNX3 | 0.98334 | 0.88195 | -0.10139 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | NUNDRWD-LNX3 | 0.98334 | 0.88195 | -0.10139 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | NUNDRWD-LNX3 | 0.98334 | 0.88195 | -0.10139 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | NUNDRWD-LNX3 | 0.98334 | 0.88195 | -0.10139 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | NUNDRWD-LNX3 | 0.98334 | 0.88195 | -0.10139 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | NUNDRWD-LNX3 | 0.98334 | 0.88195 | -0.10139 |  | 0.9 | 1.05 | 0.035579 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | NUNDRWD-LNX3 | 0.98334 | 0.88195 | -0.10139 |  | 0.9 | 1.05 | 0.03702 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | NUNDRWD-LNX3 | 0.98334 | 0.88195 | -0.10139 |  | 0.9 | 1.05 | 0.048085 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | NUNDRWD-LNX3 | 0.98334 | 0.88195 | -0.10139 |  | 0.9 | 1.05 | 0.037791 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | NUNDRWD-LNX3 | 0.98334 | 0.88195 | -0.10139 |  | 0.9 | 1.05 | 0.03831 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | NUNDRWD-LNX3 | 0.98334 | 0.88195 | -0.10139 |  | 0.9 | 1.05 | 0.036874 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | NUNDRWD-LNX3 | 0.98334 | 0.88195 | -0.10139 |  | 0.9 | 1.05 | 0.034396 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | NUNDRWD-LNX3 | 0.98334 | 0.88195 | -0.10139 |  | 0.9 | 1.05 | 0.033129 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | NUNDRWD-LNX3 | 0.98557 | 0.89668 | -0.088894 |  | 0.9 | 1.05 | 0.1484 | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | NUNDRWD4 | 0.97221 | 0.87942 | -0.09279 |  | 0.9 | 1.05 | 0.17758 | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | NUNDRWD4 | 0.98351 | 0.88222 | -0.1013 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | NUNDRWD4 | 0.98351 | 0.88222 | -0.1013 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | NUNDRWD4 | 0.98351 | 0.88222 | -0.1013 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | NUNDRWD4 | 0.98351 | 0.88222 | -0.1013 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | NUNDRWD4 | 0.98351 | 0.88222 | -0.1013 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | NUNDRWD4 | 0.98351 | 0.88222 | -0.1013 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | NUNDRWD4 | 0.98351 | 0.88222 | -0.1013 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | NUNDRWD4 | 0.98351 | 0.88222 | -0.1013 |  | 0.9 | 1.05 | 0.035579 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | NUNDRWD4 | 0.98351 | 0.88222 | -0.1013 |  | 0.9 | 1.05 | 0.03702 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | NUNDRWD4 | 0.98351 | 0.88222 | -0.1013 |  | 0.9 | 1.05 | 0.048085 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | NUNDRWD4 | 0.98351 | 0.88222 | -0.1013 |  | 0.9 | 1.05 | 0.037791 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | NUNDRWD4 | 0.98351 | 0.88222 | -0.1013 |  | 0.9 | 1.05 | 0.03831 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | NUNDRWD4 | 0.98351 | 0.88222 | -0.1013 |  | 0.9 | 1.05 | 0.036874 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | NUNDRWD4 | 0.98351 | 0.88222 | -0.1013 |  | 0.9 | 1.05 | 0.034396 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | NUNDRWD4 | 0.98351 | 0.88222 | -0.1013 |  | 0.9 | 1.05 | 0.033129 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | NUNDRWD4 | 0.98596 | 0.89733 | -0.088635 |  | 0.9 | 1.05 | 0.1484 | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | OAKDALE -MK7 | 0.94545 | 0.89482 | -0.050624 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | OAKDALE -MK7 | 0.94545 | 0.89482 | -0.050624 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | OAKDALE -MK7 | 0.94545 | 0.89482 | -0.050624 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | OAKDALE -MK7 | 0.94545 | 0.89482 | -0.050624 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | OAKDALE -MK7 | 0.94545 | 0.89482 | -0.050624 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | OAKDALE -MK7 | 0.94545 | 0.89482 | -0.050624 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | OAKDALE -MK7 | 0.94545 | 0.89482 | -0.050624 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | OAKDALE -MK7 | 0.94545 | 0.89482 | -0.050624 |  | 0.9 | 1.05 | 0.035579 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | OAKDALE -MK7 | 0.94545 | 0.89482 | -0.050624 |  | 0.9 | 1.05 | 0.03702 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | OAKDALE -MK7 | 0.94545 | 0.89482 | -0.050624 |  | 0.9 | 1.05 | 0.048085 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | OAKDALE -MK7 | 0.94545 | 0.89482 | -0.050624 |  | 0.9 | 1.05 | 0.037791 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | OAKDALE -MK7 | 0.94545 | 0.89482 | -0.050624 |  | 0.9 | 1.05 | 0.03831 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | OAKDALE -MK7 | 0.94545 | 0.89482 | -0.050624 |  | 0.9 | 1.05 | 0.036874 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | OAKDALE -MK7 | 0.94545 | 0.89482 | -0.050624 |  | 0.9 | 1.05 | 0.034396 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | OAKDALE -MK7 | 0.94545 | 0.89482 | -0.050624 |  | 0.9 | 1.05 | 0.033129 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | PR BRZ 4 | 1.0287 | 1.0566 | 0.027919 |  | 0.95 | 1.05 | 0.043705 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | PR BRZ 4 | 1.0287 | 1.0566 | 0.027919 |  | 0.95 | 1.05 | 0.043686 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | PR BRZ 4 | 1.0287 | 1.0566 | 0.027919 |  | 0.95 | 1.05 | 0.043686 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | PR BRZ 4 | 1.0287 | 1.0566 | 0.027919 |  | 0.95 | 1.05 | 0.043705 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | PR BRZ 4 | 1.0287 | 1.0566 | 0.027919 |  | 0.95 | 1.05 | 0.043705 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | PR BRZ 4 | 1.0287 | 1.0566 | 0.027919 |  | 0.95 | 1.05 | 0.043686 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | PR BRZ 4 | 1.0287 | 1.0566 | 0.027919 |  | 0.95 | 1.05 | 0.043686 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | PR BRZ 4 | 1.0287 | 1.0566 | 0.027919 |  | 0.95 | 1.05 | 0.04081 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | PR BRZ 4 | 1.0287 | 1.0566 | 0.027919 |  | 0.95 | 1.05 | 0.036358 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | PR BRZ 4 | 1.0287 | 1.0566 | 0.027919 |  | 0.95 | 1.05 | 0.095336 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | PR BRZ 4 | 1.0287 | 1.0566 | 0.027919 |  | 0.95 | 1.05 | 0.057358 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | PR BRZ 4 | 1.0287 | 1.0566 | 0.027919 |  | 0.95 | 1.05 | 0.045547 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | PR BRZ 4 | 1.0287 | 1.0565 | 0.027853 |  | 0.95 | 1.05 | 0.043705 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | PR BRZ 4 | 1.0287 | 1.0565 | 0.027853 |  | 0.95 | 1.05 | 0.043686 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | PR BRZ 4 | 1.0287 | 1.0565 | 0.027853 |  | 0.95 | 1.05 | 0.043686 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | PR BRZ 4 | 1.0287 | 1.0565 | 0.027853 |  | 0.95 | 1.05 | 0.043705 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | PR BRZ 4 | 1.0287 | 1.0565 | 0.027853 |  | 0.95 | 1.05 | 0.043705 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | PR BRZ 4 | 1.0287 | 1.0565 | 0.027853 |  | 0.95 | 1.05 | 0.043686 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | PR BRZ 4 | 1.0287 | 1.0565 | 0.027853 |  | 0.95 | 1.05 | 0.043686 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | PR BRZ 4 | 1.0287 | 1.0565 | 0.027853 |  | 0.95 | 1.05 | 0.04081 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | PR BRZ 4 | 1.0287 | 1.0565 | 0.027853 |  | 0.95 | 1.05 | 0.036358 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | PR BRZ 4 | 1.0287 | 1.0565 | 0.027853 |  | 0.95 | 1.05 | 0.095336 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | PR BRZ 4 | 1.0287 | 1.0565 | 0.027853 |  | 0.95 | 1.05 | 0.057358 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | PR BRZ 4 | 1.0287 | 1.0565 | 0.027853 |  | 0.95 | 1.05 | 0.045547 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | PR BRZ 4 | 1.0287 | 1.0564 | 0.027716 |  | 0.95 | 1.05 | 0.043705 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | PR BRZ 4 | 1.0287 | 1.0564 | 0.027716 |  | 0.95 | 1.05 | 0.043686 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | PR BRZ 4 | 1.0287 | 1.0564 | 0.027716 |  | 0.95 | 1.05 | 0.043686 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | PR BRZ 4 | 1.0287 | 1.0564 | 0.027716 |  | 0.95 | 1.05 | 0.043705 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | PR BRZ 4 | 1.0287 | 1.0564 | 0.027716 |  | 0.95 | 1.05 | 0.043705 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | PR BRZ 4 | 1.0287 | 1.0564 | 0.027716 |  | 0.95 | 1.05 | 0.043686 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | PR BRZ 4 | 1.0287 | 1.0564 | 0.027716 |  | 0.95 | 1.05 | 0.043686 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | PR BRZ 4 | 1.0287 | 1.0564 | 0.027716 |  | 0.95 | 1.05 | 0.04081 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | PR BRZ 4 | 1.0287 | 1.0564 | 0.027716 |  | 0.95 | 1.05 | 0.036358 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | PR BRZ 4 | 1.0287 | 1.0564 | 0.027716 |  | 0.95 | 1.05 | 0.095336 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | PR BRZ 4 | 1.0287 | 1.0564 | 0.027716 |  | 0.95 | 1.05 | 0.057358 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | PR BRZ 4 | 1.0287 | 1.0564 | 0.027716 |  | 0.95 | 1.05 | 0.045547 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | PR BRZ 4 | 1.0282 | 1.0553 | 0.027055 |  | 0.95 | 1.05 | 0.053201 | P12:345.0:UMZ:# N-1 #:: LINE HOLT.CO3-GRPRAR1-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | PR BRZ 4 | 1.0282 | 1.0553 | 0.027055 |  | 0.95 | 1.05 | 0.053182 | P12:345.0:UMZ:# N-1 #:: LINE HOLT.CO3-GRPRAR1-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | PR BRZ 4 | 1.0282 | 1.0553 | 0.027055 |  | 0.95 | 1.05 | 0.053182 | P12:345.0:UMZ:# N-1 #:: LINE HOLT.CO3-GRPRAR1-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | PR BRZ 4 | 1.0282 | 1.0553 | 0.027055 |  | 0.95 | 1.05 | 0.053201 | P12:345.0:UMZ:# N-1 #:: LINE HOLT.CO3-GRPRAR1-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | PR BRZ 4 | 1.0282 | 1.0553 | 0.027055 |  | 0.95 | 1.05 | 0.053201 | P12:345.0:UMZ:# N-1 #:: LINE HOLT.CO3-GRPRAR1-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | PR BRZ 4 | 1.0282 | 1.0553 | 0.027055 |  | 0.95 | 1.05 | 0.053182 | P12:345.0:UMZ:# N-1 #:: LINE HOLT.CO3-GRPRAR1-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | PR BRZ 4 | 1.0282 | 1.0553 | 0.027055 |  | 0.95 | 1.05 | 0.053182 | P12:345.0:UMZ:# N-1 #:: LINE HOLT.CO3-GRPRAR1-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | PR BRZ 4 | 1.0282 | 1.0553 | 0.027055 |  | 0.95 | 1.05 | 0.050306 | P12:345.0:UMZ:# N-1 #:: LINE HOLT.CO3-GRPRAR1-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | PR BRZ 4 | 1.0282 | 1.0553 | 0.027055 |  | 0.95 | 1.05 | 0.045853 | P12:345.0:UMZ:# N-1 #:: LINE HOLT.CO3-GRPRAR1-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | PR BRZ 4 | 1.0282 | 1.0553 | 0.027055 |  | 0.95 | 1.05 | 0.10483 | P12:345.0:UMZ:# N-1 #:: LINE HOLT.CO3-GRPRAR1-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | PR BRZ 4 | 1.0282 | 1.0553 | 0.027055 |  | 0.95 | 1.05 | 0.066853 | P12:345.0:UMZ:# N-1 #:: LINE HOLT.CO3-GRPRAR1-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | PR BRZ 4 | 1.0282 | 1.0553 | 0.027055 |  | 0.95 | 1.05 | 0.055043 | P12:345.0:UMZ:# N-1 #:: LINE HOLT.CO3-GRPRAR1-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | PR BRZ 4 | 1.0282 | 1.0553 | 0.027055 |  | 0.95 | 1.05 | 0.033456 | P12:345.0:UMZ:# N-1 #:: LINE HOLT.CO3-GRPRAR1-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | PR BRZ 4 | 1.0282 | 1.0553 | 0.027055 |  | 0.95 | 1.05 | 0.03771 | P12:345.0:UMZ:# N-1 #:: LINE HOLT.CO3-GRPRAR1-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | PR BRZ 4 | 1.0282 | 1.0553 | 0.027054 |  | 0.95 | 1.05 | 0.053201 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR1-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | PR BRZ 4 | 1.0282 | 1.0553 | 0.027054 |  | 0.95 | 1.05 | 0.053182 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR1-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | PR BRZ 4 | 1.0282 | 1.0553 | 0.027054 |  | 0.95 | 1.05 | 0.053182 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR1-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | PR BRZ 4 | 1.0282 | 1.0553 | 0.027054 |  | 0.95 | 1.05 | 0.053201 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR1-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | PR BRZ 4 | 1.0282 | 1.0553 | 0.027054 |  | 0.95 | 1.05 | 0.053201 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR1-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | PR BRZ 4 | 1.0282 | 1.0553 | 0.027054 |  | 0.95 | 1.05 | 0.053182 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR1-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | PR BRZ 4 | 1.0282 | 1.0553 | 0.027054 |  | 0.95 | 1.05 | 0.053182 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR1-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | PR BRZ 4 | 1.0282 | 1.0553 | 0.027054 |  | 0.95 | 1.05 | 0.050306 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR1-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | PR BRZ 4 | 1.0282 | 1.0553 | 0.027054 |  | 0.95 | 1.05 | 0.045853 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR1-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | PR BRZ 4 | 1.0282 | 1.0553 | 0.027054 |  | 0.95 | 1.05 | 0.10483 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR1-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | PR BRZ 4 | 1.0282 | 1.0553 | 0.027054 |  | 0.95 | 1.05 | 0.066853 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR1-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | PR BRZ 4 | 1.0282 | 1.0553 | 0.027054 |  | 0.95 | 1.05 | 0.055043 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR1-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | PR BRZ 4 | 1.0282 | 1.0553 | 0.027054 |  | 0.95 | 1.05 | 0.033456 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR1-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | PR BRZ 4 | 1.0282 | 1.0553 | 0.027054 |  | 0.95 | 1.05 | 0.03771 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR1-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | RAPIDCTY-RM8 | 0.97378 | 0.8865 | -0.087284 |  | 0.9 | 1.05 | 0.17758 | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | RAPIDCTY-RM8 | 0.98298 | 0.885 | -0.097987 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | RAPIDCTY-RM8 | 0.98298 | 0.885 | -0.097987 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | RAPIDCTY-RM8 | 0.98298 | 0.885 | -0.097987 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | RAPIDCTY-RM8 | 0.98298 | 0.885 | -0.097987 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | RAPIDCTY-RM8 | 0.98298 | 0.885 | -0.097987 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | RAPIDCTY-RM8 | 0.98298 | 0.885 | -0.097987 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | RAPIDCTY-RM8 | 0.98298 | 0.885 | -0.097987 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | RAPIDCTY-RM8 | 0.98298 | 0.885 | -0.097987 |  | 0.9 | 1.05 | 0.035579 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | RAPIDCTY-RM8 | 0.98298 | 0.885 | -0.097987 |  | 0.9 | 1.05 | 0.03702 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | RAPIDCTY-RM8 | 0.98298 | 0.885 | -0.097987 |  | 0.9 | 1.05 | 0.048085 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | RAPIDCTY-RM8 | 0.98298 | 0.885 | -0.097987 |  | 0.9 | 1.05 | 0.037791 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | RAPIDCTY-RM8 | 0.98298 | 0.885 | -0.097987 |  | 0.9 | 1.05 | 0.03831 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | RAPIDCTY-RM8 | 0.98298 | 0.885 | -0.097987 |  | 0.9 | 1.05 | 0.036874 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | RAPIDCTY-RM8 | 0.98298 | 0.885 | -0.097987 |  | 0.9 | 1.05 | 0.034396 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | RAPIDCTY-RM8 | 0.98298 | 0.885 | -0.097987 |  | 0.9 | 1.05 | 0.033129 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | RAPIDCTY-RM8 | 0.98352 | 0.89469 | -0.088833 |  | 0.9 | 1.05 | 0.1484 | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | RUSHMORE-RM7 | 0.97712 | 0.88896 | -0.088157 |  | 0.9 | 1.05 | 0.17758 | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | RUSHMORE-RM7 | 0.98696 | 0.88865 | -0.098306 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | RUSHMORE-RM7 | 0.98696 | 0.88865 | -0.098306 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | RUSHMORE-RM7 | 0.98696 | 0.88865 | -0.098306 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | RUSHMORE-RM7 | 0.98696 | 0.88865 | -0.098306 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | RUSHMORE-RM7 | 0.98696 | 0.88865 | -0.098306 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | RUSHMORE-RM7 | 0.98696 | 0.88865 | -0.098306 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | RUSHMORE-RM7 | 0.98696 | 0.88865 | -0.098306 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | RUSHMORE-RM7 | 0.98696 | 0.88865 | -0.098306 |  | 0.9 | 1.05 | 0.035579 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | RUSHMORE-RM7 | 0.98696 | 0.88865 | -0.098306 |  | 0.9 | 1.05 | 0.03702 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | RUSHMORE-RM7 | 0.98696 | 0.88865 | -0.098306 |  | 0.9 | 1.05 | 0.048085 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | RUSHMORE-RM7 | 0.98696 | 0.88865 | -0.098306 |  | 0.9 | 1.05 | 0.037791 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | RUSHMORE-RM7 | 0.98696 | 0.88865 | -0.098306 |  | 0.9 | 1.05 | 0.03831 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | RUSHMORE-RM7 | 0.98696 | 0.88865 | -0.098306 |  | 0.9 | 1.05 | 0.036874 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | RUSHMORE-RM7 | 0.98696 | 0.88865 | -0.098306 |  | 0.9 | 1.05 | 0.034396 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | RUSHMORE-RM7 | 0.98696 | 0.88865 | -0.098306 |  | 0.9 | 1.05 | 0.033129 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | RUSHMORE-RM7 | 0.98818 | 0.89978 | -0.088407 |  | 0.9 | 1.05 | 0.1484 | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | RUSHVIL7 | 0.99911 | 0.88492 | -0.11419 |  | 0.9 | 1.05 | 0.17758 | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | SANDCREK-MK7 | 0.92963 | 0.88234 | -0.047287 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | SANDCREK-MK7 | 0.92963 | 0.88234 | -0.047287 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | SANDCREK-MK7 | 0.92963 | 0.88234 | -0.047287 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | SANDCREK-MK7 | 0.92963 | 0.88234 | -0.047287 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | SANDCREK-MK7 | 0.92963 | 0.88234 | -0.047287 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | SANDCREK-MK7 | 0.92963 | 0.88234 | -0.047287 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | SANDCREK-MK7 | 0.92963 | 0.88234 | -0.047287 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | SANDCREK-MK7 | 0.92963 | 0.88234 | -0.047287 |  | 0.9 | 1.05 | 0.035579 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | SANDCREK-MK7 | 0.92963 | 0.88234 | -0.047287 |  | 0.9 | 1.05 | 0.03702 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | SANDCREK-MK7 | 0.92963 | 0.88234 | -0.047287 |  | 0.9 | 1.05 | 0.048085 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | SANDCREK-MK7 | 0.92963 | 0.88234 | -0.047287 |  | 0.9 | 1.05 | 0.037791 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | SANDCREK-MK7 | 0.92963 | 0.88234 | -0.047287 |  | 0.9 | 1.05 | 0.03831 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | SANDCREK-MK7 | 0.92963 | 0.88234 | -0.047287 |  | 0.9 | 1.05 | 0.036874 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | SANDCREK-MK7 | 0.92963 | 0.88234 | -0.047287 |  | 0.9 | 1.05 | 0.034396 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | SANDCREK-MK7 | 0.92963 | 0.88234 | -0.047287 |  | 0.9 | 1.05 | 0.033129 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | SANDCREK-MK7 | 0.94034 | 0.8913 | -0.049039 |  | 0.9 | 1.05 | 1 | Single 655902 PLSNTV_T-MW7 115 786841 GEN-2024-329 115 1 | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | SANDCREK-MK7 | 0.94034 | 0.89131 | -0.049038 |  | 0.9 | 1.05 | 1 | Single 786841 GEN-2024-329 115 786842 G24-329XFMR1 34 786857 'G24-329TER1 ' 13 1 | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | SANDCREK-MK7 | 0.94036 | 0.89134 | -0.049021 |  | 0.9 | 1.05 | 1 | GEN-2024-329_POI_655902_Generator_outage | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | SANDCREK-MK7 | 0.93429 | 0.89834 | -0.035954 |  | 0.9 | 1.05 | 0.031482 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | SANDCREK-MK7 | 0.93429 | 0.89834 | -0.035954 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | SANDCREK-MK7 | 0.93429 | 0.89834 | -0.035954 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | SANDCREK-MK7 | 0.93429 | 0.89834 | -0.035954 |  | 0.9 | 1.05 | 0.031482 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | SANDCREK-MK7 | 0.93429 | 0.89834 | -0.035954 |  | 0.9 | 1.05 | 0.031482 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | SANDCREK-MK7 | 0.93429 | 0.89834 | -0.035954 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | SANDCREK-MK7 | 0.93429 | 0.89834 | -0.035954 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | SANDCREK-MK7 | 0.93429 | 0.89834 | -0.035954 |  | 0.9 | 1.05 | 0.031809 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | SANDCREK-MK7 | 0.93429 | 0.89834 | -0.035954 |  | 0.9 | 1.05 | 0.033425 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | SANDCREK-MK7 | 0.93429 | 0.89834 | -0.035954 |  | 0.9 | 1.05 | 0.035007 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | SANDCREK-MK7 | 0.93429 | 0.89834 | -0.035954 |  | 0.9 | 1.05 | 0.036151 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | SANDCREK-MK7 | 0.93429 | 0.89834 | -0.035954 |  | 0.9 | 1.05 | 0.031351 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | SANDCREK-MK7 | 0.93429 | 0.89834 | -0.035954 |  | 0.9 | 1.05 | 0.031987 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | SANDCREK-MK7 | 0.93429 | 0.89834 | -0.035954 |  | 0.9 | 1.05 | 0.033545 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | SANDCREK-MK7 | 0.93429 | 0.89834 | -0.035954 |  | 0.9 | 1.05 | 0.032049 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | SNDCRKTP-MK7 | 0.93059 | 0.88335 | -0.047232 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | SNDCRKTP-MK7 | 0.93059 | 0.88335 | -0.047232 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | SNDCRKTP-MK7 | 0.93059 | 0.88335 | -0.047232 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | SNDCRKTP-MK7 | 0.93059 | 0.88335 | -0.047232 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | SNDCRKTP-MK7 | 0.93059 | 0.88335 | -0.047232 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | SNDCRKTP-MK7 | 0.93059 | 0.88335 | -0.047232 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | SNDCRKTP-MK7 | 0.93059 | 0.88335 | -0.047232 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | SNDCRKTP-MK7 | 0.93059 | 0.88335 | -0.047232 |  | 0.9 | 1.05 | 0.035579 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | SNDCRKTP-MK7 | 0.93059 | 0.88335 | -0.047232 |  | 0.9 | 1.05 | 0.03702 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | SNDCRKTP-MK7 | 0.93059 | 0.88335 | -0.047232 |  | 0.9 | 1.05 | 0.048085 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | SNDCRKTP-MK7 | 0.93059 | 0.88335 | -0.047232 |  | 0.9 | 1.05 | 0.037791 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | SNDCRKTP-MK7 | 0.93059 | 0.88335 | -0.047232 |  | 0.9 | 1.05 | 0.03831 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | SNDCRKTP-MK7 | 0.93059 | 0.88335 | -0.047232 |  | 0.9 | 1.05 | 0.036874 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | SNDCRKTP-MK7 | 0.93059 | 0.88335 | -0.047232 |  | 0.9 | 1.05 | 0.034396 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | SNDCRKTP-MK7 | 0.93059 | 0.88335 | -0.047232 |  | 0.9 | 1.05 | 0.033129 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | SNDCRKTP-MK7 | 0.94129 | 0.89231 | -0.048983 |  | 0.9 | 1.05 | 1 | Single 655902 PLSNTV_T-MW7 115 786841 GEN-2024-329 115 1 | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | SNDCRKTP-MK7 | 0.94129 | 0.89231 | -0.048982 |  | 0.9 | 1.05 | 1 | Single 786841 GEN-2024-329 115 786842 G24-329XFMR1 34 786857 'G24-329TER1 ' 13 1 | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | SNDCRKTP-MK7 | 0.94131 | 0.89235 | -0.048965 |  | 0.9 | 1.05 | 1 | GEN-2024-329_POI_655902_Generator_outage | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | SNDCRKTP-MK7 | 0.93525 | 0.89933 | -0.035913 |  | 0.9 | 1.05 | 0.031482 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | SNDCRKTP-MK7 | 0.93525 | 0.89933 | -0.035913 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | SNDCRKTP-MK7 | 0.93525 | 0.89933 | -0.035913 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | SNDCRKTP-MK7 | 0.93525 | 0.89933 | -0.035913 |  | 0.9 | 1.05 | 0.031482 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | SNDCRKTP-MK7 | 0.93525 | 0.89933 | -0.035913 |  | 0.9 | 1.05 | 0.031482 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | SNDCRKTP-MK7 | 0.93525 | 0.89933 | -0.035913 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | SNDCRKTP-MK7 | 0.93525 | 0.89933 | -0.035913 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | SNDCRKTP-MK7 | 0.93525 | 0.89933 | -0.035913 |  | 0.9 | 1.05 | 0.031809 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | SNDCRKTP-MK7 | 0.93525 | 0.89933 | -0.035913 |  | 0.9 | 1.05 | 0.033425 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | SNDCRKTP-MK7 | 0.93525 | 0.89933 | -0.035913 |  | 0.9 | 1.05 | 0.035007 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | SNDCRKTP-MK7 | 0.93525 | 0.89933 | -0.035913 |  | 0.9 | 1.05 | 0.036151 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | SNDCRKTP-MK7 | 0.93525 | 0.89933 | -0.035913 |  | 0.9 | 1.05 | 0.031351 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | SNDCRKTP-MK7 | 0.93525 | 0.89933 | -0.035913 |  | 0.9 | 1.05 | 0.031987 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | SNDCRKTP-MK7 | 0.93525 | 0.89933 | -0.035913 |  | 0.9 | 1.05 | 0.033545 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | SNDCRKTP-MK7 | 0.93525 | 0.89933 | -0.035913 |  | 0.9 | 1.05 | 0.032049 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | STEGALL 4 | 0.88715 | 0.84404 | -0.043109 |  | 0.9 | 1.05 | 0.12419 | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL_-MB4-1 :HV: | Add 78 MVAR switched shunt at DH_CS_EA-TS4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | STEGALL 4 | 0.89078 | 0.84491 | -0.045871 |  | 0.9 | 1.05 | 0.12419 | P13:345-230.0:UMZ:# N-1 #:: 3WND STEGALL_-MB3-STEGALL_-MB4-STEGALL_-MB9-1 SGQ KV3A:EHV: | Add 78 MVAR switched shunt at DH_CS_EA-TS4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | STEGALL-LNX3 | 0.97307 | 0.89677 | -0.076302 |  | 0.9 | 1.05 | 0.10059 | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL-LNX3-Z :HV: | Add 23 MVAR switched shunt at STEGALL-LNX3 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | STEGALL-LNX3 | 0.88715 | 0.84404 | -0.043109 |  | 0.9 | 1.05 | 0.12419 | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL_-MB4-1 :HV: | Add 78 MVAR switched shunt at DH_CS_EA-TS4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | STEGALL-LNX3 | 0.89078 | 0.84491 | -0.045871 |  | 0.9 | 1.05 | 0.12419 | P13:345-230.0:UMZ:# N-1 #:: 3WND STEGALL_-MB3-STEGALL_-MB4-STEGALL_-MB9-1 SGQ KV3A:EHV: | Add 78 MVAR switched shunt at DH_CS_EA-TS4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | STEGALL_-MB4 | 0.89079 | 0.84492 | -0.045872 |  | 0.9 | 1.05 | 0.12419 | P13:345-230.0:UMZ:# N-1 #:: 3WND STEGALL_-MB3-STEGALL_-MB4-STEGALL_-MB9-1 SGQ KV3A:EHV: | Add 78 MVAR switched shunt at DH_CS_EA-TS4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | SULPHUR | 0.99172 | 0.8832 | -0.10852 |  | 0.9 | 1.05 | 0.1484 | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | SULPHUR | 1.0022 | 0.89641 | -0.10581 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | SULPHUR | 1.0022 | 0.89641 | -0.10581 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | SULPHUR | 1.0022 | 0.89641 | -0.10581 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | SULPHUR | 1.0022 | 0.89641 | -0.10581 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | SULPHUR | 1.0022 | 0.89641 | -0.10581 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | SULPHUR | 1.0022 | 0.89641 | -0.10581 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | SULPHUR | 1.0022 | 0.89641 | -0.10581 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | SULPHUR | 1.0022 | 0.89641 | -0.10581 |  | 0.9 | 1.05 | 0.035579 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | SULPHUR | 1.0022 | 0.89641 | -0.10581 |  | 0.9 | 1.05 | 0.03702 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | SULPHUR | 1.0022 | 0.89641 | -0.10581 |  | 0.9 | 1.05 | 0.048085 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | SULPHUR | 1.0022 | 0.89641 | -0.10581 |  | 0.9 | 1.05 | 0.037791 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | SULPHUR | 1.0022 | 0.89641 | -0.10581 |  | 0.9 | 1.05 | 0.03831 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | SULPHUR | 1.0022 | 0.89641 | -0.10581 |  | 0.9 | 1.05 | 0.036874 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | SULPHUR | 1.0022 | 0.89641 | -0.10581 |  | 0.9 | 1.05 | 0.034396 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | SULPHUR | 1.0022 | 0.89641 | -0.10581 |  | 0.9 | 1.05 | 0.033129 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | SWENSON -MK7 | 0.93103 | 0.88391 | -0.047114 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | SWENSON -MK7 | 0.93103 | 0.88391 | -0.047114 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | SWENSON -MK7 | 0.93103 | 0.88391 | -0.047114 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | SWENSON -MK7 | 0.93103 | 0.88391 | -0.047114 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | SWENSON -MK7 | 0.93103 | 0.88391 | -0.047114 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | SWENSON -MK7 | 0.93103 | 0.88391 | -0.047114 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | SWENSON -MK7 | 0.93103 | 0.88391 | -0.047114 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | SWENSON -MK7 | 0.93103 | 0.88391 | -0.047114 |  | 0.9 | 1.05 | 0.035579 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | SWENSON -MK7 | 0.93103 | 0.88391 | -0.047114 |  | 0.9 | 1.05 | 0.03702 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | SWENSON -MK7 | 0.93103 | 0.88391 | -0.047114 |  | 0.9 | 1.05 | 0.048085 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | SWENSON -MK7 | 0.93103 | 0.88391 | -0.047114 |  | 0.9 | 1.05 | 0.037791 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | SWENSON -MK7 | 0.93103 | 0.88391 | -0.047114 |  | 0.9 | 1.05 | 0.03831 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | SWENSON -MK7 | 0.93103 | 0.88391 | -0.047114 |  | 0.9 | 1.05 | 0.036874 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | SWENSON -MK7 | 0.93103 | 0.88391 | -0.047114 |  | 0.9 | 1.05 | 0.034396 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | SWENSON -MK7 | 0.93103 | 0.88391 | -0.047114 |  | 0.9 | 1.05 | 0.033129 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | SWENSON -MK7 | 0.9417 | 0.89284 | -0.048863 |  | 0.9 | 1.05 | 1 | Single 655902 PLSNTV_T-MW7 115 786841 GEN-2024-329 115 1 | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | SWENSON -MK7 | 0.9417 | 0.89284 | -0.048861 |  | 0.9 | 1.05 | 1 | Single 786841 GEN-2024-329 115 786842 G24-329XFMR1 34 786857 'G24-329TER1 ' 13 1 | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | SWENSON -MK7 | 0.94172 | 0.89288 | -0.048844 |  | 0.9 | 1.05 | 1 | GEN-2024-329_POI_655902_Generator_outage | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | SWENSON -MK7 | 0.93567 | 0.89985 | -0.035825 |  | 0.9 | 1.05 | 0.031482 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | SWENSON -MK7 | 0.93567 | 0.89985 | -0.035825 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | SWENSON -MK7 | 0.93567 | 0.89985 | -0.035825 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | SWENSON -MK7 | 0.93567 | 0.89985 | -0.035825 |  | 0.9 | 1.05 | 0.031482 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | SWENSON -MK7 | 0.93567 | 0.89985 | -0.035825 |  | 0.9 | 1.05 | 0.031482 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | SWENSON -MK7 | 0.93567 | 0.89985 | -0.035825 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | SWENSON -MK7 | 0.93567 | 0.89985 | -0.035825 |  | 0.9 | 1.05 | 0.031283 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | SWENSON -MK7 | 0.93567 | 0.89985 | -0.035825 |  | 0.9 | 1.05 | 0.031809 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | SWENSON -MK7 | 0.93567 | 0.89985 | -0.035825 |  | 0.9 | 1.05 | 0.033425 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | SWENSON -MK7 | 0.93567 | 0.89985 | -0.035825 |  | 0.9 | 1.05 | 0.035007 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | SWENSON -MK7 | 0.93567 | 0.89985 | -0.035825 |  | 0.9 | 1.05 | 0.036151 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | SWENSON -MK7 | 0.93567 | 0.89985 | -0.035825 |  | 0.9 | 1.05 | 0.031351 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | SWENSON -MK7 | 0.93567 | 0.89985 | -0.035825 |  | 0.9 | 1.05 | 0.031987 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | SWENSON -MK7 | 0.93567 | 0.89985 | -0.035825 |  | 0.9 | 1.05 | 0.033545 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | SWENSON -MK7 | 0.93567 | 0.89985 | -0.035825 |  | 0.9 | 1.05 | 0.032049 | Single 659420 AV.LS-BD-BE3 345 659421 BD.LS-AV-BE3 345 1 | None
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | TABLEBUT-MK7 | 0.93496 | 0.88798 | -0.046988 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | TABLEBUT-MK7 | 0.93496 | 0.88798 | -0.046988 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | TABLEBUT-MK7 | 0.93496 | 0.88798 | -0.046988 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | TABLEBUT-MK7 | 0.93496 | 0.88798 | -0.046988 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | TABLEBUT-MK7 | 0.93496 | 0.88798 | -0.046988 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | TABLEBUT-MK7 | 0.93496 | 0.88798 | -0.046988 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | TABLEBUT-MK7 | 0.93496 | 0.88798 | -0.046988 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | TABLEBUT-MK7 | 0.93496 | 0.88798 | -0.046988 |  | 0.9 | 1.05 | 0.035579 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | TABLEBUT-MK7 | 0.93496 | 0.88798 | -0.046988 |  | 0.9 | 1.05 | 0.03702 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | TABLEBUT-MK7 | 0.93496 | 0.88798 | -0.046988 |  | 0.9 | 1.05 | 0.048085 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | TABLEBUT-MK7 | 0.93496 | 0.88798 | -0.046988 |  | 0.9 | 1.05 | 0.037791 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | TABLEBUT-MK7 | 0.93496 | 0.88798 | -0.046988 |  | 0.9 | 1.05 | 0.03831 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | TABLEBUT-MK7 | 0.93496 | 0.88798 | -0.046988 |  | 0.9 | 1.05 | 0.036874 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | TABLEBUT-MK7 | 0.93496 | 0.88798 | -0.046988 |  | 0.9 | 1.05 | 0.034396 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | TABLEBUT-MK7 | 0.93496 | 0.88798 | -0.046988 |  | 0.9 | 1.05 | 0.033129 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | TABLEBUT-MK7 | 0.94561 | 0.89688 | -0.048735 |  | 0.9 | 1.05 | 1 | Single 655902 PLSNTV_T-MW7 115 786841 GEN-2024-329 115 1 | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | TABLEBUT-MK7 | 0.94562 | 0.89688 | -0.048734 |  | 0.9 | 1.05 | 1 | Single 786841 GEN-2024-329 115 786842 G24-329XFMR1 34 786857 'G24-329TER1 ' 13 1 | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-329 | TABLEBUT-MK7 | 0.94564 | 0.89692 | -0.048717 |  | 0.9 | 1.05 | 1 | GEN-2024-329_POI_655902_Generator_outage | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | VICTRYH4 | 0.89797 | 0.86188 | -0.036089 |  | 0.9 | 1.05 | 0.12419 | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL_-MB4-1 :HV: | Add 78 MVAR switched shunt at DH_CS_EA-TS4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | VICTRYH4 | 0.90165 | 0.86262 | -0.039028 |  | 0.9 | 1.05 | 0.12419 | P13:345-230.0:UMZ:# N-1 #:: 3WND STEGALL_-MB3-STEGALL_-MB4-STEGALL_-MB9-1 SGQ KV3A:EHV: | Add 78 MVAR switched shunt at DH_CS_EA-TS4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | WAYSIDE 4 | 0.92391 | 0.77451 | -0.1494 |  | 0.9 | 1.05 | 0.17758 | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | WAYSIDE 4 | 0.96352 | 0.80773 | -0.15579 |  | 0.9 | 1.05 | 0.036305 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | WAYSIDE 4 | 0.96352 | 0.80773 | -0.15579 |  | 0.9 | 1.05 | 0.037093 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | WAYSIDE 4 | 0.96352 | 0.80773 | -0.15579 |  | 0.9 | 1.05 | 0.037093 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | WAYSIDE 4 | 0.96352 | 0.80773 | -0.15579 |  | 0.9 | 1.05 | 0.036305 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | WAYSIDE 4 | 0.96352 | 0.80773 | -0.15579 |  | 0.9 | 1.05 | 0.036305 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | WAYSIDE 4 | 0.96352 | 0.80773 | -0.15579 |  | 0.9 | 1.05 | 0.037093 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | WAYSIDE 4 | 0.96352 | 0.80773 | -0.15579 |  | 0.9 | 1.05 | 0.037093 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | WAYSIDE 4 | 0.96352 | 0.80773 | -0.15579 |  | 0.9 | 1.05 | 0.035344 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | WAYSIDE 4 | 0.96352 | 0.80773 | -0.15579 |  | 0.9 | 1.05 | 0.033047 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | WAYSIDE 4 | 0.96352 | 0.80773 | -0.15579 |  | 0.9 | 1.05 | 0.033512 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | WAYSIDE 4 | 0.96352 | 0.80773 | -0.15579 |  | 0.9 | 1.05 | 0.040089 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | WAYSIDE 4 | 0.96352 | 0.80773 | -0.15579 |  | 0.9 | 1.05 | 0.035847 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | WAYSIDE 4 | 0.96352 | 0.80773 | -0.15579 |  | 0.9 | 1.05 | 0.031537 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | WAYSIDE 4 | 0.96352 | 0.80773 | -0.15579 |  | 0.9 | 1.05 | 0.033195 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | WAYSIDE 4 | 0.96352 | 0.80773 | -0.15579 |  | 0.9 | 1.05 | 0.36504 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | WAYSIDE 4 | 0.9774 | 0.88094 | -0.09646 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | WAYSIDE 4 | 0.9774 | 0.88094 | -0.09646 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | WAYSIDE 4 | 0.9774 | 0.88094 | -0.09646 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | WAYSIDE 4 | 0.9774 | 0.88094 | -0.09646 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | WAYSIDE 4 | 0.9774 | 0.88094 | -0.09646 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | WAYSIDE 4 | 0.9774 | 0.88094 | -0.09646 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | WAYSIDE 4 | 0.9774 | 0.88094 | -0.09646 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | WAYSIDE 4 | 0.9774 | 0.88094 | -0.09646 |  | 0.9 | 1.05 | 0.035579 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | WAYSIDE 4 | 0.9774 | 0.88094 | -0.09646 |  | 0.9 | 1.05 | 0.03702 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | WAYSIDE 4 | 0.9774 | 0.88094 | -0.09646 |  | 0.9 | 1.05 | 0.048085 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | WAYSIDE 4 | 0.9774 | 0.88094 | -0.09646 |  | 0.9 | 1.05 | 0.037791 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | WAYSIDE 4 | 0.9774 | 0.88094 | -0.09646 |  | 0.9 | 1.05 | 0.03831 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | WAYSIDE 4 | 0.9774 | 0.88094 | -0.09646 |  | 0.9 | 1.05 | 0.036874 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | WAYSIDE 4 | 0.9774 | 0.88094 | -0.09646 |  | 0.9 | 1.05 | 0.034396 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | WAYSIDE 4 | 0.9774 | 0.88094 | -0.09646 |  | 0.9 | 1.05 | 0.033129 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | WAYSIDE 4 | 0.94685 | 0.88574 | -0.061108 |  | 0.9 | 1.05 | 0.12419 | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL_-MB4-1 :HV: | Add 78 MVAR switched shunt at DH_CS_EA-TS4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | WAYSIDE 4 | 0.94894 | 0.88619 | -0.062751 |  | 0.9 | 1.05 | 0.12419 | P13:345-230.0:UMZ:# N-1 #:: 3WND STEGALL_-MB3-STEGALL_-MB4-STEGALL_-MB9-1 SGQ KV3A:EHV: | Add 78 MVAR switched shunt at DH_CS_EA-TS4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | WAYSIDE 7 | 1.023 | 0.87597 | -0.14703 |  | 0.9 | 1.05 | 0.17758 | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-035 | WEBSTER CITY | 0.92837 | 0.8947 | -0.033671 |  | 0.9 | 1.05 | 0.12163 | P12:115.0:UMZ:# N-1 #:: LINE GROTON 7-GROTONSOUTH7-Z :HV: | Add 2.8 MVAR switched shunt at WEBSTER CITY 69 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-035 | WEBSTER NW | 0.92907 | 0.89542 | -0.033644 |  | 0.9 | 1.05 | 0.12163 | P12:115.0:UMZ:# N-1 #:: LINE GROTON 7-GROTONSOUTH7-Z :HV: | Add 2.8 MVAR switched shunt at WEBSTER CITY 69 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | WICKSVL7 | 0.97775 | 0.89969 | -0.078063 |  | 0.9 | 1.05 | 0.17758 | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-374 | WILCRKXFRP 3 | 0.99173 | 0.88322 | -0.10852 |  | 0.9 | 1.05 | 0.1484 | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-017 | WILCRKXFRP 3 | 1.0022 | 0.89643 | -0.10581 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-018 | WILCRKXFRP 3 | 1.0022 | 0.89643 | -0.10581 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-019 | WILCRKXFRP 3 | 1.0022 | 0.89643 | -0.10581 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-020 | WILCRKXFRP 3 | 1.0022 | 0.89643 | -0.10581 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-021 | WILCRKXFRP 3 | 1.0022 | 0.89643 | -0.10581 |  | 0.9 | 1.05 | 0.03572 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-022 | WILCRKXFRP 3 | 1.0022 | 0.89643 | -0.10581 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-023 | WILCRKXFRP 3 | 1.0022 | 0.89643 | -0.10581 |  | 0.9 | 1.05 | 0.035527 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-051 | WILCRKXFRP 3 | 1.0022 | 0.89643 | -0.10581 |  | 0.9 | 1.05 | 0.035579 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-065 | WILCRKXFRP 3 | 1.0022 | 0.89643 | -0.10581 |  | 0.9 | 1.05 | 0.03702 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-140 | WILCRKXFRP 3 | 1.0022 | 0.89643 | -0.10581 |  | 0.9 | 1.05 | 0.048085 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-162 | WILCRKXFRP 3 | 1.0022 | 0.89643 | -0.10581 |  | 0.9 | 1.05 | 0.037791 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-168 | WILCRKXFRP 3 | 1.0022 | 0.89643 | -0.10581 |  | 0.9 | 1.05 | 0.03831 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-173 | WILCRKXFRP 3 | 1.0022 | 0.89643 | -0.10581 |  | 0.9 | 1.05 | 0.036874 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-234 | WILCRKXFRP 3 | 1.0022 | 0.89643 | -0.10581 |  | 0.9 | 1.05 | 0.034396 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-372 | WILCRKXFRP 3 | 1.0022 | 0.89643 | -0.10581 |  | 0.9 | 1.05 | 0.033129 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | Add 108 MVAR switched shunt at MAURINE4 230 kV
Voltage | 00NR | 2 | 29WP | V | ASGI-2024-003 | WWRDEHV4 | 1.0303 | 1.0538 | 0.023516 |  | 0.92 | 1.05 | 0.055813 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 11 MVAR switched shunt at WWRDEHV4 138 kV
Voltage | 00NR | 2 | 29WP | V | ASGI-2024-006 | WWRDEHV4 | 1.0303 | 1.0538 | 0.023516 |  | 0.92 | 1.05 | 0.12068 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 11 MVAR switched shunt at WWRDEHV4 138 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-015 | WWRDEHV4 | 1.0303 | 1.0538 | 0.023516 |  | 0.92 | 1.05 | 0.064062 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 11 MVAR switched shunt at WWRDEHV4 138 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-041 | WWRDEHV4 | 1.0303 | 1.0538 | 0.023516 |  | 0.92 | 1.05 | 0.066281 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 11 MVAR switched shunt at WWRDEHV4 138 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-042 | WWRDEHV4 | 1.0303 | 1.0538 | 0.023516 |  | 0.92 | 1.05 | 0.066281 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 11 MVAR switched shunt at WWRDEHV4 138 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-043 | WWRDEHV4 | 1.0303 | 1.0538 | 0.023516 |  | 0.92 | 1.05 | 0.063192 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 11 MVAR switched shunt at WWRDEHV4 138 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-099 | WWRDEHV4 | 1.0303 | 1.0538 | 0.023516 |  | 0.92 | 1.05 | 0.062234 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 11 MVAR switched shunt at WWRDEHV4 138 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-109 | WWRDEHV4 | 1.0303 | 1.0538 | 0.023516 |  | 0.92 | 1.05 | 0.06286 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 11 MVAR switched shunt at WWRDEHV4 138 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-143 | WWRDEHV4 | 1.0303 | 1.0538 | 0.023516 |  | 0.92 | 1.05 | 0.057886 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 11 MVAR switched shunt at WWRDEHV4 138 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-145 | WWRDEHV4 | 1.0303 | 1.0538 | 0.023516 |  | 0.92 | 1.05 | 0.057886 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 11 MVAR switched shunt at WWRDEHV4 138 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-154 | WWRDEHV4 | 1.0303 | 1.0538 | 0.023516 |  | 0.92 | 1.05 | 0.058968 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 11 MVAR switched shunt at WWRDEHV4 138 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-159 | WWRDEHV4 | 1.0303 | 1.0538 | 0.023516 |  | 0.92 | 1.05 | 0.063043 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 11 MVAR switched shunt at WWRDEHV4 138 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-221 | WWRDEHV4 | 1.0303 | 1.0538 | 0.023516 |  | 0.92 | 1.05 | 0.06343 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 11 MVAR switched shunt at WWRDEHV4 138 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-261 | WWRDEHV4 | 1.0303 | 1.0538 | 0.023516 |  | 0.92 | 1.05 | 0.064061 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 11 MVAR switched shunt at WWRDEHV4 138 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-265 | WWRDEHV4 | 1.0303 | 1.0538 | 0.023516 |  | 0.92 | 1.05 | 0.064065 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 11 MVAR switched shunt at WWRDEHV4 138 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-280 | WWRDEHV4 | 1.0303 | 1.0538 | 0.023516 |  | 0.92 | 1.05 | 0.064037 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 11 MVAR switched shunt at WWRDEHV4 138 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-281 | WWRDEHV4 | 1.0303 | 1.0538 | 0.023516 |  | 0.92 | 1.05 | 0.064122 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 11 MVAR switched shunt at WWRDEHV4 138 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-295 | WWRDEHV4 | 1.0303 | 1.0538 | 0.023516 |  | 0.92 | 1.05 | 0.064338 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 11 MVAR switched shunt at WWRDEHV4 138 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-303 | WWRDEHV4 | 1.0303 | 1.0538 | 0.023516 |  | 0.92 | 1.05 | 0.063232 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 11 MVAR switched shunt at WWRDEHV4 138 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-304 | WWRDEHV4 | 1.0303 | 1.0538 | 0.023516 |  | 0.92 | 1.05 | 0.063232 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 11 MVAR switched shunt at WWRDEHV4 138 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-311 | WWRDEHV4 | 1.0303 | 1.0538 | 0.023516 |  | 0.92 | 1.05 | 0.063759 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 11 MVAR switched shunt at WWRDEHV4 138 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-317 | WWRDEHV4 | 1.0303 | 1.0538 | 0.023516 |  | 0.92 | 1.05 | 0.0434 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 11 MVAR switched shunt at WWRDEHV4 138 kV
Voltage | 00NR | 2 | 29WP | V | GEN-2024-336 | WWRDEHV4 | 1.0303 | 1.0538 | 0.023516 |  | 0.92 | 1.05 | 0.064087 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 11 MVAR switched shunt at WWRDEHV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | 2WEIRGAT | 0.94557 | 0.91648 | -0.029092 |  | 0.92 | 1.05 | 0.53565 | P21:138:EES:HEMPHIL4!:SIXMILE4:1:HV: | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | 2WEIRGAT | 0.93591 | 0.91649 | -0.019425 |  | 0.92 | 1.05 | 0.035519 | P21:138:EES:4HLYSPG#:4NEWTONB!:1:HV: | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | 2WEIRGAT | 0.93701 | 0.91667 | -0.02034 |  | 0.92 | 1.05 | 0.039111 | P12:345:EES:LEBROCK7!:TENRUSK7!:1:EHV: | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | 2WEIRGAT | 0.93701 | 0.91667 | -0.02034 |  | 0.92 | 1.05 | 0.05544 | P12:345:EES:LEBROCK7!:TENRUSK7!:1:EHV: | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | 2WEIRGAT | 0.93701 | 0.91667 | -0.02034 |  | 0.92 | 1.05 | 0.058995 | P12:345:EES:LEBROCK7!:TENRUSK7!:1:EHV: | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | 2WEIRGAT | 0.93701 | 0.91667 | -0.02034 |  | 0.92 | 1.05 | 0.0602 | P12:345:EES:LEBROCK7!:TENRUSK7!:1:EHV: | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | 2WEIRGAT | 0.93701 | 0.91667 | -0.02034 |  | 0.92 | 1.05 | 0.058258 | P12:345:EES:LEBROCK7!:TENRUSK7!:1:EHV: | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | 2WEIRGAT | 0.93701 | 0.91667 | -0.02034 |  | 0.92 | 1.05 | 0.046532 | P12:345:EES:LEBROCK7!:TENRUSK7!:1:EHV: | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | 2WEIRGAT | 0.93701 | 0.91667 | -0.02034 |  | 0.92 | 1.05 | 0.10858 | P12:345:EES:LEBROCK7!:TENRUSK7!:1:EHV: | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | 2WEIRGAT | 0.93701 | 0.91667 | -0.02034 |  | 0.92 | 1.05 | 0.056557 | P12:345:EES:LEBROCK7!:TENRUSK7!:1:EHV: | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | 2WEIRGAT | 0.93701 | 0.91667 | -0.02034 |  | 0.92 | 1.05 | 0.05544 | P12:345:EES:LEBROCK7!:TENRUSK7!:1:EHV: | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | 2WEIRGAT | 0.94569 | 0.9168 | -0.028898 |  | 0.92 | 1.05 | 0.53565 | P12:138:EES:4LEACH!:HEMPHIL4!:1:HV: | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | 2WEIRGAT | 0.93946 | 0.91715 | -0.022307 |  | 0.92 | 1.05 | 0.039111 | 267111 | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | 2WEIRGAT | 0.93946 | 0.91715 | -0.022307 |  | 0.92 | 1.05 | 0.05544 | 267111 | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | 2WEIRGAT | 0.93946 | 0.91715 | -0.022307 |  | 0.92 | 1.05 | 0.058995 | 267111 | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | 2WEIRGAT | 0.93946 | 0.91715 | -0.022307 |  | 0.92 | 1.05 | 0.0602 | 267111 | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | 2WEIRGAT | 0.93946 | 0.91715 | -0.022307 |  | 0.92 | 1.05 | 0.058258 | 267111 | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | 2WEIRGAT | 0.93946 | 0.91715 | -0.022307 |  | 0.92 | 1.05 | 0.046532 | 267111 | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | 2WEIRGAT | 0.93946 | 0.91715 | -0.022307 |  | 0.92 | 1.05 | 0.10858 | 267111 | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | 2WEIRGAT | 0.93946 | 0.91715 | -0.022307 |  | 0.92 | 1.05 | 0.056557 | 267111 | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | 2WEIRGAT | 0.93946 | 0.91715 | -0.022307 |  | 0.92 | 1.05 | 0.05544 | 267111 | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | ALTAMNS2 | 0.95063 | 0.91945 | -0.031175 |  | 0.93 | 1.05 | 0.10484 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | ALTAMNS2 | 0.95063 | 0.91945 | -0.031175 |  | 0.93 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | ALTAMNS2 | 0.95063 | 0.91945 | -0.031175 |  | 0.93 | 1.05 | 0.086823 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | ALTAMNS2 | 0.95063 | 0.91945 | -0.031175 |  | 0.93 | 1.05 | 0.098758 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | ALTAMNS2 | 0.95063 | 0.91945 | -0.031175 |  | 0.93 | 1.05 | 0.087817 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | ALTAMNS2 | 0.95063 | 0.91945 | -0.031175 |  | 0.93 | 1.05 | 0.11285 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | ALTAMNS2 | 0.95063 | 0.91945 | -0.031175 |  | 0.93 | 1.05 | 0.11586 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | ALTAMNS2 | 0.95063 | 0.91945 | -0.031175 |  | 0.93 | 1.05 | 0.10654 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | ALTAMNS2 | 0.95063 | 0.91945 | -0.031175 |  | 0.93 | 1.05 | 0.031666 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-219 | ALTAMNS2 | 0.95063 | 0.91945 | -0.031175 |  | 0.93 | 1.05 | 0.030863 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | ALTAMNS2 | 0.95063 | 0.91945 | -0.031175 |  | 0.93 | 1.05 | 0.099811 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | ALTAMNS2 | 0.95063 | 0.91945 | -0.031175 |  | 0.93 | 1.05 | 0.10896 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | ALTAMNS2 | 0.95063 | 0.91945 | -0.031175 |  | 0.93 | 1.05 | 0.040233 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | ALTAMNS2 | 0.95063 | 0.91945 | -0.031175 |  | 0.93 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | ALTAMNS2 | 0.95063 | 0.91945 | -0.031175 |  | 0.93 | 1.05 | 0.060046 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | ALTAMNS2 | 0.95063 | 0.91945 | -0.031175 |  | 0.93 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | ALTAMNS2 | 0.95063 | 0.91945 | -0.031175 |  | 0.93 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | ALTAMNS2 | 0.95063 | 0.91945 | -0.031175 |  | 0.93 | 1.05 | 0.032555 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | ALTAMNS2 | 0.95063 | 0.91945 | -0.031175 |  | 0.93 | 1.05 | 0.031413 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | ALTAMNS2 | 0.95063 | 0.91945 | -0.031175 |  | 0.93 | 1.05 | 0.046478 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | ALTAMNS2 | 0.95063 | 0.91945 | -0.031175 |  | 0.93 | 1.05 | 0.11534 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | ALTAMNS2 | 0.95374 | 0.92435 | -0.029388 |  | 0.93 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | ALTAMNS2 | 0.95374 | 0.92435 | -0.029388 |  | 0.93 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | ALTAMNS2 | 0.95374 | 0.92435 | -0.029388 |  | 0.93 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | ALTAMNS2 | 0.95374 | 0.92435 | -0.029388 |  | 0.93 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | ALTAMNS2 | 0.95374 | 0.92435 | -0.029388 |  | 0.93 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | ALTAMNS2 | 0.95374 | 0.92435 | -0.029388 |  | 0.93 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | ALTAMNS2 | 0.95374 | 0.92435 | -0.029388 |  | 0.93 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | ALTAMNS2 | 0.95374 | 0.92435 | -0.029388 |  | 0.93 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | ALTAMNS2 | 0.95374 | 0.92435 | -0.029388 |  | 0.93 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | ALTAMNS2 | 0.95374 | 0.92435 | -0.029388 |  | 0.93 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | ALTAMNS2 | 0.95374 | 0.92435 | -0.029388 |  | 0.93 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | ALTAMNS2 | 0.95374 | 0.92435 | -0.029388 |  | 0.93 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | ALTAMNS2 | 0.95374 | 0.92435 | -0.029388 |  | 0.93 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | ALTAMNS2 | 0.95374 | 0.92435 | -0.029388 |  | 0.93 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | ALTAMNS2 | 0.95012 | 0.91884 | -0.031282 |  | 0.93 | 1.05 | 0.076984 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | ALTAMNS2 | 0.95012 | 0.91884 | -0.031282 |  | 0.93 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | ALTAMNS2 | 0.95012 | 0.91884 | -0.031282 |  | 0.93 | 1.05 | 0.065662 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | ALTAMNS2 | 0.95012 | 0.91884 | -0.031282 |  | 0.93 | 1.05 | 0.072679 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | ALTAMNS2 | 0.95012 | 0.91884 | -0.031282 |  | 0.93 | 1.05 | 0.052268 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | ALTAMNS2 | 0.95012 | 0.91884 | -0.031282 |  | 0.93 | 1.05 | 0.080584 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | ALTAMNS2 | 0.95012 | 0.91884 | -0.031282 |  | 0.93 | 1.05 | 0.082253 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | ALTAMNS2 | 0.95012 | 0.91884 | -0.031282 |  | 0.93 | 1.05 | 0.076592 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | ALTAMNS2 | 0.95012 | 0.91884 | -0.031282 |  | 0.93 | 1.05 | 0.030918 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | ALTAMNS2 | 0.95012 | 0.91884 | -0.031282 |  | 0.93 | 1.05 | 0.073312 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | ALTAMNS2 | 0.95012 | 0.91884 | -0.031282 |  | 0.93 | 1.05 | 0.076355 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | ALTAMNS2 | 0.95012 | 0.91884 | -0.031282 |  | 0.93 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | ALTAMNS2 | 0.95012 | 0.91884 | -0.031282 |  | 0.93 | 1.05 | 0.037529 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | ALTAMNS2 | 0.95012 | 0.91884 | -0.031282 |  | 0.93 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | ALTAMNS2 | 0.95012 | 0.91884 | -0.031282 |  | 0.93 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | ALTAMNS2 | 0.95012 | 0.91884 | -0.031282 |  | 0.93 | 1.05 | 0.030301 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | ALTAMNS2 | 0.95012 | 0.91884 | -0.031282 |  | 0.93 | 1.05 | 0.041779 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | ALTAMNS2 | 0.95012 | 0.91884 | -0.031282 |  | 0.93 | 1.05 | 0.079587 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | ALTAMNS2 | 0.95456 | 0.92339 | -0.031166 |  | 0.93 | 1.05 | 0.03716 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | ALTAMNS2 | 0.95456 | 0.92339 | -0.031166 |  | 0.93 | 1.05 | 0.030931 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | ALTAMNS2 | 0.95456 | 0.92339 | -0.031166 |  | 0.93 | 1.05 | 0.044459 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | ALTAMNS2 | 0.95456 | 0.92339 | -0.031166 |  | 0.93 | 1.05 | 0.041648 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | ALTAMNS2 | 0.95456 | 0.92339 | -0.031166 |  | 0.93 | 1.05 | 0.031986 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | ALTAMNS2 | 0.95456 | 0.92339 | -0.031166 |  | 0.93 | 1.05 | 0.039776 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | ALTAMNS2 | 0.95456 | 0.92339 | -0.031166 |  | 0.93 | 1.05 | 0.042349 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | ALTAMNS2 | 0.95456 | 0.92339 | -0.031166 |  | 0.93 | 1.05 | 0.041252 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | ALTAMNS2 | 0.95456 | 0.92339 | -0.031166 |  | 0.93 | 1.05 | 0.031238 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | ALTAMNS2 | 0.95456 | 0.92339 | -0.031166 |  | 0.93 | 1.05 | 0.034893 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | ALTAMNS2 | 0.95456 | 0.92339 | -0.031166 |  | 0.93 | 1.05 | 0.046335 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | ALTAMNS2 | 0.95456 | 0.92339 | -0.031166 |  | 0.93 | 1.05 | 0.034893 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | ALTAMNS2 | 0.95456 | 0.92339 | -0.031166 |  | 0.93 | 1.05 | 0.03611 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | ALTAMNS2 | 0.95456 | 0.92339 | -0.031166 |  | 0.93 | 1.05 | 0.034555 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | ALTAMNS2 | 0.95456 | 0.92339 | -0.031166 |  | 0.93 | 1.05 | 0.033454 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | ALTAMNS2 | 0.95456 | 0.92339 | -0.031166 |  | 0.93 | 1.05 | 0.045771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | ALTAMNS2 | 0.95456 | 0.92339 | -0.031166 |  | 0.93 | 1.05 | 0.031365 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | ALTAMNS2 | 0.95456 | 0.92339 | -0.031166 |  | 0.93 | 1.05 | 0.031365 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | ALTAMNS2 | 0.95456 | 0.92339 | -0.031166 |  | 0.93 | 1.05 | 0.041921 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | ALTAMNS2 | 0.95456 | 0.92339 | -0.031166 |  | 0.93 | 1.05 | 0.033154 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | ALTAMNS2 | 0.95456 | 0.92339 | -0.031166 |  | 0.93 | 1.05 | 0.03341 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | ALTAMNS2 | 0.95456 | 0.92339 | -0.031166 |  | 0.93 | 1.05 | 0.030334 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | ALTAMNS2 | 0.95456 | 0.92339 | -0.031166 |  | 0.93 | 1.05 | 0.034718 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | ALTAMNS2 | 0.95456 | 0.92339 | -0.031166 |  | 0.93 | 1.05 | 0.033533 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | ALTAMNS2 | 0.95171 | 0.91942 | -0.032298 |  | 0.93 | 1.05 | 0.038685 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | ALTAMNS2 | 0.95171 | 0.91942 | -0.032298 |  | 0.93 | 1.05 | 0.07469 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | ALTAMNS2 | 0.95171 | 0.91942 | -0.032298 |  | 0.93 | 1.05 | 0.068062 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | ALTAMNS2 | 0.95171 | 0.91942 | -0.032298 |  | 0.93 | 1.05 | 0.034938 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | ALTAMNS2 | 0.95171 | 0.91942 | -0.032298 |  | 0.93 | 1.05 | 0.032777 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | ALTAMNS2 | 0.95171 | 0.91942 | -0.032298 |  | 0.93 | 1.05 | 0.043475 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | ALTAMNS2 | 0.95171 | 0.91942 | -0.032298 |  | 0.93 | 1.05 | 0.13386 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | ALTAMNS2 | 0.95171 | 0.91942 | -0.032298 |  | 0.93 | 1.05 | 0.036067 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | ALTAMNS2 | 0.95171 | 0.91942 | -0.032298 |  | 0.93 | 1.05 | 0.036067 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | ALTAMNS2 | 0.95171 | 0.91942 | -0.032298 |  | 0.93 | 1.05 | 0.067572 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | ALTAMNS2 | 0.95171 | 0.91942 | -0.032298 |  | 0.93 | 1.05 | 0.033583 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | ALTAMNS2 | 0.95171 | 0.91942 | -0.032298 |  | 0.93 | 1.05 | 0.034115 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | ALTAMNT2 | 0.94771 | 0.91643 | -0.031278 |  | 0.93 | 1.05 | 0.10484 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | ALTAMNT2 | 0.94771 | 0.91643 | -0.031278 |  | 0.93 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | ALTAMNT2 | 0.94771 | 0.91643 | -0.031278 |  | 0.93 | 1.05 | 0.086823 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | ALTAMNT2 | 0.94771 | 0.91643 | -0.031278 |  | 0.93 | 1.05 | 0.098758 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | ALTAMNT2 | 0.94771 | 0.91643 | -0.031278 |  | 0.93 | 1.05 | 0.087817 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | ALTAMNT2 | 0.94771 | 0.91643 | -0.031278 |  | 0.93 | 1.05 | 0.11285 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | ALTAMNT2 | 0.94771 | 0.91643 | -0.031278 |  | 0.93 | 1.05 | 0.11586 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | ALTAMNT2 | 0.94771 | 0.91643 | -0.031278 |  | 0.93 | 1.05 | 0.10654 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | ALTAMNT2 | 0.94771 | 0.91643 | -0.031278 |  | 0.93 | 1.05 | 0.031666 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-219 | ALTAMNT2 | 0.94771 | 0.91643 | -0.031278 |  | 0.93 | 1.05 | 0.030863 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | ALTAMNT2 | 0.94771 | 0.91643 | -0.031278 |  | 0.93 | 1.05 | 0.099811 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | ALTAMNT2 | 0.94771 | 0.91643 | -0.031278 |  | 0.93 | 1.05 | 0.10896 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | ALTAMNT2 | 0.94771 | 0.91643 | -0.031278 |  | 0.93 | 1.05 | 0.040233 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | ALTAMNT2 | 0.94771 | 0.91643 | -0.031278 |  | 0.93 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | ALTAMNT2 | 0.94771 | 0.91643 | -0.031278 |  | 0.93 | 1.05 | 0.060046 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | ALTAMNT2 | 0.94771 | 0.91643 | -0.031278 |  | 0.93 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | ALTAMNT2 | 0.94771 | 0.91643 | -0.031278 |  | 0.93 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | ALTAMNT2 | 0.94771 | 0.91643 | -0.031278 |  | 0.93 | 1.05 | 0.032555 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | ALTAMNT2 | 0.94771 | 0.91643 | -0.031278 |  | 0.93 | 1.05 | 0.031413 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | ALTAMNT2 | 0.94771 | 0.91643 | -0.031278 |  | 0.93 | 1.05 | 0.046478 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | ALTAMNT2 | 0.94771 | 0.91643 | -0.031278 |  | 0.93 | 1.05 | 0.11534 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | ALTAMNT2 | 0.95083 | 0.92135 | -0.029485 |  | 0.93 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | ALTAMNT2 | 0.95083 | 0.92135 | -0.029485 |  | 0.93 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | ALTAMNT2 | 0.95083 | 0.92135 | -0.029485 |  | 0.93 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | ALTAMNT2 | 0.95083 | 0.92135 | -0.029485 |  | 0.93 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | ALTAMNT2 | 0.95083 | 0.92135 | -0.029485 |  | 0.93 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | ALTAMNT2 | 0.95083 | 0.92135 | -0.029485 |  | 0.93 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | ALTAMNT2 | 0.95083 | 0.92135 | -0.029485 |  | 0.93 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | ALTAMNT2 | 0.95083 | 0.92135 | -0.029485 |  | 0.93 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | ALTAMNT2 | 0.95083 | 0.92135 | -0.029485 |  | 0.93 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | ALTAMNT2 | 0.95083 | 0.92135 | -0.029485 |  | 0.93 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | ALTAMNT2 | 0.95083 | 0.92135 | -0.029485 |  | 0.93 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | ALTAMNT2 | 0.95083 | 0.92135 | -0.029485 |  | 0.93 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | ALTAMNT2 | 0.95083 | 0.92135 | -0.029485 |  | 0.93 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | ALTAMNT2 | 0.95083 | 0.92135 | -0.029485 |  | 0.93 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | ALTAMNT2 | 0.9472 | 0.91582 | -0.031386 |  | 0.93 | 1.05 | 0.076984 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | ALTAMNT2 | 0.9472 | 0.91582 | -0.031386 |  | 0.93 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | ALTAMNT2 | 0.9472 | 0.91582 | -0.031386 |  | 0.93 | 1.05 | 0.065662 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | ALTAMNT2 | 0.9472 | 0.91582 | -0.031386 |  | 0.93 | 1.05 | 0.072679 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | ALTAMNT2 | 0.9472 | 0.91582 | -0.031386 |  | 0.93 | 1.05 | 0.052268 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | ALTAMNT2 | 0.9472 | 0.91582 | -0.031386 |  | 0.93 | 1.05 | 0.080584 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | ALTAMNT2 | 0.9472 | 0.91582 | -0.031386 |  | 0.93 | 1.05 | 0.082253 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | ALTAMNT2 | 0.9472 | 0.91582 | -0.031386 |  | 0.93 | 1.05 | 0.076592 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | ALTAMNT2 | 0.9472 | 0.91582 | -0.031386 |  | 0.93 | 1.05 | 0.030918 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | ALTAMNT2 | 0.9472 | 0.91582 | -0.031386 |  | 0.93 | 1.05 | 0.073312 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | ALTAMNT2 | 0.9472 | 0.91582 | -0.031386 |  | 0.93 | 1.05 | 0.076355 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | ALTAMNT2 | 0.9472 | 0.91582 | -0.031386 |  | 0.93 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | ALTAMNT2 | 0.9472 | 0.91582 | -0.031386 |  | 0.93 | 1.05 | 0.037529 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | ALTAMNT2 | 0.9472 | 0.91582 | -0.031386 |  | 0.93 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | ALTAMNT2 | 0.9472 | 0.91582 | -0.031386 |  | 0.93 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | ALTAMNT2 | 0.9472 | 0.91582 | -0.031386 |  | 0.93 | 1.05 | 0.030301 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | ALTAMNT2 | 0.9472 | 0.91582 | -0.031386 |  | 0.93 | 1.05 | 0.041779 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | ALTAMNT2 | 0.9472 | 0.91582 | -0.031386 |  | 0.93 | 1.05 | 0.079587 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | ALTAMNT2 | 0.95165 | 0.92038 | -0.031269 |  | 0.93 | 1.05 | 0.03716 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | ALTAMNT2 | 0.95165 | 0.92038 | -0.031269 |  | 0.93 | 1.05 | 0.030931 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | ALTAMNT2 | 0.95165 | 0.92038 | -0.031269 |  | 0.93 | 1.05 | 0.044459 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | ALTAMNT2 | 0.95165 | 0.92038 | -0.031269 |  | 0.93 | 1.05 | 0.041648 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | ALTAMNT2 | 0.95165 | 0.92038 | -0.031269 |  | 0.93 | 1.05 | 0.031986 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | ALTAMNT2 | 0.95165 | 0.92038 | -0.031269 |  | 0.93 | 1.05 | 0.039776 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | ALTAMNT2 | 0.95165 | 0.92038 | -0.031269 |  | 0.93 | 1.05 | 0.042349 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | ALTAMNT2 | 0.95165 | 0.92038 | -0.031269 |  | 0.93 | 1.05 | 0.041252 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | ALTAMNT2 | 0.95165 | 0.92038 | -0.031269 |  | 0.93 | 1.05 | 0.031238 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | ALTAMNT2 | 0.95165 | 0.92038 | -0.031269 |  | 0.93 | 1.05 | 0.034893 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | ALTAMNT2 | 0.95165 | 0.92038 | -0.031269 |  | 0.93 | 1.05 | 0.046335 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | ALTAMNT2 | 0.95165 | 0.92038 | -0.031269 |  | 0.93 | 1.05 | 0.034893 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | ALTAMNT2 | 0.95165 | 0.92038 | -0.031269 |  | 0.93 | 1.05 | 0.03611 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | ALTAMNT2 | 0.95165 | 0.92038 | -0.031269 |  | 0.93 | 1.05 | 0.034555 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | ALTAMNT2 | 0.95165 | 0.92038 | -0.031269 |  | 0.93 | 1.05 | 0.033454 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | ALTAMNT2 | 0.95165 | 0.92038 | -0.031269 |  | 0.93 | 1.05 | 0.045771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | ALTAMNT2 | 0.95165 | 0.92038 | -0.031269 |  | 0.93 | 1.05 | 0.031365 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | ALTAMNT2 | 0.95165 | 0.92038 | -0.031269 |  | 0.93 | 1.05 | 0.031365 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | ALTAMNT2 | 0.95165 | 0.92038 | -0.031269 |  | 0.93 | 1.05 | 0.041921 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | ALTAMNT2 | 0.95165 | 0.92038 | -0.031269 |  | 0.93 | 1.05 | 0.033154 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | ALTAMNT2 | 0.95165 | 0.92038 | -0.031269 |  | 0.93 | 1.05 | 0.03341 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | ALTAMNT2 | 0.95165 | 0.92038 | -0.031269 |  | 0.93 | 1.05 | 0.030334 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | ALTAMNT2 | 0.95165 | 0.92038 | -0.031269 |  | 0.93 | 1.05 | 0.034718 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | ALTAMNT2 | 0.95165 | 0.92038 | -0.031269 |  | 0.93 | 1.05 | 0.033533 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | ALTAMNT2 | 0.9488 | 0.9164 | -0.032406 |  | 0.93 | 1.05 | 0.038685 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | ALTAMNT2 | 0.9488 | 0.9164 | -0.032406 |  | 0.93 | 1.05 | 0.07469 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | ALTAMNT2 | 0.9488 | 0.9164 | -0.032406 |  | 0.93 | 1.05 | 0.068062 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | ALTAMNT2 | 0.9488 | 0.9164 | -0.032406 |  | 0.93 | 1.05 | 0.034938 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | ALTAMNT2 | 0.9488 | 0.9164 | -0.032406 |  | 0.93 | 1.05 | 0.032777 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | ALTAMNT2 | 0.9488 | 0.9164 | -0.032406 |  | 0.93 | 1.05 | 0.043475 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | ALTAMNT2 | 0.9488 | 0.9164 | -0.032406 |  | 0.93 | 1.05 | 0.13386 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | ALTAMNT2 | 0.9488 | 0.9164 | -0.032406 |  | 0.93 | 1.05 | 0.036067 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | ALTAMNT2 | 0.9488 | 0.9164 | -0.032406 |  | 0.93 | 1.05 | 0.036067 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | ALTAMNT2 | 0.9488 | 0.9164 | -0.032406 |  | 0.93 | 1.05 | 0.067572 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | ALTAMNT2 | 0.9488 | 0.9164 | -0.032406 |  | 0.93 | 1.05 | 0.033583 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | ALTAMNT2 | 0.9488 | 0.9164 | -0.032406 |  | 0.93 | 1.05 | 0.034115 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | ATLNTIC7 | 0.96885 | 0.9475 | -0.021356 |  | 0.95 | 1.05 | 0.031932 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | ATLNTIC7 | 0.96885 | 0.9475 | -0.021356 |  | 0.95 | 1.05 | 0.046406 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | ATLNTIC7 | 0.96885 | 0.9475 | -0.021356 |  | 0.95 | 1.05 | 0.034669 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | ATLNTIC7 | 0.96885 | 0.9475 | -0.021356 |  | 0.95 | 1.05 | 0.036297 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | ATLNTIC7 | 0.96885 | 0.9475 | -0.021356 |  | 0.95 | 1.05 | 0.03404 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | ATLNTIC7 | 0.96885 | 0.9475 | -0.021356 |  | 0.95 | 1.05 | 0.054677 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | ATLNTIC7 | 0.96885 | 0.9475 | -0.021356 |  | 0.95 | 1.05 | 0.036731 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | ATLNTIC7 | 0.96885 | 0.9475 | -0.021356 |  | 0.95 | 1.05 | 0.035653 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | AUR124 5 | 0.96431 | 0.9219 | -0.042412 |  | 0.925 | 1.05 | 0.076984 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | AUR124 5 | 0.96431 | 0.9219 | -0.042412 |  | 0.925 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | AUR124 5 | 0.96431 | 0.9219 | -0.042412 |  | 0.925 | 1.05 | 0.065662 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | AUR124 5 | 0.96431 | 0.9219 | -0.042412 |  | 0.925 | 1.05 | 0.072679 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | AUR124 5 | 0.96431 | 0.9219 | -0.042412 |  | 0.925 | 1.05 | 0.052268 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | AUR124 5 | 0.96431 | 0.9219 | -0.042412 |  | 0.925 | 1.05 | 0.080584 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | AUR124 5 | 0.96431 | 0.9219 | -0.042412 |  | 0.925 | 1.05 | 0.082253 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | AUR124 5 | 0.96431 | 0.9219 | -0.042412 |  | 0.925 | 1.05 | 0.076592 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | AUR124 5 | 0.96431 | 0.9219 | -0.042412 |  | 0.925 | 1.05 | 0.030918 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | AUR124 5 | 0.96431 | 0.9219 | -0.042412 |  | 0.925 | 1.05 | 0.073312 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | AUR124 5 | 0.96431 | 0.9219 | -0.042412 |  | 0.925 | 1.05 | 0.076355 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | AUR124 5 | 0.96431 | 0.9219 | -0.042412 |  | 0.925 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | AUR124 5 | 0.96431 | 0.9219 | -0.042412 |  | 0.925 | 1.05 | 0.037529 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | AUR124 5 | 0.96431 | 0.9219 | -0.042412 |  | 0.925 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | AUR124 5 | 0.96431 | 0.9219 | -0.042412 |  | 0.925 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | AUR124 5 | 0.96431 | 0.9219 | -0.042412 |  | 0.925 | 1.05 | 0.030301 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | AUR124 5 | 0.96431 | 0.9219 | -0.042412 |  | 0.925 | 1.05 | 0.041779 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | AUR124 5 | 0.96431 | 0.9219 | -0.042412 |  | 0.925 | 1.05 | 0.079587 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | AUR124 5 | 0.9654 | 0.92337 | -0.042035 |  | 0.925 | 1.05 | 0.10484 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | AUR124 5 | 0.9654 | 0.92337 | -0.042035 |  | 0.925 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | AUR124 5 | 0.9654 | 0.92337 | -0.042035 |  | 0.925 | 1.05 | 0.086823 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | AUR124 5 | 0.9654 | 0.92337 | -0.042035 |  | 0.925 | 1.05 | 0.098758 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | AUR124 5 | 0.9654 | 0.92337 | -0.042035 |  | 0.925 | 1.05 | 0.087817 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | AUR124 5 | 0.9654 | 0.92337 | -0.042035 |  | 0.925 | 1.05 | 0.11285 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | AUR124 5 | 0.9654 | 0.92337 | -0.042035 |  | 0.925 | 1.05 | 0.11586 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | AUR124 5 | 0.9654 | 0.92337 | -0.042035 |  | 0.925 | 1.05 | 0.10654 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | AUR124 5 | 0.9654 | 0.92337 | -0.042035 |  | 0.925 | 1.05 | 0.031666 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-219 | AUR124 5 | 0.9654 | 0.92337 | -0.042035 |  | 0.925 | 1.05 | 0.030863 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | AUR124 5 | 0.9654 | 0.92337 | -0.042035 |  | 0.925 | 1.05 | 0.099811 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | AUR124 5 | 0.9654 | 0.92337 | -0.042035 |  | 0.925 | 1.05 | 0.10896 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | AUR124 5 | 0.9654 | 0.92337 | -0.042035 |  | 0.925 | 1.05 | 0.040233 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | AUR124 5 | 0.9654 | 0.92337 | -0.042035 |  | 0.925 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | AUR124 5 | 0.9654 | 0.92337 | -0.042035 |  | 0.925 | 1.05 | 0.060046 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | AUR124 5 | 0.9654 | 0.92337 | -0.042035 |  | 0.925 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | AUR124 5 | 0.9654 | 0.92337 | -0.042035 |  | 0.925 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | AUR124 5 | 0.9654 | 0.92337 | -0.042035 |  | 0.925 | 1.05 | 0.032555 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | AUR124 5 | 0.9654 | 0.92337 | -0.042035 |  | 0.925 | 1.05 | 0.031413 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | AUR124 5 | 0.9654 | 0.92337 | -0.042035 |  | 0.925 | 1.05 | 0.046478 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | AUR124 5 | 0.9654 | 0.92337 | -0.042035 |  | 0.925 | 1.05 | 0.11534 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | AUR124 5 | 0.96583 | 0.92405 | -0.041782 |  | 0.925 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.09 MVAR switched shunt at NOL435 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | AUR124 5 | 0.96583 | 0.92405 | -0.041782 |  | 0.925 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.09 MVAR switched shunt at NOL435 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | AUR124 5 | 0.96583 | 0.92405 | -0.041782 |  | 0.925 | 1.05 | 0.035909 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.09 MVAR switched shunt at NOL435 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | AUR124 5 | 0.96477 | 0.92401 | -0.040757 |  | 0.925 | 1.05 | 0.0423 | P23:345:AECI:7JASPER:1182::: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | AUR124 5 | 0.96477 | 0.92401 | -0.040757 |  | 0.925 | 1.05 | 0.044676 | P23:345:AECI:7JASPER:1182::: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | AUR124 5 | 0.96477 | 0.92401 | -0.040757 |  | 0.925 | 1.05 | 0.035909 | P23:345:AECI:7JASPER:1182::: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | BIRDHOL4 | 0.92779 | 0.89578 | -0.032011 |  | 0.92 | 1.05 | 0.035206 | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | BIRDHOL4 | 0.93182 | 0.90065 | -0.031176 |  | 0.92 | 1.05 | 0.035206 | Single 509752 INOLATP4 138 510442 GUAVA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | BURNS 7 | 0.99602 | 0.9483 | -0.047718 |  | 0.95 | 1.05 | 0.039244 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | BURNS 7 | 0.99602 | 0.9483 | -0.047718 |  | 0.95 | 1.05 | 0.036827 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | BURNS 7 | 0.99602 | 0.9483 | -0.047718 |  | 0.95 | 1.05 | 0.030156 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | BURNS 7 | 0.99602 | 0.9483 | -0.047718 |  | 0.95 | 1.05 | 0.034146 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | BURNS 7 | 0.99602 | 0.9483 | -0.047718 |  | 0.95 | 1.05 | 0.034933 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | BURNS 7 | 0.99602 | 0.9483 | -0.047718 |  | 0.95 | 1.05 | 0.038105 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | BURNS 7 | 0.99602 | 0.9483 | -0.047718 |  | 0.95 | 1.05 | 0.035356 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | BURNS 7 | 0.99602 | 0.9483 | -0.047718 |  | 0.95 | 1.05 | 0.040988 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | BURNS 7 | 0.99602 | 0.9483 | -0.047718 |  | 0.95 | 1.05 | 0.035356 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | BURNS 7 | 0.99602 | 0.9483 | -0.047718 |  | 0.95 | 1.05 | 0.036081 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | BURNS 7 | 0.99602 | 0.9483 | -0.047718 |  | 0.95 | 1.05 | 0.036544 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | BURNS 7 | 0.99602 | 0.9483 | -0.047718 |  | 0.95 | 1.05 | 0.038782 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | BURNS 7 | 0.99602 | 0.9483 | -0.047718 |  | 0.95 | 1.05 | 0.034598 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | BURNS 7 | 0.99602 | 0.9483 | -0.047718 |  | 0.95 | 1.05 | 0.032427 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | BURNS 7 | 0.99602 | 0.9483 | -0.047718 |  | 0.95 | 1.05 | 0.031223 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | BURNS 7 | 0.99602 | 0.9483 | -0.047718 |  | 0.95 | 1.05 | 0.033455 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | BURNS 7 | 0.99602 | 0.9483 | -0.047718 |  | 0.95 | 1.05 | 0.034045 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | CHOUTEA4 | 0.85444 | 0.82089 | -0.033554 |  | 0.92 | 1.05 | 0.035206 | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | CHOUTEA4 | 0.86422 | 0.83248 | -0.031733 |  | 0.92 | 1.05 | 0.035206 | Single 509752 INOLATP4 138 510442 GUAVA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | COOYYAH4 | 0.86982 | 0.83731 | -0.032505 |  | 0.92 | 1.05 | 0.035206 | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | COOYYAH4 | 0.87864 | 0.84778 | -0.030854 |  | 0.92 | 1.05 | 0.035206 | Single 509752 INOLATP4 138 510442 GUAVA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | CPK446 5 | 0.96276 | 0.91633 | -0.046427 |  | 0.925 | 1.05 | 0.076984 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | CPK446 5 | 0.96276 | 0.91633 | -0.046427 |  | 0.925 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | CPK446 5 | 0.96276 | 0.91633 | -0.046427 |  | 0.925 | 1.05 | 0.065662 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | CPK446 5 | 0.96276 | 0.91633 | -0.046427 |  | 0.925 | 1.05 | 0.072679 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | CPK446 5 | 0.96276 | 0.91633 | -0.046427 |  | 0.925 | 1.05 | 0.052268 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | CPK446 5 | 0.96276 | 0.91633 | -0.046427 |  | 0.925 | 1.05 | 0.080584 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | CPK446 5 | 0.96276 | 0.91633 | -0.046427 |  | 0.925 | 1.05 | 0.082253 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | CPK446 5 | 0.96276 | 0.91633 | -0.046427 |  | 0.925 | 1.05 | 0.076592 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | CPK446 5 | 0.96276 | 0.91633 | -0.046427 |  | 0.925 | 1.05 | 0.030918 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | CPK446 5 | 0.96276 | 0.91633 | -0.046427 |  | 0.925 | 1.05 | 0.073312 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | CPK446 5 | 0.96276 | 0.91633 | -0.046427 |  | 0.925 | 1.05 | 0.076355 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | CPK446 5 | 0.96276 | 0.91633 | -0.046427 |  | 0.925 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | CPK446 5 | 0.96276 | 0.91633 | -0.046427 |  | 0.925 | 1.05 | 0.037529 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | CPK446 5 | 0.96276 | 0.91633 | -0.046427 |  | 0.925 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | CPK446 5 | 0.96276 | 0.91633 | -0.046427 |  | 0.925 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | CPK446 5 | 0.96276 | 0.91633 | -0.046427 |  | 0.925 | 1.05 | 0.030301 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | CPK446 5 | 0.96276 | 0.91633 | -0.046427 |  | 0.925 | 1.05 | 0.041779 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | CPK446 5 | 0.96276 | 0.91633 | -0.046427 |  | 0.925 | 1.05 | 0.079587 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | CPK446 5 | 0.96628 | 0.92459 | -0.041689 |  | 0.925 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | CPK446 5 | 0.96628 | 0.92459 | -0.041689 |  | 0.925 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | CPK446 5 | 0.96628 | 0.92459 | -0.041689 |  | 0.925 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | CPK446 5 | 0.96628 | 0.92459 | -0.041689 |  | 0.925 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | CPK446 5 | 0.96628 | 0.92459 | -0.041689 |  | 0.925 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | CPK446 5 | 0.96628 | 0.92459 | -0.041689 |  | 0.925 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | CPK446 5 | 0.96628 | 0.92459 | -0.041689 |  | 0.925 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | CPK446 5 | 0.96628 | 0.92459 | -0.041689 |  | 0.925 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | CPK446 5 | 0.96628 | 0.92459 | -0.041689 |  | 0.925 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | CPK446 5 | 0.96628 | 0.92459 | -0.041689 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | CPK446 5 | 0.96628 | 0.92459 | -0.041689 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | CPK446 5 | 0.96628 | 0.92459 | -0.041689 |  | 0.925 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | CPK446 5 | 0.96628 | 0.92459 | -0.041689 |  | 0.925 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | CPK446 5 | 0.96628 | 0.92459 | -0.041689 |  | 0.925 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | CPK446 5 | 0.96393 | 0.91793 | -0.046005 |  | 0.925 | 1.05 | 0.10484 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | CPK446 5 | 0.96393 | 0.91793 | -0.046005 |  | 0.925 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | CPK446 5 | 0.96393 | 0.91793 | -0.046005 |  | 0.925 | 1.05 | 0.086823 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | CPK446 5 | 0.96393 | 0.91793 | -0.046005 |  | 0.925 | 1.05 | 0.098758 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | CPK446 5 | 0.96393 | 0.91793 | -0.046005 |  | 0.925 | 1.05 | 0.087817 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | CPK446 5 | 0.96393 | 0.91793 | -0.046005 |  | 0.925 | 1.05 | 0.11285 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | CPK446 5 | 0.96393 | 0.91793 | -0.046005 |  | 0.925 | 1.05 | 0.11586 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | CPK446 5 | 0.96393 | 0.91793 | -0.046005 |  | 0.925 | 1.05 | 0.10654 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | CPK446 5 | 0.96393 | 0.91793 | -0.046005 |  | 0.925 | 1.05 | 0.031666 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-219 | CPK446 5 | 0.96393 | 0.91793 | -0.046005 |  | 0.925 | 1.05 | 0.030863 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | CPK446 5 | 0.96393 | 0.91793 | -0.046005 |  | 0.925 | 1.05 | 0.099811 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | CPK446 5 | 0.96393 | 0.91793 | -0.046005 |  | 0.925 | 1.05 | 0.10896 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | CPK446 5 | 0.96393 | 0.91793 | -0.046005 |  | 0.925 | 1.05 | 0.040233 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | CPK446 5 | 0.96393 | 0.91793 | -0.046005 |  | 0.925 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | CPK446 5 | 0.96393 | 0.91793 | -0.046005 |  | 0.925 | 1.05 | 0.060046 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | CPK446 5 | 0.96393 | 0.91793 | -0.046005 |  | 0.925 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | CPK446 5 | 0.96393 | 0.91793 | -0.046005 |  | 0.925 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | CPK446 5 | 0.96393 | 0.91793 | -0.046005 |  | 0.925 | 1.05 | 0.032555 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | CPK446 5 | 0.96393 | 0.91793 | -0.046005 |  | 0.925 | 1.05 | 0.031413 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | CPK446 5 | 0.96393 | 0.91793 | -0.046005 |  | 0.925 | 1.05 | 0.046478 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | CPK446 5 | 0.96393 | 0.91793 | -0.046005 |  | 0.925 | 1.05 | 0.11534 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | CPK446 5 | 0.96691 | 0.92353 | -0.043378 |  | 0.925 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.09 MVAR switched shunt at NOL435 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | CPK446 5 | 0.96691 | 0.92353 | -0.043378 |  | 0.925 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.09 MVAR switched shunt at NOL435 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | CPK446 5 | 0.96691 | 0.92353 | -0.043378 |  | 0.925 | 1.05 | 0.035909 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.09 MVAR switched shunt at NOL435 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | CPK446 5 | 0.96484 | 0.92252 | -0.042322 |  | 0.925 | 1.05 | 0.0423 | P23:345:AECI:7JASPER:1182::: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | CPK446 5 | 0.96484 | 0.92252 | -0.042322 |  | 0.925 | 1.05 | 0.044676 | P23:345:AECI:7JASPER:1182::: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | CPK446 5 | 0.96484 | 0.92252 | -0.042322 |  | 0.925 | 1.05 | 0.035909 | P23:345:AECI:7JASPER:1182::: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | DAD368 5 | 0.96894 | 0.91738 | -0.05156 |  | 0.925 | 1.05 | 0.076984 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | DAD368 5 | 0.96894 | 0.91738 | -0.05156 |  | 0.925 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | DAD368 5 | 0.96894 | 0.91738 | -0.05156 |  | 0.925 | 1.05 | 0.065662 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | DAD368 5 | 0.96894 | 0.91738 | -0.05156 |  | 0.925 | 1.05 | 0.072679 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | DAD368 5 | 0.96894 | 0.91738 | -0.05156 |  | 0.925 | 1.05 | 0.052268 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | DAD368 5 | 0.96894 | 0.91738 | -0.05156 |  | 0.925 | 1.05 | 0.080584 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | DAD368 5 | 0.96894 | 0.91738 | -0.05156 |  | 0.925 | 1.05 | 0.082253 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | DAD368 5 | 0.96894 | 0.91738 | -0.05156 |  | 0.925 | 1.05 | 0.076592 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | DAD368 5 | 0.96894 | 0.91738 | -0.05156 |  | 0.925 | 1.05 | 0.030918 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | DAD368 5 | 0.96894 | 0.91738 | -0.05156 |  | 0.925 | 1.05 | 0.073312 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | DAD368 5 | 0.96894 | 0.91738 | -0.05156 |  | 0.925 | 1.05 | 0.076355 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | DAD368 5 | 0.96894 | 0.91738 | -0.05156 |  | 0.925 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | DAD368 5 | 0.96894 | 0.91738 | -0.05156 |  | 0.925 | 1.05 | 0.037529 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | DAD368 5 | 0.96894 | 0.91738 | -0.05156 |  | 0.925 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | DAD368 5 | 0.96894 | 0.91738 | -0.05156 |  | 0.925 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | DAD368 5 | 0.96894 | 0.91738 | -0.05156 |  | 0.925 | 1.05 | 0.030301 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | DAD368 5 | 0.96894 | 0.91738 | -0.05156 |  | 0.925 | 1.05 | 0.041779 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | DAD368 5 | 0.96894 | 0.91738 | -0.05156 |  | 0.925 | 1.05 | 0.079587 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | DAD368 5 | 0.97029 | 0.9192 | -0.051087 |  | 0.925 | 1.05 | 0.10484 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | DAD368 5 | 0.97029 | 0.9192 | -0.051087 |  | 0.925 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | DAD368 5 | 0.97029 | 0.9192 | -0.051087 |  | 0.925 | 1.05 | 0.086823 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | DAD368 5 | 0.97029 | 0.9192 | -0.051087 |  | 0.925 | 1.05 | 0.098758 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | DAD368 5 | 0.97029 | 0.9192 | -0.051087 |  | 0.925 | 1.05 | 0.087817 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | DAD368 5 | 0.97029 | 0.9192 | -0.051087 |  | 0.925 | 1.05 | 0.11285 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | DAD368 5 | 0.97029 | 0.9192 | -0.051087 |  | 0.925 | 1.05 | 0.11586 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | DAD368 5 | 0.97029 | 0.9192 | -0.051087 |  | 0.925 | 1.05 | 0.10654 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | DAD368 5 | 0.97029 | 0.9192 | -0.051087 |  | 0.925 | 1.05 | 0.031666 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-219 | DAD368 5 | 0.97029 | 0.9192 | -0.051087 |  | 0.925 | 1.05 | 0.030863 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | DAD368 5 | 0.97029 | 0.9192 | -0.051087 |  | 0.925 | 1.05 | 0.099811 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | DAD368 5 | 0.97029 | 0.9192 | -0.051087 |  | 0.925 | 1.05 | 0.10896 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | DAD368 5 | 0.97029 | 0.9192 | -0.051087 |  | 0.925 | 1.05 | 0.040233 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | DAD368 5 | 0.97029 | 0.9192 | -0.051087 |  | 0.925 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | DAD368 5 | 0.97029 | 0.9192 | -0.051087 |  | 0.925 | 1.05 | 0.060046 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | DAD368 5 | 0.97029 | 0.9192 | -0.051087 |  | 0.925 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | DAD368 5 | 0.97029 | 0.9192 | -0.051087 |  | 0.925 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | DAD368 5 | 0.97029 | 0.9192 | -0.051087 |  | 0.925 | 1.05 | 0.032555 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | DAD368 5 | 0.97029 | 0.9192 | -0.051087 |  | 0.925 | 1.05 | 0.031413 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | DAD368 5 | 0.97029 | 0.9192 | -0.051087 |  | 0.925 | 1.05 | 0.046478 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | DAD368 5 | 0.97029 | 0.9192 | -0.051087 |  | 0.925 | 1.05 | 0.11534 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | EXPCLAR4 | 0.86925 | 0.83672 | -0.032531 |  | 0.92 | 1.05 | 0.035206 | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | EXPCLAR4 | 0.87808 | 0.8472 | -0.030879 |  | 0.92 | 1.05 | 0.035206 | Single 509752 INOLATP4 138 510442 GUAVA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | G15052_1 | 0.97247 | 0.92871 | -0.043752 |  | 0.95 | 1.05 | 0.039244 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | G15052_1 | 0.97247 | 0.92871 | -0.043752 |  | 0.95 | 1.05 | 0.036827 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | G15052_1 | 0.97247 | 0.92871 | -0.043752 |  | 0.95 | 1.05 | 0.030156 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | G15052_1 | 0.97247 | 0.92871 | -0.043752 |  | 0.95 | 1.05 | 0.034146 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | G15052_1 | 0.97247 | 0.92871 | -0.043752 |  | 0.95 | 1.05 | 0.034933 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | G15052_1 | 0.97247 | 0.92871 | -0.043752 |  | 0.95 | 1.05 | 0.038105 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | G15052_1 | 0.97247 | 0.92871 | -0.043752 |  | 0.95 | 1.05 | 0.035356 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | G15052_1 | 0.97247 | 0.92871 | -0.043752 |  | 0.95 | 1.05 | 0.040988 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | G15052_1 | 0.97247 | 0.92871 | -0.043752 |  | 0.95 | 1.05 | 0.035356 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | G15052_1 | 0.97247 | 0.92871 | -0.043752 |  | 0.95 | 1.05 | 0.036081 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | G15052_1 | 0.97247 | 0.92871 | -0.043752 |  | 0.95 | 1.05 | 0.036544 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | G15052_1 | 0.97247 | 0.92871 | -0.043752 |  | 0.95 | 1.05 | 0.038782 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | G15052_1 | 0.97247 | 0.92871 | -0.043752 |  | 0.95 | 1.05 | 0.034598 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | G15052_1 | 0.97247 | 0.92871 | -0.043752 |  | 0.95 | 1.05 | 0.032427 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | G15052_1 | 0.97247 | 0.92871 | -0.043752 |  | 0.95 | 1.05 | 0.031223 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | G15052_1 | 0.97247 | 0.92871 | -0.043752 |  | 0.95 | 1.05 | 0.033455 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | G15052_1 | 0.97247 | 0.92871 | -0.043752 |  | 0.95 | 1.05 | 0.034045 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | G15052_1 | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.085024 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | G15052_1 | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.068374 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | G15052_1 | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.036961 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | G15052_1 | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.04749 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-219 | G15052_1 | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.053642 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | G15052_1 | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.060646 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | G15052_1 | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.048916 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | G15052_1 | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.074511 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | G15052_1 | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.074511 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | G15052_1 | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.079839 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | G15052_1 | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.075254 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | G15052_1 | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.03087 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | G15052_1 | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.039114 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | G15052_1 | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.039114 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | G15052_1 | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.070577 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | G15052_1 | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.047143 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | G15052_1 | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.058151 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | G15052_1 | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.057268 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | G15052_1 | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.060696 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | G15052_1 | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.065312 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | G15052_1 | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.04053 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | G15052_1 | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.085024 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | G15052_1 | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.068374 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | G15052_1 | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.036961 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | G15052_1 | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.04749 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-219 | G15052_1 | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.053642 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | G15052_1 | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.060646 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | G15052_1 | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.048916 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | G15052_1 | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.074511 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | G15052_1 | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.074511 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | G15052_1 | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.079839 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | G15052_1 | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.075254 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | G15052_1 | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.03087 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | G15052_1 | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.039114 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | G15052_1 | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.039114 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | G15052_1 | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.070577 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | G15052_1 | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.047143 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | G15052_1 | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.058151 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | G15052_1 | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.057268 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | G15052_1 | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.060696 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | G15052_1 | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.065312 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | G15052_1 | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.04053 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | G15052_1 | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.085024 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | G15052_1 | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.068374 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | G15052_1 | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.036961 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | G15052_1 | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.04749 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-219 | G15052_1 | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.053642 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | G15052_1 | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.060646 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | G15052_1 | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.048916 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | G15052_1 | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.074511 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | G15052_1 | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.074511 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | G15052_1 | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.079839 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | G15052_1 | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.075254 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | G15052_1 | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.03087 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | G15052_1 | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.039114 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | G15052_1 | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.039114 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | G15052_1 | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.070577 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | G15052_1 | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.047143 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | G15052_1 | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.058151 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | G15052_1 | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.057268 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | G15052_1 | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.060696 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | G15052_1 | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.065312 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | G15052_1 | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.04053 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | G15052_1 | 0.97958 | 0.9372 | -0.042384 |  | 0.95 | 1.05 | 0.038121 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | G15052_1 | 0.97958 | 0.9372 | -0.042384 |  | 0.95 | 1.05 | 0.090062 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | G15052_1 | 0.97958 | 0.9372 | -0.042384 |  | 0.95 | 1.05 | 0.032262 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-219 | G15052_1 | 0.97958 | 0.9372 | -0.042384 |  | 0.95 | 1.05 | 0.035926 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | G15052_1 | 0.97958 | 0.9372 | -0.042384 |  | 0.95 | 1.05 | 0.047479 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | G15052_1 | 0.97958 | 0.9372 | -0.042384 |  | 0.95 | 1.05 | 0.047479 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | G15052_1 | 0.97958 | 0.9372 | -0.042384 |  | 0.95 | 1.05 | 0.049391 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | G15052_1 | 0.97958 | 0.9372 | -0.042384 |  | 0.95 | 1.05 | 0.04011 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | G15052_1 | 0.97958 | 0.9372 | -0.042384 |  | 0.95 | 1.05 | 0.042108 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | G15052_1 | 0.97958 | 0.9372 | -0.042384 |  | 0.95 | 1.05 | 0.032601 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | G15052_1 | 0.97958 | 0.9372 | -0.042384 |  | 0.95 | 1.05 | 0.035239 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | G15052_1 | 0.97958 | 0.9372 | -0.042384 |  | 0.95 | 1.05 | 0.048632 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | G15052_T | 0.97247 | 0.92871 | -0.043752 |  | 0.95 | 1.05 | 0.039244 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | G15052_T | 0.97247 | 0.92871 | -0.043752 |  | 0.95 | 1.05 | 0.036827 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | G15052_T | 0.97247 | 0.92871 | -0.043752 |  | 0.95 | 1.05 | 0.030156 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | G15052_T | 0.97247 | 0.92871 | -0.043752 |  | 0.95 | 1.05 | 0.034146 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | G15052_T | 0.97247 | 0.92871 | -0.043752 |  | 0.95 | 1.05 | 0.034933 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | G15052_T | 0.97247 | 0.92871 | -0.043752 |  | 0.95 | 1.05 | 0.038105 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | G15052_T | 0.97247 | 0.92871 | -0.043752 |  | 0.95 | 1.05 | 0.035356 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | G15052_T | 0.97247 | 0.92871 | -0.043752 |  | 0.95 | 1.05 | 0.040988 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | G15052_T | 0.97247 | 0.92871 | -0.043752 |  | 0.95 | 1.05 | 0.035356 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | G15052_T | 0.97247 | 0.92871 | -0.043752 |  | 0.95 | 1.05 | 0.036081 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | G15052_T | 0.97247 | 0.92871 | -0.043752 |  | 0.95 | 1.05 | 0.036544 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | G15052_T | 0.97247 | 0.92871 | -0.043752 |  | 0.95 | 1.05 | 0.038782 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | G15052_T | 0.97247 | 0.92871 | -0.043752 |  | 0.95 | 1.05 | 0.034598 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | G15052_T | 0.97247 | 0.92871 | -0.043752 |  | 0.95 | 1.05 | 0.032427 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | G15052_T | 0.97247 | 0.92871 | -0.043752 |  | 0.95 | 1.05 | 0.031223 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | G15052_T | 0.97247 | 0.92871 | -0.043752 |  | 0.95 | 1.05 | 0.033455 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | G15052_T | 0.97247 | 0.92871 | -0.043752 |  | 0.95 | 1.05 | 0.034045 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | G15052_T | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.085024 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | G15052_T | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.068374 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | G15052_T | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.036961 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | G15052_T | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.04749 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-219 | G15052_T | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.053642 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | G15052_T | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.060646 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | G15052_T | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.048916 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | G15052_T | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.074511 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | G15052_T | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.074511 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | G15052_T | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.079839 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | G15052_T | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.075254 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | G15052_T | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.03087 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | G15052_T | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.039114 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | G15052_T | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.039114 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | G15052_T | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.070577 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | G15052_T | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.047143 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | G15052_T | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.058151 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | G15052_T | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.057268 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | G15052_T | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.060696 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | G15052_T | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.065312 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | G15052_T | 0.97734 | 0.93291 | -0.044426 |  | 0.95 | 1.05 | 0.04053 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | G15052_T | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.085024 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | G15052_T | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.068374 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | G15052_T | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.036961 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | G15052_T | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.04749 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-219 | G15052_T | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.053642 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | G15052_T | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.060646 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | G15052_T | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.048916 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | G15052_T | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.074511 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | G15052_T | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.074511 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | G15052_T | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.079839 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | G15052_T | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.075254 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | G15052_T | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.03087 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | G15052_T | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.039114 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | G15052_T | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.039114 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | G15052_T | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.070577 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | G15052_T | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.047143 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | G15052_T | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.058151 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | G15052_T | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.057268 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | G15052_T | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.060696 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | G15052_T | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.065312 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | G15052_T | 0.97748 | 0.93319 | -0.044292 |  | 0.95 | 1.05 | 0.04053 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | G15052_T | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.085024 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | G15052_T | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.068374 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | G15052_T | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.036961 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | G15052_T | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.04749 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-219 | G15052_T | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.053642 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | G15052_T | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.060646 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | G15052_T | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.048916 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | G15052_T | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.074511 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | G15052_T | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.074511 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | G15052_T | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.079839 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | G15052_T | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.075254 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | G15052_T | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.03087 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | G15052_T | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.039114 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | G15052_T | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.039114 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | G15052_T | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.070577 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | G15052_T | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.047143 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | G15052_T | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.058151 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | G15052_T | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.057268 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | G15052_T | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.060696 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | G15052_T | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.065312 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | G15052_T | 0.97851 | 0.93477 | -0.043742 |  | 0.95 | 1.05 | 0.04053 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | G15052_T | 0.97958 | 0.9372 | -0.042384 |  | 0.95 | 1.05 | 0.038121 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | G15052_T | 0.97958 | 0.9372 | -0.042384 |  | 0.95 | 1.05 | 0.090062 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | G15052_T | 0.97958 | 0.9372 | -0.042384 |  | 0.95 | 1.05 | 0.032262 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-219 | G15052_T | 0.97958 | 0.9372 | -0.042384 |  | 0.95 | 1.05 | 0.035926 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | G15052_T | 0.97958 | 0.9372 | -0.042384 |  | 0.95 | 1.05 | 0.047479 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | G15052_T | 0.97958 | 0.9372 | -0.042384 |  | 0.95 | 1.05 | 0.047479 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | G15052_T | 0.97958 | 0.9372 | -0.042384 |  | 0.95 | 1.05 | 0.049391 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | G15052_T | 0.97958 | 0.9372 | -0.042384 |  | 0.95 | 1.05 | 0.04011 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | G15052_T | 0.97958 | 0.9372 | -0.042384 |  | 0.95 | 1.05 | 0.042108 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | G15052_T | 0.97958 | 0.9372 | -0.042384 |  | 0.95 | 1.05 | 0.032601 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | G15052_T | 0.97958 | 0.9372 | -0.042384 |  | 0.95 | 1.05 | 0.035239 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | G15052_T | 0.97958 | 0.9372 | -0.042384 |  | 0.95 | 1.05 | 0.048632 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | G16-111-TAP | 0.98685 | 0.94359 | -0.043255 |  | 0.95 | 1.05 | 0.03716 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | G16-111-TAP | 0.98685 | 0.94359 | -0.043255 |  | 0.95 | 1.05 | 0.030931 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | G16-111-TAP | 0.98685 | 0.94359 | -0.043255 |  | 0.95 | 1.05 | 0.044459 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | G16-111-TAP | 0.98685 | 0.94359 | -0.043255 |  | 0.95 | 1.05 | 0.041648 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | G16-111-TAP | 0.98685 | 0.94359 | -0.043255 |  | 0.95 | 1.05 | 0.031986 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | G16-111-TAP | 0.98685 | 0.94359 | -0.043255 |  | 0.95 | 1.05 | 0.039776 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | G16-111-TAP | 0.98685 | 0.94359 | -0.043255 |  | 0.95 | 1.05 | 0.042349 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | G16-111-TAP | 0.98685 | 0.94359 | -0.043255 |  | 0.95 | 1.05 | 0.041252 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | G16-111-TAP | 0.98685 | 0.94359 | -0.043255 |  | 0.95 | 1.05 | 0.031238 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | G16-111-TAP | 0.98685 | 0.94359 | -0.043255 |  | 0.95 | 1.05 | 0.034893 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | G16-111-TAP | 0.98685 | 0.94359 | -0.043255 |  | 0.95 | 1.05 | 0.046335 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | G16-111-TAP | 0.98685 | 0.94359 | -0.043255 |  | 0.95 | 1.05 | 0.034893 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | G16-111-TAP | 0.98685 | 0.94359 | -0.043255 |  | 0.95 | 1.05 | 0.03611 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | G16-111-TAP | 0.98685 | 0.94359 | -0.043255 |  | 0.95 | 1.05 | 0.034555 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | G16-111-TAP | 0.98685 | 0.94359 | -0.043255 |  | 0.95 | 1.05 | 0.033454 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | G16-111-TAP | 0.98685 | 0.94359 | -0.043255 |  | 0.95 | 1.05 | 0.045771 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | G16-111-TAP | 0.98685 | 0.94359 | -0.043255 |  | 0.95 | 1.05 | 0.031365 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | G16-111-TAP | 0.98685 | 0.94359 | -0.043255 |  | 0.95 | 1.05 | 0.031365 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | G16-111-TAP | 0.98685 | 0.94359 | -0.043255 |  | 0.95 | 1.05 | 0.041921 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | G16-111-TAP | 0.98685 | 0.94359 | -0.043255 |  | 0.95 | 1.05 | 0.033154 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | G16-111-TAP | 0.98685 | 0.94359 | -0.043255 |  | 0.95 | 1.05 | 0.03341 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | G16-111-TAP | 0.98685 | 0.94359 | -0.043255 |  | 0.95 | 1.05 | 0.030334 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | G16-111-TAP | 0.98685 | 0.94359 | -0.043255 |  | 0.95 | 1.05 | 0.034718 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | G16-111-TAP | 0.98685 | 0.94359 | -0.043255 |  | 0.95 | 1.05 | 0.033533 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | G20-092-TAP | 0.90914 | 0.87956 | -0.029577 |  | 0.92 | 1.05 | 0.035206 | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | G20-092-TAP | 0.91515 | 0.88673 | -0.02842 |  | 0.92 | 1.05 | 0.035206 | Single 509752 INOLATP4 138 510442 GUAVA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | G21-096-TAP | 0.98806 | 0.93893 | -0.049123 |  | 0.95 | 1.05 | 0.039244 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | G21-096-TAP | 0.98806 | 0.93893 | -0.049123 |  | 0.95 | 1.05 | 0.036827 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | G21-096-TAP | 0.98806 | 0.93893 | -0.049123 |  | 0.95 | 1.05 | 0.030156 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | G21-096-TAP | 0.98806 | 0.93893 | -0.049123 |  | 0.95 | 1.05 | 0.034146 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | G21-096-TAP | 0.98806 | 0.93893 | -0.049123 |  | 0.95 | 1.05 | 0.034933 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | G21-096-TAP | 0.98806 | 0.93893 | -0.049123 |  | 0.95 | 1.05 | 0.038105 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | G21-096-TAP | 0.98806 | 0.93893 | -0.049123 |  | 0.95 | 1.05 | 0.035356 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | G21-096-TAP | 0.98806 | 0.93893 | -0.049123 |  | 0.95 | 1.05 | 0.040988 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | G21-096-TAP | 0.98806 | 0.93893 | -0.049123 |  | 0.95 | 1.05 | 0.035356 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | G21-096-TAP | 0.98806 | 0.93893 | -0.049123 |  | 0.95 | 1.05 | 0.036081 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | G21-096-TAP | 0.98806 | 0.93893 | -0.049123 |  | 0.95 | 1.05 | 0.036544 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | G21-096-TAP | 0.98806 | 0.93893 | -0.049123 |  | 0.95 | 1.05 | 0.038782 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | G21-096-TAP | 0.98806 | 0.93893 | -0.049123 |  | 0.95 | 1.05 | 0.034598 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | G21-096-TAP | 0.98806 | 0.93893 | -0.049123 |  | 0.95 | 1.05 | 0.032427 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | G21-096-TAP | 0.98806 | 0.93893 | -0.049123 |  | 0.95 | 1.05 | 0.031223 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | G21-096-TAP | 0.98806 | 0.93893 | -0.049123 |  | 0.95 | 1.05 | 0.033455 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | G21-096-TAP | 0.98806 | 0.93893 | -0.049123 |  | 0.95 | 1.05 | 0.034045 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | G23-220-TAP | 0.97543 | 0.94327 | -0.032153 |  | 0.95 | 1.05 | 0.031932 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | G23-220-TAP | 0.97543 | 0.94327 | -0.032153 |  | 0.95 | 1.05 | 0.046406 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | G23-220-TAP | 0.97543 | 0.94327 | -0.032153 |  | 0.95 | 1.05 | 0.034669 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | G23-220-TAP | 0.97543 | 0.94327 | -0.032153 |  | 0.95 | 1.05 | 0.036297 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | G23-220-TAP | 0.97543 | 0.94327 | -0.032153 |  | 0.95 | 1.05 | 0.03404 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | G23-220-TAP | 0.97543 | 0.94327 | -0.032153 |  | 0.95 | 1.05 | 0.054677 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | G23-220-TAP | 0.97543 | 0.94327 | -0.032153 |  | 0.95 | 1.05 | 0.036731 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | G23-220-TAP | 0.97543 | 0.94327 | -0.032153 |  | 0.95 | 1.05 | 0.035653 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | G23-220-TAP | 0.97764 | 0.94439 | -0.033251 |  | 0.95 | 1.05 | 0.031932 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | G23-220-TAP | 0.97764 | 0.94439 | -0.033251 |  | 0.95 | 1.05 | 0.046406 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | G23-220-TAP | 0.97764 | 0.94439 | -0.033251 |  | 0.95 | 1.05 | 0.034669 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | G23-220-TAP | 0.97764 | 0.94439 | -0.033251 |  | 0.95 | 1.05 | 0.036297 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | G23-220-TAP | 0.97764 | 0.94439 | -0.033251 |  | 0.95 | 1.05 | 0.03404 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | G23-220-TAP | 0.97764 | 0.94439 | -0.033251 |  | 0.95 | 1.05 | 0.054677 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | G23-220-TAP | 0.97764 | 0.94439 | -0.033251 |  | 0.95 | 1.05 | 0.036731 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | G23-220-TAP | 0.97764 | 0.94439 | -0.033251 |  | 0.95 | 1.05 | 0.035653 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | G23-220-TAP | 0.97771 | 0.94542 | -0.032296 |  | 0.95 | 1.05 | 0.037599 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | G23-220-TAP | 0.97771 | 0.94542 | -0.032296 |  | 0.95 | 1.05 | 0.032501 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | G23-220-TAP | 0.97771 | 0.94542 | -0.032296 |  | 0.95 | 1.05 | 0.033287 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | G23-220-TAP | 0.97771 | 0.94542 | -0.032296 |  | 0.95 | 1.05 | 0.036459 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | G23-220-TAP | 0.97771 | 0.94542 | -0.032296 |  | 0.95 | 1.05 | 0.033711 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | G23-220-TAP | 0.97771 | 0.94542 | -0.032296 |  | 0.95 | 1.05 | 0.033711 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | G23-220-TAP | 0.97771 | 0.94542 | -0.032296 |  | 0.95 | 1.05 | 0.034436 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | G23-220-TAP | 0.97771 | 0.94542 | -0.032296 |  | 0.95 | 1.05 | 0.034899 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | G23-220-TAP | 0.97771 | 0.94542 | -0.032296 |  | 0.95 | 1.05 | 0.032952 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | G23-220-TAP | 0.97771 | 0.94542 | -0.032296 |  | 0.95 | 1.05 | 0.030781 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | G23-220-TAP | 0.97771 | 0.94542 | -0.032296 |  | 0.95 | 1.05 | 0.03181 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | G23-220-TAP | 0.97771 | 0.94542 | -0.032296 |  | 0.95 | 1.05 | 0.032399 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | G23-220-TAP | 0.97774 | 0.94542 | -0.032325 |  | 0.95 | 1.05 | 0.037599 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | G23-220-TAP | 0.97774 | 0.94542 | -0.032325 |  | 0.95 | 1.05 | 0.032501 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | G23-220-TAP | 0.97774 | 0.94542 | -0.032325 |  | 0.95 | 1.05 | 0.033287 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | G23-220-TAP | 0.97774 | 0.94542 | -0.032325 |  | 0.95 | 1.05 | 0.036459 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | G23-220-TAP | 0.97774 | 0.94542 | -0.032325 |  | 0.95 | 1.05 | 0.033711 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | G23-220-TAP | 0.97774 | 0.94542 | -0.032325 |  | 0.95 | 1.05 | 0.033711 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | G23-220-TAP | 0.97774 | 0.94542 | -0.032325 |  | 0.95 | 1.05 | 0.034436 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | G23-220-TAP | 0.97774 | 0.94542 | -0.032325 |  | 0.95 | 1.05 | 0.034899 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | G23-220-TAP | 0.97774 | 0.94542 | -0.032325 |  | 0.95 | 1.05 | 0.032952 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | G23-220-TAP | 0.97774 | 0.94542 | -0.032325 |  | 0.95 | 1.05 | 0.030781 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | G23-220-TAP | 0.97774 | 0.94542 | -0.032325 |  | 0.95 | 1.05 | 0.03181 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | G23-220-TAP | 0.97774 | 0.94542 | -0.032325 |  | 0.95 | 1.05 | 0.032399 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | G23-220-TAP | 0.97057 | 0.9374 | -0.033167 |  | 0.95 | 1.05 | 0.037599 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | G23-220-TAP | 0.97057 | 0.9374 | -0.033167 |  | 0.95 | 1.05 | 0.03567 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | G23-220-TAP | 0.97057 | 0.9374 | -0.033167 |  | 0.95 | 1.05 | 0.032501 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | G23-220-TAP | 0.97057 | 0.9374 | -0.033167 |  | 0.95 | 1.05 | 0.033287 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | G23-220-TAP | 0.97057 | 0.9374 | -0.033167 |  | 0.95 | 1.05 | 0.036459 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | G23-220-TAP | 0.97057 | 0.9374 | -0.033167 |  | 0.95 | 1.05 | 0.033711 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | G23-220-TAP | 0.97057 | 0.9374 | -0.033167 |  | 0.95 | 1.05 | 0.042545 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | G23-220-TAP | 0.97057 | 0.9374 | -0.033167 |  | 0.95 | 1.05 | 0.033711 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | G23-220-TAP | 0.97057 | 0.9374 | -0.033167 |  | 0.95 | 1.05 | 0.034436 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | G23-220-TAP | 0.97057 | 0.9374 | -0.033167 |  | 0.95 | 1.05 | 0.034899 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | G23-220-TAP | 0.97057 | 0.9374 | -0.033167 |  | 0.95 | 1.05 | 0.032952 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | G23-220-TAP | 0.97057 | 0.9374 | -0.033167 |  | 0.95 | 1.05 | 0.030781 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | G23-220-TAP | 0.97057 | 0.9374 | -0.033167 |  | 0.95 | 1.05 | 0.03181 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | G23-220-TAP | 0.97057 | 0.9374 | -0.033167 |  | 0.95 | 1.05 | 0.032399 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | G23-221-TAP | 0.97607 | 0.94394 | -0.032135 |  | 0.95 | 1.05 | 0.031932 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | G23-221-TAP | 0.97607 | 0.94394 | -0.032135 |  | 0.95 | 1.05 | 0.046406 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | G23-221-TAP | 0.97607 | 0.94394 | -0.032135 |  | 0.95 | 1.05 | 0.034669 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | G23-221-TAP | 0.97607 | 0.94394 | -0.032135 |  | 0.95 | 1.05 | 0.036297 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | G23-221-TAP | 0.97607 | 0.94394 | -0.032135 |  | 0.95 | 1.05 | 0.03404 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | G23-221-TAP | 0.97607 | 0.94394 | -0.032135 |  | 0.95 | 1.05 | 0.054677 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | G23-221-TAP | 0.97607 | 0.94394 | -0.032135 |  | 0.95 | 1.05 | 0.036731 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | G23-221-TAP | 0.97607 | 0.94394 | -0.032135 |  | 0.95 | 1.05 | 0.035653 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | G23-221-TAP | 0.97823 | 0.945 | -0.033227 |  | 0.95 | 1.05 | 0.031932 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | G23-221-TAP | 0.97823 | 0.945 | -0.033227 |  | 0.95 | 1.05 | 0.046406 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | G23-221-TAP | 0.97823 | 0.945 | -0.033227 |  | 0.95 | 1.05 | 0.034669 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | G23-221-TAP | 0.97823 | 0.945 | -0.033227 |  | 0.95 | 1.05 | 0.036297 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | G23-221-TAP | 0.97823 | 0.945 | -0.033227 |  | 0.95 | 1.05 | 0.03404 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | G23-221-TAP | 0.97823 | 0.945 | -0.033227 |  | 0.95 | 1.05 | 0.054677 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | G23-221-TAP | 0.97823 | 0.945 | -0.033227 |  | 0.95 | 1.05 | 0.036731 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | G23-221-TAP | 0.97823 | 0.945 | -0.033227 |  | 0.95 | 1.05 | 0.035653 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | G23-221-TAP | 0.97823 | 0.94584 | -0.032389 |  | 0.95 | 1.05 | 0.037599 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | G23-221-TAP | 0.97823 | 0.94584 | -0.032389 |  | 0.95 | 1.05 | 0.032501 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | G23-221-TAP | 0.97823 | 0.94584 | -0.032389 |  | 0.95 | 1.05 | 0.033287 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | G23-221-TAP | 0.97823 | 0.94584 | -0.032389 |  | 0.95 | 1.05 | 0.036459 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | G23-221-TAP | 0.97823 | 0.94584 | -0.032389 |  | 0.95 | 1.05 | 0.033711 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | G23-221-TAP | 0.97823 | 0.94584 | -0.032389 |  | 0.95 | 1.05 | 0.033711 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | G23-221-TAP | 0.97823 | 0.94584 | -0.032389 |  | 0.95 | 1.05 | 0.034436 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | G23-221-TAP | 0.97823 | 0.94584 | -0.032389 |  | 0.95 | 1.05 | 0.034899 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | G23-221-TAP | 0.97823 | 0.94584 | -0.032389 |  | 0.95 | 1.05 | 0.032952 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | G23-221-TAP | 0.97823 | 0.94584 | -0.032389 |  | 0.95 | 1.05 | 0.030781 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | G23-221-TAP | 0.97823 | 0.94584 | -0.032389 |  | 0.95 | 1.05 | 0.03181 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | G23-221-TAP | 0.97823 | 0.94584 | -0.032389 |  | 0.95 | 1.05 | 0.032399 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | G23-221-TAP | 0.97826 | 0.94584 | -0.032418 |  | 0.95 | 1.05 | 0.037599 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | G23-221-TAP | 0.97826 | 0.94584 | -0.032418 |  | 0.95 | 1.05 | 0.032501 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | G23-221-TAP | 0.97826 | 0.94584 | -0.032418 |  | 0.95 | 1.05 | 0.033287 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | G23-221-TAP | 0.97826 | 0.94584 | -0.032418 |  | 0.95 | 1.05 | 0.036459 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | G23-221-TAP | 0.97826 | 0.94584 | -0.032418 |  | 0.95 | 1.05 | 0.033711 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | G23-221-TAP | 0.97826 | 0.94584 | -0.032418 |  | 0.95 | 1.05 | 0.033711 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | G23-221-TAP | 0.97826 | 0.94584 | -0.032418 |  | 0.95 | 1.05 | 0.034436 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | G23-221-TAP | 0.97826 | 0.94584 | -0.032418 |  | 0.95 | 1.05 | 0.034899 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | G23-221-TAP | 0.97826 | 0.94584 | -0.032418 |  | 0.95 | 1.05 | 0.032952 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | G23-221-TAP | 0.97826 | 0.94584 | -0.032418 |  | 0.95 | 1.05 | 0.030781 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | G23-221-TAP | 0.97826 | 0.94584 | -0.032418 |  | 0.95 | 1.05 | 0.03181 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | G23-221-TAP | 0.97826 | 0.94584 | -0.032418 |  | 0.95 | 1.05 | 0.032399 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | G23-221-TAP | 0.97118 | 0.93797 | -0.033209 |  | 0.95 | 1.05 | 0.037599 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | G23-221-TAP | 0.97118 | 0.93797 | -0.033209 |  | 0.95 | 1.05 | 0.03567 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | G23-221-TAP | 0.97118 | 0.93797 | -0.033209 |  | 0.95 | 1.05 | 0.032501 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | G23-221-TAP | 0.97118 | 0.93797 | -0.033209 |  | 0.95 | 1.05 | 0.033287 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | G23-221-TAP | 0.97118 | 0.93797 | -0.033209 |  | 0.95 | 1.05 | 0.036459 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | G23-221-TAP | 0.97118 | 0.93797 | -0.033209 |  | 0.95 | 1.05 | 0.033711 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | G23-221-TAP | 0.97118 | 0.93797 | -0.033209 |  | 0.95 | 1.05 | 0.042545 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | G23-221-TAP | 0.97118 | 0.93797 | -0.033209 |  | 0.95 | 1.05 | 0.033711 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | G23-221-TAP | 0.97118 | 0.93797 | -0.033209 |  | 0.95 | 1.05 | 0.034436 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | G23-221-TAP | 0.97118 | 0.93797 | -0.033209 |  | 0.95 | 1.05 | 0.034899 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | G23-221-TAP | 0.97118 | 0.93797 | -0.033209 |  | 0.95 | 1.05 | 0.032952 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | G23-221-TAP | 0.97118 | 0.93797 | -0.033209 |  | 0.95 | 1.05 | 0.030781 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | G23-221-TAP | 0.97118 | 0.93797 | -0.033209 |  | 0.95 | 1.05 | 0.03181 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | G23-221-TAP | 0.97118 | 0.93797 | -0.033209 |  | 0.95 | 1.05 | 0.032399 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | GEN-2016-111 | 0.98776 | 0.94447 | -0.043295 |  | 0.95 | 1.05 | 0.03716 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | GEN-2016-111 | 0.98776 | 0.94447 | -0.043295 |  | 0.95 | 1.05 | 0.030931 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | GEN-2016-111 | 0.98776 | 0.94447 | -0.043295 |  | 0.95 | 1.05 | 0.044459 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | GEN-2016-111 | 0.98776 | 0.94447 | -0.043295 |  | 0.95 | 1.05 | 0.041648 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | GEN-2016-111 | 0.98776 | 0.94447 | -0.043295 |  | 0.95 | 1.05 | 0.031986 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | GEN-2016-111 | 0.98776 | 0.94447 | -0.043295 |  | 0.95 | 1.05 | 0.039776 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | GEN-2016-111 | 0.98776 | 0.94447 | -0.043295 |  | 0.95 | 1.05 | 0.042349 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | GEN-2016-111 | 0.98776 | 0.94447 | -0.043295 |  | 0.95 | 1.05 | 0.041252 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | GEN-2016-111 | 0.98776 | 0.94447 | -0.043295 |  | 0.95 | 1.05 | 0.031238 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | GEN-2016-111 | 0.98776 | 0.94447 | -0.043295 |  | 0.95 | 1.05 | 0.034893 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | GEN-2016-111 | 0.98776 | 0.94447 | -0.043295 |  | 0.95 | 1.05 | 0.046335 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | GEN-2016-111 | 0.98776 | 0.94447 | -0.043295 |  | 0.95 | 1.05 | 0.034893 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | GEN-2016-111 | 0.98776 | 0.94447 | -0.043295 |  | 0.95 | 1.05 | 0.03611 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | GEN-2016-111 | 0.98776 | 0.94447 | -0.043295 |  | 0.95 | 1.05 | 0.034555 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | GEN-2016-111 | 0.98776 | 0.94447 | -0.043295 |  | 0.95 | 1.05 | 0.033454 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | GEN-2016-111 | 0.98776 | 0.94447 | -0.043295 |  | 0.95 | 1.05 | 0.045771 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | GEN-2016-111 | 0.98776 | 0.94447 | -0.043295 |  | 0.95 | 1.05 | 0.031365 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | GEN-2016-111 | 0.98776 | 0.94447 | -0.043295 |  | 0.95 | 1.05 | 0.031365 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | GEN-2016-111 | 0.98776 | 0.94447 | -0.043295 |  | 0.95 | 1.05 | 0.041921 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | GEN-2016-111 | 0.98776 | 0.94447 | -0.043295 |  | 0.95 | 1.05 | 0.033154 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | GEN-2016-111 | 0.98776 | 0.94447 | -0.043295 |  | 0.95 | 1.05 | 0.03341 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | GEN-2016-111 | 0.98776 | 0.94447 | -0.043295 |  | 0.95 | 1.05 | 0.030334 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | GEN-2016-111 | 0.98776 | 0.94447 | -0.043295 |  | 0.95 | 1.05 | 0.034718 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | GEN-2016-111 | 0.98776 | 0.94447 | -0.043295 |  | 0.95 | 1.05 | 0.033533 | P51:13:WERE:EMPEC 7:EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | GEN-2017-074 | 0.9141 | 0.88492 | -0.029186 |  | 0.92 | 1.05 | 0.035206 | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | GEN-2017-074 | 0.91973 | 0.89163 | -0.028096 |  | 0.92 | 1.05 | 0.035206 | Single 509752 INOLATP4 138 510442 GUAVA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | GEN-2017-077 | 0.86982 | 0.83731 | -0.032505 |  | 0.92 | 1.05 | 0.035206 | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | GEN-2017-077 | 0.87864 | 0.84778 | -0.030854 |  | 0.92 | 1.05 | 0.035206 | Single 509752 INOLATP4 138 510442 GUAVA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | GEN-2017-195 | 0.96116 | 0.93704 | -0.024117 |  | 0.95 | 1.05 | 0.031932 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | GEN-2017-195 | 0.96116 | 0.93704 | -0.024117 |  | 0.95 | 1.05 | 0.046406 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | GEN-2017-195 | 0.96116 | 0.93704 | -0.024117 |  | 0.95 | 1.05 | 0.034669 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | GEN-2017-195 | 0.96116 | 0.93704 | -0.024117 |  | 0.95 | 1.05 | 0.036297 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | GEN-2017-195 | 0.96116 | 0.93704 | -0.024117 |  | 0.95 | 1.05 | 0.03404 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | GEN-2017-195 | 0.96116 | 0.93704 | -0.024117 |  | 0.95 | 1.05 | 0.054677 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | GEN-2017-195 | 0.96116 | 0.93704 | -0.024117 |  | 0.95 | 1.05 | 0.036731 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | GEN-2017-195 | 0.96116 | 0.93704 | -0.024117 |  | 0.95 | 1.05 | 0.035653 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | GEN-2017-195 | 0.97156 | 0.94564 | -0.025923 |  | 0.95 | 1.05 | 0.031932 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | GEN-2017-195 | 0.97156 | 0.94564 | -0.025923 |  | 0.95 | 1.05 | 0.046406 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | GEN-2017-195 | 0.97156 | 0.94564 | -0.025923 |  | 0.95 | 1.05 | 0.034669 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | GEN-2017-195 | 0.97156 | 0.94564 | -0.025923 |  | 0.95 | 1.05 | 0.036297 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | GEN-2017-195 | 0.97156 | 0.94564 | -0.025923 |  | 0.95 | 1.05 | 0.03404 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | GEN-2017-195 | 0.97156 | 0.94564 | -0.025923 |  | 0.95 | 1.05 | 0.054677 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | GEN-2017-195 | 0.97156 | 0.94564 | -0.025923 |  | 0.95 | 1.05 | 0.036731 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | GEN-2017-195 | 0.97156 | 0.94564 | -0.025923 |  | 0.95 | 1.05 | 0.035653 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | GEN-2019-016 | 0.96904 | 0.91747 | -0.051565 |  | 0.925 | 1.05 | 0.076984 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | GEN-2019-016 | 0.96904 | 0.91747 | -0.051565 |  | 0.925 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | GEN-2019-016 | 0.96904 | 0.91747 | -0.051565 |  | 0.925 | 1.05 | 0.065662 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | GEN-2019-016 | 0.96904 | 0.91747 | -0.051565 |  | 0.925 | 1.05 | 0.072679 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | GEN-2019-016 | 0.96904 | 0.91747 | -0.051565 |  | 0.925 | 1.05 | 0.052268 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | GEN-2019-016 | 0.96904 | 0.91747 | -0.051565 |  | 0.925 | 1.05 | 0.080584 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | GEN-2019-016 | 0.96904 | 0.91747 | -0.051565 |  | 0.925 | 1.05 | 0.082253 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | GEN-2019-016 | 0.96904 | 0.91747 | -0.051565 |  | 0.925 | 1.05 | 0.076592 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | GEN-2019-016 | 0.96904 | 0.91747 | -0.051565 |  | 0.925 | 1.05 | 0.030918 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | GEN-2019-016 | 0.96904 | 0.91747 | -0.051565 |  | 0.925 | 1.05 | 0.073312 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | GEN-2019-016 | 0.96904 | 0.91747 | -0.051565 |  | 0.925 | 1.05 | 0.076355 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | GEN-2019-016 | 0.96904 | 0.91747 | -0.051565 |  | 0.925 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | GEN-2019-016 | 0.96904 | 0.91747 | -0.051565 |  | 0.925 | 1.05 | 0.037529 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | GEN-2019-016 | 0.96904 | 0.91747 | -0.051565 |  | 0.925 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | GEN-2019-016 | 0.96904 | 0.91747 | -0.051565 |  | 0.925 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | GEN-2019-016 | 0.96904 | 0.91747 | -0.051565 |  | 0.925 | 1.05 | 0.030301 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | GEN-2019-016 | 0.96904 | 0.91747 | -0.051565 |  | 0.925 | 1.05 | 0.041779 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | GEN-2019-016 | 0.96904 | 0.91747 | -0.051565 |  | 0.925 | 1.05 | 0.079587 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | GEN-2019-016 | 0.97038 | 0.91929 | -0.051092 |  | 0.925 | 1.05 | 0.10484 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | GEN-2019-016 | 0.97038 | 0.91929 | -0.051092 |  | 0.925 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | GEN-2019-016 | 0.97038 | 0.91929 | -0.051092 |  | 0.925 | 1.05 | 0.086823 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | GEN-2019-016 | 0.97038 | 0.91929 | -0.051092 |  | 0.925 | 1.05 | 0.098758 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | GEN-2019-016 | 0.97038 | 0.91929 | -0.051092 |  | 0.925 | 1.05 | 0.087817 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | GEN-2019-016 | 0.97038 | 0.91929 | -0.051092 |  | 0.925 | 1.05 | 0.11285 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | GEN-2019-016 | 0.97038 | 0.91929 | -0.051092 |  | 0.925 | 1.05 | 0.11586 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | GEN-2019-016 | 0.97038 | 0.91929 | -0.051092 |  | 0.925 | 1.05 | 0.10654 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | GEN-2019-016 | 0.97038 | 0.91929 | -0.051092 |  | 0.925 | 1.05 | 0.031666 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-219 | GEN-2019-016 | 0.97038 | 0.91929 | -0.051092 |  | 0.925 | 1.05 | 0.030863 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | GEN-2019-016 | 0.97038 | 0.91929 | -0.051092 |  | 0.925 | 1.05 | 0.099811 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | GEN-2019-016 | 0.97038 | 0.91929 | -0.051092 |  | 0.925 | 1.05 | 0.10896 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | GEN-2019-016 | 0.97038 | 0.91929 | -0.051092 |  | 0.925 | 1.05 | 0.040233 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | GEN-2019-016 | 0.97038 | 0.91929 | -0.051092 |  | 0.925 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | GEN-2019-016 | 0.97038 | 0.91929 | -0.051092 |  | 0.925 | 1.05 | 0.060046 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | GEN-2019-016 | 0.97038 | 0.91929 | -0.051092 |  | 0.925 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | GEN-2019-016 | 0.97038 | 0.91929 | -0.051092 |  | 0.925 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | GEN-2019-016 | 0.97038 | 0.91929 | -0.051092 |  | 0.925 | 1.05 | 0.032555 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | GEN-2019-016 | 0.97038 | 0.91929 | -0.051092 |  | 0.925 | 1.05 | 0.031413 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | GEN-2019-016 | 0.97038 | 0.91929 | -0.051092 |  | 0.925 | 1.05 | 0.046478 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | GEN-2019-016 | 0.97038 | 0.91929 | -0.051092 |  | 0.925 | 1.05 | 0.11534 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | GEN-2020-057 | 0.96885 | 0.9475 | -0.021356 |  | 0.95 | 1.05 | 0.031932 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | GEN-2020-057 | 0.96885 | 0.9475 | -0.021356 |  | 0.95 | 1.05 | 0.046406 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | GEN-2020-057 | 0.96885 | 0.9475 | -0.021356 |  | 0.95 | 1.05 | 0.034669 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | GEN-2020-057 | 0.96885 | 0.9475 | -0.021356 |  | 0.95 | 1.05 | 0.036297 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | GEN-2020-057 | 0.96885 | 0.9475 | -0.021356 |  | 0.95 | 1.05 | 0.03404 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | GEN-2020-057 | 0.96885 | 0.9475 | -0.021356 |  | 0.95 | 1.05 | 0.054677 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | GEN-2020-057 | 0.96885 | 0.9475 | -0.021356 |  | 0.95 | 1.05 | 0.036731 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | GEN-2020-057 | 0.96885 | 0.9475 | -0.021356 |  | 0.95 | 1.05 | 0.035653 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | GEN-2020-058 | 0.96885 | 0.9475 | -0.021356 |  | 0.95 | 1.05 | 0.031932 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | GEN-2020-058 | 0.96885 | 0.9475 | -0.021356 |  | 0.95 | 1.05 | 0.046406 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | GEN-2020-058 | 0.96885 | 0.9475 | -0.021356 |  | 0.95 | 1.05 | 0.034669 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | GEN-2020-058 | 0.96885 | 0.9475 | -0.021356 |  | 0.95 | 1.05 | 0.036297 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | GEN-2020-058 | 0.96885 | 0.9475 | -0.021356 |  | 0.95 | 1.05 | 0.03404 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | GEN-2020-058 | 0.96885 | 0.9475 | -0.021356 |  | 0.95 | 1.05 | 0.054677 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | GEN-2020-058 | 0.96885 | 0.9475 | -0.021356 |  | 0.95 | 1.05 | 0.036731 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | GEN-2020-058 | 0.96885 | 0.9475 | -0.021356 |  | 0.95 | 1.05 | 0.035653 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | GEN-2020-092 | 0.90914 | 0.87956 | -0.029577 |  | 0.92 | 1.05 | 0.035206 | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | GEN-2020-092 | 0.91515 | 0.88673 | -0.02842 |  | 0.92 | 1.05 | 0.035206 | Single 509752 INOLATP4 138 510442 GUAVA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | GEN-2021-096 | 0.98806 | 0.93893 | -0.049123 |  | 0.95 | 1.05 | 0.039244 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | GEN-2021-096 | 0.98806 | 0.93893 | -0.049123 |  | 0.95 | 1.05 | 0.036827 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | GEN-2021-096 | 0.98806 | 0.93893 | -0.049123 |  | 0.95 | 1.05 | 0.030156 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | GEN-2021-096 | 0.98806 | 0.93893 | -0.049123 |  | 0.95 | 1.05 | 0.034146 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | GEN-2021-096 | 0.98806 | 0.93893 | -0.049123 |  | 0.95 | 1.05 | 0.034933 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | GEN-2021-096 | 0.98806 | 0.93893 | -0.049123 |  | 0.95 | 1.05 | 0.038105 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | GEN-2021-096 | 0.98806 | 0.93893 | -0.049123 |  | 0.95 | 1.05 | 0.035356 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | GEN-2021-096 | 0.98806 | 0.93893 | -0.049123 |  | 0.95 | 1.05 | 0.040988 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | GEN-2021-096 | 0.98806 | 0.93893 | -0.049123 |  | 0.95 | 1.05 | 0.035356 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | GEN-2021-096 | 0.98806 | 0.93893 | -0.049123 |  | 0.95 | 1.05 | 0.036081 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | GEN-2021-096 | 0.98806 | 0.93893 | -0.049123 |  | 0.95 | 1.05 | 0.036544 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | GEN-2021-096 | 0.98806 | 0.93893 | -0.049123 |  | 0.95 | 1.05 | 0.038782 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | GEN-2021-096 | 0.98806 | 0.93893 | -0.049123 |  | 0.95 | 1.05 | 0.034598 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | GEN-2021-096 | 0.98806 | 0.93893 | -0.049123 |  | 0.95 | 1.05 | 0.032427 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | GEN-2021-096 | 0.98806 | 0.93893 | -0.049123 |  | 0.95 | 1.05 | 0.031223 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | GEN-2021-096 | 0.98806 | 0.93893 | -0.049123 |  | 0.95 | 1.05 | 0.033455 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | GEN-2021-096 | 0.98806 | 0.93893 | -0.049123 |  | 0.95 | 1.05 | 0.034045 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | GEN-2021-107 | 0.96914 | 0.94853 | -0.020608 |  | 0.95 | 1.05 | 0.031932 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | GEN-2021-107 | 0.96914 | 0.94853 | -0.020608 |  | 0.95 | 1.05 | 0.046406 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | GEN-2021-107 | 0.96914 | 0.94853 | -0.020608 |  | 0.95 | 1.05 | 0.034669 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | GEN-2021-107 | 0.96914 | 0.94853 | -0.020608 |  | 0.95 | 1.05 | 0.036297 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | GEN-2021-107 | 0.96914 | 0.94853 | -0.020608 |  | 0.95 | 1.05 | 0.03404 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | GEN-2021-107 | 0.96914 | 0.94853 | -0.020608 |  | 0.95 | 1.05 | 0.054677 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | GEN-2021-107 | 0.96914 | 0.94853 | -0.020608 |  | 0.95 | 1.05 | 0.036731 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | GEN-2021-107 | 0.96914 | 0.94853 | -0.020608 |  | 0.95 | 1.05 | 0.035653 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | GEN-2023-220 | 0.97543 | 0.94327 | -0.032153 |  | 0.95 | 1.05 | 0.031932 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | GEN-2023-220 | 0.97543 | 0.94327 | -0.032153 |  | 0.95 | 1.05 | 0.046406 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | GEN-2023-220 | 0.97543 | 0.94327 | -0.032153 |  | 0.95 | 1.05 | 0.034669 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | GEN-2023-220 | 0.97543 | 0.94327 | -0.032153 |  | 0.95 | 1.05 | 0.036297 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | GEN-2023-220 | 0.97543 | 0.94327 | -0.032153 |  | 0.95 | 1.05 | 0.03404 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | GEN-2023-220 | 0.97543 | 0.94327 | -0.032153 |  | 0.95 | 1.05 | 0.054677 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | GEN-2023-220 | 0.97543 | 0.94327 | -0.032153 |  | 0.95 | 1.05 | 0.036731 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | GEN-2023-220 | 0.97543 | 0.94327 | -0.032153 |  | 0.95 | 1.05 | 0.035653 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | GEN-2023-220 | 0.97764 | 0.94439 | -0.033251 |  | 0.95 | 1.05 | 0.031932 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | GEN-2023-220 | 0.97764 | 0.94439 | -0.033251 |  | 0.95 | 1.05 | 0.046406 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | GEN-2023-220 | 0.97764 | 0.94439 | -0.033251 |  | 0.95 | 1.05 | 0.034669 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | GEN-2023-220 | 0.97764 | 0.94439 | -0.033251 |  | 0.95 | 1.05 | 0.036297 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | GEN-2023-220 | 0.97764 | 0.94439 | -0.033251 |  | 0.95 | 1.05 | 0.03404 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | GEN-2023-220 | 0.97764 | 0.94439 | -0.033251 |  | 0.95 | 1.05 | 0.054677 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | GEN-2023-220 | 0.97764 | 0.94439 | -0.033251 |  | 0.95 | 1.05 | 0.036731 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | GEN-2023-220 | 0.97764 | 0.94439 | -0.033251 |  | 0.95 | 1.05 | 0.035653 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | GEN-2023-220 | 0.97771 | 0.94542 | -0.032296 |  | 0.95 | 1.05 | 0.037599 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | GEN-2023-220 | 0.97771 | 0.94542 | -0.032296 |  | 0.95 | 1.05 | 0.032501 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | GEN-2023-220 | 0.97771 | 0.94542 | -0.032296 |  | 0.95 | 1.05 | 0.033287 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | GEN-2023-220 | 0.97771 | 0.94542 | -0.032296 |  | 0.95 | 1.05 | 0.036459 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | GEN-2023-220 | 0.97771 | 0.94542 | -0.032296 |  | 0.95 | 1.05 | 0.033711 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | GEN-2023-220 | 0.97771 | 0.94542 | -0.032296 |  | 0.95 | 1.05 | 0.033711 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | GEN-2023-220 | 0.97771 | 0.94542 | -0.032296 |  | 0.95 | 1.05 | 0.034436 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | GEN-2023-220 | 0.97771 | 0.94542 | -0.032296 |  | 0.95 | 1.05 | 0.034899 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | GEN-2023-220 | 0.97771 | 0.94542 | -0.032296 |  | 0.95 | 1.05 | 0.032952 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | GEN-2023-220 | 0.97771 | 0.94542 | -0.032296 |  | 0.95 | 1.05 | 0.030781 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | GEN-2023-220 | 0.97771 | 0.94542 | -0.032296 |  | 0.95 | 1.05 | 0.03181 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | GEN-2023-220 | 0.97771 | 0.94542 | -0.032296 |  | 0.95 | 1.05 | 0.032399 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | GEN-2023-220 | 0.97774 | 0.94542 | -0.032325 |  | 0.95 | 1.05 | 0.037599 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | GEN-2023-220 | 0.97774 | 0.94542 | -0.032325 |  | 0.95 | 1.05 | 0.032501 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | GEN-2023-220 | 0.97774 | 0.94542 | -0.032325 |  | 0.95 | 1.05 | 0.033287 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | GEN-2023-220 | 0.97774 | 0.94542 | -0.032325 |  | 0.95 | 1.05 | 0.036459 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | GEN-2023-220 | 0.97774 | 0.94542 | -0.032325 |  | 0.95 | 1.05 | 0.033711 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | GEN-2023-220 | 0.97774 | 0.94542 | -0.032325 |  | 0.95 | 1.05 | 0.033711 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | GEN-2023-220 | 0.97774 | 0.94542 | -0.032325 |  | 0.95 | 1.05 | 0.034436 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | GEN-2023-220 | 0.97774 | 0.94542 | -0.032325 |  | 0.95 | 1.05 | 0.034899 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | GEN-2023-220 | 0.97774 | 0.94542 | -0.032325 |  | 0.95 | 1.05 | 0.032952 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | GEN-2023-220 | 0.97774 | 0.94542 | -0.032325 |  | 0.95 | 1.05 | 0.030781 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | GEN-2023-220 | 0.97774 | 0.94542 | -0.032325 |  | 0.95 | 1.05 | 0.03181 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | GEN-2023-220 | 0.97774 | 0.94542 | -0.032325 |  | 0.95 | 1.05 | 0.032399 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | GEN-2023-220 | 0.97057 | 0.9374 | -0.033167 |  | 0.95 | 1.05 | 0.037599 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | GEN-2023-220 | 0.97057 | 0.9374 | -0.033167 |  | 0.95 | 1.05 | 0.03567 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | GEN-2023-220 | 0.97057 | 0.9374 | -0.033167 |  | 0.95 | 1.05 | 0.032501 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | GEN-2023-220 | 0.97057 | 0.9374 | -0.033167 |  | 0.95 | 1.05 | 0.033287 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | GEN-2023-220 | 0.97057 | 0.9374 | -0.033167 |  | 0.95 | 1.05 | 0.036459 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | GEN-2023-220 | 0.97057 | 0.9374 | -0.033167 |  | 0.95 | 1.05 | 0.033711 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | GEN-2023-220 | 0.97057 | 0.9374 | -0.033167 |  | 0.95 | 1.05 | 0.042545 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | GEN-2023-220 | 0.97057 | 0.9374 | -0.033167 |  | 0.95 | 1.05 | 0.033711 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | GEN-2023-220 | 0.97057 | 0.9374 | -0.033167 |  | 0.95 | 1.05 | 0.034436 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | GEN-2023-220 | 0.97057 | 0.9374 | -0.033167 |  | 0.95 | 1.05 | 0.034899 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | GEN-2023-220 | 0.97057 | 0.9374 | -0.033167 |  | 0.95 | 1.05 | 0.032952 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | GEN-2023-220 | 0.97057 | 0.9374 | -0.033167 |  | 0.95 | 1.05 | 0.030781 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | GEN-2023-220 | 0.97057 | 0.9374 | -0.033167 |  | 0.95 | 1.05 | 0.03181 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | GEN-2023-220 | 0.97057 | 0.9374 | -0.033167 |  | 0.95 | 1.05 | 0.032399 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | GEN-2023-221 | 0.97607 | 0.94394 | -0.032135 |  | 0.95 | 1.05 | 0.031932 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | GEN-2023-221 | 0.97607 | 0.94394 | -0.032135 |  | 0.95 | 1.05 | 0.046406 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | GEN-2023-221 | 0.97607 | 0.94394 | -0.032135 |  | 0.95 | 1.05 | 0.034669 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | GEN-2023-221 | 0.97607 | 0.94394 | -0.032135 |  | 0.95 | 1.05 | 0.036297 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | GEN-2023-221 | 0.97607 | 0.94394 | -0.032135 |  | 0.95 | 1.05 | 0.03404 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | GEN-2023-221 | 0.97607 | 0.94394 | -0.032135 |  | 0.95 | 1.05 | 0.054677 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | GEN-2023-221 | 0.97607 | 0.94394 | -0.032135 |  | 0.95 | 1.05 | 0.036731 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | GEN-2023-221 | 0.97607 | 0.94394 | -0.032135 |  | 0.95 | 1.05 | 0.035653 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | GEN-2023-221 | 0.97823 | 0.945 | -0.033227 |  | 0.95 | 1.05 | 0.031932 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | GEN-2023-221 | 0.97823 | 0.945 | -0.033227 |  | 0.95 | 1.05 | 0.046406 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | GEN-2023-221 | 0.97823 | 0.945 | -0.033227 |  | 0.95 | 1.05 | 0.034669 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | GEN-2023-221 | 0.97823 | 0.945 | -0.033227 |  | 0.95 | 1.05 | 0.036297 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | GEN-2023-221 | 0.97823 | 0.945 | -0.033227 |  | 0.95 | 1.05 | 0.03404 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | GEN-2023-221 | 0.97823 | 0.945 | -0.033227 |  | 0.95 | 1.05 | 0.054677 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | GEN-2023-221 | 0.97823 | 0.945 | -0.033227 |  | 0.95 | 1.05 | 0.036731 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | GEN-2023-221 | 0.97823 | 0.945 | -0.033227 |  | 0.95 | 1.05 | 0.035653 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | GEN-2023-221 | 0.97823 | 0.94584 | -0.032389 |  | 0.95 | 1.05 | 0.037599 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | GEN-2023-221 | 0.97823 | 0.94584 | -0.032389 |  | 0.95 | 1.05 | 0.032501 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | GEN-2023-221 | 0.97823 | 0.94584 | -0.032389 |  | 0.95 | 1.05 | 0.033287 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | GEN-2023-221 | 0.97823 | 0.94584 | -0.032389 |  | 0.95 | 1.05 | 0.036459 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | GEN-2023-221 | 0.97823 | 0.94584 | -0.032389 |  | 0.95 | 1.05 | 0.033711 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | GEN-2023-221 | 0.97823 | 0.94584 | -0.032389 |  | 0.95 | 1.05 | 0.033711 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | GEN-2023-221 | 0.97823 | 0.94584 | -0.032389 |  | 0.95 | 1.05 | 0.034436 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | GEN-2023-221 | 0.97823 | 0.94584 | -0.032389 |  | 0.95 | 1.05 | 0.034899 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | GEN-2023-221 | 0.97823 | 0.94584 | -0.032389 |  | 0.95 | 1.05 | 0.032952 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | GEN-2023-221 | 0.97823 | 0.94584 | -0.032389 |  | 0.95 | 1.05 | 0.030781 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | GEN-2023-221 | 0.97823 | 0.94584 | -0.032389 |  | 0.95 | 1.05 | 0.03181 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | GEN-2023-221 | 0.97823 | 0.94584 | -0.032389 |  | 0.95 | 1.05 | 0.032399 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | GEN-2023-221 | 0.97826 | 0.94584 | -0.032418 |  | 0.95 | 1.05 | 0.037599 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | GEN-2023-221 | 0.97826 | 0.94584 | -0.032418 |  | 0.95 | 1.05 | 0.032501 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | GEN-2023-221 | 0.97826 | 0.94584 | -0.032418 |  | 0.95 | 1.05 | 0.033287 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | GEN-2023-221 | 0.97826 | 0.94584 | -0.032418 |  | 0.95 | 1.05 | 0.036459 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | GEN-2023-221 | 0.97826 | 0.94584 | -0.032418 |  | 0.95 | 1.05 | 0.033711 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | GEN-2023-221 | 0.97826 | 0.94584 | -0.032418 |  | 0.95 | 1.05 | 0.033711 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | GEN-2023-221 | 0.97826 | 0.94584 | -0.032418 |  | 0.95 | 1.05 | 0.034436 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | GEN-2023-221 | 0.97826 | 0.94584 | -0.032418 |  | 0.95 | 1.05 | 0.034899 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | GEN-2023-221 | 0.97826 | 0.94584 | -0.032418 |  | 0.95 | 1.05 | 0.032952 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | GEN-2023-221 | 0.97826 | 0.94584 | -0.032418 |  | 0.95 | 1.05 | 0.030781 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | GEN-2023-221 | 0.97826 | 0.94584 | -0.032418 |  | 0.95 | 1.05 | 0.03181 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | GEN-2023-221 | 0.97826 | 0.94584 | -0.032418 |  | 0.95 | 1.05 | 0.032399 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | GEN-2023-221 | 0.97118 | 0.93797 | -0.033209 |  | 0.95 | 1.05 | 0.037599 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | GEN-2023-221 | 0.97118 | 0.93797 | -0.033209 |  | 0.95 | 1.05 | 0.03567 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | GEN-2023-221 | 0.97118 | 0.93797 | -0.033209 |  | 0.95 | 1.05 | 0.032501 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | GEN-2023-221 | 0.97118 | 0.93797 | -0.033209 |  | 0.95 | 1.05 | 0.033287 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | GEN-2023-221 | 0.97118 | 0.93797 | -0.033209 |  | 0.95 | 1.05 | 0.036459 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | GEN-2023-221 | 0.97118 | 0.93797 | -0.033209 |  | 0.95 | 1.05 | 0.033711 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | GEN-2023-221 | 0.97118 | 0.93797 | -0.033209 |  | 0.95 | 1.05 | 0.042545 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | GEN-2023-221 | 0.97118 | 0.93797 | -0.033209 |  | 0.95 | 1.05 | 0.033711 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | GEN-2023-221 | 0.97118 | 0.93797 | -0.033209 |  | 0.95 | 1.05 | 0.034436 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | GEN-2023-221 | 0.97118 | 0.93797 | -0.033209 |  | 0.95 | 1.05 | 0.034899 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | GEN-2023-221 | 0.97118 | 0.93797 | -0.033209 |  | 0.95 | 1.05 | 0.032952 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | GEN-2023-221 | 0.97118 | 0.93797 | -0.033209 |  | 0.95 | 1.05 | 0.030781 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | GEN-2023-221 | 0.97118 | 0.93797 | -0.033209 |  | 0.95 | 1.05 | 0.03181 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | GEN-2023-221 | 0.97118 | 0.93797 | -0.033209 |  | 0.95 | 1.05 | 0.032399 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | GEN-2024-249 | 0.96914 | 0.94853 | -0.020608 |  | 0.95 | 1.05 | 0.031932 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | GEN-2024-249 | 0.96914 | 0.94853 | -0.020608 |  | 0.95 | 1.05 | 0.046406 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | GEN-2024-249 | 0.96914 | 0.94853 | -0.020608 |  | 0.95 | 1.05 | 0.034669 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | GEN-2024-249 | 0.96914 | 0.94853 | -0.020608 |  | 0.95 | 1.05 | 0.036297 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | GEN-2024-249 | 0.96914 | 0.94853 | -0.020608 |  | 0.95 | 1.05 | 0.03404 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | GEN-2024-249 | 0.96914 | 0.94853 | -0.020608 |  | 0.95 | 1.05 | 0.054677 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | GEN-2024-249 | 0.96914 | 0.94853 | -0.020608 |  | 0.95 | 1.05 | 0.036731 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | GEN-2024-249 | 0.96914 | 0.94853 | -0.020608 |  | 0.95 | 1.05 | 0.035653 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | GROVE 4 | 0.95542 | 0.90663 | -0.048788 |  | 0.92 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | GROVE 4 | 0.95542 | 0.90663 | -0.048788 |  | 0.92 | 1.05 | 0.0423 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | GROVE 4 | 0.95542 | 0.90663 | -0.048788 |  | 0.92 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | GROVE 4 | 0.95542 | 0.90663 | -0.048788 |  | 0.92 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | GROVE 4 | 0.95542 | 0.90663 | -0.048788 |  | 0.92 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | GROVE 4 | 0.95542 | 0.90663 | -0.048788 |  | 0.92 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | GROVE 4 | 0.95542 | 0.90663 | -0.048788 |  | 0.92 | 1.05 | 0.044676 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | GROVE 4 | 0.95542 | 0.90663 | -0.048788 |  | 0.92 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | GROVE 4 | 0.95542 | 0.90663 | -0.048788 |  | 0.92 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | GROVE 4 | 0.95542 | 0.90663 | -0.048788 |  | 0.92 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | GROVE 4 | 0.95542 | 0.90663 | -0.048788 |  | 0.92 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | GROVE 4 | 0.95542 | 0.90663 | -0.048788 |  | 0.92 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | GROVE 4 | 0.95542 | 0.90663 | -0.048788 |  | 0.92 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | GROVE 4 | 0.95542 | 0.90663 | -0.048788 |  | 0.92 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | GROVE 4 | 0.95479 | 0.90388 | -0.050906 |  | 0.92 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | GROVE 4 | 0.95479 | 0.90388 | -0.050906 |  | 0.92 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | GROVE 4 | 0.95479 | 0.90388 | -0.050906 |  | 0.92 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | GROVE 4 | 0.95479 | 0.90388 | -0.050906 |  | 0.92 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | GROVE 4 | 0.95479 | 0.90388 | -0.050906 |  | 0.92 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | GROVE 4 | 0.95479 | 0.90388 | -0.050906 |  | 0.92 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | GROVE 4 | 0.95479 | 0.90388 | -0.050906 |  | 0.92 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | GROVE 4 | 0.95479 | 0.90388 | -0.050906 |  | 0.92 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | GROVE 4 | 0.95479 | 0.90388 | -0.050906 |  | 0.92 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | GROVE 4 | 0.95479 | 0.90388 | -0.050906 |  | 0.92 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | GROVE 4 | 0.95479 | 0.90388 | -0.050906 |  | 0.92 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | GROVE 4 | 0.95479 | 0.90388 | -0.050906 |  | 0.92 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | GROVE 4 | 0.95479 | 0.90388 | -0.050906 |  | 0.92 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | GROVE 4 | 0.95479 | 0.90388 | -0.050906 |  | 0.92 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | GROVE 4 | 0.95946 | 0.91013 | -0.049336 |  | 0.92 | 1.05 | 0.076984 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | GROVE 4 | 0.95946 | 0.91013 | -0.049336 |  | 0.92 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | GROVE 4 | 0.95946 | 0.91013 | -0.049336 |  | 0.92 | 1.05 | 0.065662 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | GROVE 4 | 0.95946 | 0.91013 | -0.049336 |  | 0.92 | 1.05 | 0.072679 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | GROVE 4 | 0.95946 | 0.91013 | -0.049336 |  | 0.92 | 1.05 | 0.052268 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | GROVE 4 | 0.95946 | 0.91013 | -0.049336 |  | 0.92 | 1.05 | 0.080584 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | GROVE 4 | 0.95946 | 0.91013 | -0.049336 |  | 0.92 | 1.05 | 0.082253 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | GROVE 4 | 0.95946 | 0.91013 | -0.049336 |  | 0.92 | 1.05 | 0.076592 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | GROVE 4 | 0.95946 | 0.91013 | -0.049336 |  | 0.92 | 1.05 | 0.030918 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | GROVE 4 | 0.95946 | 0.91013 | -0.049336 |  | 0.92 | 1.05 | 0.073312 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | GROVE 4 | 0.95946 | 0.91013 | -0.049336 |  | 0.92 | 1.05 | 0.076355 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | GROVE 4 | 0.95946 | 0.91013 | -0.049336 |  | 0.92 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | GROVE 4 | 0.95946 | 0.91013 | -0.049336 |  | 0.92 | 1.05 | 0.037529 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | GROVE 4 | 0.95946 | 0.91013 | -0.049336 |  | 0.92 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | GROVE 4 | 0.95946 | 0.91013 | -0.049336 |  | 0.92 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | GROVE 4 | 0.95946 | 0.91013 | -0.049336 |  | 0.92 | 1.05 | 0.030301 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | GROVE 4 | 0.95946 | 0.91013 | -0.049336 |  | 0.92 | 1.05 | 0.041779 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | GROVE 4 | 0.95946 | 0.91013 | -0.049336 |  | 0.92 | 1.05 | 0.079587 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | GROVE 4 | 0.96008 | 0.91085 | -0.049222 |  | 0.92 | 1.05 | 0.10484 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | GROVE 4 | 0.96008 | 0.91085 | -0.049222 |  | 0.92 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | GROVE 4 | 0.96008 | 0.91085 | -0.049222 |  | 0.92 | 1.05 | 0.086823 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | GROVE 4 | 0.96008 | 0.91085 | -0.049222 |  | 0.92 | 1.05 | 0.098758 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | GROVE 4 | 0.96008 | 0.91085 | -0.049222 |  | 0.92 | 1.05 | 0.087817 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | GROVE 4 | 0.96008 | 0.91085 | -0.049222 |  | 0.92 | 1.05 | 0.11285 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | GROVE 4 | 0.96008 | 0.91085 | -0.049222 |  | 0.92 | 1.05 | 0.11586 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | GROVE 4 | 0.96008 | 0.91085 | -0.049222 |  | 0.92 | 1.05 | 0.10654 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | GROVE 4 | 0.96008 | 0.91085 | -0.049222 |  | 0.92 | 1.05 | 0.031666 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-219 | GROVE 4 | 0.96008 | 0.91085 | -0.049222 |  | 0.92 | 1.05 | 0.030863 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | GROVE 4 | 0.96008 | 0.91085 | -0.049222 |  | 0.92 | 1.05 | 0.099811 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | GROVE 4 | 0.96008 | 0.91085 | -0.049222 |  | 0.92 | 1.05 | 0.10896 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | GROVE 4 | 0.96008 | 0.91085 | -0.049222 |  | 0.92 | 1.05 | 0.040233 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | GROVE 4 | 0.96008 | 0.91085 | -0.049222 |  | 0.92 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | GROVE 4 | 0.96008 | 0.91085 | -0.049222 |  | 0.92 | 1.05 | 0.060046 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | GROVE 4 | 0.96008 | 0.91085 | -0.049222 |  | 0.92 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | GROVE 4 | 0.96008 | 0.91085 | -0.049222 |  | 0.92 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | GROVE 4 | 0.96008 | 0.91085 | -0.049222 |  | 0.92 | 1.05 | 0.032555 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | GROVE 4 | 0.96008 | 0.91085 | -0.049222 |  | 0.92 | 1.05 | 0.031413 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | GROVE 4 | 0.96008 | 0.91085 | -0.049222 |  | 0.92 | 1.05 | 0.046478 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | GROVE 4 | 0.96008 | 0.91085 | -0.049222 |  | 0.92 | 1.05 | 0.11534 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | GROVE 4 | 0.95456 | 0.90485 | -0.049711 |  | 0.92 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | GROVE 4 | 0.95456 | 0.90485 | -0.049711 |  | 0.92 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | GROVE 4 | 0.95456 | 0.90485 | -0.049711 |  | 0.92 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | GROVE 4 | 0.95456 | 0.90485 | -0.049711 |  | 0.92 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | GROVE 4 | 0.95456 | 0.90485 | -0.049711 |  | 0.92 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | GROVE 4 | 0.95456 | 0.90485 | -0.049711 |  | 0.92 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | GROVE 4 | 0.95456 | 0.90485 | -0.049711 |  | 0.92 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | GROVE 4 | 0.95456 | 0.90485 | -0.049711 |  | 0.92 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | GROVE 4 | 0.95456 | 0.90485 | -0.049711 |  | 0.92 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | GROVE 4 | 0.95456 | 0.90485 | -0.049711 |  | 0.92 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | GROVE 4 | 0.95456 | 0.90485 | -0.049711 |  | 0.92 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | GROVE 4 | 0.95456 | 0.90485 | -0.049711 |  | 0.92 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | GROVE 4 | 0.95456 | 0.90485 | -0.049711 |  | 0.92 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | GROVE 4 | 0.95456 | 0.90485 | -0.049711 |  | 0.92 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | GROVE 5 | 0.96278 | 0.91388 | -0.048903 |  | 0.92 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | GROVE 5 | 0.96278 | 0.91388 | -0.048903 |  | 0.92 | 1.05 | 0.0423 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | GROVE 5 | 0.96278 | 0.91388 | -0.048903 |  | 0.92 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | GROVE 5 | 0.96278 | 0.91388 | -0.048903 |  | 0.92 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | GROVE 5 | 0.96278 | 0.91388 | -0.048903 |  | 0.92 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | GROVE 5 | 0.96278 | 0.91388 | -0.048903 |  | 0.92 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | GROVE 5 | 0.96278 | 0.91388 | -0.048903 |  | 0.92 | 1.05 | 0.044676 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | GROVE 5 | 0.96278 | 0.91388 | -0.048903 |  | 0.92 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | GROVE 5 | 0.96278 | 0.91388 | -0.048903 |  | 0.92 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | GROVE 5 | 0.96278 | 0.91388 | -0.048903 |  | 0.92 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | GROVE 5 | 0.96278 | 0.91388 | -0.048903 |  | 0.92 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | GROVE 5 | 0.96278 | 0.91388 | -0.048903 |  | 0.92 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | GROVE 5 | 0.96278 | 0.91388 | -0.048903 |  | 0.92 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | GROVE 5 | 0.96278 | 0.91388 | -0.048903 |  | 0.92 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | GROVE 5 | 0.96216 | 0.91078 | -0.051376 |  | 0.92 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | GROVE 5 | 0.96216 | 0.91078 | -0.051376 |  | 0.92 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | GROVE 5 | 0.96216 | 0.91078 | -0.051376 |  | 0.92 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | GROVE 5 | 0.96216 | 0.91078 | -0.051376 |  | 0.92 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | GROVE 5 | 0.96216 | 0.91078 | -0.051376 |  | 0.92 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | GROVE 5 | 0.96216 | 0.91078 | -0.051376 |  | 0.92 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | GROVE 5 | 0.96216 | 0.91078 | -0.051376 |  | 0.92 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | GROVE 5 | 0.96216 | 0.91078 | -0.051376 |  | 0.92 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | GROVE 5 | 0.96216 | 0.91078 | -0.051376 |  | 0.92 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | GROVE 5 | 0.96216 | 0.91078 | -0.051376 |  | 0.92 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | GROVE 5 | 0.96216 | 0.91078 | -0.051376 |  | 0.92 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | GROVE 5 | 0.96216 | 0.91078 | -0.051376 |  | 0.92 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | GROVE 5 | 0.96216 | 0.91078 | -0.051376 |  | 0.92 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | GROVE 5 | 0.96216 | 0.91078 | -0.051376 |  | 0.92 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | GROVE 5 | 0.96685 | 0.91707 | -0.049785 |  | 0.92 | 1.05 | 0.076984 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | GROVE 5 | 0.96685 | 0.91707 | -0.049785 |  | 0.92 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | GROVE 5 | 0.96685 | 0.91707 | -0.049785 |  | 0.92 | 1.05 | 0.065662 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | GROVE 5 | 0.96685 | 0.91707 | -0.049785 |  | 0.92 | 1.05 | 0.072679 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | GROVE 5 | 0.96685 | 0.91707 | -0.049785 |  | 0.92 | 1.05 | 0.052268 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | GROVE 5 | 0.96685 | 0.91707 | -0.049785 |  | 0.92 | 1.05 | 0.080584 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | GROVE 5 | 0.96685 | 0.91707 | -0.049785 |  | 0.92 | 1.05 | 0.082253 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | GROVE 5 | 0.96685 | 0.91707 | -0.049785 |  | 0.92 | 1.05 | 0.076592 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | GROVE 5 | 0.96685 | 0.91707 | -0.049785 |  | 0.92 | 1.05 | 0.030918 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | GROVE 5 | 0.96685 | 0.91707 | -0.049785 |  | 0.92 | 1.05 | 0.073312 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | GROVE 5 | 0.96685 | 0.91707 | -0.049785 |  | 0.92 | 1.05 | 0.076355 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | GROVE 5 | 0.96685 | 0.91707 | -0.049785 |  | 0.92 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | GROVE 5 | 0.96685 | 0.91707 | -0.049785 |  | 0.92 | 1.05 | 0.037529 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | GROVE 5 | 0.96685 | 0.91707 | -0.049785 |  | 0.92 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | GROVE 5 | 0.96685 | 0.91707 | -0.049785 |  | 0.92 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | GROVE 5 | 0.96685 | 0.91707 | -0.049785 |  | 0.92 | 1.05 | 0.030301 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | GROVE 5 | 0.96685 | 0.91707 | -0.049785 |  | 0.92 | 1.05 | 0.041779 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | GROVE 5 | 0.96685 | 0.91707 | -0.049785 |  | 0.92 | 1.05 | 0.079587 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | GROVE 5 | 0.96751 | 0.91787 | -0.049647 |  | 0.92 | 1.05 | 0.10484 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | GROVE 5 | 0.96751 | 0.91787 | -0.049647 |  | 0.92 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | GROVE 5 | 0.96751 | 0.91787 | -0.049647 |  | 0.92 | 1.05 | 0.086823 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | GROVE 5 | 0.96751 | 0.91787 | -0.049647 |  | 0.92 | 1.05 | 0.098758 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | GROVE 5 | 0.96751 | 0.91787 | -0.049647 |  | 0.92 | 1.05 | 0.087817 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | GROVE 5 | 0.96751 | 0.91787 | -0.049647 |  | 0.92 | 1.05 | 0.11285 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | GROVE 5 | 0.96751 | 0.91787 | -0.049647 |  | 0.92 | 1.05 | 0.11586 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | GROVE 5 | 0.96751 | 0.91787 | -0.049647 |  | 0.92 | 1.05 | 0.10654 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | GROVE 5 | 0.96751 | 0.91787 | -0.049647 |  | 0.92 | 1.05 | 0.031666 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-219 | GROVE 5 | 0.96751 | 0.91787 | -0.049647 |  | 0.92 | 1.05 | 0.030863 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | GROVE 5 | 0.96751 | 0.91787 | -0.049647 |  | 0.92 | 1.05 | 0.099811 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | GROVE 5 | 0.96751 | 0.91787 | -0.049647 |  | 0.92 | 1.05 | 0.10896 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | GROVE 5 | 0.96751 | 0.91787 | -0.049647 |  | 0.92 | 1.05 | 0.040233 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | GROVE 5 | 0.96751 | 0.91787 | -0.049647 |  | 0.92 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | GROVE 5 | 0.96751 | 0.91787 | -0.049647 |  | 0.92 | 1.05 | 0.060046 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | GROVE 5 | 0.96751 | 0.91787 | -0.049647 |  | 0.92 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | GROVE 5 | 0.96751 | 0.91787 | -0.049647 |  | 0.92 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | GROVE 5 | 0.96751 | 0.91787 | -0.049647 |  | 0.92 | 1.05 | 0.032555 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | GROVE 5 | 0.96751 | 0.91787 | -0.049647 |  | 0.92 | 1.05 | 0.031413 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | GROVE 5 | 0.96751 | 0.91787 | -0.049647 |  | 0.92 | 1.05 | 0.046478 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | GROVE 5 | 0.96751 | 0.91787 | -0.049647 |  | 0.92 | 1.05 | 0.11534 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | GROVE 5 | 0.96188 | 0.91187 | -0.050014 |  | 0.92 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | GROVE 5 | 0.96188 | 0.91187 | -0.050014 |  | 0.92 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | GROVE 5 | 0.96188 | 0.91187 | -0.050014 |  | 0.92 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | GROVE 5 | 0.96188 | 0.91187 | -0.050014 |  | 0.92 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | GROVE 5 | 0.96188 | 0.91187 | -0.050014 |  | 0.92 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | GROVE 5 | 0.96188 | 0.91187 | -0.050014 |  | 0.92 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | GROVE 5 | 0.96188 | 0.91187 | -0.050014 |  | 0.92 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | GROVE 5 | 0.96188 | 0.91187 | -0.050014 |  | 0.92 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | GROVE 5 | 0.96188 | 0.91187 | -0.050014 |  | 0.92 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | GROVE 5 | 0.96188 | 0.91187 | -0.050014 |  | 0.92 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | GROVE 5 | 0.96188 | 0.91187 | -0.050014 |  | 0.92 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | GROVE 5 | 0.96188 | 0.91187 | -0.050014 |  | 0.92 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | GROVE 5 | 0.96188 | 0.91187 | -0.050014 |  | 0.92 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | GROVE 5 | 0.96188 | 0.91187 | -0.050014 |  | 0.92 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | GUAVA 4 | 0.79159 | 0.75428 | -0.037305 |  | 0.92 | 1.05 | 0.035206 | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | GUAVA 4 | 0.80462 | 0.7697 | -0.034921 |  | 0.92 | 1.05 | 0.035206 | Single 509752 INOLATP4 138 510442 GUAVA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | HOYT 7 | 0.96499 | 0.94558 | -0.01941 |  | 0.95 | 1.05 | 0.031932 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | HOYT 7 | 0.96499 | 0.94558 | -0.01941 |  | 0.95 | 1.05 | 0.046406 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | HOYT 7 | 0.96499 | 0.94558 | -0.01941 |  | 0.95 | 1.05 | 0.034669 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | HOYT 7 | 0.96499 | 0.94558 | -0.01941 |  | 0.95 | 1.05 | 0.036297 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | HOYT 7 | 0.96499 | 0.94558 | -0.01941 |  | 0.95 | 1.05 | 0.03404 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | HOYT 7 | 0.96499 | 0.94558 | -0.01941 |  | 0.95 | 1.05 | 0.054677 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | HOYT 7 | 0.96499 | 0.94558 | -0.01941 |  | 0.95 | 1.05 | 0.036731 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | HOYT 7 | 0.96499 | 0.94558 | -0.01941 |  | 0.95 | 1.05 | 0.035653 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | INDEPCO5 | 0.93899 | 0.88787 | -0.051124 |  | 0.92 | 1.05 | 0.076984 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | INDEPCO5 | 0.93899 | 0.88787 | -0.051124 |  | 0.92 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | INDEPCO5 | 0.93899 | 0.88787 | -0.051124 |  | 0.92 | 1.05 | 0.065662 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | INDEPCO5 | 0.93899 | 0.88787 | -0.051124 |  | 0.92 | 1.05 | 0.072679 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | INDEPCO5 | 0.93899 | 0.88787 | -0.051124 |  | 0.92 | 1.05 | 0.052268 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | INDEPCO5 | 0.93899 | 0.88787 | -0.051124 |  | 0.92 | 1.05 | 0.080584 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | INDEPCO5 | 0.93899 | 0.88787 | -0.051124 |  | 0.92 | 1.05 | 0.082253 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | INDEPCO5 | 0.93899 | 0.88787 | -0.051124 |  | 0.92 | 1.05 | 0.076592 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | INDEPCO5 | 0.93899 | 0.88787 | -0.051124 |  | 0.92 | 1.05 | 0.030918 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | INDEPCO5 | 0.93899 | 0.88787 | -0.051124 |  | 0.92 | 1.05 | 0.073312 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | INDEPCO5 | 0.93899 | 0.88787 | -0.051124 |  | 0.92 | 1.05 | 0.076355 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | INDEPCO5 | 0.93899 | 0.88787 | -0.051124 |  | 0.92 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | INDEPCO5 | 0.93899 | 0.88787 | -0.051124 |  | 0.92 | 1.05 | 0.037529 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | INDEPCO5 | 0.93899 | 0.88787 | -0.051124 |  | 0.92 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | INDEPCO5 | 0.93899 | 0.88787 | -0.051124 |  | 0.92 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | INDEPCO5 | 0.93899 | 0.88787 | -0.051124 |  | 0.92 | 1.05 | 0.030301 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | INDEPCO5 | 0.93899 | 0.88787 | -0.051124 |  | 0.92 | 1.05 | 0.041779 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | INDEPCO5 | 0.93899 | 0.88787 | -0.051124 |  | 0.92 | 1.05 | 0.079587 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | INDEPCO5 | 0.94333 | 0.88902 | -0.054309 |  | 0.92 | 1.05 | 0.10484 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | INDEPCO5 | 0.94333 | 0.88902 | -0.054309 |  | 0.92 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | INDEPCO5 | 0.94333 | 0.88902 | -0.054309 |  | 0.92 | 1.05 | 0.086823 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | INDEPCO5 | 0.94333 | 0.88902 | -0.054309 |  | 0.92 | 1.05 | 0.098758 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | INDEPCO5 | 0.94333 | 0.88902 | -0.054309 |  | 0.92 | 1.05 | 0.087817 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | INDEPCO5 | 0.94333 | 0.88902 | -0.054309 |  | 0.92 | 1.05 | 0.11285 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | INDEPCO5 | 0.94333 | 0.88902 | -0.054309 |  | 0.92 | 1.05 | 0.11586 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | INDEPCO5 | 0.94333 | 0.88902 | -0.054309 |  | 0.92 | 1.05 | 0.10654 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | INDEPCO5 | 0.94333 | 0.88902 | -0.054309 |  | 0.92 | 1.05 | 0.031666 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-219 | INDEPCO5 | 0.94333 | 0.88902 | -0.054309 |  | 0.92 | 1.05 | 0.030863 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | INDEPCO5 | 0.94333 | 0.88902 | -0.054309 |  | 0.92 | 1.05 | 0.099811 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | INDEPCO5 | 0.94333 | 0.88902 | -0.054309 |  | 0.92 | 1.05 | 0.10896 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | INDEPCO5 | 0.94333 | 0.88902 | -0.054309 |  | 0.92 | 1.05 | 0.040233 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | INDEPCO5 | 0.94333 | 0.88902 | -0.054309 |  | 0.92 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | INDEPCO5 | 0.94333 | 0.88902 | -0.054309 |  | 0.92 | 1.05 | 0.060046 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | INDEPCO5 | 0.94333 | 0.88902 | -0.054309 |  | 0.92 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | INDEPCO5 | 0.94333 | 0.88902 | -0.054309 |  | 0.92 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | INDEPCO5 | 0.94333 | 0.88902 | -0.054309 |  | 0.92 | 1.05 | 0.032555 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | INDEPCO5 | 0.94333 | 0.88902 | -0.054309 |  | 0.92 | 1.05 | 0.031413 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | INDEPCO5 | 0.94333 | 0.88902 | -0.054309 |  | 0.92 | 1.05 | 0.046478 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | INDEPCO5 | 0.94333 | 0.88902 | -0.054309 |  | 0.92 | 1.05 | 0.11534 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | INOLA 4 | 0.79121 | 0.75389 | -0.037326 |  | 0.92 | 1.05 | 0.035206 | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | INOLATP4 | 0.79144 | 0.75412 | -0.037314 |  | 0.92 | 1.05 | 0.035206 | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | JAY 4 | 0.95717 | 0.91193 | -0.045235 |  | 0.92 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | JAY 4 | 0.95717 | 0.91193 | -0.045235 |  | 0.92 | 1.05 | 0.0423 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | JAY 4 | 0.95717 | 0.91193 | -0.045235 |  | 0.92 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | JAY 4 | 0.95717 | 0.91193 | -0.045235 |  | 0.92 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | JAY 4 | 0.95717 | 0.91193 | -0.045235 |  | 0.92 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | JAY 4 | 0.95717 | 0.91193 | -0.045235 |  | 0.92 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | JAY 4 | 0.95717 | 0.91193 | -0.045235 |  | 0.92 | 1.05 | 0.044676 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | JAY 4 | 0.95717 | 0.91193 | -0.045235 |  | 0.92 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | JAY 4 | 0.95717 | 0.91193 | -0.045235 |  | 0.92 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | JAY 4 | 0.95717 | 0.91193 | -0.045235 |  | 0.92 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | JAY 4 | 0.95717 | 0.91193 | -0.045235 |  | 0.92 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | JAY 4 | 0.95717 | 0.91193 | -0.045235 |  | 0.92 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | JAY 4 | 0.95717 | 0.91193 | -0.045235 |  | 0.92 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | JAY 4 | 0.95717 | 0.91193 | -0.045235 |  | 0.92 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | JAY 4 | 0.95657 | 0.90955 | -0.047015 |  | 0.92 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | JAY 4 | 0.95657 | 0.90955 | -0.047015 |  | 0.92 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | JAY 4 | 0.95657 | 0.90955 | -0.047015 |  | 0.92 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | JAY 4 | 0.95657 | 0.90955 | -0.047015 |  | 0.92 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | JAY 4 | 0.95657 | 0.90955 | -0.047015 |  | 0.92 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | JAY 4 | 0.95657 | 0.90955 | -0.047015 |  | 0.92 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | JAY 4 | 0.95657 | 0.90955 | -0.047015 |  | 0.92 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | JAY 4 | 0.95657 | 0.90955 | -0.047015 |  | 0.92 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | JAY 4 | 0.95657 | 0.90955 | -0.047015 |  | 0.92 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | JAY 4 | 0.95657 | 0.90955 | -0.047015 |  | 0.92 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | JAY 4 | 0.95657 | 0.90955 | -0.047015 |  | 0.92 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | JAY 4 | 0.95657 | 0.90955 | -0.047015 |  | 0.92 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | JAY 4 | 0.95657 | 0.90955 | -0.047015 |  | 0.92 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | JAY 4 | 0.95657 | 0.90955 | -0.047015 |  | 0.92 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | JAY 4 | 0.93932 | 0.90629 | -0.033024 |  | 0.92 | 1.05 | 0.035206 | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | JAY 4 | 0.94222 | 0.90987 | -0.032353 |  | 0.92 | 1.05 | 0.035206 | Single 509752 INOLATP4 138 510442 GUAVA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | JAY 4 | 0.95639 | 0.91039 | -0.045997 |  | 0.92 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | JAY 4 | 0.95639 | 0.91039 | -0.045997 |  | 0.92 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | JAY 4 | 0.95639 | 0.91039 | -0.045997 |  | 0.92 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | JAY 4 | 0.95639 | 0.91039 | -0.045997 |  | 0.92 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | JAY 4 | 0.95639 | 0.91039 | -0.045997 |  | 0.92 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | JAY 4 | 0.95639 | 0.91039 | -0.045997 |  | 0.92 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | JAY 4 | 0.95639 | 0.91039 | -0.045997 |  | 0.92 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | JAY 4 | 0.95639 | 0.91039 | -0.045997 |  | 0.92 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | JAY 4 | 0.95639 | 0.91039 | -0.045997 |  | 0.92 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | JAY 4 | 0.95639 | 0.91039 | -0.045997 |  | 0.92 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | JAY 4 | 0.95639 | 0.91039 | -0.045997 |  | 0.92 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | JAY 4 | 0.95639 | 0.91039 | -0.045997 |  | 0.92 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | JAY 4 | 0.95639 | 0.91039 | -0.045997 |  | 0.92 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | JAY 4 | 0.95639 | 0.91039 | -0.045997 |  | 0.92 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | JEC N 7 | 0.96914 | 0.94853 | -0.020608 |  | 0.95 | 1.05 | 0.031932 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | JEC N 7 | 0.96914 | 0.94853 | -0.020608 |  | 0.95 | 1.05 | 0.046406 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | JEC N 7 | 0.96914 | 0.94853 | -0.020608 |  | 0.95 | 1.05 | 0.034669 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | JEC N 7 | 0.96914 | 0.94853 | -0.020608 |  | 0.95 | 1.05 | 0.036297 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | JEC N 7 | 0.96914 | 0.94853 | -0.020608 |  | 0.95 | 1.05 | 0.03404 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | JEC N 7 | 0.96914 | 0.94853 | -0.020608 |  | 0.95 | 1.05 | 0.054677 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | JEC N 7 | 0.96914 | 0.94853 | -0.020608 |  | 0.95 | 1.05 | 0.036731 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | JEC N 7 | 0.96914 | 0.94853 | -0.020608 |  | 0.95 | 1.05 | 0.035653 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | JOP391 5 | 0.96454 | 0.9239 | -0.040634 |  | 0.925 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | JOP391 5 | 0.96454 | 0.9239 | -0.040634 |  | 0.925 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | JOP391 5 | 0.96454 | 0.9239 | -0.040634 |  | 0.925 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | JOP391 5 | 0.96454 | 0.9239 | -0.040634 |  | 0.925 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | JOP391 5 | 0.96454 | 0.9239 | -0.040634 |  | 0.925 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | JOP391 5 | 0.96454 | 0.9239 | -0.040634 |  | 0.925 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | JOP391 5 | 0.96454 | 0.9239 | -0.040634 |  | 0.925 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | JOP391 5 | 0.96454 | 0.9239 | -0.040634 |  | 0.925 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | JOP391 5 | 0.96454 | 0.9239 | -0.040634 |  | 0.925 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | JOP391 5 | 0.96454 | 0.9239 | -0.040634 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | JOP391 5 | 0.96454 | 0.9239 | -0.040634 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | JOP391 5 | 0.96454 | 0.9239 | -0.040634 |  | 0.925 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | JOP391 5 | 0.96454 | 0.9239 | -0.040634 |  | 0.925 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | JOP391 5 | 0.96454 | 0.9239 | -0.040634 |  | 0.925 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | JOP391 5 | 0.96416 | 0.92486 | -0.039296 |  | 0.925 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | JOP391 5 | 0.96416 | 0.92486 | -0.039296 |  | 0.925 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | JOP391 5 | 0.96416 | 0.92486 | -0.039296 |  | 0.925 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | JOP391 5 | 0.96416 | 0.92486 | -0.039296 |  | 0.925 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | JOP391 5 | 0.96416 | 0.92486 | -0.039296 |  | 0.925 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | JOP391 5 | 0.96416 | 0.92486 | -0.039296 |  | 0.925 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | JOP391 5 | 0.96416 | 0.92486 | -0.039296 |  | 0.925 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | JOP391 5 | 0.96416 | 0.92486 | -0.039296 |  | 0.925 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | JOP391 5 | 0.96416 | 0.92486 | -0.039296 |  | 0.925 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | JOP391 5 | 0.96416 | 0.92486 | -0.039296 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | JOP391 5 | 0.96416 | 0.92486 | -0.039296 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | JOP391 5 | 0.96416 | 0.92486 | -0.039296 |  | 0.925 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | JOP391 5 | 0.96416 | 0.92486 | -0.039296 |  | 0.925 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | JOP391 5 | 0.96416 | 0.92486 | -0.039296 |  | 0.925 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | LABETTE2 | 0.95492 | 0.9242 | -0.030726 |  | 0.93 | 1.05 | 0.10484 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | LABETTE2 | 0.95492 | 0.9242 | -0.030726 |  | 0.93 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | LABETTE2 | 0.95492 | 0.9242 | -0.030726 |  | 0.93 | 1.05 | 0.086823 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | LABETTE2 | 0.95492 | 0.9242 | -0.030726 |  | 0.93 | 1.05 | 0.098758 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | LABETTE2 | 0.95492 | 0.9242 | -0.030726 |  | 0.93 | 1.05 | 0.087817 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | LABETTE2 | 0.95492 | 0.9242 | -0.030726 |  | 0.93 | 1.05 | 0.11285 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | LABETTE2 | 0.95492 | 0.9242 | -0.030726 |  | 0.93 | 1.05 | 0.11586 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | LABETTE2 | 0.95492 | 0.9242 | -0.030726 |  | 0.93 | 1.05 | 0.10654 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | LABETTE2 | 0.95492 | 0.9242 | -0.030726 |  | 0.93 | 1.05 | 0.031666 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-219 | LABETTE2 | 0.95492 | 0.9242 | -0.030726 |  | 0.93 | 1.05 | 0.030863 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | LABETTE2 | 0.95492 | 0.9242 | -0.030726 |  | 0.93 | 1.05 | 0.099811 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | LABETTE2 | 0.95492 | 0.9242 | -0.030726 |  | 0.93 | 1.05 | 0.10896 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | LABETTE2 | 0.95492 | 0.9242 | -0.030726 |  | 0.93 | 1.05 | 0.040233 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | LABETTE2 | 0.95492 | 0.9242 | -0.030726 |  | 0.93 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | LABETTE2 | 0.95492 | 0.9242 | -0.030726 |  | 0.93 | 1.05 | 0.060046 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | LABETTE2 | 0.95492 | 0.9242 | -0.030726 |  | 0.93 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | LABETTE2 | 0.95492 | 0.9242 | -0.030726 |  | 0.93 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | LABETTE2 | 0.95492 | 0.9242 | -0.030726 |  | 0.93 | 1.05 | 0.032555 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | LABETTE2 | 0.95492 | 0.9242 | -0.030726 |  | 0.93 | 1.05 | 0.031413 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | LABETTE2 | 0.95492 | 0.9242 | -0.030726 |  | 0.93 | 1.05 | 0.046478 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | LABETTE2 | 0.95492 | 0.9242 | -0.030726 |  | 0.93 | 1.05 | 0.11534 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | LABETTE2 | 0.95799 | 0.92902 | -0.028968 |  | 0.93 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | LABETTE2 | 0.95799 | 0.92902 | -0.028968 |  | 0.93 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | LABETTE2 | 0.95799 | 0.92902 | -0.028968 |  | 0.93 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | LABETTE2 | 0.95799 | 0.92902 | -0.028968 |  | 0.93 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | LABETTE2 | 0.95799 | 0.92902 | -0.028968 |  | 0.93 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | LABETTE2 | 0.95799 | 0.92902 | -0.028968 |  | 0.93 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | LABETTE2 | 0.95799 | 0.92902 | -0.028968 |  | 0.93 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | LABETTE2 | 0.95799 | 0.92902 | -0.028968 |  | 0.93 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | LABETTE2 | 0.95799 | 0.92902 | -0.028968 |  | 0.93 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | LABETTE2 | 0.95799 | 0.92902 | -0.028968 |  | 0.93 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | LABETTE2 | 0.95799 | 0.92902 | -0.028968 |  | 0.93 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | LABETTE2 | 0.95799 | 0.92902 | -0.028968 |  | 0.93 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | LABETTE2 | 0.95799 | 0.92902 | -0.028968 |  | 0.93 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | LABETTE2 | 0.95799 | 0.92902 | -0.028968 |  | 0.93 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | LABETTE2 | 0.95443 | 0.92359 | -0.030831 |  | 0.93 | 1.05 | 0.076984 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | LABETTE2 | 0.95443 | 0.92359 | -0.030831 |  | 0.93 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | LABETTE2 | 0.95443 | 0.92359 | -0.030831 |  | 0.93 | 1.05 | 0.065662 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | LABETTE2 | 0.95443 | 0.92359 | -0.030831 |  | 0.93 | 1.05 | 0.072679 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | LABETTE2 | 0.95443 | 0.92359 | -0.030831 |  | 0.93 | 1.05 | 0.052268 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | LABETTE2 | 0.95443 | 0.92359 | -0.030831 |  | 0.93 | 1.05 | 0.080584 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | LABETTE2 | 0.95443 | 0.92359 | -0.030831 |  | 0.93 | 1.05 | 0.082253 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | LABETTE2 | 0.95443 | 0.92359 | -0.030831 |  | 0.93 | 1.05 | 0.076592 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | LABETTE2 | 0.95443 | 0.92359 | -0.030831 |  | 0.93 | 1.05 | 0.030918 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | LABETTE2 | 0.95443 | 0.92359 | -0.030831 |  | 0.93 | 1.05 | 0.073312 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | LABETTE2 | 0.95443 | 0.92359 | -0.030831 |  | 0.93 | 1.05 | 0.076355 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | LABETTE2 | 0.95443 | 0.92359 | -0.030831 |  | 0.93 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | LABETTE2 | 0.95443 | 0.92359 | -0.030831 |  | 0.93 | 1.05 | 0.037529 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | LABETTE2 | 0.95443 | 0.92359 | -0.030831 |  | 0.93 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | LABETTE2 | 0.95443 | 0.92359 | -0.030831 |  | 0.93 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | LABETTE2 | 0.95443 | 0.92359 | -0.030831 |  | 0.93 | 1.05 | 0.030301 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | LABETTE2 | 0.95443 | 0.92359 | -0.030831 |  | 0.93 | 1.05 | 0.041779 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | LABETTE2 | 0.95443 | 0.92359 | -0.030831 |  | 0.93 | 1.05 | 0.079587 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | LABETTE2 | 0.9588 | 0.92808 | -0.03072 |  | 0.93 | 1.05 | 0.03716 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | LABETTE2 | 0.9588 | 0.92808 | -0.03072 |  | 0.93 | 1.05 | 0.030931 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | LABETTE2 | 0.9588 | 0.92808 | -0.03072 |  | 0.93 | 1.05 | 0.044459 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | LABETTE2 | 0.9588 | 0.92808 | -0.03072 |  | 0.93 | 1.05 | 0.041648 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | LABETTE2 | 0.9588 | 0.92808 | -0.03072 |  | 0.93 | 1.05 | 0.031986 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | LABETTE2 | 0.9588 | 0.92808 | -0.03072 |  | 0.93 | 1.05 | 0.039776 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | LABETTE2 | 0.9588 | 0.92808 | -0.03072 |  | 0.93 | 1.05 | 0.042349 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | LABETTE2 | 0.9588 | 0.92808 | -0.03072 |  | 0.93 | 1.05 | 0.041252 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | LABETTE2 | 0.9588 | 0.92808 | -0.03072 |  | 0.93 | 1.05 | 0.031238 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | LABETTE2 | 0.9588 | 0.92808 | -0.03072 |  | 0.93 | 1.05 | 0.034893 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | LABETTE2 | 0.9588 | 0.92808 | -0.03072 |  | 0.93 | 1.05 | 0.046335 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | LABETTE2 | 0.9588 | 0.92808 | -0.03072 |  | 0.93 | 1.05 | 0.034893 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | LABETTE2 | 0.9588 | 0.92808 | -0.03072 |  | 0.93 | 1.05 | 0.03611 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | LABETTE2 | 0.9588 | 0.92808 | -0.03072 |  | 0.93 | 1.05 | 0.034555 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | LABETTE2 | 0.9588 | 0.92808 | -0.03072 |  | 0.93 | 1.05 | 0.033454 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | LABETTE2 | 0.9588 | 0.92808 | -0.03072 |  | 0.93 | 1.05 | 0.045771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | LABETTE2 | 0.9588 | 0.92808 | -0.03072 |  | 0.93 | 1.05 | 0.031365 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | LABETTE2 | 0.9588 | 0.92808 | -0.03072 |  | 0.93 | 1.05 | 0.031365 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | LABETTE2 | 0.9588 | 0.92808 | -0.03072 |  | 0.93 | 1.05 | 0.041921 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | LABETTE2 | 0.9588 | 0.92808 | -0.03072 |  | 0.93 | 1.05 | 0.033154 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | LABETTE2 | 0.9588 | 0.92808 | -0.03072 |  | 0.93 | 1.05 | 0.03341 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | LABETTE2 | 0.9588 | 0.92808 | -0.03072 |  | 0.93 | 1.05 | 0.030334 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | LABETTE2 | 0.9588 | 0.92808 | -0.03072 |  | 0.93 | 1.05 | 0.034718 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | LABETTE2 | 0.9588 | 0.92808 | -0.03072 |  | 0.93 | 1.05 | 0.033533 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | LABETTE2 | 0.95599 | 0.92416 | -0.031834 |  | 0.93 | 1.05 | 0.038685 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | LABETTE2 | 0.95599 | 0.92416 | -0.031834 |  | 0.93 | 1.05 | 0.07469 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | LABETTE2 | 0.95599 | 0.92416 | -0.031834 |  | 0.93 | 1.05 | 0.068062 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | LABETTE2 | 0.95599 | 0.92416 | -0.031834 |  | 0.93 | 1.05 | 0.034938 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | LABETTE2 | 0.95599 | 0.92416 | -0.031834 |  | 0.93 | 1.05 | 0.032777 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | LABETTE2 | 0.95599 | 0.92416 | -0.031834 |  | 0.93 | 1.05 | 0.043475 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | LABETTE2 | 0.95599 | 0.92416 | -0.031834 |  | 0.93 | 1.05 | 0.13386 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | LABETTE2 | 0.95599 | 0.92416 | -0.031834 |  | 0.93 | 1.05 | 0.036067 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | LABETTE2 | 0.95599 | 0.92416 | -0.031834 |  | 0.93 | 1.05 | 0.036067 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | LABETTE2 | 0.95599 | 0.92416 | -0.031834 |  | 0.93 | 1.05 | 0.067572 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | LABETTE2 | 0.95599 | 0.92416 | -0.031834 |  | 0.93 | 1.05 | 0.033583 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | LABETTE2 | 0.95599 | 0.92416 | -0.031834 |  | 0.93 | 1.05 | 0.034115 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | LABETTS2 | 0.95567 | 0.92497 | -0.030698 |  | 0.93 | 1.05 | 0.10484 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | LABETTS2 | 0.95567 | 0.92497 | -0.030698 |  | 0.93 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | LABETTS2 | 0.95567 | 0.92497 | -0.030698 |  | 0.93 | 1.05 | 0.086823 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | LABETTS2 | 0.95567 | 0.92497 | -0.030698 |  | 0.93 | 1.05 | 0.098758 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | LABETTS2 | 0.95567 | 0.92497 | -0.030698 |  | 0.93 | 1.05 | 0.087817 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | LABETTS2 | 0.95567 | 0.92497 | -0.030698 |  | 0.93 | 1.05 | 0.11285 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | LABETTS2 | 0.95567 | 0.92497 | -0.030698 |  | 0.93 | 1.05 | 0.11586 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | LABETTS2 | 0.95567 | 0.92497 | -0.030698 |  | 0.93 | 1.05 | 0.10654 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | LABETTS2 | 0.95567 | 0.92497 | -0.030698 |  | 0.93 | 1.05 | 0.031666 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-219 | LABETTS2 | 0.95567 | 0.92497 | -0.030698 |  | 0.93 | 1.05 | 0.030863 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | LABETTS2 | 0.95567 | 0.92497 | -0.030698 |  | 0.93 | 1.05 | 0.099811 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | LABETTS2 | 0.95567 | 0.92497 | -0.030698 |  | 0.93 | 1.05 | 0.10896 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | LABETTS2 | 0.95567 | 0.92497 | -0.030698 |  | 0.93 | 1.05 | 0.040233 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | LABETTS2 | 0.95567 | 0.92497 | -0.030698 |  | 0.93 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | LABETTS2 | 0.95567 | 0.92497 | -0.030698 |  | 0.93 | 1.05 | 0.060046 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | LABETTS2 | 0.95567 | 0.92497 | -0.030698 |  | 0.93 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | LABETTS2 | 0.95567 | 0.92497 | -0.030698 |  | 0.93 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | LABETTS2 | 0.95567 | 0.92497 | -0.030698 |  | 0.93 | 1.05 | 0.032555 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | LABETTS2 | 0.95567 | 0.92497 | -0.030698 |  | 0.93 | 1.05 | 0.031413 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | LABETTS2 | 0.95567 | 0.92497 | -0.030698 |  | 0.93 | 1.05 | 0.046478 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | LABETTS2 | 0.95567 | 0.92497 | -0.030698 |  | 0.93 | 1.05 | 0.11534 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | LABETTS2 | 0.95874 | 0.9298 | -0.028942 |  | 0.93 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | LABETTS2 | 0.95874 | 0.9298 | -0.028942 |  | 0.93 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | LABETTS2 | 0.95874 | 0.9298 | -0.028942 |  | 0.93 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | LABETTS2 | 0.95874 | 0.9298 | -0.028942 |  | 0.93 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | LABETTS2 | 0.95874 | 0.9298 | -0.028942 |  | 0.93 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | LABETTS2 | 0.95874 | 0.9298 | -0.028942 |  | 0.93 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | LABETTS2 | 0.95874 | 0.9298 | -0.028942 |  | 0.93 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | LABETTS2 | 0.95874 | 0.9298 | -0.028942 |  | 0.93 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | LABETTS2 | 0.95874 | 0.9298 | -0.028942 |  | 0.93 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | LABETTS2 | 0.95874 | 0.9298 | -0.028942 |  | 0.93 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | LABETTS2 | 0.95874 | 0.9298 | -0.028942 |  | 0.93 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | LABETTS2 | 0.95874 | 0.9298 | -0.028942 |  | 0.93 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | LABETTS2 | 0.95874 | 0.9298 | -0.028942 |  | 0.93 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | LABETTS2 | 0.95874 | 0.9298 | -0.028942 |  | 0.93 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | LABETTS2 | 0.95518 | 0.92437 | -0.030803 |  | 0.93 | 1.05 | 0.076984 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | LABETTS2 | 0.95518 | 0.92437 | -0.030803 |  | 0.93 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | LABETTS2 | 0.95518 | 0.92437 | -0.030803 |  | 0.93 | 1.05 | 0.065662 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | LABETTS2 | 0.95518 | 0.92437 | -0.030803 |  | 0.93 | 1.05 | 0.072679 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | LABETTS2 | 0.95518 | 0.92437 | -0.030803 |  | 0.93 | 1.05 | 0.052268 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | LABETTS2 | 0.95518 | 0.92437 | -0.030803 |  | 0.93 | 1.05 | 0.080584 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | LABETTS2 | 0.95518 | 0.92437 | -0.030803 |  | 0.93 | 1.05 | 0.082253 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | LABETTS2 | 0.95518 | 0.92437 | -0.030803 |  | 0.93 | 1.05 | 0.076592 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | LABETTS2 | 0.95518 | 0.92437 | -0.030803 |  | 0.93 | 1.05 | 0.030918 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | LABETTS2 | 0.95518 | 0.92437 | -0.030803 |  | 0.93 | 1.05 | 0.073312 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | LABETTS2 | 0.95518 | 0.92437 | -0.030803 |  | 0.93 | 1.05 | 0.076355 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | LABETTS2 | 0.95518 | 0.92437 | -0.030803 |  | 0.93 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | LABETTS2 | 0.95518 | 0.92437 | -0.030803 |  | 0.93 | 1.05 | 0.037529 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | LABETTS2 | 0.95518 | 0.92437 | -0.030803 |  | 0.93 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | LABETTS2 | 0.95518 | 0.92437 | -0.030803 |  | 0.93 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | LABETTS2 | 0.95518 | 0.92437 | -0.030803 |  | 0.93 | 1.05 | 0.030301 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | LABETTS2 | 0.95518 | 0.92437 | -0.030803 |  | 0.93 | 1.05 | 0.041779 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | LABETTS2 | 0.95518 | 0.92437 | -0.030803 |  | 0.93 | 1.05 | 0.079587 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | LABETTS2 | 0.95954 | 0.92885 | -0.030693 |  | 0.93 | 1.05 | 0.03716 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | LABETTS2 | 0.95954 | 0.92885 | -0.030693 |  | 0.93 | 1.05 | 0.030931 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | LABETTS2 | 0.95954 | 0.92885 | -0.030693 |  | 0.93 | 1.05 | 0.044459 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | LABETTS2 | 0.95954 | 0.92885 | -0.030693 |  | 0.93 | 1.05 | 0.041648 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | LABETTS2 | 0.95954 | 0.92885 | -0.030693 |  | 0.93 | 1.05 | 0.031986 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | LABETTS2 | 0.95954 | 0.92885 | -0.030693 |  | 0.93 | 1.05 | 0.039776 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | LABETTS2 | 0.95954 | 0.92885 | -0.030693 |  | 0.93 | 1.05 | 0.042349 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | LABETTS2 | 0.95954 | 0.92885 | -0.030693 |  | 0.93 | 1.05 | 0.041252 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | LABETTS2 | 0.95954 | 0.92885 | -0.030693 |  | 0.93 | 1.05 | 0.031238 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | LABETTS2 | 0.95954 | 0.92885 | -0.030693 |  | 0.93 | 1.05 | 0.034893 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | LABETTS2 | 0.95954 | 0.92885 | -0.030693 |  | 0.93 | 1.05 | 0.046335 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | LABETTS2 | 0.95954 | 0.92885 | -0.030693 |  | 0.93 | 1.05 | 0.034893 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | LABETTS2 | 0.95954 | 0.92885 | -0.030693 |  | 0.93 | 1.05 | 0.03611 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | LABETTS2 | 0.95954 | 0.92885 | -0.030693 |  | 0.93 | 1.05 | 0.034555 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | LABETTS2 | 0.95954 | 0.92885 | -0.030693 |  | 0.93 | 1.05 | 0.033454 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | LABETTS2 | 0.95954 | 0.92885 | -0.030693 |  | 0.93 | 1.05 | 0.045771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | LABETTS2 | 0.95954 | 0.92885 | -0.030693 |  | 0.93 | 1.05 | 0.031365 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | LABETTS2 | 0.95954 | 0.92885 | -0.030693 |  | 0.93 | 1.05 | 0.031365 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | LABETTS2 | 0.95954 | 0.92885 | -0.030693 |  | 0.93 | 1.05 | 0.041921 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | LABETTS2 | 0.95954 | 0.92885 | -0.030693 |  | 0.93 | 1.05 | 0.033154 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | LABETTS2 | 0.95954 | 0.92885 | -0.030693 |  | 0.93 | 1.05 | 0.03341 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | LABETTS2 | 0.95954 | 0.92885 | -0.030693 |  | 0.93 | 1.05 | 0.030334 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | LABETTS2 | 0.95954 | 0.92885 | -0.030693 |  | 0.93 | 1.05 | 0.034718 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | LABETTS2 | 0.95954 | 0.92885 | -0.030693 |  | 0.93 | 1.05 | 0.033533 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | LABETTS2 | 0.95674 | 0.92494 | -0.031806 |  | 0.93 | 1.05 | 0.038685 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | LABETTS2 | 0.95674 | 0.92494 | -0.031806 |  | 0.93 | 1.05 | 0.07469 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | LABETTS2 | 0.95674 | 0.92494 | -0.031806 |  | 0.93 | 1.05 | 0.068062 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | LABETTS2 | 0.95674 | 0.92494 | -0.031806 |  | 0.93 | 1.05 | 0.034938 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | LABETTS2 | 0.95674 | 0.92494 | -0.031806 |  | 0.93 | 1.05 | 0.032777 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | LABETTS2 | 0.95674 | 0.92494 | -0.031806 |  | 0.93 | 1.05 | 0.043475 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | LABETTS2 | 0.95674 | 0.92494 | -0.031806 |  | 0.93 | 1.05 | 0.13386 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | LABETTS2 | 0.95674 | 0.92494 | -0.031806 |  | 0.93 | 1.05 | 0.036067 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | LABETTS2 | 0.95674 | 0.92494 | -0.031806 |  | 0.93 | 1.05 | 0.036067 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | LABETTS2 | 0.95674 | 0.92494 | -0.031806 |  | 0.93 | 1.05 | 0.067572 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | LABETTS2 | 0.95674 | 0.92494 | -0.031806 |  | 0.93 | 1.05 | 0.033583 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | LABETTS2 | 0.95674 | 0.92494 | -0.031806 |  | 0.93 | 1.05 | 0.034115 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | LANG 7 | 0.98968 | 0.94664 | -0.043044 |  | 0.95 | 1.05 | 0.039244 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | LANG 7 | 0.98968 | 0.94664 | -0.043044 |  | 0.95 | 1.05 | 0.036827 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | LANG 7 | 0.98968 | 0.94664 | -0.043044 |  | 0.95 | 1.05 | 0.030156 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | LANG 7 | 0.98968 | 0.94664 | -0.043044 |  | 0.95 | 1.05 | 0.034146 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | LANG 7 | 0.98968 | 0.94664 | -0.043044 |  | 0.95 | 1.05 | 0.034933 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | LANG 7 | 0.98968 | 0.94664 | -0.043044 |  | 0.95 | 1.05 | 0.038105 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | LANG 7 | 0.98968 | 0.94664 | -0.043044 |  | 0.95 | 1.05 | 0.035356 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | LANG 7 | 0.98968 | 0.94664 | -0.043044 |  | 0.95 | 1.05 | 0.040988 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | LANG 7 | 0.98968 | 0.94664 | -0.043044 |  | 0.95 | 1.05 | 0.035356 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | LANG 7 | 0.98968 | 0.94664 | -0.043044 |  | 0.95 | 1.05 | 0.036081 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | LANG 7 | 0.98968 | 0.94664 | -0.043044 |  | 0.95 | 1.05 | 0.036544 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | LANG 7 | 0.98968 | 0.94664 | -0.043044 |  | 0.95 | 1.05 | 0.038782 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | LANG 7 | 0.98968 | 0.94664 | -0.043044 |  | 0.95 | 1.05 | 0.034598 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | LANG 7 | 0.98968 | 0.94664 | -0.043044 |  | 0.95 | 1.05 | 0.032427 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | LANG 7 | 0.98968 | 0.94664 | -0.043044 |  | 0.95 | 1.05 | 0.031223 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | LANG 7 | 0.98968 | 0.94664 | -0.043044 |  | 0.95 | 1.05 | 0.033455 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | LANG 7 | 0.98968 | 0.94664 | -0.043044 |  | 0.95 | 1.05 | 0.034045 | P51:25:WERE:WOLFCRK7:EHV: | Add 280 MVAR SVC at G15052_1 345 kV; Add 28 MVAR switched shunt at G21-096-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | LANG 7 | 0.97996 | 0.94767 | -0.032284 |  | 0.95 | 1.05 | 0.037599 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | LANG 7 | 0.97996 | 0.94767 | -0.032284 |  | 0.95 | 1.05 | 0.03567 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | LANG 7 | 0.97996 | 0.94767 | -0.032284 |  | 0.95 | 1.05 | 0.032501 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | LANG 7 | 0.97996 | 0.94767 | -0.032284 |  | 0.95 | 1.05 | 0.033287 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | LANG 7 | 0.97996 | 0.94767 | -0.032284 |  | 0.95 | 1.05 | 0.036459 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | LANG 7 | 0.97996 | 0.94767 | -0.032284 |  | 0.95 | 1.05 | 0.033711 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | LANG 7 | 0.97996 | 0.94767 | -0.032284 |  | 0.95 | 1.05 | 0.042545 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | LANG 7 | 0.97996 | 0.94767 | -0.032284 |  | 0.95 | 1.05 | 0.033711 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | LANG 7 | 0.97996 | 0.94767 | -0.032284 |  | 0.95 | 1.05 | 0.034436 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | LANG 7 | 0.97996 | 0.94767 | -0.032284 |  | 0.95 | 1.05 | 0.034899 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | LANG 7 | 0.97996 | 0.94767 | -0.032284 |  | 0.95 | 1.05 | 0.032952 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | LANG 7 | 0.97996 | 0.94767 | -0.032284 |  | 0.95 | 1.05 | 0.030781 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | LANG 7 | 0.97996 | 0.94767 | -0.032284 |  | 0.95 | 1.05 | 0.03181 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | LANG 7 | 0.97996 | 0.94767 | -0.032284 |  | 0.95 | 1.05 | 0.032399 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | LANG 7 | 0.8803 | 0.84891 | -0.031392 |  | 0.95 | 1.05 | 0.03716 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | LANG 7 | 0.8803 | 0.84891 | -0.031392 |  | 0.95 | 1.05 | 0.030931 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | LANG 7 | 0.8803 | 0.84891 | -0.031392 |  | 0.95 | 1.05 | 0.044459 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | LANG 7 | 0.8803 | 0.84891 | -0.031392 |  | 0.95 | 1.05 | 0.041648 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | LANG 7 | 0.8803 | 0.84891 | -0.031392 |  | 0.95 | 1.05 | 0.031986 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | LANG 7 | 0.8803 | 0.84891 | -0.031392 |  | 0.95 | 1.05 | 0.039776 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | LANG 7 | 0.8803 | 0.84891 | -0.031392 |  | 0.95 | 1.05 | 0.042349 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | LANG 7 | 0.8803 | 0.84891 | -0.031392 |  | 0.95 | 1.05 | 0.041252 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | LANG 7 | 0.8803 | 0.84891 | -0.031392 |  | 0.95 | 1.05 | 0.031238 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | LANG 7 | 0.8803 | 0.84891 | -0.031392 |  | 0.95 | 1.05 | 0.034893 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | LANG 7 | 0.8803 | 0.84891 | -0.031392 |  | 0.95 | 1.05 | 0.046335 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | LANG 7 | 0.8803 | 0.84891 | -0.031392 |  | 0.95 | 1.05 | 0.034893 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | LANG 7 | 0.8803 | 0.84891 | -0.031392 |  | 0.95 | 1.05 | 0.03611 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | LANG 7 | 0.8803 | 0.84891 | -0.031392 |  | 0.95 | 1.05 | 0.034555 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | LANG 7 | 0.8803 | 0.84891 | -0.031392 |  | 0.95 | 1.05 | 0.033454 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | LANG 7 | 0.8803 | 0.84891 | -0.031392 |  | 0.95 | 1.05 | 0.045771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | LANG 7 | 0.8803 | 0.84891 | -0.031392 |  | 0.95 | 1.05 | 0.031365 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | LANG 7 | 0.8803 | 0.84891 | -0.031392 |  | 0.95 | 1.05 | 0.031365 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | LANG 7 | 0.8803 | 0.84891 | -0.031392 |  | 0.95 | 1.05 | 0.041921 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | LANG 7 | 0.8803 | 0.84891 | -0.031392 |  | 0.95 | 1.05 | 0.033154 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | LANG 7 | 0.8803 | 0.84891 | -0.031392 |  | 0.95 | 1.05 | 0.03341 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | LANG 7 | 0.8803 | 0.84891 | -0.031392 |  | 0.95 | 1.05 | 0.030334 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | LANG 7 | 0.8803 | 0.84891 | -0.031392 |  | 0.95 | 1.05 | 0.034718 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | LANG 7 | 0.8803 | 0.84891 | -0.031392 |  | 0.95 | 1.05 | 0.033533 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | LAWHILL6 | 0.96558 | 0.94454 | -0.021042 |  | 0.95 | 1.05 | 0.031932 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | LAWHILL6 | 0.96558 | 0.94454 | -0.021042 |  | 0.95 | 1.05 | 0.046406 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | LAWHILL6 | 0.96558 | 0.94454 | -0.021042 |  | 0.95 | 1.05 | 0.034669 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | LAWHILL6 | 0.96558 | 0.94454 | -0.021042 |  | 0.95 | 1.05 | 0.036297 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | LAWHILL6 | 0.96558 | 0.94454 | -0.021042 |  | 0.95 | 1.05 | 0.03404 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | LAWHILL6 | 0.96558 | 0.94454 | -0.021042 |  | 0.95 | 1.05 | 0.054677 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | LAWHILL6 | 0.96558 | 0.94454 | -0.021042 |  | 0.95 | 1.05 | 0.036731 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | LAWHILL6 | 0.96558 | 0.94454 | -0.021042 |  | 0.95 | 1.05 | 0.035653 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | LEC U5 6 | 0.96558 | 0.94454 | -0.021042 |  | 0.95 | 1.05 | 0.031932 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | LEC U5 6 | 0.96558 | 0.94454 | -0.021042 |  | 0.95 | 1.05 | 0.046406 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | LEC U5 6 | 0.96558 | 0.94454 | -0.021042 |  | 0.95 | 1.05 | 0.034669 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | LEC U5 6 | 0.96558 | 0.94454 | -0.021042 |  | 0.95 | 1.05 | 0.036297 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | LEC U5 6 | 0.96558 | 0.94454 | -0.021042 |  | 0.95 | 1.05 | 0.03404 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | LEC U5 6 | 0.96558 | 0.94454 | -0.021042 |  | 0.95 | 1.05 | 0.054677 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | LEC U5 6 | 0.96558 | 0.94454 | -0.021042 |  | 0.95 | 1.05 | 0.036731 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | LEC U5 6 | 0.96558 | 0.94454 | -0.021042 |  | 0.95 | 1.05 | 0.035653 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | LIBERTY4 | 0.96262 | 0.92941 | -0.033204 |  | 0.93 | 1.05 | 0.090803 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | LIBERTY4 | 0.96262 | 0.92941 | -0.033204 |  | 0.93 | 1.05 | 0.030422 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | LIBERTY4 | 0.96262 | 0.92941 | -0.033204 |  | 0.93 | 1.05 | 0.040015 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | LIBERTY4 | 0.96262 | 0.92941 | -0.033204 |  | 0.93 | 1.05 | 0.056985 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | LIBERTY4 | 0.96262 | 0.92941 | -0.033204 |  | 0.93 | 1.05 | 0.053029 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | LIBERTY4 | 0.96262 | 0.92941 | -0.033204 |  | 0.93 | 1.05 | 0.040244 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-219 | LIBERTY4 | 0.96262 | 0.92941 | -0.033204 |  | 0.93 | 1.05 | 0.044635 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | LIBERTY4 | 0.96262 | 0.92941 | -0.033204 |  | 0.93 | 1.05 | 0.12486 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | LIBERTY4 | 0.96262 | 0.92941 | -0.033204 |  | 0.93 | 1.05 | 0.044133 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | LIBERTY4 | 0.96262 | 0.92941 | -0.033204 |  | 0.93 | 1.05 | 0.056119 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | LIBERTY4 | 0.96262 | 0.92941 | -0.033204 |  | 0.93 | 1.05 | 0.056119 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | LIBERTY4 | 0.96262 | 0.92941 | -0.033204 |  | 0.93 | 1.05 | 0.056496 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | LIBERTY4 | 0.96262 | 0.92941 | -0.033204 |  | 0.93 | 1.05 | 0.073384 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | LIBERTY4 | 0.96262 | 0.92941 | -0.033204 |  | 0.93 | 1.05 | 0.035942 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | LIBERTY4 | 0.96262 | 0.92941 | -0.033204 |  | 0.93 | 1.05 | 0.03343 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | LIBERTY4 | 0.96262 | 0.92941 | -0.033204 |  | 0.93 | 1.05 | 0.038724 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | LIBERTY4 | 0.96262 | 0.92941 | -0.033204 |  | 0.93 | 1.05 | 0.038724 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | LIBERTY4 | 0.96262 | 0.92941 | -0.033204 |  | 0.93 | 1.05 | 0.046894 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | LIBERTY4 | 0.96262 | 0.92941 | -0.033204 |  | 0.93 | 1.05 | 0.056872 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | LIBERTY4 | 0.96262 | 0.92941 | -0.033204 |  | 0.93 | 1.05 | 0.039954 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | LIBERTY4 | 0.96262 | 0.92941 | -0.033204 |  | 0.93 | 1.05 | 0.054164 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | LIBERTY4 | 0.96262 | 0.92941 | -0.033204 |  | 0.93 | 1.05 | 0.048427 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | LIBERTY4 | 0.96262 | 0.92941 | -0.033204 |  | 0.93 | 1.05 | 0.062555 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | LIBERTY4 | 0.96262 | 0.92941 | -0.033204 |  | 0.93 | 1.05 | 0.05027 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | LIBERTY4 | 0.96262 | 0.92941 | -0.033204 |  | 0.93 | 1.05 | 0.034642 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | MCARBDE4 | 0.89524 | 0.8646 | -0.030636 |  | 0.92 | 1.05 | 0.035206 | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | MCARBDE4 | 0.90228 | 0.87298 | -0.0293 |  | 0.92 | 1.05 | 0.035206 | Single 509752 INOLATP4 138 510442 GUAVA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | MIDLAND6 | 0.96611 | 0.94528 | -0.020826 |  | 0.95 | 1.05 | 0.031932 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | MIDLAND6 | 0.96611 | 0.94528 | -0.020826 |  | 0.95 | 1.05 | 0.046406 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | MIDLAND6 | 0.96611 | 0.94528 | -0.020826 |  | 0.95 | 1.05 | 0.034669 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | MIDLAND6 | 0.96611 | 0.94528 | -0.020826 |  | 0.95 | 1.05 | 0.036297 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | MIDLAND6 | 0.96611 | 0.94528 | -0.020826 |  | 0.95 | 1.05 | 0.03404 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | MIDLAND6 | 0.96611 | 0.94528 | -0.020826 |  | 0.95 | 1.05 | 0.054677 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | MIDLAND6 | 0.96611 | 0.94528 | -0.020826 |  | 0.95 | 1.05 | 0.036731 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | MIDLAND6 | 0.96611 | 0.94528 | -0.020826 |  | 0.95 | 1.05 | 0.035653 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | NEO184 5 | 0.96407 | 0.92274 | -0.041326 |  | 0.925 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | NEO184 5 | 0.96407 | 0.92274 | -0.041326 |  | 0.925 | 1.05 | 0.0423 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | NEO184 5 | 0.96407 | 0.92274 | -0.041326 |  | 0.925 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | NEO184 5 | 0.96407 | 0.92274 | -0.041326 |  | 0.925 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | NEO184 5 | 0.96407 | 0.92274 | -0.041326 |  | 0.925 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | NEO184 5 | 0.96407 | 0.92274 | -0.041326 |  | 0.925 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | NEO184 5 | 0.96407 | 0.92274 | -0.041326 |  | 0.925 | 1.05 | 0.044676 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | NEO184 5 | 0.96407 | 0.92274 | -0.041326 |  | 0.925 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | NEO184 5 | 0.96407 | 0.92274 | -0.041326 |  | 0.925 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | NEO184 5 | 0.96407 | 0.92274 | -0.041326 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | NEO184 5 | 0.96407 | 0.92274 | -0.041326 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | NEO184 5 | 0.96407 | 0.92274 | -0.041326 |  | 0.925 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | NEO184 5 | 0.96407 | 0.92274 | -0.041326 |  | 0.925 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | NEO184 5 | 0.96407 | 0.92274 | -0.041326 |  | 0.925 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | NEO184 5 | 0.96335 | 0.91888 | -0.044469 |  | 0.925 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | NEO184 5 | 0.96335 | 0.91888 | -0.044469 |  | 0.925 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | NEO184 5 | 0.96335 | 0.91888 | -0.044469 |  | 0.925 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | NEO184 5 | 0.96335 | 0.91888 | -0.044469 |  | 0.925 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | NEO184 5 | 0.96335 | 0.91888 | -0.044469 |  | 0.925 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | NEO184 5 | 0.96335 | 0.91888 | -0.044469 |  | 0.925 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | NEO184 5 | 0.96335 | 0.91888 | -0.044469 |  | 0.925 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | NEO184 5 | 0.96335 | 0.91888 | -0.044469 |  | 0.925 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | NEO184 5 | 0.96335 | 0.91888 | -0.044469 |  | 0.925 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | NEO184 5 | 0.96335 | 0.91888 | -0.044469 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | NEO184 5 | 0.96335 | 0.91888 | -0.044469 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | NEO184 5 | 0.96335 | 0.91888 | -0.044469 |  | 0.925 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | NEO184 5 | 0.96335 | 0.91888 | -0.044469 |  | 0.925 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | NEO184 5 | 0.96335 | 0.91888 | -0.044469 |  | 0.925 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | NEO184 5 | 0.96702 | 0.92357 | -0.043447 |  | 0.925 | 1.05 | 0.076984 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | NEO184 5 | 0.96702 | 0.92357 | -0.043447 |  | 0.925 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | NEO184 5 | 0.96702 | 0.92357 | -0.043447 |  | 0.925 | 1.05 | 0.065662 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | NEO184 5 | 0.96702 | 0.92357 | -0.043447 |  | 0.925 | 1.05 | 0.072679 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | NEO184 5 | 0.96702 | 0.92357 | -0.043447 |  | 0.925 | 1.05 | 0.052268 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | NEO184 5 | 0.96702 | 0.92357 | -0.043447 |  | 0.925 | 1.05 | 0.080584 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | NEO184 5 | 0.96702 | 0.92357 | -0.043447 |  | 0.925 | 1.05 | 0.082253 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | NEO184 5 | 0.96702 | 0.92357 | -0.043447 |  | 0.925 | 1.05 | 0.076592 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | NEO184 5 | 0.96702 | 0.92357 | -0.043447 |  | 0.925 | 1.05 | 0.030918 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | NEO184 5 | 0.96702 | 0.92357 | -0.043447 |  | 0.925 | 1.05 | 0.073312 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | NEO184 5 | 0.96702 | 0.92357 | -0.043447 |  | 0.925 | 1.05 | 0.076355 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | NEO184 5 | 0.96702 | 0.92357 | -0.043447 |  | 0.925 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | NEO184 5 | 0.96702 | 0.92357 | -0.043447 |  | 0.925 | 1.05 | 0.037529 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | NEO184 5 | 0.96702 | 0.92357 | -0.043447 |  | 0.925 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | NEO184 5 | 0.96702 | 0.92357 | -0.043447 |  | 0.925 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | NEO184 5 | 0.96702 | 0.92357 | -0.043447 |  | 0.925 | 1.05 | 0.030301 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | NEO184 5 | 0.96702 | 0.92357 | -0.043447 |  | 0.925 | 1.05 | 0.041779 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | NEO184 5 | 0.96702 | 0.92357 | -0.043447 |  | 0.925 | 1.05 | 0.079587 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | NEO184 5 | 0.96564 | 0.92381 | -0.041833 |  | 0.925 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.09 MVAR switched shunt at NOL435 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | NEO184 5 | 0.96564 | 0.92381 | -0.041833 |  | 0.925 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.09 MVAR switched shunt at NOL435 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | NEO184 5 | 0.96564 | 0.92381 | -0.041833 |  | 0.925 | 1.05 | 0.035909 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.09 MVAR switched shunt at NOL435 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | NEO184 5 | 0.96298 | 0.91997 | -0.04301 |  | 0.925 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | NEO184 5 | 0.96298 | 0.91997 | -0.04301 |  | 0.925 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | NEO184 5 | 0.96298 | 0.91997 | -0.04301 |  | 0.925 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | NEO184 5 | 0.96298 | 0.91997 | -0.04301 |  | 0.925 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | NEO184 5 | 0.96298 | 0.91997 | -0.04301 |  | 0.925 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | NEO184 5 | 0.96298 | 0.91997 | -0.04301 |  | 0.925 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | NEO184 5 | 0.96298 | 0.91997 | -0.04301 |  | 0.925 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | NEO184 5 | 0.96298 | 0.91997 | -0.04301 |  | 0.925 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | NEO184 5 | 0.96298 | 0.91997 | -0.04301 |  | 0.925 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | NEO184 5 | 0.96298 | 0.91997 | -0.04301 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | NEO184 5 | 0.96298 | 0.91997 | -0.04301 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | NEO184 5 | 0.96298 | 0.91997 | -0.04301 |  | 0.925 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | NEO184 5 | 0.96298 | 0.91997 | -0.04301 |  | 0.925 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | NEO184 5 | 0.96298 | 0.91997 | -0.04301 |  | 0.925 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | NEOSHO 4 | 0.94532 | 0.91205 | -0.033266 |  | 0.93 | 1.05 | 0.10484 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | NEOSHO 4 | 0.94532 | 0.91205 | -0.033266 |  | 0.93 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | NEOSHO 4 | 0.94532 | 0.91205 | -0.033266 |  | 0.93 | 1.05 | 0.086823 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | NEOSHO 4 | 0.94532 | 0.91205 | -0.033266 |  | 0.93 | 1.05 | 0.098758 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | NEOSHO 4 | 0.94532 | 0.91205 | -0.033266 |  | 0.93 | 1.05 | 0.087817 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | NEOSHO 4 | 0.94532 | 0.91205 | -0.033266 |  | 0.93 | 1.05 | 0.11285 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | NEOSHO 4 | 0.94532 | 0.91205 | -0.033266 |  | 0.93 | 1.05 | 0.11586 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | NEOSHO 4 | 0.94532 | 0.91205 | -0.033266 |  | 0.93 | 1.05 | 0.10654 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | NEOSHO 4 | 0.94532 | 0.91205 | -0.033266 |  | 0.93 | 1.05 | 0.031666 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-219 | NEOSHO 4 | 0.94532 | 0.91205 | -0.033266 |  | 0.93 | 1.05 | 0.030863 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | NEOSHO 4 | 0.94532 | 0.91205 | -0.033266 |  | 0.93 | 1.05 | 0.099811 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | NEOSHO 4 | 0.94532 | 0.91205 | -0.033266 |  | 0.93 | 1.05 | 0.10896 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | NEOSHO 4 | 0.94532 | 0.91205 | -0.033266 |  | 0.93 | 1.05 | 0.040233 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | NEOSHO 4 | 0.94532 | 0.91205 | -0.033266 |  | 0.93 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | NEOSHO 4 | 0.94532 | 0.91205 | -0.033266 |  | 0.93 | 1.05 | 0.060046 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | NEOSHO 4 | 0.94532 | 0.91205 | -0.033266 |  | 0.93 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | NEOSHO 4 | 0.94532 | 0.91205 | -0.033266 |  | 0.93 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | NEOSHO 4 | 0.94532 | 0.91205 | -0.033266 |  | 0.93 | 1.05 | 0.032555 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | NEOSHO 4 | 0.94532 | 0.91205 | -0.033266 |  | 0.93 | 1.05 | 0.031413 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | NEOSHO 4 | 0.94532 | 0.91205 | -0.033266 |  | 0.93 | 1.05 | 0.046478 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | NEOSHO 4 | 0.94532 | 0.91205 | -0.033266 |  | 0.93 | 1.05 | 0.11534 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | NEOSHO 4 | 0.9487 | 0.91728 | -0.031426 |  | 0.93 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | NEOSHO 4 | 0.9487 | 0.91728 | -0.031426 |  | 0.93 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | NEOSHO 4 | 0.9487 | 0.91728 | -0.031426 |  | 0.93 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | NEOSHO 4 | 0.9487 | 0.91728 | -0.031426 |  | 0.93 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | NEOSHO 4 | 0.9487 | 0.91728 | -0.031426 |  | 0.93 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | NEOSHO 4 | 0.9487 | 0.91728 | -0.031426 |  | 0.93 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | NEOSHO 4 | 0.9487 | 0.91728 | -0.031426 |  | 0.93 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | NEOSHO 4 | 0.9487 | 0.91728 | -0.031426 |  | 0.93 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | NEOSHO 4 | 0.9487 | 0.91728 | -0.031426 |  | 0.93 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | NEOSHO 4 | 0.9487 | 0.91728 | -0.031426 |  | 0.93 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | NEOSHO 4 | 0.9487 | 0.91728 | -0.031426 |  | 0.93 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | NEOSHO 4 | 0.9487 | 0.91728 | -0.031426 |  | 0.93 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | NEOSHO 4 | 0.9487 | 0.91728 | -0.031426 |  | 0.93 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | NEOSHO 4 | 0.9487 | 0.91728 | -0.031426 |  | 0.93 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | NEOSHO 4 | 0.94483 | 0.9113 | -0.033535 |  | 0.93 | 1.05 | 0.076984 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | NEOSHO 4 | 0.94483 | 0.9113 | -0.033535 |  | 0.93 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | NEOSHO 4 | 0.94483 | 0.9113 | -0.033535 |  | 0.93 | 1.05 | 0.065662 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | NEOSHO 4 | 0.94483 | 0.9113 | -0.033535 |  | 0.93 | 1.05 | 0.072679 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | NEOSHO 4 | 0.94483 | 0.9113 | -0.033535 |  | 0.93 | 1.05 | 0.052268 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | NEOSHO 4 | 0.94483 | 0.9113 | -0.033535 |  | 0.93 | 1.05 | 0.080584 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | NEOSHO 4 | 0.94483 | 0.9113 | -0.033535 |  | 0.93 | 1.05 | 0.082253 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | NEOSHO 4 | 0.94483 | 0.9113 | -0.033535 |  | 0.93 | 1.05 | 0.076592 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | NEOSHO 4 | 0.94483 | 0.9113 | -0.033535 |  | 0.93 | 1.05 | 0.030918 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | NEOSHO 4 | 0.94483 | 0.9113 | -0.033535 |  | 0.93 | 1.05 | 0.073312 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | NEOSHO 4 | 0.94483 | 0.9113 | -0.033535 |  | 0.93 | 1.05 | 0.076355 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | NEOSHO 4 | 0.94483 | 0.9113 | -0.033535 |  | 0.93 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | NEOSHO 4 | 0.94483 | 0.9113 | -0.033535 |  | 0.93 | 1.05 | 0.037529 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | NEOSHO 4 | 0.94483 | 0.9113 | -0.033535 |  | 0.93 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | NEOSHO 4 | 0.94483 | 0.9113 | -0.033535 |  | 0.93 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | NEOSHO 4 | 0.94483 | 0.9113 | -0.033535 |  | 0.93 | 1.05 | 0.030301 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | NEOSHO 4 | 0.94483 | 0.9113 | -0.033535 |  | 0.93 | 1.05 | 0.041779 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | NEOSHO 4 | 0.94483 | 0.9113 | -0.033535 |  | 0.93 | 1.05 | 0.079587 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | NEOSHO 4 | 0.94937 | 0.91605 | -0.033315 |  | 0.93 | 1.05 | 0.03716 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | NEOSHO 4 | 0.94937 | 0.91605 | -0.033315 |  | 0.93 | 1.05 | 0.030931 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | NEOSHO 4 | 0.94937 | 0.91605 | -0.033315 |  | 0.93 | 1.05 | 0.044459 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | NEOSHO 4 | 0.94937 | 0.91605 | -0.033315 |  | 0.93 | 1.05 | 0.041648 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | NEOSHO 4 | 0.94937 | 0.91605 | -0.033315 |  | 0.93 | 1.05 | 0.031986 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | NEOSHO 4 | 0.94937 | 0.91605 | -0.033315 |  | 0.93 | 1.05 | 0.039776 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | NEOSHO 4 | 0.94937 | 0.91605 | -0.033315 |  | 0.93 | 1.05 | 0.042349 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | NEOSHO 4 | 0.94937 | 0.91605 | -0.033315 |  | 0.93 | 1.05 | 0.041252 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | NEOSHO 4 | 0.94937 | 0.91605 | -0.033315 |  | 0.93 | 1.05 | 0.031238 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | NEOSHO 4 | 0.94937 | 0.91605 | -0.033315 |  | 0.93 | 1.05 | 0.034893 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | NEOSHO 4 | 0.94937 | 0.91605 | -0.033315 |  | 0.93 | 1.05 | 0.046335 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | NEOSHO 4 | 0.94937 | 0.91605 | -0.033315 |  | 0.93 | 1.05 | 0.034893 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | NEOSHO 4 | 0.94937 | 0.91605 | -0.033315 |  | 0.93 | 1.05 | 0.03611 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | NEOSHO 4 | 0.94937 | 0.91605 | -0.033315 |  | 0.93 | 1.05 | 0.034555 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | NEOSHO 4 | 0.94937 | 0.91605 | -0.033315 |  | 0.93 | 1.05 | 0.033454 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | NEOSHO 4 | 0.94937 | 0.91605 | -0.033315 |  | 0.93 | 1.05 | 0.045771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | NEOSHO 4 | 0.94937 | 0.91605 | -0.033315 |  | 0.93 | 1.05 | 0.031365 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | NEOSHO 4 | 0.94937 | 0.91605 | -0.033315 |  | 0.93 | 1.05 | 0.031365 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | NEOSHO 4 | 0.94937 | 0.91605 | -0.033315 |  | 0.93 | 1.05 | 0.041921 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | NEOSHO 4 | 0.94937 | 0.91605 | -0.033315 |  | 0.93 | 1.05 | 0.033154 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | NEOSHO 4 | 0.94937 | 0.91605 | -0.033315 |  | 0.93 | 1.05 | 0.03341 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | NEOSHO 4 | 0.94937 | 0.91605 | -0.033315 |  | 0.93 | 1.05 | 0.030334 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | NEOSHO 4 | 0.94937 | 0.91605 | -0.033315 |  | 0.93 | 1.05 | 0.034718 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | NEOSHO 4 | 0.94937 | 0.91605 | -0.033315 |  | 0.93 | 1.05 | 0.033533 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | NEOSHO 4 | 0.94647 | 0.91211 | -0.034358 |  | 0.93 | 1.05 | 0.038685 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | NEOSHO 4 | 0.94647 | 0.91211 | -0.034358 |  | 0.93 | 1.05 | 0.07469 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | NEOSHO 4 | 0.94647 | 0.91211 | -0.034358 |  | 0.93 | 1.05 | 0.068062 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | NEOSHO 4 | 0.94647 | 0.91211 | -0.034358 |  | 0.93 | 1.05 | 0.034938 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | NEOSHO 4 | 0.94647 | 0.91211 | -0.034358 |  | 0.93 | 1.05 | 0.032777 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | NEOSHO 4 | 0.94647 | 0.91211 | -0.034358 |  | 0.93 | 1.05 | 0.043475 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | NEOSHO 4 | 0.94647 | 0.91211 | -0.034358 |  | 0.93 | 1.05 | 0.13386 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | NEOSHO 4 | 0.94647 | 0.91211 | -0.034358 |  | 0.93 | 1.05 | 0.036067 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | NEOSHO 4 | 0.94647 | 0.91211 | -0.034358 |  | 0.93 | 1.05 | 0.036067 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | NEOSHO 4 | 0.94647 | 0.91211 | -0.034358 |  | 0.93 | 1.05 | 0.067572 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | NEOSHO 4 | 0.94647 | 0.91211 | -0.034358 |  | 0.93 | 1.05 | 0.033583 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | NEOSHO 4 | 0.94647 | 0.91211 | -0.034358 |  | 0.93 | 1.05 | 0.034115 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | NEOSHON2 | 0.95378 | 0.92319 | -0.030589 |  | 0.93 | 1.05 | 0.10484 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | NEOSHON2 | 0.95378 | 0.92319 | -0.030589 |  | 0.93 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | NEOSHON2 | 0.95378 | 0.92319 | -0.030589 |  | 0.93 | 1.05 | 0.086823 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | NEOSHON2 | 0.95378 | 0.92319 | -0.030589 |  | 0.93 | 1.05 | 0.098758 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | NEOSHON2 | 0.95378 | 0.92319 | -0.030589 |  | 0.93 | 1.05 | 0.087817 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | NEOSHON2 | 0.95378 | 0.92319 | -0.030589 |  | 0.93 | 1.05 | 0.11285 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | NEOSHON2 | 0.95378 | 0.92319 | -0.030589 |  | 0.93 | 1.05 | 0.11586 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | NEOSHON2 | 0.95378 | 0.92319 | -0.030589 |  | 0.93 | 1.05 | 0.10654 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | NEOSHON2 | 0.95378 | 0.92319 | -0.030589 |  | 0.93 | 1.05 | 0.031666 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-219 | NEOSHON2 | 0.95378 | 0.92319 | -0.030589 |  | 0.93 | 1.05 | 0.030863 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | NEOSHON2 | 0.95378 | 0.92319 | -0.030589 |  | 0.93 | 1.05 | 0.099811 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | NEOSHON2 | 0.95378 | 0.92319 | -0.030589 |  | 0.93 | 1.05 | 0.10896 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | NEOSHON2 | 0.95378 | 0.92319 | -0.030589 |  | 0.93 | 1.05 | 0.040233 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | NEOSHON2 | 0.95378 | 0.92319 | -0.030589 |  | 0.93 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | NEOSHON2 | 0.95378 | 0.92319 | -0.030589 |  | 0.93 | 1.05 | 0.060046 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | NEOSHON2 | 0.95378 | 0.92319 | -0.030589 |  | 0.93 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | NEOSHON2 | 0.95378 | 0.92319 | -0.030589 |  | 0.93 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | NEOSHON2 | 0.95378 | 0.92319 | -0.030589 |  | 0.93 | 1.05 | 0.032555 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | NEOSHON2 | 0.95378 | 0.92319 | -0.030589 |  | 0.93 | 1.05 | 0.031413 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | NEOSHON2 | 0.95378 | 0.92319 | -0.030589 |  | 0.93 | 1.05 | 0.046478 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | NEOSHON2 | 0.95378 | 0.92319 | -0.030589 |  | 0.93 | 1.05 | 0.11534 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | NEOSHON2 | 0.95684 | 0.928 | -0.028839 |  | 0.93 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | NEOSHON2 | 0.95684 | 0.928 | -0.028839 |  | 0.93 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | NEOSHON2 | 0.95684 | 0.928 | -0.028839 |  | 0.93 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | NEOSHON2 | 0.95684 | 0.928 | -0.028839 |  | 0.93 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | NEOSHON2 | 0.95684 | 0.928 | -0.028839 |  | 0.93 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | NEOSHON2 | 0.95684 | 0.928 | -0.028839 |  | 0.93 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | NEOSHON2 | 0.95684 | 0.928 | -0.028839 |  | 0.93 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | NEOSHON2 | 0.95684 | 0.928 | -0.028839 |  | 0.93 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | NEOSHON2 | 0.95684 | 0.928 | -0.028839 |  | 0.93 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | NEOSHON2 | 0.95684 | 0.928 | -0.028839 |  | 0.93 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | NEOSHON2 | 0.95684 | 0.928 | -0.028839 |  | 0.93 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | NEOSHON2 | 0.95684 | 0.928 | -0.028839 |  | 0.93 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | NEOSHON2 | 0.95684 | 0.928 | -0.028839 |  | 0.93 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | NEOSHON2 | 0.95684 | 0.928 | -0.028839 |  | 0.93 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | NEOSHON2 | 0.95329 | 0.92259 | -0.030693 |  | 0.93 | 1.05 | 0.076984 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | NEOSHON2 | 0.95329 | 0.92259 | -0.030693 |  | 0.93 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | NEOSHON2 | 0.95329 | 0.92259 | -0.030693 |  | 0.93 | 1.05 | 0.065662 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | NEOSHON2 | 0.95329 | 0.92259 | -0.030693 |  | 0.93 | 1.05 | 0.072679 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | NEOSHON2 | 0.95329 | 0.92259 | -0.030693 |  | 0.93 | 1.05 | 0.052268 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | NEOSHON2 | 0.95329 | 0.92259 | -0.030693 |  | 0.93 | 1.05 | 0.080584 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | NEOSHON2 | 0.95329 | 0.92259 | -0.030693 |  | 0.93 | 1.05 | 0.082253 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | NEOSHON2 | 0.95329 | 0.92259 | -0.030693 |  | 0.93 | 1.05 | 0.076592 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | NEOSHON2 | 0.95329 | 0.92259 | -0.030693 |  | 0.93 | 1.05 | 0.030918 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | NEOSHON2 | 0.95329 | 0.92259 | -0.030693 |  | 0.93 | 1.05 | 0.073312 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | NEOSHON2 | 0.95329 | 0.92259 | -0.030693 |  | 0.93 | 1.05 | 0.076355 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | NEOSHON2 | 0.95329 | 0.92259 | -0.030693 |  | 0.93 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | NEOSHON2 | 0.95329 | 0.92259 | -0.030693 |  | 0.93 | 1.05 | 0.037529 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | NEOSHON2 | 0.95329 | 0.92259 | -0.030693 |  | 0.93 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | NEOSHON2 | 0.95329 | 0.92259 | -0.030693 |  | 0.93 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | NEOSHON2 | 0.95329 | 0.92259 | -0.030693 |  | 0.93 | 1.05 | 0.030301 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | NEOSHON2 | 0.95329 | 0.92259 | -0.030693 |  | 0.93 | 1.05 | 0.041779 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | NEOSHON2 | 0.95329 | 0.92259 | -0.030693 |  | 0.93 | 1.05 | 0.079587 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | NEOSHON2 | 0.95764 | 0.92706 | -0.030583 |  | 0.93 | 1.05 | 0.03716 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | NEOSHON2 | 0.95764 | 0.92706 | -0.030583 |  | 0.93 | 1.05 | 0.030931 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | NEOSHON2 | 0.95764 | 0.92706 | -0.030583 |  | 0.93 | 1.05 | 0.044459 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | NEOSHON2 | 0.95764 | 0.92706 | -0.030583 |  | 0.93 | 1.05 | 0.041648 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | NEOSHON2 | 0.95764 | 0.92706 | -0.030583 |  | 0.93 | 1.05 | 0.031986 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | NEOSHON2 | 0.95764 | 0.92706 | -0.030583 |  | 0.93 | 1.05 | 0.039776 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | NEOSHON2 | 0.95764 | 0.92706 | -0.030583 |  | 0.93 | 1.05 | 0.042349 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | NEOSHON2 | 0.95764 | 0.92706 | -0.030583 |  | 0.93 | 1.05 | 0.041252 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | NEOSHON2 | 0.95764 | 0.92706 | -0.030583 |  | 0.93 | 1.05 | 0.031238 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | NEOSHON2 | 0.95764 | 0.92706 | -0.030583 |  | 0.93 | 1.05 | 0.034893 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | NEOSHON2 | 0.95764 | 0.92706 | -0.030583 |  | 0.93 | 1.05 | 0.046335 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | NEOSHON2 | 0.95764 | 0.92706 | -0.030583 |  | 0.93 | 1.05 | 0.034893 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | NEOSHON2 | 0.95764 | 0.92706 | -0.030583 |  | 0.93 | 1.05 | 0.03611 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | NEOSHON2 | 0.95764 | 0.92706 | -0.030583 |  | 0.93 | 1.05 | 0.034555 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | NEOSHON2 | 0.95764 | 0.92706 | -0.030583 |  | 0.93 | 1.05 | 0.033454 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | NEOSHON2 | 0.95764 | 0.92706 | -0.030583 |  | 0.93 | 1.05 | 0.045771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | NEOSHON2 | 0.95764 | 0.92706 | -0.030583 |  | 0.93 | 1.05 | 0.031365 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | NEOSHON2 | 0.95764 | 0.92706 | -0.030583 |  | 0.93 | 1.05 | 0.031365 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | NEOSHON2 | 0.95764 | 0.92706 | -0.030583 |  | 0.93 | 1.05 | 0.041921 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | NEOSHON2 | 0.95764 | 0.92706 | -0.030583 |  | 0.93 | 1.05 | 0.033154 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | NEOSHON2 | 0.95764 | 0.92706 | -0.030583 |  | 0.93 | 1.05 | 0.03341 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | NEOSHON2 | 0.95764 | 0.92706 | -0.030583 |  | 0.93 | 1.05 | 0.030334 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | NEOSHON2 | 0.95764 | 0.92706 | -0.030583 |  | 0.93 | 1.05 | 0.034718 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | NEOSHON2 | 0.95764 | 0.92706 | -0.030583 |  | 0.93 | 1.05 | 0.033533 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | NEOSHON2 | 0.95485 | 0.92316 | -0.031692 |  | 0.93 | 1.05 | 0.038685 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | NEOSHON2 | 0.95485 | 0.92316 | -0.031692 |  | 0.93 | 1.05 | 0.07469 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | NEOSHON2 | 0.95485 | 0.92316 | -0.031692 |  | 0.93 | 1.05 | 0.068062 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | NEOSHON2 | 0.95485 | 0.92316 | -0.031692 |  | 0.93 | 1.05 | 0.034938 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | NEOSHON2 | 0.95485 | 0.92316 | -0.031692 |  | 0.93 | 1.05 | 0.032777 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | NEOSHON2 | 0.95485 | 0.92316 | -0.031692 |  | 0.93 | 1.05 | 0.043475 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | NEOSHON2 | 0.95485 | 0.92316 | -0.031692 |  | 0.93 | 1.05 | 0.13386 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | NEOSHON2 | 0.95485 | 0.92316 | -0.031692 |  | 0.93 | 1.05 | 0.036067 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | NEOSHON2 | 0.95485 | 0.92316 | -0.031692 |  | 0.93 | 1.05 | 0.036067 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | NEOSHON2 | 0.95485 | 0.92316 | -0.031692 |  | 0.93 | 1.05 | 0.067572 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | NEOSHON2 | 0.95485 | 0.92316 | -0.031692 |  | 0.93 | 1.05 | 0.033583 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | NEOSHON2 | 0.95485 | 0.92316 | -0.031692 |  | 0.93 | 1.05 | 0.034115 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | NEOSHON4 | 0.94538 | 0.91213 | -0.033255 |  | 0.93 | 1.05 | 0.10484 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | NEOSHON4 | 0.94538 | 0.91213 | -0.033255 |  | 0.93 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | NEOSHON4 | 0.94538 | 0.91213 | -0.033255 |  | 0.93 | 1.05 | 0.086823 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | NEOSHON4 | 0.94538 | 0.91213 | -0.033255 |  | 0.93 | 1.05 | 0.098758 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | NEOSHON4 | 0.94538 | 0.91213 | -0.033255 |  | 0.93 | 1.05 | 0.087817 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | NEOSHON4 | 0.94538 | 0.91213 | -0.033255 |  | 0.93 | 1.05 | 0.11285 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | NEOSHON4 | 0.94538 | 0.91213 | -0.033255 |  | 0.93 | 1.05 | 0.11586 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | NEOSHON4 | 0.94538 | 0.91213 | -0.033255 |  | 0.93 | 1.05 | 0.10654 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | NEOSHON4 | 0.94538 | 0.91213 | -0.033255 |  | 0.93 | 1.05 | 0.031666 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-219 | NEOSHON4 | 0.94538 | 0.91213 | -0.033255 |  | 0.93 | 1.05 | 0.030863 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | NEOSHON4 | 0.94538 | 0.91213 | -0.033255 |  | 0.93 | 1.05 | 0.099811 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | NEOSHON4 | 0.94538 | 0.91213 | -0.033255 |  | 0.93 | 1.05 | 0.10896 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | NEOSHON4 | 0.94538 | 0.91213 | -0.033255 |  | 0.93 | 1.05 | 0.040233 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | NEOSHON4 | 0.94538 | 0.91213 | -0.033255 |  | 0.93 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | NEOSHON4 | 0.94538 | 0.91213 | -0.033255 |  | 0.93 | 1.05 | 0.060046 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | NEOSHON4 | 0.94538 | 0.91213 | -0.033255 |  | 0.93 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | NEOSHON4 | 0.94538 | 0.91213 | -0.033255 |  | 0.93 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | NEOSHON4 | 0.94538 | 0.91213 | -0.033255 |  | 0.93 | 1.05 | 0.032555 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | NEOSHON4 | 0.94538 | 0.91213 | -0.033255 |  | 0.93 | 1.05 | 0.031413 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | NEOSHON4 | 0.94538 | 0.91213 | -0.033255 |  | 0.93 | 1.05 | 0.046478 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | NEOSHON4 | 0.94538 | 0.91213 | -0.033255 |  | 0.93 | 1.05 | 0.11534 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | NEOSHON4 | 0.94877 | 0.91735 | -0.031417 |  | 0.93 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | NEOSHON4 | 0.94877 | 0.91735 | -0.031417 |  | 0.93 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | NEOSHON4 | 0.94877 | 0.91735 | -0.031417 |  | 0.93 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | NEOSHON4 | 0.94877 | 0.91735 | -0.031417 |  | 0.93 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | NEOSHON4 | 0.94877 | 0.91735 | -0.031417 |  | 0.93 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | NEOSHON4 | 0.94877 | 0.91735 | -0.031417 |  | 0.93 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | NEOSHON4 | 0.94877 | 0.91735 | -0.031417 |  | 0.93 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | NEOSHON4 | 0.94877 | 0.91735 | -0.031417 |  | 0.93 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | NEOSHON4 | 0.94877 | 0.91735 | -0.031417 |  | 0.93 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | NEOSHON4 | 0.94877 | 0.91735 | -0.031417 |  | 0.93 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | NEOSHON4 | 0.94877 | 0.91735 | -0.031417 |  | 0.93 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | NEOSHON4 | 0.94877 | 0.91735 | -0.031417 |  | 0.93 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | NEOSHON4 | 0.94877 | 0.91735 | -0.031417 |  | 0.93 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | NEOSHON4 | 0.94877 | 0.91735 | -0.031417 |  | 0.93 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | NEOSHON4 | 0.94489 | 0.91137 | -0.033524 |  | 0.93 | 1.05 | 0.076984 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | NEOSHON4 | 0.94489 | 0.91137 | -0.033524 |  | 0.93 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | NEOSHON4 | 0.94489 | 0.91137 | -0.033524 |  | 0.93 | 1.05 | 0.065662 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | NEOSHON4 | 0.94489 | 0.91137 | -0.033524 |  | 0.93 | 1.05 | 0.072679 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | NEOSHON4 | 0.94489 | 0.91137 | -0.033524 |  | 0.93 | 1.05 | 0.052268 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | NEOSHON4 | 0.94489 | 0.91137 | -0.033524 |  | 0.93 | 1.05 | 0.080584 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | NEOSHON4 | 0.94489 | 0.91137 | -0.033524 |  | 0.93 | 1.05 | 0.082253 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | NEOSHON4 | 0.94489 | 0.91137 | -0.033524 |  | 0.93 | 1.05 | 0.076592 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | NEOSHON4 | 0.94489 | 0.91137 | -0.033524 |  | 0.93 | 1.05 | 0.030918 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | NEOSHON4 | 0.94489 | 0.91137 | -0.033524 |  | 0.93 | 1.05 | 0.073312 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | NEOSHON4 | 0.94489 | 0.91137 | -0.033524 |  | 0.93 | 1.05 | 0.076355 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | NEOSHON4 | 0.94489 | 0.91137 | -0.033524 |  | 0.93 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | NEOSHON4 | 0.94489 | 0.91137 | -0.033524 |  | 0.93 | 1.05 | 0.037529 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | NEOSHON4 | 0.94489 | 0.91137 | -0.033524 |  | 0.93 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | NEOSHON4 | 0.94489 | 0.91137 | -0.033524 |  | 0.93 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | NEOSHON4 | 0.94489 | 0.91137 | -0.033524 |  | 0.93 | 1.05 | 0.030301 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | NEOSHON4 | 0.94489 | 0.91137 | -0.033524 |  | 0.93 | 1.05 | 0.041779 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | NEOSHON4 | 0.94489 | 0.91137 | -0.033524 |  | 0.93 | 1.05 | 0.079587 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | NEOSHON4 | 0.94943 | 0.91612 | -0.033306 |  | 0.93 | 1.05 | 0.03716 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | NEOSHON4 | 0.94943 | 0.91612 | -0.033306 |  | 0.93 | 1.05 | 0.030931 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | NEOSHON4 | 0.94943 | 0.91612 | -0.033306 |  | 0.93 | 1.05 | 0.044459 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | NEOSHON4 | 0.94943 | 0.91612 | -0.033306 |  | 0.93 | 1.05 | 0.041648 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | NEOSHON4 | 0.94943 | 0.91612 | -0.033306 |  | 0.93 | 1.05 | 0.031986 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | NEOSHON4 | 0.94943 | 0.91612 | -0.033306 |  | 0.93 | 1.05 | 0.039776 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | NEOSHON4 | 0.94943 | 0.91612 | -0.033306 |  | 0.93 | 1.05 | 0.042349 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | NEOSHON4 | 0.94943 | 0.91612 | -0.033306 |  | 0.93 | 1.05 | 0.041252 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | NEOSHON4 | 0.94943 | 0.91612 | -0.033306 |  | 0.93 | 1.05 | 0.031238 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | NEOSHON4 | 0.94943 | 0.91612 | -0.033306 |  | 0.93 | 1.05 | 0.034893 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | NEOSHON4 | 0.94943 | 0.91612 | -0.033306 |  | 0.93 | 1.05 | 0.046335 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | NEOSHON4 | 0.94943 | 0.91612 | -0.033306 |  | 0.93 | 1.05 | 0.034893 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | NEOSHON4 | 0.94943 | 0.91612 | -0.033306 |  | 0.93 | 1.05 | 0.03611 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | NEOSHON4 | 0.94943 | 0.91612 | -0.033306 |  | 0.93 | 1.05 | 0.034555 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | NEOSHON4 | 0.94943 | 0.91612 | -0.033306 |  | 0.93 | 1.05 | 0.033454 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | NEOSHON4 | 0.94943 | 0.91612 | -0.033306 |  | 0.93 | 1.05 | 0.045771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | NEOSHON4 | 0.94943 | 0.91612 | -0.033306 |  | 0.93 | 1.05 | 0.031365 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | NEOSHON4 | 0.94943 | 0.91612 | -0.033306 |  | 0.93 | 1.05 | 0.031365 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | NEOSHON4 | 0.94943 | 0.91612 | -0.033306 |  | 0.93 | 1.05 | 0.041921 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | NEOSHON4 | 0.94943 | 0.91612 | -0.033306 |  | 0.93 | 1.05 | 0.033154 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | NEOSHON4 | 0.94943 | 0.91612 | -0.033306 |  | 0.93 | 1.05 | 0.03341 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | NEOSHON4 | 0.94943 | 0.91612 | -0.033306 |  | 0.93 | 1.05 | 0.030334 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | NEOSHON4 | 0.94943 | 0.91612 | -0.033306 |  | 0.93 | 1.05 | 0.034718 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | NEOSHON4 | 0.94943 | 0.91612 | -0.033306 |  | 0.93 | 1.05 | 0.033533 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | NEOSHON4 | 0.94653 | 0.91219 | -0.034348 |  | 0.93 | 1.05 | 0.038685 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | NEOSHON4 | 0.94653 | 0.91219 | -0.034348 |  | 0.93 | 1.05 | 0.07469 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | NEOSHON4 | 0.94653 | 0.91219 | -0.034348 |  | 0.93 | 1.05 | 0.068062 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | NEOSHON4 | 0.94653 | 0.91219 | -0.034348 |  | 0.93 | 1.05 | 0.034938 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | NEOSHON4 | 0.94653 | 0.91219 | -0.034348 |  | 0.93 | 1.05 | 0.032777 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | NEOSHON4 | 0.94653 | 0.91219 | -0.034348 |  | 0.93 | 1.05 | 0.043475 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | NEOSHON4 | 0.94653 | 0.91219 | -0.034348 |  | 0.93 | 1.05 | 0.13386 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | NEOSHON4 | 0.94653 | 0.91219 | -0.034348 |  | 0.93 | 1.05 | 0.036067 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | NEOSHON4 | 0.94653 | 0.91219 | -0.034348 |  | 0.93 | 1.05 | 0.036067 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | NEOSHON4 | 0.94653 | 0.91219 | -0.034348 |  | 0.93 | 1.05 | 0.067572 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | NEOSHON4 | 0.94653 | 0.91219 | -0.034348 |  | 0.93 | 1.05 | 0.033583 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | NEOSHON4 | 0.94653 | 0.91219 | -0.034348 |  | 0.93 | 1.05 | 0.034115 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | NEOSHOS2 | 0.95379 | 0.92321 | -0.030585 |  | 0.93 | 1.05 | 0.10484 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | NEOSHOS2 | 0.95379 | 0.92321 | -0.030585 |  | 0.93 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | NEOSHOS2 | 0.95379 | 0.92321 | -0.030585 |  | 0.93 | 1.05 | 0.086823 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | NEOSHOS2 | 0.95379 | 0.92321 | -0.030585 |  | 0.93 | 1.05 | 0.098758 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | NEOSHOS2 | 0.95379 | 0.92321 | -0.030585 |  | 0.93 | 1.05 | 0.087817 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | NEOSHOS2 | 0.95379 | 0.92321 | -0.030585 |  | 0.93 | 1.05 | 0.11285 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | NEOSHOS2 | 0.95379 | 0.92321 | -0.030585 |  | 0.93 | 1.05 | 0.11586 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | NEOSHOS2 | 0.95379 | 0.92321 | -0.030585 |  | 0.93 | 1.05 | 0.10654 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | NEOSHOS2 | 0.95379 | 0.92321 | -0.030585 |  | 0.93 | 1.05 | 0.031666 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-219 | NEOSHOS2 | 0.95379 | 0.92321 | -0.030585 |  | 0.93 | 1.05 | 0.030863 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | NEOSHOS2 | 0.95379 | 0.92321 | -0.030585 |  | 0.93 | 1.05 | 0.099811 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | NEOSHOS2 | 0.95379 | 0.92321 | -0.030585 |  | 0.93 | 1.05 | 0.10896 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | NEOSHOS2 | 0.95379 | 0.92321 | -0.030585 |  | 0.93 | 1.05 | 0.040233 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | NEOSHOS2 | 0.95379 | 0.92321 | -0.030585 |  | 0.93 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | NEOSHOS2 | 0.95379 | 0.92321 | -0.030585 |  | 0.93 | 1.05 | 0.060046 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | NEOSHOS2 | 0.95379 | 0.92321 | -0.030585 |  | 0.93 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | NEOSHOS2 | 0.95379 | 0.92321 | -0.030585 |  | 0.93 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | NEOSHOS2 | 0.95379 | 0.92321 | -0.030585 |  | 0.93 | 1.05 | 0.032555 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | NEOSHOS2 | 0.95379 | 0.92321 | -0.030585 |  | 0.93 | 1.05 | 0.031413 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | NEOSHOS2 | 0.95379 | 0.92321 | -0.030585 |  | 0.93 | 1.05 | 0.046478 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | NEOSHOS2 | 0.95379 | 0.92321 | -0.030585 |  | 0.93 | 1.05 | 0.11534 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | NEOSHOS2 | 0.95685 | 0.92801 | -0.028835 |  | 0.93 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | NEOSHOS2 | 0.95685 | 0.92801 | -0.028835 |  | 0.93 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | NEOSHOS2 | 0.95685 | 0.92801 | -0.028835 |  | 0.93 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | NEOSHOS2 | 0.95685 | 0.92801 | -0.028835 |  | 0.93 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | NEOSHOS2 | 0.95685 | 0.92801 | -0.028835 |  | 0.93 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | NEOSHOS2 | 0.95685 | 0.92801 | -0.028835 |  | 0.93 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | NEOSHOS2 | 0.95685 | 0.92801 | -0.028835 |  | 0.93 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | NEOSHOS2 | 0.95685 | 0.92801 | -0.028835 |  | 0.93 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | NEOSHOS2 | 0.95685 | 0.92801 | -0.028835 |  | 0.93 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | NEOSHOS2 | 0.95685 | 0.92801 | -0.028835 |  | 0.93 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | NEOSHOS2 | 0.95685 | 0.92801 | -0.028835 |  | 0.93 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | NEOSHOS2 | 0.95685 | 0.92801 | -0.028835 |  | 0.93 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | NEOSHOS2 | 0.95685 | 0.92801 | -0.028835 |  | 0.93 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | NEOSHOS2 | 0.95685 | 0.92801 | -0.028835 |  | 0.93 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | NEOSHOS2 | 0.9533 | 0.92261 | -0.030689 |  | 0.93 | 1.05 | 0.076984 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | NEOSHOS2 | 0.9533 | 0.92261 | -0.030689 |  | 0.93 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | NEOSHOS2 | 0.9533 | 0.92261 | -0.030689 |  | 0.93 | 1.05 | 0.065662 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | NEOSHOS2 | 0.9533 | 0.92261 | -0.030689 |  | 0.93 | 1.05 | 0.072679 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | NEOSHOS2 | 0.9533 | 0.92261 | -0.030689 |  | 0.93 | 1.05 | 0.052268 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | NEOSHOS2 | 0.9533 | 0.92261 | -0.030689 |  | 0.93 | 1.05 | 0.080584 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | NEOSHOS2 | 0.9533 | 0.92261 | -0.030689 |  | 0.93 | 1.05 | 0.082253 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | NEOSHOS2 | 0.9533 | 0.92261 | -0.030689 |  | 0.93 | 1.05 | 0.076592 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | NEOSHOS2 | 0.9533 | 0.92261 | -0.030689 |  | 0.93 | 1.05 | 0.030918 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | NEOSHOS2 | 0.9533 | 0.92261 | -0.030689 |  | 0.93 | 1.05 | 0.073312 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | NEOSHOS2 | 0.9533 | 0.92261 | -0.030689 |  | 0.93 | 1.05 | 0.076355 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | NEOSHOS2 | 0.9533 | 0.92261 | -0.030689 |  | 0.93 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | NEOSHOS2 | 0.9533 | 0.92261 | -0.030689 |  | 0.93 | 1.05 | 0.037529 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | NEOSHOS2 | 0.9533 | 0.92261 | -0.030689 |  | 0.93 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | NEOSHOS2 | 0.9533 | 0.92261 | -0.030689 |  | 0.93 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | NEOSHOS2 | 0.9533 | 0.92261 | -0.030689 |  | 0.93 | 1.05 | 0.030301 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | NEOSHOS2 | 0.9533 | 0.92261 | -0.030689 |  | 0.93 | 1.05 | 0.041779 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | NEOSHOS2 | 0.9533 | 0.92261 | -0.030689 |  | 0.93 | 1.05 | 0.079587 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | NEOSHOS2 | 0.95765 | 0.92707 | -0.030579 |  | 0.93 | 1.05 | 0.03716 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | NEOSHOS2 | 0.95765 | 0.92707 | -0.030579 |  | 0.93 | 1.05 | 0.030931 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | NEOSHOS2 | 0.95765 | 0.92707 | -0.030579 |  | 0.93 | 1.05 | 0.044459 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | NEOSHOS2 | 0.95765 | 0.92707 | -0.030579 |  | 0.93 | 1.05 | 0.041648 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | NEOSHOS2 | 0.95765 | 0.92707 | -0.030579 |  | 0.93 | 1.05 | 0.031986 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | NEOSHOS2 | 0.95765 | 0.92707 | -0.030579 |  | 0.93 | 1.05 | 0.039776 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | NEOSHOS2 | 0.95765 | 0.92707 | -0.030579 |  | 0.93 | 1.05 | 0.042349 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | NEOSHOS2 | 0.95765 | 0.92707 | -0.030579 |  | 0.93 | 1.05 | 0.041252 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | NEOSHOS2 | 0.95765 | 0.92707 | -0.030579 |  | 0.93 | 1.05 | 0.031238 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | NEOSHOS2 | 0.95765 | 0.92707 | -0.030579 |  | 0.93 | 1.05 | 0.034893 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | NEOSHOS2 | 0.95765 | 0.92707 | -0.030579 |  | 0.93 | 1.05 | 0.046335 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | NEOSHOS2 | 0.95765 | 0.92707 | -0.030579 |  | 0.93 | 1.05 | 0.034893 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | NEOSHOS2 | 0.95765 | 0.92707 | -0.030579 |  | 0.93 | 1.05 | 0.03611 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | NEOSHOS2 | 0.95765 | 0.92707 | -0.030579 |  | 0.93 | 1.05 | 0.034555 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | NEOSHOS2 | 0.95765 | 0.92707 | -0.030579 |  | 0.93 | 1.05 | 0.033454 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | NEOSHOS2 | 0.95765 | 0.92707 | -0.030579 |  | 0.93 | 1.05 | 0.045771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | NEOSHOS2 | 0.95765 | 0.92707 | -0.030579 |  | 0.93 | 1.05 | 0.031365 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | NEOSHOS2 | 0.95765 | 0.92707 | -0.030579 |  | 0.93 | 1.05 | 0.031365 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | NEOSHOS2 | 0.95765 | 0.92707 | -0.030579 |  | 0.93 | 1.05 | 0.041921 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | NEOSHOS2 | 0.95765 | 0.92707 | -0.030579 |  | 0.93 | 1.05 | 0.033154 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | NEOSHOS2 | 0.95765 | 0.92707 | -0.030579 |  | 0.93 | 1.05 | 0.03341 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | NEOSHOS2 | 0.95765 | 0.92707 | -0.030579 |  | 0.93 | 1.05 | 0.030334 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | NEOSHOS2 | 0.95765 | 0.92707 | -0.030579 |  | 0.93 | 1.05 | 0.034718 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | NEOSHOS2 | 0.95765 | 0.92707 | -0.030579 |  | 0.93 | 1.05 | 0.033533 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | NEOSHOS2 | 0.95486 | 0.92317 | -0.031688 |  | 0.93 | 1.05 | 0.038685 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | NEOSHOS2 | 0.95486 | 0.92317 | -0.031688 |  | 0.93 | 1.05 | 0.07469 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | NEOSHOS2 | 0.95486 | 0.92317 | -0.031688 |  | 0.93 | 1.05 | 0.068062 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | NEOSHOS2 | 0.95486 | 0.92317 | -0.031688 |  | 0.93 | 1.05 | 0.034938 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | NEOSHOS2 | 0.95486 | 0.92317 | -0.031688 |  | 0.93 | 1.05 | 0.032777 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | NEOSHOS2 | 0.95486 | 0.92317 | -0.031688 |  | 0.93 | 1.05 | 0.043475 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | NEOSHOS2 | 0.95486 | 0.92317 | -0.031688 |  | 0.93 | 1.05 | 0.13386 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | NEOSHOS2 | 0.95486 | 0.92317 | -0.031688 |  | 0.93 | 1.05 | 0.036067 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | NEOSHOS2 | 0.95486 | 0.92317 | -0.031688 |  | 0.93 | 1.05 | 0.036067 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | NEOSHOS2 | 0.95486 | 0.92317 | -0.031688 |  | 0.93 | 1.05 | 0.067572 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | NEOSHOS2 | 0.95486 | 0.92317 | -0.031688 |  | 0.93 | 1.05 | 0.033583 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | NEOSHOS2 | 0.95486 | 0.92317 | -0.031688 |  | 0.93 | 1.05 | 0.034115 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | NEOSHOS4 | 0.94548 | 0.9122 | -0.03328 |  | 0.93 | 1.05 | 0.10484 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | NEOSHOS4 | 0.94548 | 0.9122 | -0.03328 |  | 0.93 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | NEOSHOS4 | 0.94548 | 0.9122 | -0.03328 |  | 0.93 | 1.05 | 0.086823 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | NEOSHOS4 | 0.94548 | 0.9122 | -0.03328 |  | 0.93 | 1.05 | 0.098758 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | NEOSHOS4 | 0.94548 | 0.9122 | -0.03328 |  | 0.93 | 1.05 | 0.087817 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | NEOSHOS4 | 0.94548 | 0.9122 | -0.03328 |  | 0.93 | 1.05 | 0.11285 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | NEOSHOS4 | 0.94548 | 0.9122 | -0.03328 |  | 0.93 | 1.05 | 0.11586 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | NEOSHOS4 | 0.94548 | 0.9122 | -0.03328 |  | 0.93 | 1.05 | 0.10654 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | NEOSHOS4 | 0.94548 | 0.9122 | -0.03328 |  | 0.93 | 1.05 | 0.031666 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-219 | NEOSHOS4 | 0.94548 | 0.9122 | -0.03328 |  | 0.93 | 1.05 | 0.030863 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | NEOSHOS4 | 0.94548 | 0.9122 | -0.03328 |  | 0.93 | 1.05 | 0.099811 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | NEOSHOS4 | 0.94548 | 0.9122 | -0.03328 |  | 0.93 | 1.05 | 0.10896 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | NEOSHOS4 | 0.94548 | 0.9122 | -0.03328 |  | 0.93 | 1.05 | 0.040233 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | NEOSHOS4 | 0.94548 | 0.9122 | -0.03328 |  | 0.93 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | NEOSHOS4 | 0.94548 | 0.9122 | -0.03328 |  | 0.93 | 1.05 | 0.060046 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | NEOSHOS4 | 0.94548 | 0.9122 | -0.03328 |  | 0.93 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | NEOSHOS4 | 0.94548 | 0.9122 | -0.03328 |  | 0.93 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | NEOSHOS4 | 0.94548 | 0.9122 | -0.03328 |  | 0.93 | 1.05 | 0.032555 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | NEOSHOS4 | 0.94548 | 0.9122 | -0.03328 |  | 0.93 | 1.05 | 0.031413 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | NEOSHOS4 | 0.94548 | 0.9122 | -0.03328 |  | 0.93 | 1.05 | 0.046478 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | NEOSHOS4 | 0.94548 | 0.9122 | -0.03328 |  | 0.93 | 1.05 | 0.11534 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | NEOSHOS4 | 0.95374 | 0.9323 | -0.021444 |  | 0.95 | 1.05 | 0.14495 | System Intact | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | NEOSHOS4 | 0.94886 | 0.91742 | -0.031441 |  | 0.93 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | NEOSHOS4 | 0.94886 | 0.91742 | -0.031441 |  | 0.93 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | NEOSHOS4 | 0.94886 | 0.91742 | -0.031441 |  | 0.93 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | NEOSHOS4 | 0.94886 | 0.91742 | -0.031441 |  | 0.93 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | NEOSHOS4 | 0.94886 | 0.91742 | -0.031441 |  | 0.93 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | NEOSHOS4 | 0.94886 | 0.91742 | -0.031441 |  | 0.93 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | NEOSHOS4 | 0.94886 | 0.91742 | -0.031441 |  | 0.93 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | NEOSHOS4 | 0.94886 | 0.91742 | -0.031441 |  | 0.93 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | NEOSHOS4 | 0.94886 | 0.91742 | -0.031441 |  | 0.93 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | NEOSHOS4 | 0.94886 | 0.91742 | -0.031441 |  | 0.93 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | NEOSHOS4 | 0.94886 | 0.91742 | -0.031441 |  | 0.93 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | NEOSHOS4 | 0.94886 | 0.91742 | -0.031441 |  | 0.93 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | NEOSHOS4 | 0.94886 | 0.91742 | -0.031441 |  | 0.93 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | NEOSHOS4 | 0.94886 | 0.91742 | -0.031441 |  | 0.93 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | NEOSHOS4 | 0.94499 | 0.91144 | -0.03355 |  | 0.93 | 1.05 | 0.076984 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | NEOSHOS4 | 0.94499 | 0.91144 | -0.03355 |  | 0.93 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | NEOSHOS4 | 0.94499 | 0.91144 | -0.03355 |  | 0.93 | 1.05 | 0.065662 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | NEOSHOS4 | 0.94499 | 0.91144 | -0.03355 |  | 0.93 | 1.05 | 0.072679 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | NEOSHOS4 | 0.94499 | 0.91144 | -0.03355 |  | 0.93 | 1.05 | 0.052268 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | NEOSHOS4 | 0.94499 | 0.91144 | -0.03355 |  | 0.93 | 1.05 | 0.080584 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | NEOSHOS4 | 0.94499 | 0.91144 | -0.03355 |  | 0.93 | 1.05 | 0.082253 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | NEOSHOS4 | 0.94499 | 0.91144 | -0.03355 |  | 0.93 | 1.05 | 0.076592 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | NEOSHOS4 | 0.94499 | 0.91144 | -0.03355 |  | 0.93 | 1.05 | 0.030918 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | NEOSHOS4 | 0.94499 | 0.91144 | -0.03355 |  | 0.93 | 1.05 | 0.073312 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | NEOSHOS4 | 0.94499 | 0.91144 | -0.03355 |  | 0.93 | 1.05 | 0.076355 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | NEOSHOS4 | 0.94499 | 0.91144 | -0.03355 |  | 0.93 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | NEOSHOS4 | 0.94499 | 0.91144 | -0.03355 |  | 0.93 | 1.05 | 0.037529 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | NEOSHOS4 | 0.94499 | 0.91144 | -0.03355 |  | 0.93 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | NEOSHOS4 | 0.94499 | 0.91144 | -0.03355 |  | 0.93 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | NEOSHOS4 | 0.94499 | 0.91144 | -0.03355 |  | 0.93 | 1.05 | 0.030301 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | NEOSHOS4 | 0.94499 | 0.91144 | -0.03355 |  | 0.93 | 1.05 | 0.041779 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | NEOSHOS4 | 0.94499 | 0.91144 | -0.03355 |  | 0.93 | 1.05 | 0.079587 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | NEOSHOS4 | 0.94953 | 0.9162 | -0.033325 |  | 0.93 | 1.05 | 0.03716 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | NEOSHOS4 | 0.94953 | 0.9162 | -0.033325 |  | 0.93 | 1.05 | 0.030931 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | NEOSHOS4 | 0.94953 | 0.9162 | -0.033325 |  | 0.93 | 1.05 | 0.044459 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | NEOSHOS4 | 0.94953 | 0.9162 | -0.033325 |  | 0.93 | 1.05 | 0.041648 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | NEOSHOS4 | 0.94953 | 0.9162 | -0.033325 |  | 0.93 | 1.05 | 0.031986 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | NEOSHOS4 | 0.94953 | 0.9162 | -0.033325 |  | 0.93 | 1.05 | 0.039776 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | NEOSHOS4 | 0.94953 | 0.9162 | -0.033325 |  | 0.93 | 1.05 | 0.042349 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | NEOSHOS4 | 0.94953 | 0.9162 | -0.033325 |  | 0.93 | 1.05 | 0.041252 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | NEOSHOS4 | 0.94953 | 0.9162 | -0.033325 |  | 0.93 | 1.05 | 0.031238 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | NEOSHOS4 | 0.94953 | 0.9162 | -0.033325 |  | 0.93 | 1.05 | 0.034893 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | NEOSHOS4 | 0.94953 | 0.9162 | -0.033325 |  | 0.93 | 1.05 | 0.046335 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | NEOSHOS4 | 0.94953 | 0.9162 | -0.033325 |  | 0.93 | 1.05 | 0.034893 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | NEOSHOS4 | 0.94953 | 0.9162 | -0.033325 |  | 0.93 | 1.05 | 0.03611 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | NEOSHOS4 | 0.94953 | 0.9162 | -0.033325 |  | 0.93 | 1.05 | 0.034555 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | NEOSHOS4 | 0.94953 | 0.9162 | -0.033325 |  | 0.93 | 1.05 | 0.033454 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | NEOSHOS4 | 0.94953 | 0.9162 | -0.033325 |  | 0.93 | 1.05 | 0.045771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | NEOSHOS4 | 0.94953 | 0.9162 | -0.033325 |  | 0.93 | 1.05 | 0.031365 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | NEOSHOS4 | 0.94953 | 0.9162 | -0.033325 |  | 0.93 | 1.05 | 0.031365 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | NEOSHOS4 | 0.94953 | 0.9162 | -0.033325 |  | 0.93 | 1.05 | 0.041921 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | NEOSHOS4 | 0.94953 | 0.9162 | -0.033325 |  | 0.93 | 1.05 | 0.033154 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | NEOSHOS4 | 0.94953 | 0.9162 | -0.033325 |  | 0.93 | 1.05 | 0.03341 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | NEOSHOS4 | 0.94953 | 0.9162 | -0.033325 |  | 0.93 | 1.05 | 0.030334 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | NEOSHOS4 | 0.94953 | 0.9162 | -0.033325 |  | 0.93 | 1.05 | 0.034718 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | NEOSHOS4 | 0.94953 | 0.9162 | -0.033325 |  | 0.93 | 1.05 | 0.033533 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | NEOSHOS4 | 0.94663 | 0.91226 | -0.03437 |  | 0.93 | 1.05 | 0.038685 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | NEOSHOS4 | 0.94663 | 0.91226 | -0.03437 |  | 0.93 | 1.05 | 0.07469 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | NEOSHOS4 | 0.94663 | 0.91226 | -0.03437 |  | 0.93 | 1.05 | 0.068062 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | NEOSHOS4 | 0.94663 | 0.91226 | -0.03437 |  | 0.93 | 1.05 | 0.034938 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | NEOSHOS4 | 0.94663 | 0.91226 | -0.03437 |  | 0.93 | 1.05 | 0.032777 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | NEOSHOS4 | 0.94663 | 0.91226 | -0.03437 |  | 0.93 | 1.05 | 0.043475 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | NEOSHOS4 | 0.94663 | 0.91226 | -0.03437 |  | 0.93 | 1.05 | 0.13386 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | NEOSHOS4 | 0.94663 | 0.91226 | -0.03437 |  | 0.93 | 1.05 | 0.036067 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | NEOSHOS4 | 0.94663 | 0.91226 | -0.03437 |  | 0.93 | 1.05 | 0.036067 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | NEOSHOS4 | 0.94663 | 0.91226 | -0.03437 |  | 0.93 | 1.05 | 0.067572 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | NEOSHOS4 | 0.94663 | 0.91226 | -0.03437 |  | 0.93 | 1.05 | 0.033583 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | NEOSHOS4 | 0.94663 | 0.91226 | -0.03437 |  | 0.93 | 1.05 | 0.034115 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | NOL435 5 | 0.96568 | 0.91578 | -0.049904 |  | 0.925 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | NOL435 5 | 0.96568 | 0.91578 | -0.049904 |  | 0.925 | 1.05 | 0.0423 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | NOL435 5 | 0.96568 | 0.91578 | -0.049904 |  | 0.925 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | NOL435 5 | 0.96568 | 0.91578 | -0.049904 |  | 0.925 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | NOL435 5 | 0.96568 | 0.91578 | -0.049904 |  | 0.925 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | NOL435 5 | 0.96568 | 0.91578 | -0.049904 |  | 0.925 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | NOL435 5 | 0.96568 | 0.91578 | -0.049904 |  | 0.925 | 1.05 | 0.044676 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | NOL435 5 | 0.96568 | 0.91578 | -0.049904 |  | 0.925 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | NOL435 5 | 0.96568 | 0.91578 | -0.049904 |  | 0.925 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | NOL435 5 | 0.96568 | 0.91578 | -0.049904 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | NOL435 5 | 0.96568 | 0.91578 | -0.049904 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | NOL435 5 | 0.96568 | 0.91578 | -0.049904 |  | 0.925 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | NOL435 5 | 0.96568 | 0.91578 | -0.049904 |  | 0.925 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | NOL435 5 | 0.96568 | 0.91578 | -0.049904 |  | 0.925 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | NOL435 5 | 0.96505 | 0.9124 | -0.052648 |  | 0.925 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | NOL435 5 | 0.96505 | 0.9124 | -0.052648 |  | 0.925 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | NOL435 5 | 0.96505 | 0.9124 | -0.052648 |  | 0.925 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | NOL435 5 | 0.96505 | 0.9124 | -0.052648 |  | 0.925 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | NOL435 5 | 0.96505 | 0.9124 | -0.052648 |  | 0.925 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | NOL435 5 | 0.96505 | 0.9124 | -0.052648 |  | 0.925 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | NOL435 5 | 0.96505 | 0.9124 | -0.052648 |  | 0.925 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | NOL435 5 | 0.96505 | 0.9124 | -0.052648 |  | 0.925 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | NOL435 5 | 0.96505 | 0.9124 | -0.052648 |  | 0.925 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | NOL435 5 | 0.96505 | 0.9124 | -0.052648 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | NOL435 5 | 0.96505 | 0.9124 | -0.052648 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | NOL435 5 | 0.96505 | 0.9124 | -0.052648 |  | 0.925 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | NOL435 5 | 0.96505 | 0.9124 | -0.052648 |  | 0.925 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | NOL435 5 | 0.96505 | 0.9124 | -0.052648 |  | 0.925 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | NOL435 5 | 0.97 | 0.91895 | -0.051056 |  | 0.925 | 1.05 | 0.076984 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | NOL435 5 | 0.97 | 0.91895 | -0.051056 |  | 0.925 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | NOL435 5 | 0.97 | 0.91895 | -0.051056 |  | 0.925 | 1.05 | 0.065662 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | NOL435 5 | 0.97 | 0.91895 | -0.051056 |  | 0.925 | 1.05 | 0.072679 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | NOL435 5 | 0.97 | 0.91895 | -0.051056 |  | 0.925 | 1.05 | 0.052268 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | NOL435 5 | 0.97 | 0.91895 | -0.051056 |  | 0.925 | 1.05 | 0.080584 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | NOL435 5 | 0.97 | 0.91895 | -0.051056 |  | 0.925 | 1.05 | 0.082253 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | NOL435 5 | 0.97 | 0.91895 | -0.051056 |  | 0.925 | 1.05 | 0.076592 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | NOL435 5 | 0.97 | 0.91895 | -0.051056 |  | 0.925 | 1.05 | 0.030918 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | NOL435 5 | 0.97 | 0.91895 | -0.051056 |  | 0.925 | 1.05 | 0.073312 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | NOL435 5 | 0.97 | 0.91895 | -0.051056 |  | 0.925 | 1.05 | 0.076355 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | NOL435 5 | 0.97 | 0.91895 | -0.051056 |  | 0.925 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | NOL435 5 | 0.97 | 0.91895 | -0.051056 |  | 0.925 | 1.05 | 0.037529 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | NOL435 5 | 0.97 | 0.91895 | -0.051056 |  | 0.925 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | NOL435 5 | 0.97 | 0.91895 | -0.051056 |  | 0.925 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | NOL435 5 | 0.97 | 0.91895 | -0.051056 |  | 0.925 | 1.05 | 0.030301 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | NOL435 5 | 0.97 | 0.91895 | -0.051056 |  | 0.925 | 1.05 | 0.041779 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | NOL435 5 | 0.97 | 0.91895 | -0.051056 |  | 0.925 | 1.05 | 0.079587 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | NOL435 5 | 0.96888 | 0.91972 | -0.049158 |  | 0.925 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.09 MVAR switched shunt at NOL435 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | NOL435 5 | 0.96888 | 0.91972 | -0.049158 |  | 0.925 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.09 MVAR switched shunt at NOL435 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | NOL435 5 | 0.96888 | 0.91972 | -0.049158 |  | 0.925 | 1.05 | 0.035909 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.09 MVAR switched shunt at NOL435 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | NOL435 5 | 0.96473 | 0.91358 | -0.051154 |  | 0.925 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | NOL435 5 | 0.96473 | 0.91358 | -0.051154 |  | 0.925 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | NOL435 5 | 0.96473 | 0.91358 | -0.051154 |  | 0.925 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | NOL435 5 | 0.96473 | 0.91358 | -0.051154 |  | 0.925 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | NOL435 5 | 0.96473 | 0.91358 | -0.051154 |  | 0.925 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | NOL435 5 | 0.96473 | 0.91358 | -0.051154 |  | 0.925 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | NOL435 5 | 0.96473 | 0.91358 | -0.051154 |  | 0.925 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | NOL435 5 | 0.96473 | 0.91358 | -0.051154 |  | 0.925 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | NOL435 5 | 0.96473 | 0.91358 | -0.051154 |  | 0.925 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | NOL435 5 | 0.96473 | 0.91358 | -0.051154 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | NOL435 5 | 0.96473 | 0.91358 | -0.051154 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | NOL435 5 | 0.96473 | 0.91358 | -0.051154 |  | 0.925 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | NOL435 5 | 0.96473 | 0.91358 | -0.051154 |  | 0.925 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | NOL435 5 | 0.96473 | 0.91358 | -0.051154 |  | 0.925 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | ORDNCE 2 | 0.95331 | 0.9224 | -0.030908 |  | 0.93 | 1.05 | 0.10484 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | ORDNCE 2 | 0.95331 | 0.9224 | -0.030908 |  | 0.93 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | ORDNCE 2 | 0.95331 | 0.9224 | -0.030908 |  | 0.93 | 1.05 | 0.086823 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | ORDNCE 2 | 0.95331 | 0.9224 | -0.030908 |  | 0.93 | 1.05 | 0.098758 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | ORDNCE 2 | 0.95331 | 0.9224 | -0.030908 |  | 0.93 | 1.05 | 0.087817 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | ORDNCE 2 | 0.95331 | 0.9224 | -0.030908 |  | 0.93 | 1.05 | 0.11285 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | ORDNCE 2 | 0.95331 | 0.9224 | -0.030908 |  | 0.93 | 1.05 | 0.11586 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | ORDNCE 2 | 0.95331 | 0.9224 | -0.030908 |  | 0.93 | 1.05 | 0.10654 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | ORDNCE 2 | 0.95331 | 0.9224 | -0.030908 |  | 0.93 | 1.05 | 0.031666 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-219 | ORDNCE 2 | 0.95331 | 0.9224 | -0.030908 |  | 0.93 | 1.05 | 0.030863 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | ORDNCE 2 | 0.95331 | 0.9224 | -0.030908 |  | 0.93 | 1.05 | 0.099811 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | ORDNCE 2 | 0.95331 | 0.9224 | -0.030908 |  | 0.93 | 1.05 | 0.10896 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | ORDNCE 2 | 0.95331 | 0.9224 | -0.030908 |  | 0.93 | 1.05 | 0.040233 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | ORDNCE 2 | 0.95331 | 0.9224 | -0.030908 |  | 0.93 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | ORDNCE 2 | 0.95331 | 0.9224 | -0.030908 |  | 0.93 | 1.05 | 0.060046 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | ORDNCE 2 | 0.95331 | 0.9224 | -0.030908 |  | 0.93 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | ORDNCE 2 | 0.95331 | 0.9224 | -0.030908 |  | 0.93 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | ORDNCE 2 | 0.95331 | 0.9224 | -0.030908 |  | 0.93 | 1.05 | 0.032555 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | ORDNCE 2 | 0.95331 | 0.9224 | -0.030908 |  | 0.93 | 1.05 | 0.031413 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | ORDNCE 2 | 0.95331 | 0.9224 | -0.030908 |  | 0.93 | 1.05 | 0.046478 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | ORDNCE 2 | 0.95331 | 0.9224 | -0.030908 |  | 0.93 | 1.05 | 0.11534 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | ORDNCE 2 | 0.95639 | 0.92726 | -0.029139 |  | 0.93 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | ORDNCE 2 | 0.95639 | 0.92726 | -0.029139 |  | 0.93 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | ORDNCE 2 | 0.95639 | 0.92726 | -0.029139 |  | 0.93 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | ORDNCE 2 | 0.95639 | 0.92726 | -0.029139 |  | 0.93 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | ORDNCE 2 | 0.95639 | 0.92726 | -0.029139 |  | 0.93 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | ORDNCE 2 | 0.95639 | 0.92726 | -0.029139 |  | 0.93 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | ORDNCE 2 | 0.95639 | 0.92726 | -0.029139 |  | 0.93 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | ORDNCE 2 | 0.95639 | 0.92726 | -0.029139 |  | 0.93 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | ORDNCE 2 | 0.95639 | 0.92726 | -0.029139 |  | 0.93 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | ORDNCE 2 | 0.95639 | 0.92726 | -0.029139 |  | 0.93 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | ORDNCE 2 | 0.95639 | 0.92726 | -0.029139 |  | 0.93 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | ORDNCE 2 | 0.95639 | 0.92726 | -0.029139 |  | 0.93 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | ORDNCE 2 | 0.95639 | 0.92726 | -0.029139 |  | 0.93 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | ORDNCE 2 | 0.95639 | 0.92726 | -0.029139 |  | 0.93 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | ORDNCE 2 | 0.95281 | 0.92179 | -0.031014 |  | 0.93 | 1.05 | 0.076984 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | ORDNCE 2 | 0.95281 | 0.92179 | -0.031014 |  | 0.93 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | ORDNCE 2 | 0.95281 | 0.92179 | -0.031014 |  | 0.93 | 1.05 | 0.065662 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | ORDNCE 2 | 0.95281 | 0.92179 | -0.031014 |  | 0.93 | 1.05 | 0.072679 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | ORDNCE 2 | 0.95281 | 0.92179 | -0.031014 |  | 0.93 | 1.05 | 0.052268 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | ORDNCE 2 | 0.95281 | 0.92179 | -0.031014 |  | 0.93 | 1.05 | 0.080584 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | ORDNCE 2 | 0.95281 | 0.92179 | -0.031014 |  | 0.93 | 1.05 | 0.082253 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | ORDNCE 2 | 0.95281 | 0.92179 | -0.031014 |  | 0.93 | 1.05 | 0.076592 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | ORDNCE 2 | 0.95281 | 0.92179 | -0.031014 |  | 0.93 | 1.05 | 0.030918 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | ORDNCE 2 | 0.95281 | 0.92179 | -0.031014 |  | 0.93 | 1.05 | 0.073312 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | ORDNCE 2 | 0.95281 | 0.92179 | -0.031014 |  | 0.93 | 1.05 | 0.076355 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | ORDNCE 2 | 0.95281 | 0.92179 | -0.031014 |  | 0.93 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | ORDNCE 2 | 0.95281 | 0.92179 | -0.031014 |  | 0.93 | 1.05 | 0.037529 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | ORDNCE 2 | 0.95281 | 0.92179 | -0.031014 |  | 0.93 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | ORDNCE 2 | 0.95281 | 0.92179 | -0.031014 |  | 0.93 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | ORDNCE 2 | 0.95281 | 0.92179 | -0.031014 |  | 0.93 | 1.05 | 0.030301 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | ORDNCE 2 | 0.95281 | 0.92179 | -0.031014 |  | 0.93 | 1.05 | 0.041779 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | ORDNCE 2 | 0.95281 | 0.92179 | -0.031014 |  | 0.93 | 1.05 | 0.079587 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | ORDNCE 2 | 0.9572 | 0.9263 | -0.030901 |  | 0.93 | 1.05 | 0.03716 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | ORDNCE 2 | 0.9572 | 0.9263 | -0.030901 |  | 0.93 | 1.05 | 0.030931 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | ORDNCE 2 | 0.9572 | 0.9263 | -0.030901 |  | 0.93 | 1.05 | 0.044459 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | ORDNCE 2 | 0.9572 | 0.9263 | -0.030901 |  | 0.93 | 1.05 | 0.041648 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | ORDNCE 2 | 0.9572 | 0.9263 | -0.030901 |  | 0.93 | 1.05 | 0.031986 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | ORDNCE 2 | 0.9572 | 0.9263 | -0.030901 |  | 0.93 | 1.05 | 0.039776 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | ORDNCE 2 | 0.9572 | 0.9263 | -0.030901 |  | 0.93 | 1.05 | 0.042349 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | ORDNCE 2 | 0.9572 | 0.9263 | -0.030901 |  | 0.93 | 1.05 | 0.041252 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | ORDNCE 2 | 0.9572 | 0.9263 | -0.030901 |  | 0.93 | 1.05 | 0.031238 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | ORDNCE 2 | 0.9572 | 0.9263 | -0.030901 |  | 0.93 | 1.05 | 0.034893 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | ORDNCE 2 | 0.9572 | 0.9263 | -0.030901 |  | 0.93 | 1.05 | 0.046335 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | ORDNCE 2 | 0.9572 | 0.9263 | -0.030901 |  | 0.93 | 1.05 | 0.034893 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | ORDNCE 2 | 0.9572 | 0.9263 | -0.030901 |  | 0.93 | 1.05 | 0.03611 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | ORDNCE 2 | 0.9572 | 0.9263 | -0.030901 |  | 0.93 | 1.05 | 0.034555 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | ORDNCE 2 | 0.9572 | 0.9263 | -0.030901 |  | 0.93 | 1.05 | 0.033454 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | ORDNCE 2 | 0.9572 | 0.9263 | -0.030901 |  | 0.93 | 1.05 | 0.045771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | ORDNCE 2 | 0.9572 | 0.9263 | -0.030901 |  | 0.93 | 1.05 | 0.031365 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | ORDNCE 2 | 0.9572 | 0.9263 | -0.030901 |  | 0.93 | 1.05 | 0.031365 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | ORDNCE 2 | 0.9572 | 0.9263 | -0.030901 |  | 0.93 | 1.05 | 0.041921 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | ORDNCE 2 | 0.9572 | 0.9263 | -0.030901 |  | 0.93 | 1.05 | 0.033154 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | ORDNCE 2 | 0.9572 | 0.9263 | -0.030901 |  | 0.93 | 1.05 | 0.03341 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | ORDNCE 2 | 0.9572 | 0.9263 | -0.030901 |  | 0.93 | 1.05 | 0.030334 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | ORDNCE 2 | 0.9572 | 0.9263 | -0.030901 |  | 0.93 | 1.05 | 0.034718 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | ORDNCE 2 | 0.9572 | 0.9263 | -0.030901 |  | 0.93 | 1.05 | 0.033533 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | ORDNCE 2 | 0.95438 | 0.92236 | -0.032023 |  | 0.93 | 1.05 | 0.038685 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | ORDNCE 2 | 0.95438 | 0.92236 | -0.032023 |  | 0.93 | 1.05 | 0.07469 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | ORDNCE 2 | 0.95438 | 0.92236 | -0.032023 |  | 0.93 | 1.05 | 0.068062 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | ORDNCE 2 | 0.95438 | 0.92236 | -0.032023 |  | 0.93 | 1.05 | 0.034938 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | ORDNCE 2 | 0.95438 | 0.92236 | -0.032023 |  | 0.93 | 1.05 | 0.032777 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | ORDNCE 2 | 0.95438 | 0.92236 | -0.032023 |  | 0.93 | 1.05 | 0.043475 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | ORDNCE 2 | 0.95438 | 0.92236 | -0.032023 |  | 0.93 | 1.05 | 0.13386 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | ORDNCE 2 | 0.95438 | 0.92236 | -0.032023 |  | 0.93 | 1.05 | 0.036067 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | ORDNCE 2 | 0.95438 | 0.92236 | -0.032023 |  | 0.93 | 1.05 | 0.036067 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | ORDNCE 2 | 0.95438 | 0.92236 | -0.032023 |  | 0.93 | 1.05 | 0.067572 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | ORDNCE 2 | 0.95438 | 0.92236 | -0.032023 |  | 0.93 | 1.05 | 0.033583 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | ORDNCE 2 | 0.95438 | 0.92236 | -0.032023 |  | 0.93 | 1.05 | 0.034115 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | ORDNJCT2 | 0.95361 | 0.92272 | -0.030898 |  | 0.93 | 1.05 | 0.10484 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | ORDNJCT2 | 0.95361 | 0.92272 | -0.030898 |  | 0.93 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | ORDNJCT2 | 0.95361 | 0.92272 | -0.030898 |  | 0.93 | 1.05 | 0.086823 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | ORDNJCT2 | 0.95361 | 0.92272 | -0.030898 |  | 0.93 | 1.05 | 0.098758 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | ORDNJCT2 | 0.95361 | 0.92272 | -0.030898 |  | 0.93 | 1.05 | 0.087817 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | ORDNJCT2 | 0.95361 | 0.92272 | -0.030898 |  | 0.93 | 1.05 | 0.11285 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | ORDNJCT2 | 0.95361 | 0.92272 | -0.030898 |  | 0.93 | 1.05 | 0.11586 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | ORDNJCT2 | 0.95361 | 0.92272 | -0.030898 |  | 0.93 | 1.05 | 0.10654 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | ORDNJCT2 | 0.95361 | 0.92272 | -0.030898 |  | 0.93 | 1.05 | 0.031666 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-219 | ORDNJCT2 | 0.95361 | 0.92272 | -0.030898 |  | 0.93 | 1.05 | 0.030863 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | ORDNJCT2 | 0.95361 | 0.92272 | -0.030898 |  | 0.93 | 1.05 | 0.099811 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | ORDNJCT2 | 0.95361 | 0.92272 | -0.030898 |  | 0.93 | 1.05 | 0.10896 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | ORDNJCT2 | 0.95361 | 0.92272 | -0.030898 |  | 0.93 | 1.05 | 0.040233 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | ORDNJCT2 | 0.95361 | 0.92272 | -0.030898 |  | 0.93 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | ORDNJCT2 | 0.95361 | 0.92272 | -0.030898 |  | 0.93 | 1.05 | 0.060046 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | ORDNJCT2 | 0.95361 | 0.92272 | -0.030898 |  | 0.93 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | ORDNJCT2 | 0.95361 | 0.92272 | -0.030898 |  | 0.93 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | ORDNJCT2 | 0.95361 | 0.92272 | -0.030898 |  | 0.93 | 1.05 | 0.032555 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | ORDNJCT2 | 0.95361 | 0.92272 | -0.030898 |  | 0.93 | 1.05 | 0.031413 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | ORDNJCT2 | 0.95361 | 0.92272 | -0.030898 |  | 0.93 | 1.05 | 0.046478 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | ORDNJCT2 | 0.95361 | 0.92272 | -0.030898 |  | 0.93 | 1.05 | 0.11534 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | ORDNJCT2 | 0.9567 | 0.92757 | -0.029129 |  | 0.93 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | ORDNJCT2 | 0.9567 | 0.92757 | -0.029129 |  | 0.93 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | ORDNJCT2 | 0.9567 | 0.92757 | -0.029129 |  | 0.93 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | ORDNJCT2 | 0.9567 | 0.92757 | -0.029129 |  | 0.93 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | ORDNJCT2 | 0.9567 | 0.92757 | -0.029129 |  | 0.93 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | ORDNJCT2 | 0.9567 | 0.92757 | -0.029129 |  | 0.93 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | ORDNJCT2 | 0.9567 | 0.92757 | -0.029129 |  | 0.93 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | ORDNJCT2 | 0.9567 | 0.92757 | -0.029129 |  | 0.93 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | ORDNJCT2 | 0.9567 | 0.92757 | -0.029129 |  | 0.93 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | ORDNJCT2 | 0.9567 | 0.92757 | -0.029129 |  | 0.93 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | ORDNJCT2 | 0.9567 | 0.92757 | -0.029129 |  | 0.93 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | ORDNJCT2 | 0.9567 | 0.92757 | -0.029129 |  | 0.93 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | ORDNJCT2 | 0.9567 | 0.92757 | -0.029129 |  | 0.93 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | ORDNJCT2 | 0.9567 | 0.92757 | -0.029129 |  | 0.93 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | ORDNJCT2 | 0.95311 | 0.92211 | -0.031003 |  | 0.93 | 1.05 | 0.076984 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | ORDNJCT2 | 0.95311 | 0.92211 | -0.031003 |  | 0.93 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | ORDNJCT2 | 0.95311 | 0.92211 | -0.031003 |  | 0.93 | 1.05 | 0.065662 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | ORDNJCT2 | 0.95311 | 0.92211 | -0.031003 |  | 0.93 | 1.05 | 0.072679 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | ORDNJCT2 | 0.95311 | 0.92211 | -0.031003 |  | 0.93 | 1.05 | 0.052268 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | ORDNJCT2 | 0.95311 | 0.92211 | -0.031003 |  | 0.93 | 1.05 | 0.080584 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | ORDNJCT2 | 0.95311 | 0.92211 | -0.031003 |  | 0.93 | 1.05 | 0.082253 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | ORDNJCT2 | 0.95311 | 0.92211 | -0.031003 |  | 0.93 | 1.05 | 0.076592 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | ORDNJCT2 | 0.95311 | 0.92211 | -0.031003 |  | 0.93 | 1.05 | 0.030918 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | ORDNJCT2 | 0.95311 | 0.92211 | -0.031003 |  | 0.93 | 1.05 | 0.073312 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | ORDNJCT2 | 0.95311 | 0.92211 | -0.031003 |  | 0.93 | 1.05 | 0.076355 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | ORDNJCT2 | 0.95311 | 0.92211 | -0.031003 |  | 0.93 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | ORDNJCT2 | 0.95311 | 0.92211 | -0.031003 |  | 0.93 | 1.05 | 0.037529 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | ORDNJCT2 | 0.95311 | 0.92211 | -0.031003 |  | 0.93 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | ORDNJCT2 | 0.95311 | 0.92211 | -0.031003 |  | 0.93 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | ORDNJCT2 | 0.95311 | 0.92211 | -0.031003 |  | 0.93 | 1.05 | 0.030301 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | ORDNJCT2 | 0.95311 | 0.92211 | -0.031003 |  | 0.93 | 1.05 | 0.041779 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | ORDNJCT2 | 0.95311 | 0.92211 | -0.031003 |  | 0.93 | 1.05 | 0.079587 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | ORDNJCT2 | 0.95751 | 0.92662 | -0.030891 |  | 0.93 | 1.05 | 0.03716 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | ORDNJCT2 | 0.95751 | 0.92662 | -0.030891 |  | 0.93 | 1.05 | 0.030931 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | ORDNJCT2 | 0.95751 | 0.92662 | -0.030891 |  | 0.93 | 1.05 | 0.044459 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | ORDNJCT2 | 0.95751 | 0.92662 | -0.030891 |  | 0.93 | 1.05 | 0.041648 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | ORDNJCT2 | 0.95751 | 0.92662 | -0.030891 |  | 0.93 | 1.05 | 0.031986 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | ORDNJCT2 | 0.95751 | 0.92662 | -0.030891 |  | 0.93 | 1.05 | 0.039776 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | ORDNJCT2 | 0.95751 | 0.92662 | -0.030891 |  | 0.93 | 1.05 | 0.042349 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | ORDNJCT2 | 0.95751 | 0.92662 | -0.030891 |  | 0.93 | 1.05 | 0.041252 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | ORDNJCT2 | 0.95751 | 0.92662 | -0.030891 |  | 0.93 | 1.05 | 0.031238 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | ORDNJCT2 | 0.95751 | 0.92662 | -0.030891 |  | 0.93 | 1.05 | 0.034893 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | ORDNJCT2 | 0.95751 | 0.92662 | -0.030891 |  | 0.93 | 1.05 | 0.046335 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | ORDNJCT2 | 0.95751 | 0.92662 | -0.030891 |  | 0.93 | 1.05 | 0.034893 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | ORDNJCT2 | 0.95751 | 0.92662 | -0.030891 |  | 0.93 | 1.05 | 0.03611 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | ORDNJCT2 | 0.95751 | 0.92662 | -0.030891 |  | 0.93 | 1.05 | 0.034555 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | ORDNJCT2 | 0.95751 | 0.92662 | -0.030891 |  | 0.93 | 1.05 | 0.033454 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | ORDNJCT2 | 0.95751 | 0.92662 | -0.030891 |  | 0.93 | 1.05 | 0.045771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | ORDNJCT2 | 0.95751 | 0.92662 | -0.030891 |  | 0.93 | 1.05 | 0.031365 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | ORDNJCT2 | 0.95751 | 0.92662 | -0.030891 |  | 0.93 | 1.05 | 0.031365 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | ORDNJCT2 | 0.95751 | 0.92662 | -0.030891 |  | 0.93 | 1.05 | 0.041921 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | ORDNJCT2 | 0.95751 | 0.92662 | -0.030891 |  | 0.93 | 1.05 | 0.033154 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | ORDNJCT2 | 0.95751 | 0.92662 | -0.030891 |  | 0.93 | 1.05 | 0.03341 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | ORDNJCT2 | 0.95751 | 0.92662 | -0.030891 |  | 0.93 | 1.05 | 0.030334 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | ORDNJCT2 | 0.95751 | 0.92662 | -0.030891 |  | 0.93 | 1.05 | 0.034718 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | ORDNJCT2 | 0.95751 | 0.92662 | -0.030891 |  | 0.93 | 1.05 | 0.033533 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | ORDNJCT2 | 0.95469 | 0.92268 | -0.032012 |  | 0.93 | 1.05 | 0.038685 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | ORDNJCT2 | 0.95469 | 0.92268 | -0.032012 |  | 0.93 | 1.05 | 0.07469 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | ORDNJCT2 | 0.95469 | 0.92268 | -0.032012 |  | 0.93 | 1.05 | 0.068062 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | ORDNJCT2 | 0.95469 | 0.92268 | -0.032012 |  | 0.93 | 1.05 | 0.034938 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | ORDNJCT2 | 0.95469 | 0.92268 | -0.032012 |  | 0.93 | 1.05 | 0.032777 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | ORDNJCT2 | 0.95469 | 0.92268 | -0.032012 |  | 0.93 | 1.05 | 0.043475 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | ORDNJCT2 | 0.95469 | 0.92268 | -0.032012 |  | 0.93 | 1.05 | 0.13386 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | ORDNJCT2 | 0.95469 | 0.92268 | -0.032012 |  | 0.93 | 1.05 | 0.036067 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | ORDNJCT2 | 0.95469 | 0.92268 | -0.032012 |  | 0.93 | 1.05 | 0.036067 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | ORDNJCT2 | 0.95469 | 0.92268 | -0.032012 |  | 0.93 | 1.05 | 0.067572 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | ORDNJCT2 | 0.95469 | 0.92268 | -0.032012 |  | 0.93 | 1.05 | 0.033583 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | ORDNJCT2 | 0.95469 | 0.92268 | -0.032012 |  | 0.93 | 1.05 | 0.034115 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | PRY-JCT2 | 0.94268 | 0.91433 | -0.02835 |  | 0.92 | 1.05 | 0.035206 | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | PRY-JCT2 | 0.94707 | 0.91957 | -0.027502 |  | 0.92 | 1.05 | 0.035206 | Single 509752 INOLATP4 138 510442 GUAVA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | PRY-JCT3 | 0.92609 | 0.89874 | -0.027347 |  | 0.92 | 1.05 | 0.035206 | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | PRY-JCT3 | 0.93084 | 0.90442 | -0.026421 |  | 0.92 | 1.05 | 0.035206 | Single 509752 INOLATP4 138 510442 GUAVA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | PRY-JCT4 | 0.91409 | 0.8849 | -0.029186 |  | 0.92 | 1.05 | 0.035206 | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | PRY-JCT4 | 0.91971 | 0.89162 | -0.028096 |  | 0.92 | 1.05 | 0.035206 | Single 509752 INOLATP4 138 510442 GUAVA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | PRY_CRK4 | 0.87872 | 0.84685 | -0.031866 |  | 0.92 | 1.05 | 0.035206 | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | PRY_CRK4 | 0.88694 | 0.85662 | -0.030322 |  | 0.92 | 1.05 | 0.035206 | Single 509752 INOLATP4 138 510442 GUAVA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | RNM393 5 | 0.96386 | 0.92279 | -0.041063 |  | 0.925 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | RNM393 5 | 0.96386 | 0.92279 | -0.041063 |  | 0.925 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | RNM393 5 | 0.96386 | 0.92279 | -0.041063 |  | 0.925 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | RNM393 5 | 0.96386 | 0.92279 | -0.041063 |  | 0.925 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | RNM393 5 | 0.96386 | 0.92279 | -0.041063 |  | 0.925 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | RNM393 5 | 0.96386 | 0.92279 | -0.041063 |  | 0.925 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | RNM393 5 | 0.96386 | 0.92279 | -0.041063 |  | 0.925 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | RNM393 5 | 0.96386 | 0.92279 | -0.041063 |  | 0.925 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | RNM393 5 | 0.96386 | 0.92279 | -0.041063 |  | 0.925 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | RNM393 5 | 0.96386 | 0.92279 | -0.041063 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | RNM393 5 | 0.96386 | 0.92279 | -0.041063 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | RNM393 5 | 0.96386 | 0.92279 | -0.041063 |  | 0.925 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | RNM393 5 | 0.96386 | 0.92279 | -0.041063 |  | 0.925 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | RNM393 5 | 0.96386 | 0.92279 | -0.041063 |  | 0.925 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | RNM393 5 | 0.96348 | 0.92376 | -0.039719 |  | 0.925 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | RNM393 5 | 0.96348 | 0.92376 | -0.039719 |  | 0.925 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | RNM393 5 | 0.96348 | 0.92376 | -0.039719 |  | 0.925 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | RNM393 5 | 0.96348 | 0.92376 | -0.039719 |  | 0.925 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | RNM393 5 | 0.96348 | 0.92376 | -0.039719 |  | 0.925 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | RNM393 5 | 0.96348 | 0.92376 | -0.039719 |  | 0.925 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | RNM393 5 | 0.96348 | 0.92376 | -0.039719 |  | 0.925 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | RNM393 5 | 0.96348 | 0.92376 | -0.039719 |  | 0.925 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | RNM393 5 | 0.96348 | 0.92376 | -0.039719 |  | 0.925 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | RNM393 5 | 0.96348 | 0.92376 | -0.039719 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | RNM393 5 | 0.96348 | 0.92376 | -0.039719 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | RNM393 5 | 0.96348 | 0.92376 | -0.039719 |  | 0.925 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | RNM393 5 | 0.96348 | 0.92376 | -0.039719 |  | 0.925 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | RNM393 5 | 0.96348 | 0.92376 | -0.039719 |  | 0.925 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | ROCKPT-4 | 0.79664 | 0.75959 | -0.037049 |  | 0.92 | 1.05 | 0.035206 | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | ROCKPT-4 | 0.80944 | 0.77474 | -0.034699 |  | 0.92 | 1.05 | 0.035206 | Single 509752 INOLATP4 138 510442 GUAVA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | SIBLEYRD2 | 0.96858 | 0.9174 | -0.051185 |  | 0.925 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | SIBLEYRD2 | 0.96858 | 0.9174 | -0.051185 |  | 0.925 | 1.05 | 0.0423 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | SIBLEYRD2 | 0.96858 | 0.9174 | -0.051185 |  | 0.925 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | SIBLEYRD2 | 0.96858 | 0.9174 | -0.051185 |  | 0.925 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | SIBLEYRD2 | 0.96858 | 0.9174 | -0.051185 |  | 0.925 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | SIBLEYRD2 | 0.96858 | 0.9174 | -0.051185 |  | 0.925 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | SIBLEYRD2 | 0.96858 | 0.9174 | -0.051185 |  | 0.925 | 1.05 | 0.044676 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | SIBLEYRD2 | 0.96858 | 0.9174 | -0.051185 |  | 0.925 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | SIBLEYRD2 | 0.96858 | 0.9174 | -0.051185 |  | 0.925 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | SIBLEYRD2 | 0.96858 | 0.9174 | -0.051185 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | SIBLEYRD2 | 0.96858 | 0.9174 | -0.051185 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | SIBLEYRD2 | 0.96858 | 0.9174 | -0.051185 |  | 0.925 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | SIBLEYRD2 | 0.96858 | 0.9174 | -0.051185 |  | 0.925 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | SIBLEYRD2 | 0.96858 | 0.9174 | -0.051185 |  | 0.925 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | SIBLEYRD2 | 0.96799 | 0.91428 | -0.053707 |  | 0.925 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | SIBLEYRD2 | 0.96799 | 0.91428 | -0.053707 |  | 0.925 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | SIBLEYRD2 | 0.96799 | 0.91428 | -0.053707 |  | 0.925 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | SIBLEYRD2 | 0.96799 | 0.91428 | -0.053707 |  | 0.925 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | SIBLEYRD2 | 0.96799 | 0.91428 | -0.053707 |  | 0.925 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | SIBLEYRD2 | 0.96799 | 0.91428 | -0.053707 |  | 0.925 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | SIBLEYRD2 | 0.96799 | 0.91428 | -0.053707 |  | 0.925 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | SIBLEYRD2 | 0.96799 | 0.91428 | -0.053707 |  | 0.925 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | SIBLEYRD2 | 0.96799 | 0.91428 | -0.053707 |  | 0.925 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | SIBLEYRD2 | 0.96799 | 0.91428 | -0.053707 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | SIBLEYRD2 | 0.96799 | 0.91428 | -0.053707 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | SIBLEYRD2 | 0.96799 | 0.91428 | -0.053707 |  | 0.925 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | SIBLEYRD2 | 0.96799 | 0.91428 | -0.053707 |  | 0.925 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | SIBLEYRD2 | 0.96799 | 0.91428 | -0.053707 |  | 0.925 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | SIBLEYRD2 | 0.97292 | 0.92076 | -0.05216 |  | 0.925 | 1.05 | 0.076984 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | SIBLEYRD2 | 0.97292 | 0.92076 | -0.05216 |  | 0.925 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | SIBLEYRD2 | 0.97292 | 0.92076 | -0.05216 |  | 0.925 | 1.05 | 0.065662 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | SIBLEYRD2 | 0.97292 | 0.92076 | -0.05216 |  | 0.925 | 1.05 | 0.072679 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | SIBLEYRD2 | 0.97292 | 0.92076 | -0.05216 |  | 0.925 | 1.05 | 0.052268 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | SIBLEYRD2 | 0.97292 | 0.92076 | -0.05216 |  | 0.925 | 1.05 | 0.080584 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | SIBLEYRD2 | 0.97292 | 0.92076 | -0.05216 |  | 0.925 | 1.05 | 0.082253 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | SIBLEYRD2 | 0.97292 | 0.92076 | -0.05216 |  | 0.925 | 1.05 | 0.076592 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | SIBLEYRD2 | 0.97292 | 0.92076 | -0.05216 |  | 0.925 | 1.05 | 0.030918 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | SIBLEYRD2 | 0.97292 | 0.92076 | -0.05216 |  | 0.925 | 1.05 | 0.073312 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | SIBLEYRD2 | 0.97292 | 0.92076 | -0.05216 |  | 0.925 | 1.05 | 0.076355 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | SIBLEYRD2 | 0.97292 | 0.92076 | -0.05216 |  | 0.925 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | SIBLEYRD2 | 0.97292 | 0.92076 | -0.05216 |  | 0.925 | 1.05 | 0.037529 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | SIBLEYRD2 | 0.97292 | 0.92076 | -0.05216 |  | 0.925 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | SIBLEYRD2 | 0.97292 | 0.92076 | -0.05216 |  | 0.925 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | SIBLEYRD2 | 0.97292 | 0.92076 | -0.05216 |  | 0.925 | 1.05 | 0.030301 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | SIBLEYRD2 | 0.97292 | 0.92076 | -0.05216 |  | 0.925 | 1.05 | 0.041779 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | SIBLEYRD2 | 0.97292 | 0.92076 | -0.05216 |  | 0.925 | 1.05 | 0.079587 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | SIBLEYRD2 | 0.97362 | 0.92159 | -0.052037 |  | 0.925 | 1.05 | 0.10484 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | SIBLEYRD2 | 0.97362 | 0.92159 | -0.052037 |  | 0.925 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | SIBLEYRD2 | 0.97362 | 0.92159 | -0.052037 |  | 0.925 | 1.05 | 0.086823 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | SIBLEYRD2 | 0.97362 | 0.92159 | -0.052037 |  | 0.925 | 1.05 | 0.098758 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | SIBLEYRD2 | 0.97362 | 0.92159 | -0.052037 |  | 0.925 | 1.05 | 0.087817 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | SIBLEYRD2 | 0.97362 | 0.92159 | -0.052037 |  | 0.925 | 1.05 | 0.11285 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | SIBLEYRD2 | 0.97362 | 0.92159 | -0.052037 |  | 0.925 | 1.05 | 0.11586 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | SIBLEYRD2 | 0.97362 | 0.92159 | -0.052037 |  | 0.925 | 1.05 | 0.10654 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | SIBLEYRD2 | 0.97362 | 0.92159 | -0.052037 |  | 0.925 | 1.05 | 0.031666 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-219 | SIBLEYRD2 | 0.97362 | 0.92159 | -0.052037 |  | 0.925 | 1.05 | 0.030863 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | SIBLEYRD2 | 0.97362 | 0.92159 | -0.052037 |  | 0.925 | 1.05 | 0.099811 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | SIBLEYRD2 | 0.97362 | 0.92159 | -0.052037 |  | 0.925 | 1.05 | 0.10896 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | SIBLEYRD2 | 0.97362 | 0.92159 | -0.052037 |  | 0.925 | 1.05 | 0.040233 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | SIBLEYRD2 | 0.97362 | 0.92159 | -0.052037 |  | 0.925 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | SIBLEYRD2 | 0.97362 | 0.92159 | -0.052037 |  | 0.925 | 1.05 | 0.060046 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | SIBLEYRD2 | 0.97362 | 0.92159 | -0.052037 |  | 0.925 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | SIBLEYRD2 | 0.97362 | 0.92159 | -0.052037 |  | 0.925 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | SIBLEYRD2 | 0.97362 | 0.92159 | -0.052037 |  | 0.925 | 1.05 | 0.032555 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | SIBLEYRD2 | 0.97362 | 0.92159 | -0.052037 |  | 0.925 | 1.05 | 0.031413 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | SIBLEYRD2 | 0.97362 | 0.92159 | -0.052037 |  | 0.925 | 1.05 | 0.046478 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | SIBLEYRD2 | 0.97362 | 0.92159 | -0.052037 |  | 0.925 | 1.05 | 0.11534 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | SIBLEYRD2 | 0.96767 | 0.9155 | -0.052177 |  | 0.925 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | SIBLEYRD2 | 0.96767 | 0.9155 | -0.052177 |  | 0.925 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | SIBLEYRD2 | 0.96767 | 0.9155 | -0.052177 |  | 0.925 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | SIBLEYRD2 | 0.96767 | 0.9155 | -0.052177 |  | 0.925 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | SIBLEYRD2 | 0.96767 | 0.9155 | -0.052177 |  | 0.925 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | SIBLEYRD2 | 0.96767 | 0.9155 | -0.052177 |  | 0.925 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | SIBLEYRD2 | 0.96767 | 0.9155 | -0.052177 |  | 0.925 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | SIBLEYRD2 | 0.96767 | 0.9155 | -0.052177 |  | 0.925 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | SIBLEYRD2 | 0.96767 | 0.9155 | -0.052177 |  | 0.925 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | SIBLEYRD2 | 0.96767 | 0.9155 | -0.052177 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | SIBLEYRD2 | 0.96767 | 0.9155 | -0.052177 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | SIBLEYRD2 | 0.96767 | 0.9155 | -0.052177 |  | 0.925 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | SIBLEYRD2 | 0.96767 | 0.9155 | -0.052177 |  | 0.925 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | SIBLEYRD2 | 0.96767 | 0.9155 | -0.052177 |  | 0.925 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | SIBLEYRD5 | 0.96949 | 0.91847 | -0.051024 |  | 0.925 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | SIBLEYRD5 | 0.96949 | 0.91847 | -0.051024 |  | 0.925 | 1.05 | 0.0423 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | SIBLEYRD5 | 0.96949 | 0.91847 | -0.051024 |  | 0.925 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | SIBLEYRD5 | 0.96949 | 0.91847 | -0.051024 |  | 0.925 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | SIBLEYRD5 | 0.96949 | 0.91847 | -0.051024 |  | 0.925 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | SIBLEYRD5 | 0.96949 | 0.91847 | -0.051024 |  | 0.925 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | SIBLEYRD5 | 0.96949 | 0.91847 | -0.051024 |  | 0.925 | 1.05 | 0.044676 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | SIBLEYRD5 | 0.96949 | 0.91847 | -0.051024 |  | 0.925 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | SIBLEYRD5 | 0.96949 | 0.91847 | -0.051024 |  | 0.925 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | SIBLEYRD5 | 0.96949 | 0.91847 | -0.051024 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | SIBLEYRD5 | 0.96949 | 0.91847 | -0.051024 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | SIBLEYRD5 | 0.96949 | 0.91847 | -0.051024 |  | 0.925 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | SIBLEYRD5 | 0.96949 | 0.91847 | -0.051024 |  | 0.925 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | SIBLEYRD5 | 0.96949 | 0.91847 | -0.051024 |  | 0.925 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | SIBLEYRD5 | 0.9689 | 0.91536 | -0.053537 |  | 0.925 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | SIBLEYRD5 | 0.9689 | 0.91536 | -0.053537 |  | 0.925 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | SIBLEYRD5 | 0.9689 | 0.91536 | -0.053537 |  | 0.925 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | SIBLEYRD5 | 0.9689 | 0.91536 | -0.053537 |  | 0.925 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | SIBLEYRD5 | 0.9689 | 0.91536 | -0.053537 |  | 0.925 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | SIBLEYRD5 | 0.9689 | 0.91536 | -0.053537 |  | 0.925 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | SIBLEYRD5 | 0.9689 | 0.91536 | -0.053537 |  | 0.925 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | SIBLEYRD5 | 0.9689 | 0.91536 | -0.053537 |  | 0.925 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | SIBLEYRD5 | 0.9689 | 0.91536 | -0.053537 |  | 0.925 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | SIBLEYRD5 | 0.9689 | 0.91536 | -0.053537 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | SIBLEYRD5 | 0.9689 | 0.91536 | -0.053537 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | SIBLEYRD5 | 0.9689 | 0.91536 | -0.053537 |  | 0.925 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | SIBLEYRD5 | 0.9689 | 0.91536 | -0.053537 |  | 0.925 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | SIBLEYRD5 | 0.9689 | 0.91536 | -0.053537 |  | 0.925 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | SIBLEYRD5 | 0.97381 | 0.92182 | -0.051999 |  | 0.925 | 1.05 | 0.076984 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | SIBLEYRD5 | 0.97381 | 0.92182 | -0.051999 |  | 0.925 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | SIBLEYRD5 | 0.97381 | 0.92182 | -0.051999 |  | 0.925 | 1.05 | 0.065662 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | SIBLEYRD5 | 0.97381 | 0.92182 | -0.051999 |  | 0.925 | 1.05 | 0.072679 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | SIBLEYRD5 | 0.97381 | 0.92182 | -0.051999 |  | 0.925 | 1.05 | 0.052268 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | SIBLEYRD5 | 0.97381 | 0.92182 | -0.051999 |  | 0.925 | 1.05 | 0.080584 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | SIBLEYRD5 | 0.97381 | 0.92182 | -0.051999 |  | 0.925 | 1.05 | 0.082253 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | SIBLEYRD5 | 0.97381 | 0.92182 | -0.051999 |  | 0.925 | 1.05 | 0.076592 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | SIBLEYRD5 | 0.97381 | 0.92182 | -0.051999 |  | 0.925 | 1.05 | 0.030918 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | SIBLEYRD5 | 0.97381 | 0.92182 | -0.051999 |  | 0.925 | 1.05 | 0.073312 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | SIBLEYRD5 | 0.97381 | 0.92182 | -0.051999 |  | 0.925 | 1.05 | 0.076355 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | SIBLEYRD5 | 0.97381 | 0.92182 | -0.051999 |  | 0.925 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | SIBLEYRD5 | 0.97381 | 0.92182 | -0.051999 |  | 0.925 | 1.05 | 0.037529 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | SIBLEYRD5 | 0.97381 | 0.92182 | -0.051999 |  | 0.925 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | SIBLEYRD5 | 0.97381 | 0.92182 | -0.051999 |  | 0.925 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | SIBLEYRD5 | 0.97381 | 0.92182 | -0.051999 |  | 0.925 | 1.05 | 0.030301 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | SIBLEYRD5 | 0.97381 | 0.92182 | -0.051999 |  | 0.925 | 1.05 | 0.041779 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | SIBLEYRD5 | 0.97381 | 0.92182 | -0.051999 |  | 0.925 | 1.05 | 0.079587 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 11 MVAR switched shunt at DAD368 5 161 kV; Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | SIBLEYRD5 | 0.97452 | 0.92264 | -0.051877 |  | 0.925 | 1.05 | 0.10484 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | SIBLEYRD5 | 0.97452 | 0.92264 | -0.051877 |  | 0.925 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | SIBLEYRD5 | 0.97452 | 0.92264 | -0.051877 |  | 0.925 | 1.05 | 0.086823 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | SIBLEYRD5 | 0.97452 | 0.92264 | -0.051877 |  | 0.925 | 1.05 | 0.098758 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | SIBLEYRD5 | 0.97452 | 0.92264 | -0.051877 |  | 0.925 | 1.05 | 0.087817 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | SIBLEYRD5 | 0.97452 | 0.92264 | -0.051877 |  | 0.925 | 1.05 | 0.11285 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | SIBLEYRD5 | 0.97452 | 0.92264 | -0.051877 |  | 0.925 | 1.05 | 0.11586 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | SIBLEYRD5 | 0.97452 | 0.92264 | -0.051877 |  | 0.925 | 1.05 | 0.10654 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | SIBLEYRD5 | 0.97452 | 0.92264 | -0.051877 |  | 0.925 | 1.05 | 0.031666 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-219 | SIBLEYRD5 | 0.97452 | 0.92264 | -0.051877 |  | 0.925 | 1.05 | 0.030863 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | SIBLEYRD5 | 0.97452 | 0.92264 | -0.051877 |  | 0.925 | 1.05 | 0.099811 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | SIBLEYRD5 | 0.97452 | 0.92264 | -0.051877 |  | 0.925 | 1.05 | 0.10896 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | SIBLEYRD5 | 0.97452 | 0.92264 | -0.051877 |  | 0.925 | 1.05 | 0.040233 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | SIBLEYRD5 | 0.97452 | 0.92264 | -0.051877 |  | 0.925 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | SIBLEYRD5 | 0.97452 | 0.92264 | -0.051877 |  | 0.925 | 1.05 | 0.060046 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | SIBLEYRD5 | 0.97452 | 0.92264 | -0.051877 |  | 0.925 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | SIBLEYRD5 | 0.97452 | 0.92264 | -0.051877 |  | 0.925 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | SIBLEYRD5 | 0.97452 | 0.92264 | -0.051877 |  | 0.925 | 1.05 | 0.032555 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | SIBLEYRD5 | 0.97452 | 0.92264 | -0.051877 |  | 0.925 | 1.05 | 0.031413 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | SIBLEYRD5 | 0.97452 | 0.92264 | -0.051877 |  | 0.925 | 1.05 | 0.046478 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | SIBLEYRD5 | 0.97452 | 0.92264 | -0.051877 |  | 0.925 | 1.05 | 0.11534 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | SIBLEYRD5 | 0.96858 | 0.91657 | -0.052012 |  | 0.925 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | SIBLEYRD5 | 0.96858 | 0.91657 | -0.052012 |  | 0.925 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | SIBLEYRD5 | 0.96858 | 0.91657 | -0.052012 |  | 0.925 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | SIBLEYRD5 | 0.96858 | 0.91657 | -0.052012 |  | 0.925 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | SIBLEYRD5 | 0.96858 | 0.91657 | -0.052012 |  | 0.925 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | SIBLEYRD5 | 0.96858 | 0.91657 | -0.052012 |  | 0.925 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | SIBLEYRD5 | 0.96858 | 0.91657 | -0.052012 |  | 0.925 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | SIBLEYRD5 | 0.96858 | 0.91657 | -0.052012 |  | 0.925 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | SIBLEYRD5 | 0.96858 | 0.91657 | -0.052012 |  | 0.925 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | SIBLEYRD5 | 0.96858 | 0.91657 | -0.052012 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | SIBLEYRD5 | 0.96858 | 0.91657 | -0.052012 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | SIBLEYRD5 | 0.96858 | 0.91657 | -0.052012 |  | 0.925 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | SIBLEYRD5 | 0.96858 | 0.91657 | -0.052012 |  | 0.925 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | SIBLEYRD5 | 0.96858 | 0.91657 | -0.052012 |  | 0.925 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:6_3::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | STILWEL7 | 0.9579 | 0.93667 | -0.021225 |  | 0.95 | 1.05 | 0.031932 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | STILWEL7 | 0.9579 | 0.93667 | -0.021225 |  | 0.95 | 1.05 | 0.046406 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | STILWEL7 | 0.9579 | 0.93667 | -0.021225 |  | 0.95 | 1.05 | 0.034669 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | STILWEL7 | 0.9579 | 0.93667 | -0.021225 |  | 0.95 | 1.05 | 0.036297 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | STILWEL7 | 0.9579 | 0.93667 | -0.021225 |  | 0.95 | 1.05 | 0.03404 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | STILWEL7 | 0.9579 | 0.93667 | -0.021225 |  | 0.95 | 1.05 | 0.054677 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | STILWEL7 | 0.9579 | 0.93667 | -0.021225 |  | 0.95 | 1.05 | 0.036731 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | STILWEL7 | 0.9579 | 0.93667 | -0.021225 |  | 0.95 | 1.05 | 0.035653 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | SWISVAL6 | 0.96299 | 0.93974 | -0.023251 |  | 0.95 | 1.05 | 0.031932 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | SWISVAL6 | 0.96299 | 0.93974 | -0.023251 |  | 0.95 | 1.05 | 0.046406 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | SWISVAL6 | 0.96299 | 0.93974 | -0.023251 |  | 0.95 | 1.05 | 0.034669 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | SWISVAL6 | 0.96299 | 0.93974 | -0.023251 |  | 0.95 | 1.05 | 0.036297 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | SWISVAL6 | 0.96299 | 0.93974 | -0.023251 |  | 0.95 | 1.05 | 0.03404 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | SWISVAL6 | 0.96299 | 0.93974 | -0.023251 |  | 0.95 | 1.05 | 0.054677 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | SWISVAL6 | 0.96299 | 0.93974 | -0.023251 |  | 0.95 | 1.05 | 0.036731 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | SWISVAL6 | 0.96299 | 0.93974 | -0.023251 |  | 0.95 | 1.05 | 0.035653 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | SWISVAL6 | 0.96531 | 0.94211 | -0.023201 |  | 0.95 | 1.05 | 0.031932 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | SWISVAL6 | 0.96531 | 0.94211 | -0.023201 |  | 0.95 | 1.05 | 0.046406 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | SWISVAL6 | 0.96531 | 0.94211 | -0.023201 |  | 0.95 | 1.05 | 0.034669 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | SWISVAL6 | 0.96531 | 0.94211 | -0.023201 |  | 0.95 | 1.05 | 0.036297 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | SWISVAL6 | 0.96531 | 0.94211 | -0.023201 |  | 0.95 | 1.05 | 0.03404 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | SWISVAL6 | 0.96531 | 0.94211 | -0.023201 |  | 0.95 | 1.05 | 0.054677 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | SWISVAL6 | 0.96531 | 0.94211 | -0.023201 |  | 0.95 | 1.05 | 0.036731 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | SWISVAL6 | 0.96531 | 0.94211 | -0.023201 |  | 0.95 | 1.05 | 0.035653 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | SWISVAL6 | 0.9686 | 0.94849 | -0.020115 |  | 0.95 | 1.05 | 0.037599 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.09 MVAR switched shunt at SWISVAL6 230 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | SWISVAL6 | 0.9686 | 0.94849 | -0.020115 |  | 0.95 | 1.05 | 0.032501 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.09 MVAR switched shunt at SWISVAL6 230 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | SWISVAL6 | 0.9686 | 0.94849 | -0.020115 |  | 0.95 | 1.05 | 0.033287 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.09 MVAR switched shunt at SWISVAL6 230 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | SWISVAL6 | 0.9686 | 0.94849 | -0.020115 |  | 0.95 | 1.05 | 0.036459 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.09 MVAR switched shunt at SWISVAL6 230 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | SWISVAL6 | 0.9686 | 0.94849 | -0.020115 |  | 0.95 | 1.05 | 0.033711 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.09 MVAR switched shunt at SWISVAL6 230 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | SWISVAL6 | 0.9686 | 0.94849 | -0.020115 |  | 0.95 | 1.05 | 0.033711 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.09 MVAR switched shunt at SWISVAL6 230 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | SWISVAL6 | 0.9686 | 0.94849 | -0.020115 |  | 0.95 | 1.05 | 0.034436 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.09 MVAR switched shunt at SWISVAL6 230 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | SWISVAL6 | 0.9686 | 0.94849 | -0.020115 |  | 0.95 | 1.05 | 0.034899 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.09 MVAR switched shunt at SWISVAL6 230 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | SWISVAL6 | 0.9686 | 0.94849 | -0.020115 |  | 0.95 | 1.05 | 0.032952 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.09 MVAR switched shunt at SWISVAL6 230 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | SWISVAL6 | 0.9686 | 0.94849 | -0.020115 |  | 0.95 | 1.05 | 0.030781 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.09 MVAR switched shunt at SWISVAL6 230 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | SWISVAL6 | 0.9686 | 0.94849 | -0.020115 |  | 0.95 | 1.05 | 0.03181 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.09 MVAR switched shunt at SWISVAL6 230 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | SWISVAL6 | 0.9686 | 0.94849 | -0.020115 |  | 0.95 | 1.05 | 0.032399 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | Add 0.09 MVAR switched shunt at SWISVAL6 230 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | SWISVAL6 | 0.96774 | 0.94838 | -0.019358 |  | 0.95 | 1.05 | 0.037599 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | SWISVAL6 | 0.96774 | 0.94838 | -0.019358 |  | 0.95 | 1.05 | 0.032501 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | SWISVAL6 | 0.96774 | 0.94838 | -0.019358 |  | 0.95 | 1.05 | 0.033287 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | SWISVAL6 | 0.96774 | 0.94838 | -0.019358 |  | 0.95 | 1.05 | 0.036459 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | SWISVAL6 | 0.96774 | 0.94838 | -0.019358 |  | 0.95 | 1.05 | 0.033711 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | SWISVAL6 | 0.96774 | 0.94838 | -0.019358 |  | 0.95 | 1.05 | 0.033711 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | SWISVAL6 | 0.96774 | 0.94838 | -0.019358 |  | 0.95 | 1.05 | 0.034436 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | SWISVAL6 | 0.96774 | 0.94838 | -0.019358 |  | 0.95 | 1.05 | 0.034899 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | SWISVAL6 | 0.96774 | 0.94838 | -0.019358 |  | 0.95 | 1.05 | 0.032952 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | SWISVAL6 | 0.96774 | 0.94838 | -0.019358 |  | 0.95 | 1.05 | 0.030781 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | SWISVAL6 | 0.96774 | 0.94838 | -0.019358 |  | 0.95 | 1.05 | 0.03181 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | SWISVAL6 | 0.96774 | 0.94838 | -0.019358 |  | 0.95 | 1.05 | 0.032399 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | SWISVAL6 | 0.96047 | 0.94049 | -0.019982 |  | 0.95 | 1.05 | 0.037599 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | SWISVAL6 | 0.96047 | 0.94049 | -0.019982 |  | 0.95 | 1.05 | 0.03567 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | SWISVAL6 | 0.96047 | 0.94049 | -0.019982 |  | 0.95 | 1.05 | 0.032501 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | SWISVAL6 | 0.96047 | 0.94049 | -0.019982 |  | 0.95 | 1.05 | 0.033287 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | SWISVAL6 | 0.96047 | 0.94049 | -0.019982 |  | 0.95 | 1.05 | 0.036459 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | SWISVAL6 | 0.96047 | 0.94049 | -0.019982 |  | 0.95 | 1.05 | 0.033711 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | SWISVAL6 | 0.96047 | 0.94049 | -0.019982 |  | 0.95 | 1.05 | 0.042545 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | SWISVAL6 | 0.96047 | 0.94049 | -0.019982 |  | 0.95 | 1.05 | 0.033711 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | SWISVAL6 | 0.96047 | 0.94049 | -0.019982 |  | 0.95 | 1.05 | 0.034436 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | SWISVAL6 | 0.96047 | 0.94049 | -0.019982 |  | 0.95 | 1.05 | 0.034899 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | SWISVAL6 | 0.96047 | 0.94049 | -0.019982 |  | 0.95 | 1.05 | 0.032952 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | SWISVAL6 | 0.96047 | 0.94049 | -0.019982 |  | 0.95 | 1.05 | 0.030781 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | SWISVAL6 | 0.96047 | 0.94049 | -0.019982 |  | 0.95 | 1.05 | 0.03181 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | SWISVAL6 | 0.96047 | 0.94049 | -0.019982 |  | 0.95 | 1.05 | 0.032399 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | SWISVAL7 | 0.96356 | 0.93503 | -0.028537 |  | 0.95 | 1.05 | 0.031932 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | SWISVAL7 | 0.96356 | 0.93503 | -0.028537 |  | 0.95 | 1.05 | 0.046406 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | SWISVAL7 | 0.96356 | 0.93503 | -0.028537 |  | 0.95 | 1.05 | 0.034669 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | SWISVAL7 | 0.96356 | 0.93503 | -0.028537 |  | 0.95 | 1.05 | 0.036297 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | SWISVAL7 | 0.96356 | 0.93503 | -0.028537 |  | 0.95 | 1.05 | 0.03404 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | SWISVAL7 | 0.96356 | 0.93503 | -0.028537 |  | 0.95 | 1.05 | 0.054677 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | SWISVAL7 | 0.96356 | 0.93503 | -0.028537 |  | 0.95 | 1.05 | 0.036731 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | SWISVAL7 | 0.96356 | 0.93503 | -0.028537 |  | 0.95 | 1.05 | 0.035653 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | SWISVAL7 | 0.96754 | 0.93809 | -0.029457 |  | 0.95 | 1.05 | 0.031932 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | SWISVAL7 | 0.96754 | 0.93809 | -0.029457 |  | 0.95 | 1.05 | 0.046406 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | SWISVAL7 | 0.96754 | 0.93809 | -0.029457 |  | 0.95 | 1.05 | 0.034669 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | SWISVAL7 | 0.96754 | 0.93809 | -0.029457 |  | 0.95 | 1.05 | 0.036297 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | SWISVAL7 | 0.96754 | 0.93809 | -0.029457 |  | 0.95 | 1.05 | 0.03404 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | SWISVAL7 | 0.96754 | 0.93809 | -0.029457 |  | 0.95 | 1.05 | 0.054677 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | SWISVAL7 | 0.96754 | 0.93809 | -0.029457 |  | 0.95 | 1.05 | 0.036731 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | SWISVAL7 | 0.96754 | 0.93809 | -0.029457 |  | 0.95 | 1.05 | 0.035653 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | SWISVAL7 | 0.96421 | 0.94004 | -0.024173 |  | 0.95 | 1.05 | 0.031932 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | SWISVAL7 | 0.96421 | 0.94004 | -0.024173 |  | 0.95 | 1.05 | 0.046406 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | SWISVAL7 | 0.96421 | 0.94004 | -0.024173 |  | 0.95 | 1.05 | 0.034669 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | SWISVAL7 | 0.96421 | 0.94004 | -0.024173 |  | 0.95 | 1.05 | 0.036297 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | SWISVAL7 | 0.96421 | 0.94004 | -0.024173 |  | 0.95 | 1.05 | 0.03404 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | SWISVAL7 | 0.96421 | 0.94004 | -0.024173 |  | 0.95 | 1.05 | 0.054677 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | SWISVAL7 | 0.96421 | 0.94004 | -0.024173 |  | 0.95 | 1.05 | 0.036731 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | SWISVAL7 | 0.96421 | 0.94004 | -0.024173 |  | 0.95 | 1.05 | 0.035653 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | SWISVAL7 | 0.96464 | 0.94063 | -0.024008 |  | 0.95 | 1.05 | 0.031932 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | SWISVAL7 | 0.96464 | 0.94063 | -0.024008 |  | 0.95 | 1.05 | 0.046406 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | SWISVAL7 | 0.96464 | 0.94063 | -0.024008 |  | 0.95 | 1.05 | 0.034669 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | SWISVAL7 | 0.96464 | 0.94063 | -0.024008 |  | 0.95 | 1.05 | 0.036297 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | SWISVAL7 | 0.96464 | 0.94063 | -0.024008 |  | 0.95 | 1.05 | 0.03404 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | SWISVAL7 | 0.96464 | 0.94063 | -0.024008 |  | 0.95 | 1.05 | 0.054677 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | SWISVAL7 | 0.96464 | 0.94063 | -0.024008 |  | 0.95 | 1.05 | 0.036731 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | SWISVAL7 | 0.96464 | 0.94063 | -0.024008 |  | 0.95 | 1.05 | 0.035653 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | SWISVAL7 | 0.96195 | 0.93595 | -0.026 |  | 0.95 | 1.05 | 0.037599 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | SWISVAL7 | 0.96195 | 0.93595 | -0.026 |  | 0.95 | 1.05 | 0.03567 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | SWISVAL7 | 0.96195 | 0.93595 | -0.026 |  | 0.95 | 1.05 | 0.032501 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | SWISVAL7 | 0.96195 | 0.93595 | -0.026 |  | 0.95 | 1.05 | 0.033287 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | SWISVAL7 | 0.96195 | 0.93595 | -0.026 |  | 0.95 | 1.05 | 0.036459 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | SWISVAL7 | 0.96195 | 0.93595 | -0.026 |  | 0.95 | 1.05 | 0.033711 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | SWISVAL7 | 0.96195 | 0.93595 | -0.026 |  | 0.95 | 1.05 | 0.042545 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | SWISVAL7 | 0.96195 | 0.93595 | -0.026 |  | 0.95 | 1.05 | 0.033711 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | SWISVAL7 | 0.96195 | 0.93595 | -0.026 |  | 0.95 | 1.05 | 0.034436 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | SWISVAL7 | 0.96195 | 0.93595 | -0.026 |  | 0.95 | 1.05 | 0.034899 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | SWISVAL7 | 0.96195 | 0.93595 | -0.026 |  | 0.95 | 1.05 | 0.032952 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | SWISVAL7 | 0.96195 | 0.93595 | -0.026 |  | 0.95 | 1.05 | 0.030781 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | SWISVAL7 | 0.96195 | 0.93595 | -0.026 |  | 0.95 | 1.05 | 0.03181 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | SWISVAL7 | 0.96195 | 0.93595 | -0.026 |  | 0.95 | 1.05 | 0.032399 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | TIP292 5 | 0.96534 | 0.92487 | -0.040473 |  | 0.925 | 1.05 | 0.038685 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | TIP292 5 | 0.96534 | 0.92487 | -0.040473 |  | 0.925 | 1.05 | 0.069714 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | TIP292 5 | 0.96534 | 0.92487 | -0.040473 |  | 0.925 | 1.05 | 0.07469 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | TIP292 5 | 0.96534 | 0.92487 | -0.040473 |  | 0.925 | 1.05 | 0.068062 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | TIP292 5 | 0.96534 | 0.92487 | -0.040473 |  | 0.925 | 1.05 | 0.034938 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | TIP292 5 | 0.96534 | 0.92487 | -0.040473 |  | 0.925 | 1.05 | 0.032777 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | TIP292 5 | 0.96534 | 0.92487 | -0.040473 |  | 0.925 | 1.05 | 0.11363 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | TIP292 5 | 0.96534 | 0.92487 | -0.040473 |  | 0.925 | 1.05 | 0.043475 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | TIP292 5 | 0.96534 | 0.92487 | -0.040473 |  | 0.925 | 1.05 | 0.13386 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | TIP292 5 | 0.96534 | 0.92487 | -0.040473 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | TIP292 5 | 0.96534 | 0.92487 | -0.040473 |  | 0.925 | 1.05 | 0.036067 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | TIP292 5 | 0.96534 | 0.92487 | -0.040473 |  | 0.925 | 1.05 | 0.067572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | TIP292 5 | 0.96534 | 0.92487 | -0.040473 |  | 0.925 | 1.05 | 0.033583 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | TIP292 5 | 0.96534 | 0.92487 | -0.040473 |  | 0.925 | 1.05 | 0.034115 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | TV1MNDV4 | 0.95966 | 0.92608 | -0.033577 |  | 0.93 | 1.05 | 0.090803 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | TV1MNDV4 | 0.95966 | 0.92608 | -0.033577 |  | 0.93 | 1.05 | 0.030422 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | TV1MNDV4 | 0.95966 | 0.92608 | -0.033577 |  | 0.93 | 1.05 | 0.040015 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | TV1MNDV4 | 0.95966 | 0.92608 | -0.033577 |  | 0.93 | 1.05 | 0.056985 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | TV1MNDV4 | 0.95966 | 0.92608 | -0.033577 |  | 0.93 | 1.05 | 0.053029 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | TV1MNDV4 | 0.95966 | 0.92608 | -0.033577 |  | 0.93 | 1.05 | 0.040244 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-219 | TV1MNDV4 | 0.95966 | 0.92608 | -0.033577 |  | 0.93 | 1.05 | 0.044635 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | TV1MNDV4 | 0.95966 | 0.92608 | -0.033577 |  | 0.93 | 1.05 | 0.12486 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | TV1MNDV4 | 0.95966 | 0.92608 | -0.033577 |  | 0.93 | 1.05 | 0.044133 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | TV1MNDV4 | 0.95966 | 0.92608 | -0.033577 |  | 0.93 | 1.05 | 0.056119 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | TV1MNDV4 | 0.95966 | 0.92608 | -0.033577 |  | 0.93 | 1.05 | 0.056119 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | TV1MNDV4 | 0.95966 | 0.92608 | -0.033577 |  | 0.93 | 1.05 | 0.056496 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | TV1MNDV4 | 0.95966 | 0.92608 | -0.033577 |  | 0.93 | 1.05 | 0.073384 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | TV1MNDV4 | 0.95966 | 0.92608 | -0.033577 |  | 0.93 | 1.05 | 0.035942 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | TV1MNDV4 | 0.95966 | 0.92608 | -0.033577 |  | 0.93 | 1.05 | 0.03343 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | TV1MNDV4 | 0.95966 | 0.92608 | -0.033577 |  | 0.93 | 1.05 | 0.038724 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | TV1MNDV4 | 0.95966 | 0.92608 | -0.033577 |  | 0.93 | 1.05 | 0.038724 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | TV1MNDV4 | 0.95966 | 0.92608 | -0.033577 |  | 0.93 | 1.05 | 0.046894 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | TV1MNDV4 | 0.95966 | 0.92608 | -0.033577 |  | 0.93 | 1.05 | 0.056872 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | TV1MNDV4 | 0.95966 | 0.92608 | -0.033577 |  | 0.93 | 1.05 | 0.039954 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | TV1MNDV4 | 0.95966 | 0.92608 | -0.033577 |  | 0.93 | 1.05 | 0.054164 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | TV1MNDV4 | 0.95966 | 0.92608 | -0.033577 |  | 0.93 | 1.05 | 0.048427 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | TV1MNDV4 | 0.95966 | 0.92608 | -0.033577 |  | 0.93 | 1.05 | 0.062555 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | TV1MNDV4 | 0.95966 | 0.92608 | -0.033577 |  | 0.93 | 1.05 | 0.05027 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | TV1MNDV4 | 0.95966 | 0.92608 | -0.033577 |  | 0.93 | 1.05 | 0.034642 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | TV1MNDV4 | 0.96017 | 0.92972 | -0.030445 |  | 0.93 | 1.05 | 0.039244 | P51:25:WERE:WOLFCRK7:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | TV1MNDV4 | 0.96017 | 0.92972 | -0.030445 |  | 0.93 | 1.05 | 0.036827 | P51:25:WERE:WOLFCRK7:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | TV1MNDV4 | 0.96017 | 0.92972 | -0.030445 |  | 0.93 | 1.05 | 0.030156 | P51:25:WERE:WOLFCRK7:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-120 | TV1MNDV4 | 0.96017 | 0.92972 | -0.030445 |  | 0.93 | 1.05 | 0.034146 | P51:25:WERE:WOLFCRK7:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-154 | TV1MNDV4 | 0.96017 | 0.92972 | -0.030445 |  | 0.93 | 1.05 | 0.034933 | P51:25:WERE:WOLFCRK7:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | TV1MNDV4 | 0.96017 | 0.92972 | -0.030445 |  | 0.93 | 1.05 | 0.038105 | P51:25:WERE:WOLFCRK7:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-239 | TV1MNDV4 | 0.96017 | 0.92972 | -0.030445 |  | 0.93 | 1.05 | 0.035356 | P51:25:WERE:WOLFCRK7:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | TV1MNDV4 | 0.96017 | 0.92972 | -0.030445 |  | 0.93 | 1.05 | 0.040988 | P51:25:WERE:WOLFCRK7:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-252 | TV1MNDV4 | 0.96017 | 0.92972 | -0.030445 |  | 0.93 | 1.05 | 0.035356 | P51:25:WERE:WOLFCRK7:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-254 | TV1MNDV4 | 0.96017 | 0.92972 | -0.030445 |  | 0.93 | 1.05 | 0.036081 | P51:25:WERE:WOLFCRK7:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-255 | TV1MNDV4 | 0.96017 | 0.92972 | -0.030445 |  | 0.93 | 1.05 | 0.036544 | P51:25:WERE:WOLFCRK7:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | TV1MNDV4 | 0.96017 | 0.92972 | -0.030445 |  | 0.93 | 1.05 | 0.038782 | P51:25:WERE:WOLFCRK7:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-333 | TV1MNDV4 | 0.96017 | 0.92972 | -0.030445 |  | 0.93 | 1.05 | 0.034598 | P51:25:WERE:WOLFCRK7:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | TV1MNDV4 | 0.96017 | 0.92972 | -0.030445 |  | 0.93 | 1.05 | 0.032427 | P51:25:WERE:WOLFCRK7:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | TV1MNDV4 | 0.96017 | 0.92972 | -0.030445 |  | 0.93 | 1.05 | 0.031223 | P51:25:WERE:WOLFCRK7:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | TV1MNDV4 | 0.96017 | 0.92972 | -0.030445 |  | 0.93 | 1.05 | 0.033455 | P51:25:WERE:WOLFCRK7:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-362 | TV1MNDV4 | 0.96017 | 0.92972 | -0.030445 |  | 0.93 | 1.05 | 0.034045 | P51:25:WERE:WOLFCRK7:EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | TV1MNDV4 | 0.96656 | 0.94558 | -0.020979 |  | 0.95 | 1.05 | 0.14495 | System Intact | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | TV1MNDV4 | 0.95826 | 0.92618 | -0.032083 |  | 0.93 | 1.05 | 0.10484 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | TV1MNDV4 | 0.95826 | 0.92618 | -0.032083 |  | 0.93 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | TV1MNDV4 | 0.95826 | 0.92618 | -0.032083 |  | 0.93 | 1.05 | 0.086823 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | TV1MNDV4 | 0.95826 | 0.92618 | -0.032083 |  | 0.93 | 1.05 | 0.098758 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | TV1MNDV4 | 0.95826 | 0.92618 | -0.032083 |  | 0.93 | 1.05 | 0.087817 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | TV1MNDV4 | 0.95826 | 0.92618 | -0.032083 |  | 0.93 | 1.05 | 0.11285 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | TV1MNDV4 | 0.95826 | 0.92618 | -0.032083 |  | 0.93 | 1.05 | 0.11586 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | TV1MNDV4 | 0.95826 | 0.92618 | -0.032083 |  | 0.93 | 1.05 | 0.10654 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | TV1MNDV4 | 0.95826 | 0.92618 | -0.032083 |  | 0.93 | 1.05 | 0.031666 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-219 | TV1MNDV4 | 0.95826 | 0.92618 | -0.032083 |  | 0.93 | 1.05 | 0.030863 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | TV1MNDV4 | 0.95826 | 0.92618 | -0.032083 |  | 0.93 | 1.05 | 0.099811 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | TV1MNDV4 | 0.95826 | 0.92618 | -0.032083 |  | 0.93 | 1.05 | 0.10896 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | TV1MNDV4 | 0.95826 | 0.92618 | -0.032083 |  | 0.93 | 1.05 | 0.040233 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | TV1MNDV4 | 0.95826 | 0.92618 | -0.032083 |  | 0.93 | 1.05 | 0.083313 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | TV1MNDV4 | 0.95826 | 0.92618 | -0.032083 |  | 0.93 | 1.05 | 0.060046 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | TV1MNDV4 | 0.95826 | 0.92618 | -0.032083 |  | 0.93 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | TV1MNDV4 | 0.95826 | 0.92618 | -0.032083 |  | 0.93 | 1.05 | 0.046197 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | TV1MNDV4 | 0.95826 | 0.92618 | -0.032083 |  | 0.93 | 1.05 | 0.032555 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-360 | TV1MNDV4 | 0.95826 | 0.92618 | -0.032083 |  | 0.93 | 1.05 | 0.031413 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | TV1MNDV4 | 0.95826 | 0.92618 | -0.032083 |  | 0.93 | 1.05 | 0.046478 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | TV1MNDV4 | 0.95826 | 0.92618 | -0.032083 |  | 0.93 | 1.05 | 0.11534 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 29WP | V | ASGI-2024-023 | TV1MNDV4 | 0.95801 | 0.92545 | -0.032565 |  | 0.93 | 1.05 | 0.076984 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-025 | TV1MNDV4 | 0.95801 | 0.92545 | -0.032565 |  | 0.93 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-068 | TV1MNDV4 | 0.95801 | 0.92545 | -0.032565 |  | 0.93 | 1.05 | 0.065662 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-071 | TV1MNDV4 | 0.95801 | 0.92545 | -0.032565 |  | 0.93 | 1.05 | 0.072679 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | TV1MNDV4 | 0.95801 | 0.92545 | -0.032565 |  | 0.93 | 1.05 | 0.052268 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-122 | TV1MNDV4 | 0.95801 | 0.92545 | -0.032565 |  | 0.93 | 1.05 | 0.080584 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-177 | TV1MNDV4 | 0.95801 | 0.92545 | -0.032565 |  | 0.93 | 1.05 | 0.082253 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-178 | TV1MNDV4 | 0.95801 | 0.92545 | -0.032565 |  | 0.93 | 1.05 | 0.076592 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-204 | TV1MNDV4 | 0.95801 | 0.92545 | -0.032565 |  | 0.93 | 1.05 | 0.030918 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-220 | TV1MNDV4 | 0.95801 | 0.92545 | -0.032565 |  | 0.93 | 1.05 | 0.073312 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-232 | TV1MNDV4 | 0.95801 | 0.92545 | -0.032565 |  | 0.93 | 1.05 | 0.076355 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-241 | TV1MNDV4 | 0.95801 | 0.92545 | -0.032565 |  | 0.93 | 1.05 | 0.06366 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | TV1MNDV4 | 0.95801 | 0.92545 | -0.032565 |  | 0.93 | 1.05 | 0.037529 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | TV1MNDV4 | 0.95801 | 0.92545 | -0.032565 |  | 0.93 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | TV1MNDV4 | 0.95801 | 0.92545 | -0.032565 |  | 0.93 | 1.05 | 0.033385 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-338 | TV1MNDV4 | 0.95801 | 0.92545 | -0.032565 |  | 0.93 | 1.05 | 0.030301 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-373 | TV1MNDV4 | 0.95801 | 0.92545 | -0.032565 |  | 0.93 | 1.05 | 0.041779 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-376 | TV1MNDV4 | 0.95801 | 0.92545 | -0.032565 |  | 0.93 | 1.05 | 0.079587 | P23:500:EES-EAI:KEO:B4941::EHV: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-113 | TV1MNDV4 | 0.95939 | 0.92485 | -0.034543 |  | 0.93 | 1.05 | 0.038685 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | TV1MNDV4 | 0.95939 | 0.92485 | -0.034543 |  | 0.93 | 1.05 | 0.07469 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | TV1MNDV4 | 0.95939 | 0.92485 | -0.034543 |  | 0.93 | 1.05 | 0.068062 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | TV1MNDV4 | 0.95939 | 0.92485 | -0.034543 |  | 0.93 | 1.05 | 0.034938 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-236 | TV1MNDV4 | 0.95939 | 0.92485 | -0.034543 |  | 0.93 | 1.05 | 0.032777 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-268 | TV1MNDV4 | 0.95939 | 0.92485 | -0.034543 |  | 0.93 | 1.05 | 0.043475 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | TV1MNDV4 | 0.95939 | 0.92485 | -0.034543 |  | 0.93 | 1.05 | 0.13386 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-296 | TV1MNDV4 | 0.95939 | 0.92485 | -0.034543 |  | 0.93 | 1.05 | 0.036067 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-297 | TV1MNDV4 | 0.95939 | 0.92485 | -0.034543 |  | 0.93 | 1.05 | 0.036067 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | TV1MNDV4 | 0.95939 | 0.92485 | -0.034543 |  | 0.93 | 1.05 | 0.067572 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-344 | TV1MNDV4 | 0.95939 | 0.92485 | -0.034543 |  | 0.93 | 1.05 | 0.033583 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-361 | TV1MNDV4 | 0.95939 | 0.92485 | -0.034543 |  | 0.93 | 1.05 | 0.034115 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | None
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | W.GRDNR7 | 0.96116 | 0.93704 | -0.024117 |  | 0.95 | 1.05 | 0.031932 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | W.GRDNR7 | 0.96116 | 0.93704 | -0.024117 |  | 0.95 | 1.05 | 0.046406 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | W.GRDNR7 | 0.96116 | 0.93704 | -0.024117 |  | 0.95 | 1.05 | 0.034669 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | W.GRDNR7 | 0.96116 | 0.93704 | -0.024117 |  | 0.95 | 1.05 | 0.036297 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | W.GRDNR7 | 0.96116 | 0.93704 | -0.024117 |  | 0.95 | 1.05 | 0.03404 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | W.GRDNR7 | 0.96116 | 0.93704 | -0.024117 |  | 0.95 | 1.05 | 0.054677 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | W.GRDNR7 | 0.96116 | 0.93704 | -0.024117 |  | 0.95 | 1.05 | 0.036731 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | W.GRDNR7 | 0.96116 | 0.93704 | -0.024117 |  | 0.95 | 1.05 | 0.035653 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-056 | W.GRDNR7 | 0.97156 | 0.94564 | -0.025923 |  | 0.95 | 1.05 | 0.031932 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-117 | W.GRDNR7 | 0.97156 | 0.94564 | -0.025923 |  | 0.95 | 1.05 | 0.046406 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-118 | W.GRDNR7 | 0.97156 | 0.94564 | -0.025923 |  | 0.95 | 1.05 | 0.034669 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-171 | W.GRDNR7 | 0.97156 | 0.94564 | -0.025923 |  | 0.95 | 1.05 | 0.036297 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-235 | W.GRDNR7 | 0.97156 | 0.94564 | -0.025923 |  | 0.95 | 1.05 | 0.03404 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-240 | W.GRDNR7 | 0.97156 | 0.94564 | -0.025923 |  | 0.95 | 1.05 | 0.054677 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-294 | W.GRDNR7 | 0.97156 | 0.94564 | -0.025923 |  | 0.95 | 1.05 | 0.036731 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 04ALL | 2 | 29WP | V | GEN-2024-318 | W.GRDNR7 | 0.97156 | 0.94564 | -0.025923 |  | 0.95 | 1.05 | 0.035653 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV
Voltage | 05ALL | 2 | 29WP | V | GEN-2024-295 | BLACKRIVER 3 | 0.90588 | 0.85361 | -0.052275 |  | 0.9 | 1.05 | 1 | P12:115:SPS:U27.1.NLVNG.MLGBND:::HV: | None
Voltage | 05ALL | 2 | 29WP | V | GEN-2024-310 | BLACKRIVER 3 | 0.90588 | 0.85361 | -0.052275 |  | 0.9 | 1.05 | 0.044189 | P12:115:SPS:U27.1.NLVNG.MLGBND:::HV: | None
Voltage | 05ALL | 2 | 29WP | V | GEN-2024-311 | BLACKRIVER 3 | 0.90588 | 0.85361 | -0.052275 |  | 0.9 | 1.05 | 0.044189 | P12:115:SPS:U27.1.NLVNG.MLGBND:::HV: | None
Voltage | 05ALL | 2 | 29WP | V | GEN-2024-295 | BLACKRIVER 3 | 0.90022 | 0.851 | -0.049219 |  | 0.9 | 1.05 | 0.13002 | Single 528182 NORTH_LOVNG3 115 528193 BLACKRIVER3 115 1 | None
Voltage | 05ALL | 2 | 29WP | V | GEN-2024-143 | RB-NMO1_SW 2 | 0.90183 | 0.8666 | -0.035236 |  | 0.9 | 1.05 | 0.1594 | Single 523220 XIT_INTG3 115 523228 DALLAM3 115 1 | Add 2.1 MVAR switched shunt at RB-TEXLINE 2 69 kV
Voltage | 05ALL | 2 | 29WP | V | GEN-2024-145 | RB-NMO1_SW 2 | 0.90183 | 0.8666 | -0.035236 |  | 0.9 | 1.05 | 0.1594 | Single 523220 XIT_INTG3 115 523228 DALLAM3 115 1 | Add 2.1 MVAR switched shunt at RB-TEXLINE 2 69 kV
Voltage | 05ALL | 2 | 29WP | V | GEN-2024-143 | RB-NMO1_SW 2 | 0.90183 | 0.8666 | -0.035236 |  | 0.9 | 1.05 | 0.1594 | P12:115:SPS:W80.1.XIT.DALM:::HV: | Add 2.1 MVAR switched shunt at RB-TEXLINE 2 69 kV
Voltage | 05ALL | 2 | 29WP | V | GEN-2024-145 | RB-NMO1_SW 2 | 0.90183 | 0.8666 | -0.035236 |  | 0.9 | 1.05 | 0.1594 | P12:115:SPS:W80.1.XIT.DALM:::HV: | Add 2.1 MVAR switched shunt at RB-TEXLINE 2 69 kV
Voltage | 05ALL | 2 | 29WP | V | GEN-2024-143 | RB-N_SEDAN 2 | 0.92453 | 0.89033 | -0.034198 |  | 0.9 | 1.05 | 0.1594 | Single 523220 XIT_INTG3 115 523228 DALLAM3 115 1 | Add 2.1 MVAR switched shunt at RB-TEXLINE 2 69 kV
Voltage | 05ALL | 2 | 29WP | V | GEN-2024-145 | RB-N_SEDAN 2 | 0.92453 | 0.89033 | -0.034198 |  | 0.9 | 1.05 | 0.1594 | Single 523220 XIT_INTG3 115 523228 DALLAM3 115 1 | Add 2.1 MVAR switched shunt at RB-TEXLINE 2 69 kV
Voltage | 05ALL | 2 | 29WP | V | GEN-2024-143 | RB-N_SEDAN 2 | 0.92453 | 0.89033 | -0.034198 |  | 0.9 | 1.05 | 0.1594 | P12:115:SPS:W80.1.XIT.DALM:::HV: | Add 2.1 MVAR switched shunt at RB-TEXLINE 2 69 kV
Voltage | 05ALL | 2 | 29WP | V | GEN-2024-145 | RB-N_SEDAN 2 | 0.92453 | 0.89033 | -0.034198 |  | 0.9 | 1.05 | 0.1594 | P12:115:SPS:W80.1.XIT.DALM:::HV: | Add 2.1 MVAR switched shunt at RB-TEXLINE 2 69 kV
Voltage | 05ALL | 2 | 29WP | V | GEN-2024-143 | RB-TEXLINE 2 | 0.90183 | 0.8666 | -0.035236 |  | 0.9 | 1.05 | 0.1594 | Single 523220 XIT_INTG3 115 523228 DALLAM3 115 1 | Add 2.1 MVAR switched shunt at RB-TEXLINE 2 69 kV
Voltage | 05ALL | 2 | 29WP | V | GEN-2024-145 | RB-TEXLINE 2 | 0.90183 | 0.8666 | -0.035236 |  | 0.9 | 1.05 | 0.1594 | Single 523220 XIT_INTG3 115 523228 DALLAM3 115 1 | Add 2.1 MVAR switched shunt at RB-TEXLINE 2 69 kV
Voltage | 05ALL | 2 | 29WP | V | GEN-2024-143 | RB-TEXLINE 2 | 0.90183 | 0.8666 | -0.035236 |  | 0.9 | 1.05 | 0.1594 | P12:115:SPS:W80.1.XIT.DALM:::HV: | Add 2.1 MVAR switched shunt at RB-TEXLINE 2 69 kV
Voltage | 05ALL | 2 | 29WP | V | GEN-2024-145 | RB-TEXLINE 2 | 0.90183 | 0.8666 | -0.035236 |  | 0.9 | 1.05 | 0.1594 | P12:115:SPS:W80.1.XIT.DALM:::HV: | Add 2.1 MVAR switched shunt at RB-TEXLINE 2 69 kV
Voltage | 05ALL | 2 | 29WP | V | GEN-2024-143 | RB-TEXLN_SW2 | 0.9073 | 0.87231 | -0.034999 |  | 0.9 | 1.05 | 0.1594 | Single 523220 XIT_INTG3 115 523228 DALLAM3 115 1 | Add 2.1 MVAR switched shunt at RB-TEXLINE 2 69 kV
Voltage | 05ALL | 2 | 29WP | V | GEN-2024-145 | RB-TEXLN_SW2 | 0.9073 | 0.87231 | -0.034999 |  | 0.9 | 1.05 | 0.1594 | Single 523220 XIT_INTG3 115 523228 DALLAM3 115 1 | Add 2.1 MVAR switched shunt at RB-TEXLINE 2 69 kV
Voltage | 05ALL | 2 | 29WP | V | GEN-2024-143 | RB-TEXLN_SW2 | 0.9073 | 0.87231 | -0.034999 |  | 0.9 | 1.05 | 0.1594 | P12:115:SPS:W80.1.XIT.DALM:::HV: | Add 2.1 MVAR switched shunt at RB-TEXLINE 2 69 kV
Voltage | 05ALL | 2 | 29WP | V | GEN-2024-145 | RB-TEXLN_SW2 | 0.9073 | 0.87231 | -0.034999 |  | 0.9 | 1.05 | 0.1594 | P12:115:SPS:W80.1.XIT.DALM:::HV: | Add 2.1 MVAR switched shunt at RB-TEXLINE 2 69 kV
Voltage | 05ALL | 2 | 29WP | V | GEN-2024-143 | RB-TEXRURAL2 | 0.90512 | 0.87003 | -0.035089 |  | 0.9 | 1.05 | 0.1594 | Single 523220 XIT_INTG3 115 523228 DALLAM3 115 1 | Add 2.1 MVAR switched shunt at RB-TEXLINE 2 69 kV
Voltage | 05ALL | 2 | 29WP | V | GEN-2024-145 | RB-TEXRURAL2 | 0.90512 | 0.87003 | -0.035089 |  | 0.9 | 1.05 | 0.1594 | Single 523220 XIT_INTG3 115 523228 DALLAM3 115 1 | Add 2.1 MVAR switched shunt at RB-TEXLINE 2 69 kV
Voltage | 05ALL | 2 | 29WP | V | GEN-2024-143 | RB-TEXRURAL2 | 0.90512 | 0.87003 | -0.035089 |  | 0.9 | 1.05 | 0.1594 | P12:115:SPS:W80.1.XIT.DALM:::HV: | Add 2.1 MVAR switched shunt at RB-TEXLINE 2 69 kV
Voltage | 05ALL | 2 | 29WP | V | GEN-2024-145 | RB-TEXRURAL2 | 0.90512 | 0.87003 | -0.035089 |  | 0.9 | 1.05 | 0.1594 | P12:115:SPS:W80.1.XIT.DALM:::HV: | Add 2.1 MVAR switched shunt at RB-TEXLINE 2 69 kV
Voltage | 05ALL | 2 | 29WP | V | GEN-2024-295 | SENDERO +3 | 0.90644 | 0.8542 | -0.052241 |  | 0.9 | 1.05 | 1 | P12:115:SPS:U27.1.NLVNG.MLGBND:::HV: | None
Voltage | 05ALL | 2 | 29WP | V | GEN-2024-310 | SENDERO +3 | 0.90644 | 0.8542 | -0.052241 |  | 0.9 | 1.05 | 0.044189 | P12:115:SPS:U27.1.NLVNG.MLGBND:::HV: | None
Voltage | 05ALL | 2 | 29WP | V | GEN-2024-311 | SENDERO +3 | 0.90644 | 0.8542 | -0.052241 |  | 0.9 | 1.05 | 0.044189 | P12:115:SPS:U27.1.NLVNG.MLGBND:::HV: | None
Voltage | 05ALL | 2 | 29WP | V | GEN-2024-295 | SENDERO +3 | 0.90079 | 0.8516 | -0.049186 |  | 0.9 | 1.05 | 0.13002 | Single 528182 NORTH_LOVNG3 115 528193 BLACKRIVER3 115 1 | None
Voltage | WECC | 2 | 31SP | WECC | N/A | None | [7 empty] | None | None
Voltage | WECC | 2 | 31WP | WECC | N/A | None | [7 empty] | None | None

## Short Circuit Ratio
Study Request | Current Cluster | Cluster Group | Transmission Owner | Capacity | Service Type | Generation Type | Point of Interconnection | GEN Bus # | Gen ID | POI Bus # | DIS241-TC00ALL-29SP.raw |  | DIS241-TC01ALL-29L.raw |  | DIS241-TC01ALL-29SP.raw |  | DIS241-TC02ALL-29L.raw |  | DIS241-TC02ALL-29SP.raw |  | DIS241-TC03ALL-29L.raw |  | DIS241-TC03ALL-29SP.raw |  | DIS241-TC04ALL-29L.raw |  | DIS241-TC04ALL-29SP.raw |  | DIS241-TC05ALL-29L.raw |  | DIS241-TC05ALL-29SP.raw
[11 empty] | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio
ASGI-2024-001 | DIS-24-1 | 01 NORTH | WAPA | 17.1 | ER | Thermal | Pine Lake 12.47 kV | 656779 | 1 | 656751 | 384.07 | 31.2252 | 380.08 | N/A | 384.04 | N/A | 380.14 | N/A | 384.06 | N/A | 380.07 | N/A | 384.04 | N/A | 380.07 | N/A | 384.04 | N/A | 380.07 | N/A | 384.04 | N/A
ASGI-2024-002 | DIS-24-1 | 05 SOUTHWEST | SPS | 30 | ER | Solar | GridLiance's Cougar 69 kV Substation | 788365 | 1 | 522919 | 166.33 | 4.9503 | 160.6 | N/A | 163.75 | 4.8735 | 160.55 | N/A | 163.83 | 4.8759 | 160.97 | N/A | 162.88 | 4.8476 | 162.43 | N/A | 163.62 | 4.8696 | 161.31 | N/A | 166.01 | 4.9408
ASGI-2024-002 | DIS-24-1 | 05 SOUTHWEST | SPS | 30 | ER | Battery/Storage | GridLiance's Cougar 69 kV Substation | 788367 | 1 | 522919 | 166.33 | 4.9503 | 160.6 | N/A | 163.75 | N/A | 160.55 | N/A | 163.83 | N/A | 160.97 | N/A | 162.88 | N/A | 162.43 | N/A | 163.62 | N/A | 161.31 | N/A | 166.01 | 4.9408
ASGI-2024-003 | DIS-24-1 | 03 CENTRAL | SUNC | 79.8 | ER/NR | Solar | Rolla 115 kV Substation | 788350 | 1 | 531395 | 418.08 | 5.1711 | 398.56 | N/A | 410.33 | 5.0752 | 398.58 | N/A | 410.34 | 5.0753 | 400.14 | N/A | 412.16 | 5.0978 | 398.67 | N/A | 410.43 | 5.0764 | 399.65 | N/A | 409.94 | 5.0704
ASGI-2024-006 | DIS-24-1 | 03 CENTRAL | KCPL | 50 | ER/NR | Solar | Y-road 115 kV switching station | 788381 | 1 | 522912 | 1043.73 | 20.6214 | 979.1 | N/A | 992.21 | 19.6035 | 979.03 | N/A | 992.44 | 19.608 | 971.67 | N/A | 970.48 | 19.1741 | 983.1 | N/A | 993.94 | 19.6377 | 999.88 | N/A | 1010.97 | 19.9741
ASGI-2024-006 | DIS-24-1 | 03 CENTRAL | KCPL | 50 | ER/NR | Solar | Y-road 115 kV switching station | 788383 | 1 | 522912 | 1043.73 | 20.6214 | 979.1 | N/A | 992.21 | 19.6035 | 979.03 | N/A | 992.44 | 19.608 | 971.67 | N/A | 970.48 | 19.1741 | 983.1 | N/A | 993.94 | 19.6377 | 999.88 | N/A | 1010.97 | 19.9741
ASGI-2024-007 | DIS-24-1 | 03 CENTRAL | KCPL | 3.87 | ER/NR | Thermal | Marshall Miami 161 kV Substation | 788393 | 1 | 543073 | 1551.72 | 258.62 | 1418.1 | N/A | 1495.97 | N/A | 1418.07 | N/A | 1496 | N/A | 1419.68 | N/A | 1536.64 | N/A | 1419.41 | N/A | 1497.2 | N/A | 1417.94 | N/A | 1495.68 | N/A
ASGI-2024-007 | DIS-24-1 | 03 CENTRAL | KCPL | 3.87 | ER/NR | Thermal | Marshall Miami 161 kV Substation | 788393 | 2 | 543073 | 1551.72 | 258.62 | 1418.1 | N/A | 1495.97 | N/A | 1418.07 | N/A | 1496 | N/A | 1419.68 | N/A | 1536.64 | N/A | 1419.41 | N/A | 1497.2 | N/A | 1417.94 | N/A | 1495.68 | N/A
ASGI-2024-007 | DIS-24-1 | 03 CENTRAL | KCPL | 15.48 | ER/NR | Thermal | Marshall Miami 161 kV Substation | 788393 | 3 | 543073 | 1551.72 | 64.655 | 1418.1 | N/A | 1495.97 | N/A | 1418.07 | N/A | 1496 | N/A | 1419.68 | N/A | 1536.64 | N/A | 1419.41 | N/A | 1497.2 | N/A | 1417.94 | N/A | 1495.68 | N/A
ASGI-2024-007 | DIS-24-1 | 03 CENTRAL | KCPL | 15.48 | ER/NR | Thermal | Marshall Miami 161 kV Substation | 788393 | 4 | 543073 | 1551.72 | 64.655 | 1418.1 | N/A | 1495.97 | N/A | 1418.07 | N/A | 1496 | N/A | 1419.68 | N/A | 1536.64 | N/A | 1419.41 | N/A | 1497.2 | N/A | 1417.94 | N/A | 1495.68 | N/A
ASGI-2024-007 | DIS-24-1 | 03 CENTRAL | KCPL | 9.29 | ER/NR | Thermal | Marshall Miami 161 kV Substation | 788393 | 5 | 543073 | 1551.72 | 107.7583 | 1418.1 | N/A | 1495.97 | N/A | 1418.07 | N/A | 1496 | N/A | 1419.68 | N/A | 1536.64 | N/A | 1419.41 | N/A | 1497.2 | N/A | 1417.94 | N/A | 1495.68 | N/A
ASGI-2024-008 | DIS-24-1 | 03 CENTRAL | KCPL | 43 | ER/NR | Thermal | Marshall Miami 161 kV Substation | 788408 | 1 | 543073 | 1551.72 | 36.0865 | 1418.1 | N/A | 1495.97 | N/A | 1418.07 | N/A | 1496 | N/A | 1419.68 | N/A | 1536.64 | N/A | 1419.41 | N/A | 1497.2 | N/A | 1417.94 | N/A | 1495.68 | N/A
ASGI-2024-008 | DIS-24-1 | 03 CENTRAL | KCPL | 43 | ER/NR | Thermal | Marshall Miami 161 kV Substation | 788409 | 1 | 543073 | 1551.72 | 36.0865 | 1418.1 | N/A | 1495.97 | N/A | 1418.07 | N/A | 1496 | N/A | 1419.68 | N/A | 1536.64 | N/A | 1419.41 | N/A | 1497.2 | N/A | 1417.94 | N/A | 1495.68 | N/A
ASGI-2024-020 | DIS-24-1 | 03 CENTRAL | WERE | 65.79 | ER/NR | Thermal | Johns-Manville 115 kV Substation | 778384 | 1 | 533426 | 2295.26 | 34.8877 | 1686.09 | N/A | 2274.68 | N/A | 1686.58 | N/A | 2275.18 | N/A | 1692.57 | N/A | 2278.96 | N/A | 1672.94 | N/A | 2262.23 | N/A | 1678.46 | N/A | 2265.55 | N/A
ASGI-2024-020 | DIS-24-1 | 03 CENTRAL | WERE | 65.79 | ER/NR | Thermal | Johns-Manville 115 kV Substation | 778387 | 1 | 533426 | 2295.26 | 34.8877 | 1686.09 | N/A | 2274.68 | N/A | 1686.58 | N/A | 2275.18 | N/A | 1692.57 | N/A | 2278.96 | N/A | 1672.94 | N/A | 2262.23 | N/A | 1678.46 | N/A | 2265.55 | N/A
ASGI-2024-023 | DIS-24-1 | 04 SOUTHEAST | AEPW | 120 | ER/NR | Solar | Hope Switching Station to Hope W&L Pole | 783394 | 1 | 783390 | 1593.89 | 13.0856 | 1415.85 | N/A | 1587.09 | 13.0298 | 1415.86 | N/A | 1587.09 | 13.0298 | 1415.87 | N/A | 1587.09 | 13.0298 | 1416.6 | N/A | 1589.42 | 13.0489 | 1415.9 | N/A | 1586.98 | 13.0289
ASGI-2024-023 | DIS-24-1 | 04 SOUTHEAST | AEPW | 120 | ER/NR | Storage | Hope Switching Station to Hope W&L Pole | 783397 | 1 | 783390 | 1593.89 | 13.0668 | 1415.85 | N/A | 1587.09 | N/A | 1415.86 | N/A | 1587.09 | N/A | 1415.87 | N/A | 1587.09 | N/A | 1416.6 | N/A | 1589.42 | 13.0302 | 1415.9 | N/A | 1586.98 | N/A
ASGI-2024-024 | DIS-24-1 | 03 CENTRAL | KCPL | 79 | ER/NR | Battery/Storage | Alabama St 161 kV Substation | 787414 | 1 | 541354 | 3115.63 | 39.4384 | 2646.04 | N/A | 3092.57 | N/A | 2648.29 | N/A | 3093.81 | N/A | 2666.08 | N/A | 3105.23 | 39.3067 | 2646.44 | N/A | 3092.61 | N/A | 2646.78 | N/A | 3092.79 | N/A
GEN-2024-003 | DIS-24-1 | 04 SOUTHEAST | AECC | 102.2 | ER | Thermal | Fitzhugh 161kV | 777064 | 1 | 503902 | 3080.94 | 61.1298 | 1987.2 | N/A | 2992.79 | N/A | 1987.2 | N/A | 2992.79 | N/A | 1987.28 | N/A | 2992.81 | N/A | 1986.76 | N/A | 3035.18 | N/A | 1987.31 | N/A | 2992.79 | N/A
GEN-2024-003 | DIS-24-1 | 04 SOUTHEAST | AECC | 102.2 | ER | Thermal | Fitzhugh 161kV | 777064 | 2 | 503902 | 3080.94 | 59.4776 | 1987.2 | N/A | 2992.79 | N/A | 1987.2 | N/A | 2992.79 | N/A | 1987.28 | N/A | 2992.81 | N/A | 1986.76 | N/A | 3035.18 | N/A | 1987.31 | N/A | 2992.79 | N/A
GEN-2024-007 | DIS-24-1 | 03 CENTRAL | MIDW | 80 | ER/NR | Solar | Seward 115 kV Substation | 777184 | 1 | 530679 | 995.05 | 12.2242 | 903.11 | N/A | 975.61 | 11.9854 | 904.31 | N/A | 975.94 | 11.9894 | 912.46 | N/A | 985.25 | 12.1038 | 903.03 | N/A | 974.46 | 11.9713 | 904.15 | N/A | 972.44 | 11.9464
GEN-2024-007 | DIS-24-1 | 03 CENTRAL | MIDW | 80 | ER/NR | Battery/Storage | Seward 115 kV Substation | 777187 | 1 | 530679 | 995.05 | 12.2906 | 903.11 | N/A | 975.61 | N/A | 904.31 | N/A | 975.94 | N/A | 912.46 | N/A | 985.25 | 12.1696 | 903.03 | N/A | 974.46 | N/A | 904.15 | N/A | 972.44 | N/A
GEN-2024-013 | DIS-24-1 | 04 SOUTHEAST | OGE | 496 | ER/NR | Thermal | Norman Hills 345 kV | 777364 | 1 | 516096 | 18124.38 | 73.0822 | 13428.42 | N/A | 16757.22 | N/A | 13429.03 | N/A | 16757 | N/A | 13467.39 | N/A | 16787.9 | N/A | 14202.73 | N/A | 17331.79 | N/A | 13512.16 | N/A | 16757.91 | N/A
GEN-2024-013 | DIS-24-1 | 04 SOUTHEAST | OGE | 496 | ER/NR | Thermal | Norman Hills 345 kV | 777367 | 1 | 516096 | 18124.38 | 73.0822 | 13428.42 | N/A | 16757.22 | N/A | 13429.03 | N/A | 16757 | N/A | 13467.39 | N/A | 16787.9 | N/A | 14202.73 | N/A | 17331.79 | N/A | 13512.16 | N/A | 16757.91 | N/A
GEN-2024-015 | DIS-24-1 | 05 SOUTHWEST | SPS | 280 | ER/NR | Solar | Sundown-Amaco-Yoakum 230 kV Substation | 777424 | 1 | 777420 | 4491.78 | 15.6969 | 3536.7 | N/A | 4372.49 | 15.28 | 3536.09 | N/A | 4372.71 | 15.2808 | 3537.68 | N/A | 4372.91 | 15.2815 | 3541.46 | N/A | 4373.62 | 15.284 | 3595.72 | N/A | 4444.42 | 15.5314
GEN-2024-015 | DIS-24-1 | 05 SOUTHWEST | SPS | 280 | ER/NR | Battery/Storage | Sundown-Amaco-Yoakum 230 kV Substation | 777427 | 1 | 777420 | 4491.78 | 25.3807 | 3536.7 | N/A | 4372.49 | N/A | 3536.09 | N/A | 4372.71 | N/A | 3537.68 | N/A | 4372.91 | N/A | 3541.46 | N/A | 4373.62 | N/A | 3595.72 | N/A | 4444.42 | 25.1131
GEN-2024-016 | DIS-24-1 | 03 CENTRAL | ITCGP | 300 | ER/NR | Wind | Post Rock - Macon 345 kV Line | 777454 | 1 | 777450 | 3942.91 | 26.2861 | 3480.65 | 23.2043 | 3652.95 | 24.353 | 3567.6 | 23.784 | 3792.47 | 25.2831 | 3538.66 | 23.5911 | 3791.76 | 25.2784 | 3496.76 | 23.3117 | 3697.15 | 24.6477 | 3490.87 | 23.2725 | 3692.26 | 24.6151
GEN-2024-016 | DIS-24-1 | 03 CENTRAL | ITCGP | 300 | ER/NR | Wind | Post Rock - Macon 345 kV Line | 777457 | 1 | 777450 | 3942.91 | 26.2861 | 3480.65 | 23.2043 | 3652.95 | 24.353 | 3567.6 | 23.784 | 3792.47 | 25.2831 | 3538.66 | 23.5911 | 3791.76 | 25.2784 | 3496.76 | 23.3117 | 3697.15 | 24.6477 | 3490.87 | 23.2725 | 3692.26 | 24.6151
GEN-2024-017 | DIS-24-1 | 02 NEBRASKA | NPPD | 62 | ER/NR | Thermal | Olive Creek 345 kV Substation | 776464 | 2 | 640590 | 19192.83 | 619.1235 | 11418.91 | N/A | 14087.53 | N/A | 12047.14 | N/A | 14986.91 | N/A | 11645.79 | N/A | 14522.08 | N/A | 11484.63 | N/A | 14233.83 | N/A | 11434.14 | N/A | 14180.49 | N/A
GEN-2024-017 | DIS-24-1 | 02 NEBRASKA | NPPD | 62 | ER/NR | Thermal | Olive Creek 345 kV Substation | 776467 | 2 | 640590 | 19192.83 | 619.1235 | 11418.91 | N/A | 14087.53 | N/A | 12047.14 | N/A | 14986.91 | N/A | 11645.79 | N/A | 14522.08 | N/A | 11484.63 | N/A | 14233.83 | N/A | 11434.14 | N/A | 14180.49 | N/A
GEN-2024-018 | DIS-24-1 | 02 NEBRASKA | NPPD | 31 | ER/NR | Thermal | New Beatrice Power Station 345 kV | 776444 | 2 | 771999 | 10785.18 | 347.909 | 7196.55 | N/A | 8427.71 | N/A | 7527.3 | N/A | 8811.62 | N/A | 7282.03 | N/A | 8558.93 | N/A | 7210.81 | N/A | 8467.73 | N/A | 7200.32 | N/A | 8455.2 | N/A
GEN-2024-019 | DIS-24-1 | 02 NEBRASKA | NPPD | 62 | ER/NR | Thermal | New Beatrice Power Station 345 kV Substation | 776424 | 2 | 771999 | 10785.18 | 347.909 | 7196.55 | N/A | 8427.71 | N/A | 7527.3 | N/A | 8811.62 | N/A | 7282.03 | N/A | 8558.93 | N/A | 7210.81 | N/A | 8467.73 | N/A | 7200.32 | N/A | 8455.2 | N/A
GEN-2024-019 | DIS-24-1 | 02 NEBRASKA | NPPD | 62 | ER/NR | Thermal | New Beatrice Power Station 345 kV Substation | 776427 | 2 | 771999 | 10785.18 | 347.909 | 7196.55 | N/A | 8427.71 | N/A | 7527.3 | N/A | 8811.62 | N/A | 7282.03 | N/A | 8558.93 | N/A | 7210.81 | N/A | 8467.73 | N/A | 7200.32 | N/A | 8455.2 | N/A
GEN-2024-020 | DIS-24-1 | 02 NEBRASKA | NPPD | 390 | ER/NR | Thermal | Olive Creek 345 kV Substation | 777574 | 1 | 640590 | 19192.83 | 49.2124 | 11418.91 | N/A | 14087.53 | N/A | 12047.14 | N/A | 14986.91 | N/A | 11645.79 | N/A | 14522.08 | N/A | 11484.63 | N/A | 14233.83 | N/A | 11434.14 | N/A | 14180.49 | N/A
GEN-2024-021 | DIS-24-1 | 02 NEBRASKA | NPPD | 540 | ER/NR | Thermal | Olive Creek 345 kV Substation | 777604 | 1 | 640590 | 19192.83 | 71.0846 | 11418.91 | N/A | 14087.53 | N/A | 12047.14 | N/A | 14986.91 | N/A | 11645.79 | N/A | 14522.08 | N/A | 11484.63 | N/A | 14233.83 | N/A | 11434.14 | N/A | 14180.49 | N/A
GEN-2024-021 | DIS-24-1 | 02 NEBRASKA | NPPD | 540 | ER/NR | Thermal | Olive Creek 345 kV Substation | 777607 | 1 | 640590 | 19192.83 | 71.0846 | 11418.91 | N/A | 14087.53 | N/A | 12047.14 | N/A | 14986.91 | N/A | 11645.79 | N/A | 14522.08 | N/A | 11484.63 | N/A | 14233.83 | N/A | 11434.14 | N/A | 14180.49 | N/A
GEN-2024-022 | DIS-24-1 | 02 NEBRASKA | NPPD | 390 | ER/NR | Thermal | New Beatrice Power Station 345 kV | 777634 | 1 | 771999 | 10785.18 | 27.6543 | 7196.55 | N/A | 8427.71 | N/A | 7527.3 | N/A | 8811.62 | N/A | 7282.03 | N/A | 8558.93 | N/A | 7210.81 | N/A | 8467.73 | N/A | 7200.32 | N/A | 8455.2 | N/A
GEN-2024-023 | DIS-24-1 | 02 NEBRASKA | NPPD | 270 | ER/NR | Thermal | New Beatrice Power Station 345 kV | 777664 | 1 | 771999 | 10785.18 | 39.9451 | 7196.55 | N/A | 8427.71 | N/A | 7527.3 | N/A | 8811.62 | N/A | 7282.03 | N/A | 8558.93 | N/A | 7210.81 | N/A | 8467.73 | N/A | 7200.32 | N/A | 8455.2 | N/A
GEN-2024-025 | DIS-24-1 | 04 SOUTHEAST | AEP | 300 | ER/NR | Solar | Lydia 345 kV Substation | 777724 | 1 | 508298 | 8704.63 | 58.0309 | 5513.92 | N/A | 7327.81 | 48.8521 | 5513.94 | N/A | 7327.81 | 48.8521 | 5515 | N/A | 7328.12 | 48.8541 | 5583.3 | N/A | 7643.19 | 50.9546 | 5517.58 | N/A | 7304.48 | 48.6965
GEN-2024-025 | DIS-24-1 | 04 SOUTHEAST | AEP | 300 | ER/NR | Solar | Lydia 345 kV Substation | 777727 | 1 | 508298 | 8704.63 | 58.0309 | 5513.92 | N/A | 7327.81 | 48.8521 | 5513.94 | N/A | 7327.81 | 48.8521 | 5515 | N/A | 7328.12 | 48.8541 | 5583.3 | N/A | 7643.19 | 50.9546 | 5517.58 | N/A | 7304.48 | 48.6965
GEN-2024-029 | DIS-24-1 | 04 SOUTHEAST | OGE | 150 | ER/NR | Battery/Storage | Crescent 138 kV Substation | 777844 | 1 | 515377 | 2188.67 | 14.5911 | 2019.75 | N/A | 2112.32 | N/A | 2019.77 | N/A | 2112.32 | N/A | 2020.83 | N/A | 2112.92 | N/A | 2084.71 | N/A | 2179.06 | 14.5271 | 2020.84 | N/A | 2112.4 | N/A
GEN-2024-030 | DIS-24-1 | 03 CENTRAL | SUNC | 150 | ER/NR | Solar | Santa Fe 115 kV Substation | 777874 | 1 | 531213 | 540.02 | 3.6001 | 511.98 | N/A | 533.01 | 3.5534 | 512.01 | N/A | 533.03 | 3.5535 | 514.93 | N/A | 537.47 | 3.5831 | 512.08 | N/A | 533.08 | 3.5539 | 512.72 | N/A | 532.99 | 3.5533
GEN-2024-032 | DIS-24-1 | 03 CENTRAL | SUNC | 250 | ER/NR | Solar | Hugoton 115 kV Substation | 777934 | 1 | 531481 | 1255.99 | 5.024 | 1048.48 | N/A | 1199.22 | 4.7969 | 1048.62 | N/A | 1199.3 | 4.7972 | 1059.61 | N/A | 1213.31 | 4.8532 | 1049.31 | N/A | 1200.03 | 4.8001 | 1056.12 | N/A | 1196.27 | 4.7851
GEN-2024-034 | DIS-24-1 | 01 NORTH | WAPA | 175 | ER/NR | Battery/Storage | Forman 115 kV Substation | 777994 | 1 | 652438 | 1658.7 | 9.4783 | 1589.42 | N/A | 1657.48 | 9.4713 | 1590.59 | N/A | 1647.73 | N/A | 1590.53 | N/A | 1647.7 | N/A | 1590.53 | N/A | 1647.7 | N/A | 1591.29 | N/A | 1647.75 | N/A
GEN-2024-035 | DIS-24-1 | 01 NORTH | BEPC | 270 | ER/NR | Solar | Groton 345 kV Substation | 778024 | 1 | 659160 | 3574.92 | 12.9276 | 3290.91 | N/A | 3504.32 | 12.6723 | 3227.36 | N/A | 3519.96 | 12.7289 | 3226.52 | N/A | 3519.64 | 12.7277 | 3226.47 | N/A | 3519.62 | 12.7276 | 3227.05 | N/A | 3519.62 | 12.7276
GEN-2024-035 | DIS-24-1 | 01 NORTH | BEPC | 270 | ER/NR | Battery/Storage | Groton 345 kV Substation | 778027 | 1 | 659160 | 3574.92 | 22.5433 | 3290.91 | N/A | 3504.32 | 22.0981 | 3227.36 | N/A | 3519.96 | N/A | 3226.52 | N/A | 3519.64 | N/A | 3226.47 | N/A | 3519.62 | N/A | 3227.05 | N/A | 3519.62 | N/A
GEN-2024-038 | DIS-24-1 | 02 NEBRASKA | OPPD | 300 | ER/NR | Solar | Cooper - S12080 161 kV line | 778114 | 1 | 778110 | 2932.65 | 19.551 | 2761.62 | N/A | 2859.74 | 19.0649 | 2766.71 | N/A | 2910.31 | 19.4021 | 2765.8 | N/A | 2859.54 | 19.0636 | 2759.35 | N/A | 2857.89 | 19.0526 | 2760.7 | N/A | 2858.87 | 19.0591
GEN-2024-038 | DIS-24-1 | 02 NEBRASKA | OPPD | 300 | ER/NR | Solar | Cooper - S12080 161 kV line | 778117 | 1 | 778110 | 2932.65 | 19.551 | 2761.62 | N/A | 2859.74 | 19.0649 | 2766.71 | N/A | 2910.31 | 19.4021 | 2765.8 | N/A | 2859.54 | 19.0636 | 2759.35 | N/A | 2857.89 | 19.0526 | 2760.7 | N/A | 2858.87 | 19.0591
GEN-2024-039 | DIS-24-1 | 02 NEBRASKA | OPPD | 250 | ER/NR | Solar | Humboldt - S1280 161 kV line | 778144 | 1 | 778140 | 2354.58 | 18.8366 | 2218.26 | N/A | 2300.97 | 18.4078 | 2221.78 | N/A | 2339.12 | 18.713 | 2220.88 | N/A | 2299.06 | 18.3925 | 2215.35 | N/A | 2298.45 | 18.3876 | 2217.1 | N/A | 2299.88 | 18.399
GEN-2024-039 | DIS-24-1 | 02 NEBRASKA | OPPD | 250 | ER/NR | Solar | Humboldt - S1280 161 kV line | 778147 | 1 | 778140 | 2354.58 | 18.8366 | 2218.26 | N/A | 2300.97 | 18.4078 | 2221.78 | N/A | 2339.12 | 18.713 | 2220.88 | N/A | 2299.06 | 18.3925 | 2215.35 | N/A | 2298.45 | 18.3876 | 2217.1 | N/A | 2299.88 | 18.399
GEN-2024-040 | DIS-24-1 | 02 NEBRASKA | OPPD | 174 | ER/NR | Solar | S3458 to Cooper 345 kV line | 778174 | 1 | 778170 | 14400.12 | 82.7593 | 12298.85 | N/A | 13626.92 | 78.3156 | 12395.57 | N/A | 13771.93 | 79.149 | 12410.72 | N/A | 13707.34 | 78.7778 | 12303.06 | N/A | 13635.08 | 78.3625 | 12298.77 | N/A | 13631.45 | 78.3417
GEN-2024-041 | DIS-24-1 | 05 SOUTHWEST | SPS | 250 | ER/NR | Wind | Tuco - Whirlwind 345 kV Line | 778204 | 1 | 778200 | 14075.03 | 112.6002 | 10759.64 | 86.0771 | 13238.11 | 105.9049 | 10757.95 | 86.0636 | 13239.27 | 105.9142 | 10771.19 | 86.1695 | 13263.03 | 106.1042 | 10959.08 | 87.6726 | 13360.5 | 106.884 | 11197.73 | 89.5818 | 13323.71 | 106.5897
GEN-2024-041 | DIS-24-1 | 05 SOUTHWEST | SPS | 250 | ER/NR | Wind | Tuco - Whirlwind 345 kV Line | 778207 | 1 | 778200 | 14075.03 | 112.6002 | 10759.64 | 86.0771 | 13238.11 | 105.9049 | 10757.95 | 86.0636 | 13239.27 | 105.9142 | 10771.19 | 86.1695 | 13263.03 | 106.1042 | 10959.08 | 87.6726 | 13360.5 | 106.884 | 11197.73 | 89.5818 | 13323.71 | 106.5897
GEN-2024-042 | DIS-24-1 | 05 SOUTHWEST | SPS | 250 | ER/NR | Wind | Tuco - Whirlwind 345 kV line | 778234 | 1 | 778200 | 14075.03 | 112.6002 | 10759.64 | 86.0771 | 13238.11 | 105.9049 | 10757.95 | 86.0636 | 13239.27 | 105.9142 | 10771.19 | 86.1695 | 13263.03 | 106.1042 | 10959.08 | 87.6726 | 13360.5 | 106.884 | 11197.73 | 89.5818 | 13323.71 | 106.5897
GEN-2024-042 | DIS-24-1 | 05 SOUTHWEST | SPS | 250 | ER/NR | Wind | Tuco - Whirlwind 345 kV line | 778237 | 1 | 778200 | 14075.03 | 112.6002 | 10759.64 | 86.0771 | 13238.11 | 105.9049 | 10757.95 | 86.0636 | 13239.27 | 105.9142 | 10771.19 | 86.1695 | 13263.03 | 106.1042 | 10959.08 | 87.6726 | 13360.5 | 106.884 | 11197.73 | 89.5818 | 13323.71 | 106.5897
GEN-2024-043 | DIS-24-1 | 05 SOUTHWEST | SPS | 250 | ER/NR | Wind | Crossroads - Tolk 345 kV Line | 778264 | 1 | 778260 | 9707.85 | 77.6628 | 8402.65 | 67.2212 | 9514.37 | 76.115 | 8400.53 | 67.2042 | 9514.02 | 76.1122 | 8401.55 | 67.2124 | 9518.86 | 76.1509 | 8431.49 | 67.4519 | 9524.67 | 76.1974 | 8578.29 | 68.6263 | 9436.77 | 75.4942
GEN-2024-043 | DIS-24-1 | 05 SOUTHWEST | SPS | 250 | ER/NR | Wind | Crossroads - Tolk 345 kV Line | 778267 | 1 | 778260 | 9707.85 | 77.6628 | 8402.65 | 67.2212 | 9514.37 | 76.115 | 8400.53 | 67.2042 | 9514.02 | 76.1122 | 8401.55 | 67.2124 | 9518.86 | 76.1509 | 8431.49 | 67.4519 | 9524.67 | 76.1974 | 8578.29 | 68.6263 | 9436.77 | 75.4942
GEN-2024-044 | DIS-24-1 | 04 SOUTHEAST | AEP | 36 | ER/NR | Solar | Hosston - Plain Dealing 69 kV Line | 778294 | 1 | 778290 | 640.73 | 17.6831 | 575.89 | N/A | 589.59 | 16.2717 | 575.89 | N/A | 589.59 | 16.2717 | 575.89 | N/A | 589.59 | 16.2717 | 576.09 | N/A | 638.08 | 17.61 | 575.9 | N/A | 589.55 | 16.2706
GEN-2024-044 | DIS-24-1 | 04 SOUTHEAST | AEP | 36 | ER/NR | Battery/Storage | Hosston - Plain Dealing 69 kV Line | 778297 | 1 | 778290 | 640.73 | 16.8973 | 575.89 | N/A | 589.59 | N/A | 575.89 | N/A | 589.59 | N/A | 575.89 | N/A | 589.59 | N/A | 576.09 | N/A | 638.08 | 16.8274 | 575.9 | N/A | 589.55 | N/A
GEN-2024-045 | DIS-24-1 | 05 SOUTHWEST | SPS | 345 | ER/NR | Solar | Hitchland - Moore 230kV line | 778324 | 1 | 778320 | 2604.28 | 15.0973 | 2330.06 | N/A | 2479.51 | 14.374 | 2330.03 | N/A | 2479.72 | 14.3752 | 2337.38 | N/A | 2487.98 | 14.4231 | 2335.76 | N/A | 2483.42 | 14.3966 | 2467.96 | N/A | 2587.16 | 14.998
GEN-2024-045 | DIS-24-1 | 05 SOUTHWEST | SPS | 345 | ER/NR | Solar | Hitchland - Moore 230kV line | 778327 | 1 | 778320 | 2604.28 | 15.0973 | 2330.06 | N/A | 2479.51 | 14.374 | 2330.03 | N/A | 2479.72 | 14.3752 | 2337.38 | N/A | 2487.98 | 14.4231 | 2335.76 | N/A | 2483.42 | 14.3966 | 2467.96 | N/A | 2587.16 | 14.998
GEN-2024-046 | DIS-24-1 | 05 SOUTHWEST | SPS | 345 | ER/NR | Solar | Hitchland-Moore 230 kV line | 777094 | 1 | 778320 | 2604.28 | 15.0973 | 2330.06 | N/A | 2479.51 | 14.374 | 2330.03 | N/A | 2479.72 | 14.3752 | 2337.38 | N/A | 2487.98 | 14.4231 | 2335.76 | N/A | 2483.42 | 14.3966 | 2467.96 | N/A | 2587.16 | 14.998
GEN-2024-046 | DIS-24-1 | 05 SOUTHWEST | SPS | 345 | ER/NR | Solar | Hitchland-Moore 230 kV line | 777097 | 1 | 778320 | 2604.28 | 15.0973 | 2330.06 | N/A | 2479.51 | 14.374 | 2330.03 | N/A | 2479.72 | 14.3752 | 2337.38 | N/A | 2487.98 | 14.4231 | 2335.76 | N/A | 2483.42 | 14.3966 | 2467.96 | N/A | 2587.16 | 14.998
GEN-2024-050 | DIS-24-1 | 05 SOUTHWEST | SPS | 300 | ER/NR | Solar | Olson 230 kV Substation | 778474 | 1 | 525520 | 3093.68 | 9.2207 | 2685.32 | N/A | 2950.82 | 8.7949 | 2681.48 | N/A | 2950.86 | 8.795 | 2682.25 | N/A | 2951.31 | 8.7963 | 2696.45 | N/A | 2951.66 | 8.7974 | 2834.39 | N/A | 3059.22 | 9.118
GEN-2024-050 | DIS-24-1 | 05 SOUTHWEST | SPS | 300 | ER/NR | Battery/Storage | Olson 230 kV Substation | 778477 | 1 | 525520 | 3093.68 | 18.1247 | 2685.32 | N/A | 2950.82 | N/A | 2681.48 | N/A | 2950.86 | N/A | 2682.25 | N/A | 2951.31 | N/A | 2696.45 | N/A | 2951.66 | N/A | 2834.39 | N/A | 3059.22 | 17.9228
GEN-2024-051 | DIS-24-1 | 02 NEBRASKA | LES | 170 | ER/NR | Battery/Storage | Waverly 115 kV Substation | 778504 | 1 | 778500 | 4357.55 | 25.6326 | 3585.43 | N/A | 4095.36 | N/A | 3616.95 | N/A | 4188.3 | 24.6371 | 3583.7 | N/A | 4094.92 | N/A | 3580.57 | N/A | 4094.35 | N/A | 3583.85 | N/A | 4095.14 | N/A
GEN-2024-052 | DIS-24-1 | 04 SOUTHEAST | WFEC | 42 | ER/NR | Solar | Unger - West Bank Tap 138 kV Line | 778534 | 1 | 778530 | 1353.84 | 32.0208 | 1134.02 | N/A | 1237.57 | 29.2708 | 1134.03 | N/A | 1237.57 | 29.2708 | 1134.1 | N/A | 1237.59 | 29.2713 | 1143.88 | N/A | 1323.9 | 31.3127 | 1134.41 | N/A | 1237.52 | 29.2696
GEN-2024-052 | DIS-24-1 | 04 SOUTHEAST | WFEC | 42 | ER/NR | Battery/Storage | Unger - West Bank Tap 138 kV Line | 778537 | 1 | 778530 | 1353.84 | 30.6146 | 1134.02 | N/A | 1237.57 | N/A | 1134.03 | N/A | 1237.57 | N/A | 1134.1 | N/A | 1237.59 | N/A | 1143.88 | N/A | 1323.9 | 29.9376 | 1134.41 | N/A | 1237.52 | N/A
GEN-2024-054 | DIS-24-1 | 03 CENTRAL | WERE | 120 | ER/NR | Solar | Overton - Sedalia East 161 kV line | 778594 | 1 | 768980 | 2189.93 | 18.2494 | 1956.3 | N/A | 2028.56 | 16.9047 | 1956.25 | N/A | 2028.73 | 16.9061 | 1955.55 | N/A | 2159.88 | 17.999 | 1952.65 | N/A | 2026.68 | 16.889 | 1954.7 | N/A | 2027.72 | 16.8977
GEN-2024-055 | DIS-24-1 | 03 CENTRAL | WERE | 175 | ER/NR | Solar | Butler - Nevada 161 kV line | 778624 | 1 | 778620 | 1765.84 | 10.0905 | 1628.18 | N/A | 1740.57 | 9.9461 | 1629.6 | N/A | 1740.92 | 9.9481 | 1627.66 | N/A | 1762.89 | 10.0737 | 1631.18 | N/A | 1750.09 | 10.0005 | 1634.88 | N/A | 1742.32 | 9.9561
GEN-2024-056 | DIS-24-1 | 04 SOUTHEAST | OGE | 120 | ER/NR | Solar | Cow Creek - Morrison 138 kV line | 778654 | 1 | 778650 | 2690.98 | 22.4248 | 2558.5 | N/A | 2609.98 | 21.7498 | 2558.52 | N/A | 2609.98 | 21.7498 | 2560.26 | N/A | 2611.17 | 21.7597 | 2577.14 | N/A | 2630.59 | 21.9216 | 2559.19 | N/A | 2609.82 | 21.7485
GEN-2024-058 | DIS-24-1 | 04 SOUTHEAST | AEP | 200 | ER/NR | Wind | Farmland - Delaware 138 kV line | 778714 | 1 | 778710 | 2041.86 | 20.4186 | 1683.64 | 16.8364 | 1947.22 | 19.4722 | 1683.61 | 16.8361 | 1947.23 | 19.4723 | 1685.05 | 16.8505 | 1951.8 | 19.518 | 1690.74 | 16.9074 | 2018.57 | 20.1857 | 1684.15 | 16.8415 | 1947.18 | 19.4718
GEN-2024-058 | DIS-24-1 | 04 SOUTHEAST | AEP | 200 | ER/NR | Wind | Farmland - Delaware 138 kV line | 778717 | 1 | 778710 | 2041.86 | 20.4186 | 1683.64 | 16.8364 | 1947.22 | 19.4722 | 1683.61 | 16.8361 | 1947.23 | 19.4723 | 1685.05 | 16.8505 | 1951.8 | 19.518 | 1690.74 | 16.9074 | 2018.57 | 20.1857 | 1684.15 | 16.8415 | 1947.18 | 19.4718
GEN-2024-061 | DIS-24-1 | 03 CENTRAL | WERE | 200 | ER/NR | Battery/Storage | Creswell 138 kV Substation | 778804 | 1 | 532981 | 2672.3 | 13.3615 | 2173.24 | N/A | 2303.9 | N/A | 2172.94 | N/A | 2304.46 | N/A | 2206.78 | N/A | 2336.73 | 11.6837 | 2508.3 | N/A | 2589.99 | N/A | 2179.72 | N/A | 2287.35 | N/A
GEN-2024-062 | DIS-24-1 | 04 SOUTHEAST | WFEC | 230 | ER/NR | Battery/Storage | Dover SW 138 kV Substation | 778834 | 1 | 520882 | 2671.65 | 11.6159 | 2230.84 | N/A | 2339.59 | N/A | 2230.87 | N/A | 2339.59 | N/A | 2232.18 | N/A | 2340.49 | N/A | 2489.23 | N/A | 2662.35 | 11.5754 | 2232.07 | N/A | 2339.64 | N/A
GEN-2024-063 | DIS-24-1 | 05 SOUTHWEST | SPS | 256 | ER/NR | Solar | Plant X 230 kV Substation | 778864 | 1 | 525481 | 9413.71 | 73.5446 | 7128.04 | N/A | 8947.53 | 69.9026 | 7117.65 | N/A | 8947.74 | 69.9042 | 7120.93 | N/A | 8950.17 | 69.9232 | 7143.38 | N/A | 8953.13 | 69.9463 | 7552.74 | N/A | 9318.31 | 72.7993
GEN-2024-063 | DIS-24-1 | 05 SOUTHWEST | SPS | 256 | ER/NR | Solar | Plant X 230 kV Substation | 778867 | 1 | 525481 | 9413.71 | 73.5446 | 7128.04 | N/A | 8947.53 | 69.9026 | 7117.65 | N/A | 8947.74 | 69.9042 | 7120.93 | N/A | 8950.17 | 69.9232 | 7143.38 | N/A | 8953.13 | 69.9463 | 7552.74 | N/A | 9318.31 | 72.7993
GEN-2024-065 | DIS-24-1 | 02 NEBRASKA | NPPD | 150 | ER/NR | Battery/Storage | FREMONT7 115 kV Substation | 778924 | 1 | 640173 | 1336.18 | 8.9079 | 1221.59 | N/A | 1329.39 | N/A | 1226.35 | N/A | 1334.18 | 8.8945 | 1221.25 | N/A | 1328.02 | N/A | 1221.32 | N/A | 1329.23 | N/A | 1221.31 | N/A | 1329.25 | N/A
GEN-2024-067 | DIS-24-1 | 03 CENTRAL | ITCGP | 380 | ER/NR | Solar | Cirrus 345 kV Substation | 778984 | 1 | 539863 | 6411.62 | 33.7454 | 5348.92 | N/A | 5865.67 | 30.8719 | 5396.02 | N/A | 5903.99 | 31.0736 | 5678.5 | N/A | 6186.96 | 32.5629 | 5358.97 | N/A | 5878.1 | 30.9374 | 5354.47 | N/A | 5881.28 | 30.9541
GEN-2024-067 | DIS-24-1 | 03 CENTRAL | ITCGP | 380 | ER/NR | Solar | Cirrus 345 kV Substation | 778987 | 1 | 539863 | 6411.62 | 33.7454 | 5348.92 | N/A | 5865.67 | 30.8719 | 5396.02 | N/A | 5903.99 | 31.0736 | 5678.5 | N/A | 6186.96 | 32.5629 | 5358.97 | N/A | 5878.1 | 30.9374 | 5354.47 | N/A | 5881.28 | 30.9541
GEN-2024-068 | DIS-24-1 | 04 SOUTHEAST | AEP | 300 | ER/NR | Solar | Lydia - Welsh 345 kV Line | 779014 | 1 | 779010 | 8668.11 | 57.7874 | 5357.49 | N/A | 7267.07 | 48.4471 | 5357.5 | N/A | 7267.07 | 48.4471 | 5358.45 | N/A | 7267.35 | 48.449 | 5414.93 | N/A | 7511.25 | 50.075 | 5360.65 | N/A | 7238.83 | 48.2589
GEN-2024-068 | DIS-24-1 | 04 SOUTHEAST | AEP | 300 | ER/NR | Solar | Lydia - Welsh 345 kV Line | 779017 | 1 | 779010 | 8668.11 | 57.7874 | 5357.49 | N/A | 7267.07 | 48.4471 | 5357.5 | N/A | 7267.07 | 48.4471 | 5358.45 | N/A | 7267.35 | 48.449 | 5414.93 | N/A | 7511.25 | 50.075 | 5360.65 | N/A | 7238.83 | 48.2589
GEN-2024-069 | DIS-24-1 | 03 CENTRAL | WERE | 228 | ER/NR | Storage | Franklin 69 kV Substation | 779044 | 1 | 533876 | 1647.08 | 7.1221 | 1599.28 | N/A | 1624.12 | N/A | 1599.63 | N/A | 1624.12 | N/A | 1574.62 | N/A | 1639.72 | 7.0903 | 1546.48 | N/A | 1606.55 | N/A | 1585.34 | N/A | 1624.19 | N/A
GEN-2024-069 | DIS-24-1 | 03 CENTRAL | WERE | 228 | ER/NR | Solar | Franklin 69 kV Substation | 779047 | 1 | 533876 | 1647.08 | 7.0873 | 1599.28 | N/A | 1624.12 | 6.9885 | 1599.63 | N/A | 1624.12 | 6.9885 | 1574.62 | N/A | 1639.72 | 7.0556 | 1546.48 | N/A | 1606.55 | 6.9129 | 1585.34 | N/A | 1624.19 | 6.9888
GEN-2024-071 | DIS-24-1 | 04 SOUTHEAST | AEP | 75 | ER/NR | Solar | West Atlanta - Atlanta 69 kV Line | 779104 | 1 | 779100 | 824.34 | 32.7145 | 786.4 | N/A | 815.05 | 32.3458 | 786.4 | N/A | 815.05 | 32.3458 | 786.42 | N/A | 815.05 | 32.3458 | 786.98 | N/A | 819.71 | 32.5308 | 786.44 | N/A | 814.91 | 32.3403
GEN-2024-071 | DIS-24-1 | 04 SOUTHEAST | AEP | 75 | ER/NR | Storage | West Atlanta - Atlanta 69 kV Line | 779107 | 1 | 779100 | 824.34 | 15.9607 | 786.4 | N/A | 815.05 | N/A | 786.4 | N/A | 815.05 | N/A | 786.42 | N/A | 815.05 | N/A | 786.98 | N/A | 819.71 | 15.8711 | 786.44 | N/A | 814.91 | N/A
GEN-2024-072 | DIS-24-1 | 03 CENTRAL | SUNC | 160 | ER/NR | Solar | Beloit 115 kV Substation | 779134 | 1 | 539650 | 657.98 | 4.1124 | 634.82 | N/A | 654.76 | 4.0922 | 635.26 | N/A | 655.03 | 4.0939 | 637.71 | N/A | 657.77 | 4.1111 | 635.71 | N/A | 655.47 | 4.0967 | 635.18 | N/A | 655.23 | 4.0952
GEN-2024-073 | DIS-24-1 | 05 SOUTHWEST | NEETSW | 500 | ER/NR | Solar | Crossroads - Hobbs 345 kV Substation | 779164 | 1 | 779160 | 8827.67 | 34.1228 | 7431.16 | N/A | 8675.49 | 33.5346 | 7430.01 | N/A | 8679.03 | 33.5482 | 7431.91 | N/A | 8679.34 | 33.5494 | 7453.85 | N/A | 8682.31 | 33.5609 | 7529.74 | N/A | 8541.18 | 33.0154
GEN-2024-073 | DIS-24-1 | 05 SOUTHWEST | NEETSW | 500 | ER/NR | Battery/Storage | Crossroads - Hobbs 345 kV Substation | 779167 | 1 | 779160 | 8827.67 | 30.6202 | 7431.16 | N/A | 8675.49 | N/A | 7430.01 | N/A | 8679.03 | N/A | 7431.91 | N/A | 8679.34 | N/A | 7453.85 | N/A | 8682.31 | N/A | 7529.74 | N/A | 8541.18 | 29.6264
GEN-2024-073 | DIS-24-1 | 05 SOUTHWEST | NEETSW | 500 | ER/NR | Solar | Crossroads - Hobbs 345 kV Substation | 779170 | 1 | 779160 | 8827.67 | 34.1228 | 7431.16 | N/A | 8675.49 | 33.5346 | 7430.01 | N/A | 8679.03 | 33.5482 | 7431.91 | N/A | 8679.34 | 33.5494 | 7453.85 | N/A | 8682.31 | 33.5609 | 7529.74 | N/A | 8541.18 | 33.0154
GEN-2024-073 | DIS-24-1 | 05 SOUTHWEST | NEETSW | 500 | ER/NR | Battery/Storage | Crossroads - Hobbs 345 kV Substation | 779173 | 1 | 779160 | 8827.67 | 30.7477 | 7431.16 | N/A | 8675.49 | N/A | 7430.01 | N/A | 8679.03 | N/A | 7431.91 | N/A | 8679.34 | N/A | 7453.85 | N/A | 8682.31 | N/A | 7529.74 | N/A | 8541.18 | 29.7498
GEN-2024-074 | DIS-24-1 | 03 CENTRAL | WERE | 200 | ER/NR | Battery/Storage | Duncan Road 161 kV Substation | 779194 | 1 | 541235 | 5523.49 | 27.6175 | 4385.6 | N/A | 5325.73 | N/A | 4387.69 | N/A | 5326.27 | N/A | 4414.71 | N/A | 5383.21 | 26.916 | 4385.39 | N/A | 5328.26 | N/A | 4388.37 | N/A | 5326.51 | N/A
GEN-2024-076 | DIS-24-1 | 03 CENTRAL | WERE | 130 | ER/NR | Solar | Neosho - LaCygne 345 kV Line | 779254 | 1 | 779250 | 7120.09 | 54.7699 | 5596.15 | N/A | 6371.08 | 49.0083 | 5597.37 | N/A | 6371.28 | 49.0098 | 5628.07 | N/A | 6895.16 | 53.0397 | 5627.48 | N/A | 6400.83 | 49.2372 | 5605.33 | N/A | 6371.61 | 49.0124
GEN-2024-077 | DIS-24-1 | 05 SOUTHWEST | SPS | 300 | ER/NR | Solar | Pringle 230 kV Substation | 779284 | 1 | 523267 | 1756.42 | 11.7095 | 1636.77 | N/A | 1711.68 | 11.4112 | 1636.68 | N/A | 1711.71 | 11.4114 | 1636.43 | N/A | 1708.65 | 11.391 | 1638.41 | N/A | 1711.44 | 11.4096 | 1687.9 | N/A | 1748.24 | 11.6549
GEN-2024-077 | DIS-24-1 | 05 SOUTHWEST | SPS | 300 | ER/NR | Solar | Pringle 230 kV Substation | 779287 | 1 | 523267 | 1756.42 | 11.7095 | 1636.77 | N/A | 1711.68 | 11.4112 | 1636.68 | N/A | 1711.71 | 11.4114 | 1636.43 | N/A | 1708.65 | 11.391 | 1638.41 | N/A | 1711.44 | 11.4096 | 1687.9 | N/A | 1748.24 | 11.6549
GEN-2024-078 | DIS-24-1 | 05 SOUTHWEST | SPS | 300 | ER/NR | Solar | Pringle 230 kV Substation | 779314 | 1 | 523267 | 1756.42 | 11.7095 | 1636.77 | N/A | 1711.68 | 11.4112 | 1636.68 | N/A | 1711.71 | 11.4114 | 1636.43 | N/A | 1708.65 | 11.391 | 1638.41 | N/A | 1711.44 | 11.4096 | 1687.9 | N/A | 1748.24 | 11.6549
GEN-2024-078 | DIS-24-1 | 05 SOUTHWEST | SPS | 300 | ER/NR | Solar | Pringle 230 kV Substation | 779317 | 1 | 523267 | 1756.42 | 11.7095 | 1636.77 | N/A | 1711.68 | 11.4112 | 1636.68 | N/A | 1711.71 | 11.4114 | 1636.43 | N/A | 1708.65 | 11.391 | 1638.41 | N/A | 1711.44 | 11.4096 | 1687.9 | N/A | 1748.24 | 11.6549
GEN-2024-079 | DIS-24-1 | 05 SOUTHWEST | SPS | 250 | ER/NR | Solar | San Juan 230 kV Substation | 779344 | 1 | 524885 | 1566.69 | 12.5335 | 1468.97 | N/A | 1538.61 | 12.3089 | 1468.79 | N/A | 1538.64 | 12.3091 | 1468.88 | N/A | 1538.68 | 12.3094 | 1469.67 | N/A | 1538.75 | 12.31 | 1468.49 | N/A | 1560.58 | 12.4846
GEN-2024-079 | DIS-24-1 | 05 SOUTHWEST | SPS | 250 | ER/NR | Solar | San Juan 230 kV Substation | 779347 | 1 | 524885 | 1566.69 | 12.5335 | 1468.97 | N/A | 1538.61 | 12.3089 | 1468.79 | N/A | 1538.64 | 12.3091 | 1468.88 | N/A | 1538.68 | 12.3094 | 1469.67 | N/A | 1538.75 | 12.31 | 1468.49 | N/A | 1560.58 | 12.4846
GEN-2024-080 | DIS-24-1 | 05 SOUTHWEST | SPS | 250 | ER/NR | Solar | San Juan 230 kV Substation | 779374 | 1 | 524885 | 1566.69 | 12.5335 | 1468.97 | N/A | 1538.61 | 12.3089 | 1468.79 | N/A | 1538.64 | 12.3091 | 1468.88 | N/A | 1538.68 | 12.3094 | 1469.67 | N/A | 1538.75 | 12.31 | 1468.49 | N/A | 1560.58 | 12.4846
GEN-2024-080 | DIS-24-1 | 05 SOUTHWEST | SPS | 250 | ER/NR | Solar | San Juan 230 kV Substation | 779377 | 1 | 524885 | 1566.69 | 12.5335 | 1468.97 | N/A | 1538.61 | 12.3089 | 1468.79 | N/A | 1538.64 | 12.3091 | 1468.88 | N/A | 1538.68 | 12.3094 | 1469.67 | N/A | 1538.75 | 12.31 | 1468.49 | N/A | 1560.58 | 12.4846
GEN-2024-081 | DIS-24-1 | 01 NORTH | BEPC | 745 | ER | Thermal | Springbrook - Tande 345 kV Line | 779404 | 1 | 779400 | 5228.75 | 11.8131 | 4255.67 | N/A | 5168.68 | N/A | 4020.48 | N/A | 4959.7 | N/A | 4021.46 | N/A | 4953.32 | N/A | 4021.95 | N/A | 4952.24 | N/A | 4020.72 | N/A | 4958.26 | N/A
GEN-2024-081 | DIS-24-1 | 01 NORTH | BEPC | 745 | ER | Thermal | Springbrook - Tande 345 kV Line | 779407 | 1 | 779400 | 5228.75 | 17.2921 | 4255.67 | N/A | 5168.68 | N/A | 4020.48 | N/A | 4959.7 | N/A | 4021.46 | N/A | 4953.32 | N/A | 4021.95 | N/A | 4952.24 | N/A | 4020.72 | N/A | 4958.26 | N/A
GEN-2024-082 | DIS-24-1 | 01 NORTH | BEPC | 745 | ER | Thermal | Springbrook - Tande 345 kV Line | 779434 | 1 | 779400 | 5228.75 | 12.2167 | 4255.67 | N/A | 5168.68 | N/A | 4020.48 | N/A | 4959.7 | N/A | 4021.46 | N/A | 4953.32 | N/A | 4021.95 | N/A | 4952.24 | N/A | 4020.72 | N/A | 4958.26 | N/A
GEN-2024-082 | DIS-24-1 | 01 NORTH | BEPC | 745 | ER | Thermal | Springbrook - Tande 345 kV Line | 779437 | 1 | 779400 | 5228.75 | 16.4945 | 4255.67 | N/A | 5168.68 | N/A | 4020.48 | N/A | 4959.7 | N/A | 4021.46 | N/A | 4953.32 | N/A | 4021.95 | N/A | 4952.24 | N/A | 4020.72 | N/A | 4958.26 | N/A
GEN-2024-083 | DIS-24-1 | 04 SOUTHEAST | ITCGP | 250 | ER/NR | Solar | Hugo 345 kV Substation | 779464 | 1 | 521157 | 7599.69 | 60.7975 | 4764.52 | N/A | 6305.83 | 50.4466 | 4764.55 | N/A | 6305.82 | 50.4466 | 4765.88 | N/A | 6306.36 | 50.4509 | 4900.76 | N/A | 6690.3 | 53.5224 | 4770.7 | N/A | 6301.49 | 50.4119
GEN-2024-083 | DIS-24-1 | 04 SOUTHEAST | ITCGP | 250 | ER/NR | Solar | Hugo 345 kV Substation | 779467 | 1 | 521157 | 7599.69 | 60.7975 | 4764.52 | N/A | 6305.83 | 50.4466 | 4764.55 | N/A | 6305.82 | 50.4466 | 4765.88 | N/A | 6306.36 | 50.4509 | 4900.76 | N/A | 6690.3 | 53.5224 | 4770.7 | N/A | 6301.49 | 50.4119
GEN-2024-084 | DIS-24-1 | 03 CENTRAL | EMDE | 167 | ER/NR | Battery/Storage | Reeds Spring - Aurora 161 kV Line | 779494 | 1 | 779490 | 2727.84 | 16.3344 | 2420.75 | N/A | 2683.07 | N/A | 2420.83 | N/A | 2683.08 | N/A | 2420.88 | N/A | 2695.19 | 16.1389 | 2419.45 | N/A | 2687.16 | N/A | 2420.06 | N/A | 2682.94 | N/A
GEN-2024-085 | DIS-24-1 | 03 CENTRAL | SUNC | 160 | ER/NR | Solar | Otis 115 kV Substation | 779524 | 1 | 539684 | 597.87 | 3.7367 | 554.98 | N/A | 588.89 | 3.6806 | 555.15 | N/A | 588.99 | 3.6812 | 557.72 | N/A | 596.24 | 3.7265 | 554.9 | N/A | 589.2 | 3.6825 | 555 | N/A | 589.13 | 3.6821
GEN-2024-088 | DIS-24-1 | 03 CENTRAL | SPRM | 145 | ER/NR | Thermal | McCartney 161 kV Substation | 779614 | 1 | 549968 | 4142.51 | 85.7077 | 3173.82 | N/A | 4123.36 | N/A | 3174.34 | N/A | 4123.37 | N/A | 3171.46 | N/A | 4135.02 | N/A | 3165.16 | N/A | 4124.47 | N/A | 3169.6 | N/A | 4125.09 | N/A
GEN-2024-088 | DIS-24-1 | 03 CENTRAL | SPRM | 145 | ER/NR | Thermal | McCartney 161 kV Substation | 779617 | 1 | 549968 | 4142.51 | 85.7077 | 3173.82 | N/A | 4123.36 | N/A | 3174.34 | N/A | 4123.37 | N/A | 3171.46 | N/A | 4135.02 | N/A | 3165.16 | N/A | 4124.47 | N/A | 3169.6 | N/A | 4125.09 | N/A
GEN-2024-088 | DIS-24-1 | 03 CENTRAL | SPRM | 145 | ER/NR | Thermal | McCartney 161 kV Substation | 779620 | 1 | 549968 | 4142.51 | 85.7077 | 3173.82 | N/A | 4123.36 | N/A | 3174.34 | N/A | 4123.37 | N/A | 3171.46 | N/A | 4135.02 | N/A | 3165.16 | N/A | 4124.47 | N/A | 3169.6 | N/A | 4125.09 | N/A
GEN-2024-089 | DIS-24-1 | 05 SOUTHWEST | SPS | 195 | ER | Wind | Pleasant Hills 230 kV Substation | 779644 | 1 | 524770 | 2498.35 | 21.9229 | 2127.59 | 18.6695 | 2380.58 | 20.8894 | 2126.92 | 18.6636 | 2380.6 | 20.8896 | 2127.15 | 18.6656 | 2380.74 | 20.8908 | 2129.17 | 18.6833 | 2380.92 | 20.8924 | 2173.7 | 19.0741 | 2490.15 | 21.8509
GEN-2024-089 | DIS-24-1 | 05 SOUTHWEST | SPS | 195 | ER | Wind | Pleasant Hills 230 kV Substation | 779647 | 1 | 524770 | 2498.35 | 30.829 | 2127.59 | 26.2539 | 2380.58 | 29.3757 | 2126.92 | 26.2456 | 2380.6 | 29.376 | 2127.15 | 26.2485 | 2380.74 | 29.3777 | 2129.17 | 26.2734 | 2380.92 | 29.3799 | 2173.7 | 26.8229 | 2490.15 | 30.7278
GEN-2024-090 | DIS-24-1 | 03 CENTRAL | WERE | 100 | ER/NR | Battery/Storage | Smithville 161 kV Substation | 779674 | 1 | 541204 | 6925.61 | 69.2561 | 5322.72 | N/A | 6585.85 | N/A | 5328.11 | N/A | 6588.29 | N/A | 5406.35 | N/A | 6656.28 | 66.5628 | 5329.34 | N/A | 6591.58 | N/A | 5330.64 | N/A | 6588.02 | N/A
GEN-2024-091 | DIS-24-1 | 03 CENTRAL | EDE | 100 | ER/NR | Battery/Storage | 145 JOPLIN WEST 7TH 161 kV Substation | 779704 | 1 | 547470 | 5553.42 | 55.5342 | 3369.46 | N/A | 5349.83 | N/A | 3370.5 | N/A | 5349.84 | N/A | 3365.48 | N/A | 5430.9 | 54.309 | 3356.34 | N/A | 5350.41 | N/A | 3366.08 | N/A | 5349.13 | N/A
GEN-2024-092 | DIS-24-1 | 05 SOUTHWEST | SPS | 199.5 | ER/NR | Battery/Storage | Portales 115 kV Substation | 779734 | 1 | 524924 | 1447.73 | 7.2568 | 1388.53 | N/A | 1402.09 | N/A | 1388.24 | N/A | 1402.1 | N/A | 1388.34 | N/A | 1402.15 | N/A | 1389.22 | N/A | 1402.21 | N/A | 1379.36 | N/A | 1428.09 | 7.1583
GEN-2024-099 | DIS-24-1 | 05 SOUTHWEST | SPS | 300 | ER/NR | Solar | Newhart 230 kV Substation | 779944 | 1 | 525461 | 4482.05 | 29.8803 | 3778.58 | N/A | 4250.57 | 28.3371 | 3771.03 | N/A | 4250.65 | 28.3377 | 3772.95 | N/A | 4251.69 | 28.3446 | 3781.37 | N/A | 4252.82 | 28.3521 | 4005.75 | N/A | 4454.56 | 29.6971
GEN-2024-099 | DIS-24-1 | 05 SOUTHWEST | SPS | 300 | ER/NR | Solar | Newhart 230 kV Substation | 779947 | 1 | 525461 | 4482.05 | 29.8803 | 3778.58 | N/A | 4250.57 | 28.3371 | 3771.03 | N/A | 4250.65 | 28.3377 | 3772.95 | N/A | 4251.69 | 28.3446 | 3781.37 | N/A | 4252.82 | 28.3521 | 4005.75 | N/A | 4454.56 | 29.6971
GEN-2024-102 | DIS-24-1 | 03 CENTRAL | SUNC | 400.5 | ER/NR | Wind | Holcomb 345 kV Substation | 780034 | 1 | 531449 | 7776.12 | 57.6009 | 5890.77 | 43.6353 | 6439.94 | 47.7033 | 5899.46 | 43.6997 | 6446.91 | 47.7549 | 6627.46 | 49.0923 | 7494.07 | 55.5116 | 5915.59 | 43.8192 | 6459.34 | 47.847 | 6013.51 | 44.5445 | 6434.31 | 47.6616
GEN-2024-102 | DIS-24-1 | 03 CENTRAL | SUNC | 400.5 | ER/NR | Wind | Holcomb 345 kV Substation | 780037 | 1 | 531449 | 7776.12 | 57.6009 | 5890.77 | 43.6353 | 6439.94 | 47.7033 | 5899.46 | 43.6997 | 6446.91 | 47.7549 | 6627.46 | 49.0923 | 7494.07 | 55.5116 | 5915.59 | 43.8192 | 6459.34 | 47.847 | 6013.51 | 44.5445 | 6434.31 | 47.6616
GEN-2024-102 | DIS-24-1 | 03 CENTRAL | SUNC | 400.5 | ER/NR | Wind | Holcomb 345 kV Substation | 780040 | 1 | 531449 | 7776.12 | 59.5871 | 5890.77 | 45.14 | 6439.94 | 49.3482 | 5899.46 | 45.2066 | 6446.91 | 49.4016 | 6627.46 | 50.7851 | 7494.07 | 57.4258 | 5915.59 | 45.3302 | 6459.34 | 49.4969 | 6013.51 | 46.0805 | 6434.31 | 49.3051
GEN-2024-109 | DIS-24-1 | 05 SOUTHWEST | SPS | 400.5 | ER/NR | Wind | Tolk - Crossroads 345 kV line | 780244 | 1 | 780240 | 7843.49 | 58.0999 | 6842.25 | 50.6833 | 7623.22 | 56.4683 | 6839.04 | 50.6596 | 7623.32 | 56.469 | 6841.5 | 50.6778 | 7626.27 | 56.4909 | 6859.13 | 50.8084 | 7629.45 | 56.5144 | 7064.13 | 52.3269 | 7740.81 | 57.3393
GEN-2024-109 | DIS-24-1 | 05 SOUTHWEST | SPS | 400.5 | ER/NR | Wind | Tolk - Crossroads 345 kV line | 780247 | 1 | 780240 | 7843.49 | 58.0999 | 6842.25 | 50.6833 | 7623.22 | 56.4683 | 6839.04 | 50.6596 | 7623.32 | 56.469 | 6841.5 | 50.6778 | 7626.27 | 56.4909 | 6859.13 | 50.8084 | 7629.45 | 56.5144 | 7064.13 | 52.3269 | 7740.81 | 57.3393
GEN-2024-109 | DIS-24-1 | 05 SOUTHWEST | SPS | 400.5 | ER/NR | Wind | Tolk - Crossroads 345 kV line | 780250 | 1 | 780240 | 7843.49 | 60.1034 | 6842.25 | 52.431 | 7623.22 | 58.4155 | 6839.04 | 52.4064 | 7623.32 | 58.4162 | 6841.5 | 52.4253 | 7626.27 | 58.4389 | 6859.13 | 52.5604 | 7629.45 | 58.4632 | 7064.13 | 54.1313 | 7740.81 | 59.3166
GEN-2024-113 | DIS-24-1 | 04 SOUTHEAST | OGE | 300 | ER/NR | Solar | Muskogee - Ft. Smith 345 kV Line | 780364 | 1 | 780360 | 7593.86 | 24.9954 | 6269.84 | N/A | 6702.15 | 22.0603 | 6269.87 | N/A | 6702.15 | 22.0603 | 6271.62 | N/A | 6702.78 | 22.0624 | 6292.95 | N/A | 6783.3 | 22.3274 | 6271.36 | N/A | 6702.18 | 22.0604
GEN-2024-113 | DIS-24-1 | 04 SOUTHEAST | OGE | 300 | ER/NR | Storage | Muskogee - Ft. Smith 345 kV Line | 780366 | 1 | 780360 | 7593.86 | 107.4765 | 6269.84 | N/A | 6702.15 | N/A | 6269.87 | N/A | 6702.15 | N/A | 6271.62 | N/A | 6702.78 | N/A | 6292.95 | N/A | 6783.3 | 96.0046 | 6271.36 | N/A | 6702.18 | N/A
GEN-2024-114 | DIS-24-1 | 04 SOUTHEAST | SWPA | 199 | ER/NR | Solar | Jonesboro - Independence County 161 kV Line | 780394 | 1 | 780390 | 1648.97 | 8.1823 | 1532.62 | N/A | 1588.67 | 7.8831 | 1532.62 | N/A | 1588.67 | 7.8831 | 1532.62 | N/A | 1588.68 | 7.8832 | 1532.3 | N/A | 1648.85 | 8.1817 | 1532.61 | N/A | 1588.67 | 7.8831
GEN-2024-114 | DIS-24-1 | 04 SOUTHEAST | SWPA | 199 | ER/NR | Battery/Storage | Jonesboro - Independence County 161 kV Line | 780397 | 1 | 780390 | 1648.97 | 32.6348 | 1532.62 | N/A | 1588.67 | N/A | 1532.62 | N/A | 1588.67 | N/A | 1532.62 | N/A | 1588.68 | N/A | 1532.3 | N/A | 1648.85 | 32.6324 | 1532.61 | N/A | 1588.67 | N/A
GEN-2024-117 | DIS-24-1 | 04 SOUTHEAST | AEP | 150 | ER/NR | Solar | Coffeyville Tap - North Bartlesville 138kV Line | 780484 | 1 | 780480 | 2227.91 | 14.6625 | 2013.46 | N/A | 2202.78 | 14.4971 | 2013.34 | N/A | 2202.78 | 14.4971 | 2015.17 | N/A | 2208.67 | 14.5359 | 2020.22 | N/A | 2214.14 | 14.5719 | 2014.03 | N/A | 2202.69 | 14.4965
GEN-2024-117 | DIS-24-1 | 04 SOUTHEAST | AEP | 150 | ER/NR | Battery/Storage | Coffeyville Tap - North Bartlesville 138kV Line | 780487 | 1 | 780480 | 2227.91 | 55.1408 | 2013.46 | N/A | 2202.78 | N/A | 2013.34 | N/A | 2202.78 | N/A | 2015.17 | N/A | 2208.67 | N/A | 2020.22 | N/A | 2214.14 | 54.8 | 2014.03 | N/A | 2202.69 | N/A
GEN-2024-118 | DIS-24-1 | 04 SOUTHEAST | AEP | 199 | ER/NR | Battery/Storage | East 11th Street 138kV Substation | 780514 | 1 | 509804 | 7689.74 | 38.6419 | 6499.12 | N/A | 7493.9 | N/A | 6499.29 | N/A | 7493.84 | N/A | 6507.5 | N/A | 7499.91 | N/A | 6549.5 | N/A | 7594.83 | 38.165 | 6502.03 | N/A | 7493.94 | N/A
GEN-2024-119 | DIS-24-1 | 04 SOUTHEAST | WFEC | 199 | ER/NR | Battery/Storage | Lexington 138 kV Substation | 780544 | 1 | 520973 | 1794.55 | 9.0178 | 1691.79 | N/A | 1762.21 | N/A | 1691.8 | N/A | 1762.21 | N/A | 1692.09 | N/A | 1762.36 | N/A | 1706.18 | N/A | 1776.58 | 8.9275 | 1693.05 | N/A | 1762.21 | N/A
GEN-2024-120 | DIS-24-1 | 04 SOUTHEAST | OGE | 199 | ER/NR | Battery/Storage | JNS KAMO 138 kV Substation | 780574 | 1 | 514906 | 5050.63 | 25.3801 | 4232.3 | N/A | 4916.93 | N/A | 4232.37 | N/A | 4916.92 | N/A | 4239.93 | N/A | 4920.12 | N/A | 4325.57 | N/A | 4959.48 | 24.922 | 4240.44 | N/A | 4919.03 | N/A
GEN-2024-121 | DIS-24-1 | 03 CENTRAL | WERE | 199 | ER/NR | Battery/Storage | Jarbalo 115 kV Substation | 780604 | 1 | 533244 | 5318.72 | 26.7272 | 4548.24 | N/A | 5217.54 | N/A | 4552.05 | N/A | 5219.29 | N/A | 4607.7 | N/A | 5279.49 | 26.5301 | 4529.6 | N/A | 5210.67 | N/A | 4547.27 | N/A | 5217.67 | N/A
GEN-2024-122 | DIS-24-1 | 04 SOUTHEAST | AEP | 160 | ER/NR | Solar | Lieberman - IPC Jefferson 138 kV Line | 780634 | 1 | 780630 | 2446.26 | 13.7693 | 2202.79 | N/A | 2359.89 | 13.2832 | 2202.79 | N/A | 2359.89 | 13.2832 | 2202.9 | N/A | 2359.92 | 13.2833 | 2205.39 | N/A | 2390.07 | 13.4531 | 2203.04 | N/A | 2359.31 | 13.2799
GEN-2024-122 | DIS-24-1 | 04 SOUTHEAST | AEP | 160 | ER/NR | Battery/Storage | Lieberman - IPC Jefferson 138 kV Line | 780637 | 1 | 780630 | 2446.26 | 12.4937 | 2202.79 | N/A | 2359.89 | N/A | 2202.79 | N/A | 2359.89 | N/A | 2202.9 | N/A | 2359.92 | N/A | 2205.39 | N/A | 2390.07 | 12.2067 | 2203.04 | N/A | 2359.31 | N/A
GEN-2024-123 | DIS-24-1 | 04 SOUTHEAST | AEP | 120 | ER/NR | Solar | Center - Tenaha 138 kV Line | 780664 | 1 | 780660 | 1917.96 | 31.966 | 1715.1 | N/A | 1874.11 | 31.2352 | 1715.1 | N/A | 1874.11 | 31.2352 | 1715.14 | N/A | 1874.13 | 31.2355 | 1716.13 | N/A | 1884.82 | 31.4137 | 1715.2 | N/A | 1873.92 | 31.232
GEN-2024-123 | DIS-24-1 | 04 SOUTHEAST | AEP | 120 | ER/NR | Solar | Center - Tenaha 138 kV Line | 780667 | 1 | 780660 | 1917.96 | 31.966 | 1715.1 | N/A | 1874.11 | 31.2352 | 1715.1 | N/A | 1874.11 | 31.2352 | 1715.14 | N/A | 1874.13 | 31.2355 | 1716.13 | N/A | 1884.82 | 31.4137 | 1715.2 | N/A | 1873.92 | 31.232
GEN-2024-124 | DIS-24-1 | 05 SOUTHWEST | NEETSW | 420 | ER/NR | Solar | Crossroads-Hobbs-Roadrunner 345 kV Line | 780694 | 1 | 780690 | 8254.22 | 56.6444 | 6991.5 | N/A | 8120.5 | 55.7267 | 6990.51 | N/A | 8123.91 | 55.7501 | 6992.27 | N/A | 8123.87 | 55.7499 | 7011.43 | N/A | 8126.27 | 55.7663 | 7076.38 | N/A | 7999.29 | 54.8949
GEN-2024-124 | DIS-24-1 | 05 SOUTHWEST | NEETSW | 420 | ER/NR | Solar | Crossroads-Hobbs-Roadrunner 345 kV Line | 780697 | 1 | 780690 | 8254.22 | 58.1353 | 6991.5 | N/A | 8120.5 | 57.1935 | 6990.51 | N/A | 8123.91 | 57.2175 | 6992.27 | N/A | 8123.87 | 57.2172 | 7011.43 | N/A | 8126.27 | 57.2341 | 7076.38 | N/A | 7999.29 | 56.3398
GEN-2024-124 | DIS-24-1 | 05 SOUTHWEST | NEETSW | 420 | ER/NR | Battery/Storage | Crossroads-Hobbs-Roadrunner 345 kV Line | 780700 | 1 | 780690 | 8254.22 | 56.0231 | 6991.5 | N/A | 8120.5 | N/A | 6990.51 | N/A | 8123.91 | N/A | 6992.27 | N/A | 8123.87 | N/A | 7011.43 | N/A | 8126.27 | N/A | 7076.38 | N/A | 7999.29 | 54.2928
GEN-2024-125 | DIS-24-1 | 03 CENTRAL | WERE | 400 | ER/NR | Solar | Neosho Ridge - Caney River 345 kV Line | 780724 | 1 | 780720 | 6176.56 | 30.8828 | 4969.3 | N/A | 5054.81 | 25.274 | 4969.83 | N/A | 5055.32 | 25.2766 | 5014.77 | N/A | 5239.35 | 26.1968 | 5010.73 | N/A | 5101.02 | 25.5051 | 4981.44 | N/A | 5060.31 | 25.3015
GEN-2024-125 | DIS-24-1 | 03 CENTRAL | WERE | 400 | ER/NR | Solar | Neosho Ridge - Caney River 345 kV Line | 780727 | 1 | 780720 | 6176.56 | 30.8828 | 4969.3 | N/A | 5054.81 | 25.274 | 4969.83 | N/A | 5055.32 | 25.2766 | 5014.77 | N/A | 5239.35 | 26.1968 | 5010.73 | N/A | 5101.02 | 25.5051 | 4981.44 | N/A | 5060.31 | 25.3015
GEN-2024-128 | DIS-24-1 | 04 SOUTHEAST | OGE | 690 | ER/NR | Thermal | Gracemont - Lawton 345 kV Line | 780814 | 1 | 780810 | 10417.9 | 45.2952 | 7836.42 | N/A | 9315.67 | N/A | 7836.53 | N/A | 9315.93 | N/A | 7845.1 | N/A | 9326.14 | N/A | 8555.59 | N/A | 10121.21 | N/A | 7934.86 | N/A | 9306.72 | N/A
GEN-2024-128 | DIS-24-1 | 04 SOUTHEAST | OGE | 690 | ER/NR | Thermal | Gracemont - Lawton 345 kV Line | 780817 | 1 | 780810 | 10417.9 | 45.2952 | 7836.42 | N/A | 9315.67 | N/A | 7836.53 | N/A | 9315.93 | N/A | 7845.1 | N/A | 9326.14 | N/A | 8555.59 | N/A | 10121.21 | N/A | 7934.86 | N/A | 9306.72 | N/A
GEN-2024-128 | DIS-24-1 | 04 SOUTHEAST | OGE | 690 | ER/NR | Thermal | Gracemont - Lawton 345 kV Line | 780820 | 1 | 780810 | 10417.9 | 45.2952 | 7836.42 | N/A | 9315.67 | N/A | 7836.53 | N/A | 9315.93 | N/A | 7845.1 | N/A | 9326.14 | N/A | 8555.59 | N/A | 10121.21 | N/A | 7934.86 | N/A | 9306.72 | N/A
GEN-2024-129 | DIS-24-1 | 03 CENTRAL | WERE | 910 | ER/NR | Thermal | Caney River - Neosho 345 kV Line | 780844 | 1 | 780840 | 5878.92 | 25.8414 | 5436.01 | N/A | 5663.07 | N/A | 5436.64 | N/A | 5663.41 | N/A | 5475.73 | N/A | 5811.23 | N/A | 5486.14 | N/A | 5712.97 | N/A | 5449.53 | N/A | 5665.9 | N/A
GEN-2024-129 | DIS-24-1 | 03 CENTRAL | WERE | 910 | ER/NR | Thermal | Caney River - Neosho 345 kV Line | 780847 | 1 | 780840 | 5878.92 | 25.8414 | 5436.01 | N/A | 5663.07 | N/A | 5436.64 | N/A | 5663.41 | N/A | 5475.73 | N/A | 5811.23 | N/A | 5486.14 | N/A | 5712.97 | N/A | 5449.53 | N/A | 5665.9 | N/A
GEN-2024-129 | DIS-24-1 | 03 CENTRAL | WERE | 910 | ER/NR | Thermal | Caney River - Neosho 345 kV Line | 780850 | 1 | 780840 | 5878.92 | 25.8414 | 5436.01 | N/A | 5663.07 | N/A | 5436.64 | N/A | 5663.41 | N/A | 5475.73 | N/A | 5811.23 | N/A | 5486.14 | N/A | 5712.97 | N/A | 5449.53 | N/A | 5665.9 | N/A
GEN-2024-129 | DIS-24-1 | 03 CENTRAL | WERE | 910 | ER/NR | Thermal | Caney River - Neosho 345 kV Line | 780853 | 1 | 780840 | 5878.92 | 25.8414 | 5436.01 | N/A | 5663.07 | N/A | 5436.64 | N/A | 5663.41 | N/A | 5475.73 | N/A | 5811.23 | N/A | 5486.14 | N/A | 5712.97 | N/A | 5449.53 | N/A | 5665.9 | N/A
GEN-2024-132 | DIS-24-1 | 04 SOUTHEAST | OGE | 1300 | ER/NR | Thermal | Hugo (71 miles) - Sunnyside (42 miles) 345 kV Line | 780934 | 1 | 560088 | 4513.31 | 10.9225 | 3419.26 | N/A | 3829.75 | N/A | 3419.28 | N/A | 3829.74 | N/A | 3420.19 | N/A | 3830.3 | N/A | 3582.8 | N/A | 4278.01 | N/A | 3426.67 | N/A | 3829.71 | N/A
GEN-2024-132 | DIS-24-1 | 04 SOUTHEAST | OGE | 1300 | ER/NR | Thermal | Hugo (71 miles) - Sunnyside (42 miles) 345 kV Line | 780937 | 1 | 560088 | 4513.31 | 10.9225 | 3419.26 | N/A | 3829.75 | N/A | 3419.28 | N/A | 3829.74 | N/A | 3420.19 | N/A | 3830.3 | N/A | 3582.8 | N/A | 4278.01 | N/A | 3426.67 | N/A | 3829.71 | N/A
GEN-2024-132 | DIS-24-1 | 04 SOUTHEAST | OGE | 1300 | ER/NR | Thermal | Hugo (71 miles) - Sunnyside (42 miles) 345 kV Line | 780940 | 1 | 560088 | 4513.31 | 19.0607 | 3419.26 | N/A | 3829.75 | N/A | 3419.28 | N/A | 3829.74 | N/A | 3420.19 | N/A | 3830.3 | N/A | 3582.8 | N/A | 4278.01 | N/A | 3426.67 | N/A | 3829.71 | N/A
GEN-2024-132 | DIS-24-1 | 04 SOUTHEAST | OGE | 1300 | ER/NR | Thermal | Hugo (71 miles) - Sunnyside (42 miles) 345 kV Line | 780943 | 1 | 560088 | 4513.31 | 19.0607 | 3419.26 | N/A | 3829.75 | N/A | 3419.28 | N/A | 3829.74 | N/A | 3420.19 | N/A | 3830.3 | N/A | 3582.8 | N/A | 4278.01 | N/A | 3426.67 | N/A | 3829.71 | N/A
GEN-2024-134 | DIS-24-1 | 04 SOUTHEAST | OGE | 250 | ER/NR | Wind | Degrasse 345 kV Substation | 780994 | 1 | 515852 | 10141.45 | 80.2305 | 8292.85 | 65.6059 | 8677.8 | 68.6513 | 8295.55 | 65.6273 | 8680.41 | 68.672 | 8441.12 | 66.7789 | 9004.97 | 71.2396 | 8532.68 | 67.5032 | 9615.12 | 76.0666 | 8359.88 | 66.1362 | 8695.98 | 68.7951
GEN-2024-134 | DIS-24-1 | 04 SOUTHEAST | OGE | 250 | ER/NR | Wind | Degrasse 345 kV Substation | 780997 | 1 | 515852 | 10141.45 | 82.0532 | 8292.85 | 67.0964 | 8677.8 | 70.211 | 8295.55 | 67.1183 | 8680.41 | 70.2321 | 8441.12 | 68.2961 | 9004.97 | 72.8581 | 8532.68 | 69.0369 | 9615.12 | 77.7948 | 8359.88 | 67.6388 | 8695.98 | 70.3581
GEN-2024-135 | DIS-24-1 | 04 SOUTHEAST | OGE | 250 | ER/NR | Wind | Degrasse 345 kV Substation | 781024 | 1 | 515852 | 10141.45 | 80.2305 | 8292.85 | 65.6059 | 8677.8 | 68.6513 | 8295.55 | 65.6273 | 8680.41 | 68.672 | 8441.12 | 66.7789 | 9004.97 | 71.2396 | 8532.68 | 67.5032 | 9615.12 | 76.0666 | 8359.88 | 66.1362 | 8695.98 | 68.7951
GEN-2024-135 | DIS-24-1 | 04 SOUTHEAST | OGE | 250 | ER/NR | Wind | Degrasse 345 kV Substation | 781027 | 1 | 515852 | 10141.45 | 82.0532 | 8292.85 | 67.0964 | 8677.8 | 70.211 | 8295.55 | 67.1183 | 8680.41 | 70.2321 | 8441.12 | 68.2961 | 9004.97 | 72.8581 | 8532.68 | 69.0369 | 9615.12 | 77.7948 | 8359.88 | 67.6388 | 8695.98 | 70.3581
GEN-2024-136 | DIS-24-1 | 03 CENTRAL | SUNC | 400 | ER/NR | Solar | Setab 345 kV Substation | 781054 | 1 | 531465 | 4759.37 | 23.7968 | 3750.1 | N/A | 4037.62 | 20.1881 | 3757.8 | N/A | 4043.58 | 20.2179 | 4279.38 | N/A | 4645.39 | 23.2269 | 3757.57 | N/A | 4028.36 | 20.1418 | 3789.62 | N/A | 3970.99 | 19.8549
GEN-2024-136 | DIS-24-1 | 03 CENTRAL | SUNC | 400 | ER/NR | Solar | Setab 345 kV Substation | 781057 | 1 | 531465 | 4759.37 | 23.7968 | 3750.1 | N/A | 4037.62 | 20.1881 | 3757.8 | N/A | 4043.58 | 20.2179 | 4279.38 | N/A | 4645.39 | 23.2269 | 3757.57 | N/A | 4028.36 | 20.1418 | 3789.62 | N/A | 3970.99 | 19.8549
GEN-2024-137 | DIS-24-1 | 03 CENTRAL | SUNC | 300 | ER/NR | Wind | Setab 345 kV Substation | 781084 | 1 | 531465 | 4759.37 | 31.8063 | 3750.1 | 25.0615 | 4037.62 | 26.9829 | 3757.8 | 25.1129 | 4043.58 | 27.0228 | 4279.38 | 28.5986 | 4645.39 | 31.0446 | 3757.57 | 25.1114 | 4028.36 | 26.9211 | 3789.62 | 25.3256 | 3970.99 | 26.5377
GEN-2024-137 | DIS-24-1 | 03 CENTRAL | SUNC | 300 | ER/NR | Wind | Setab 345 kV Substation | 781087 | 1 | 531465 | 4759.37 | 32.4066 | 3750.1 | 25.5345 | 4037.62 | 27.4922 | 3757.8 | 25.5869 | 4043.58 | 27.5328 | 4279.38 | 29.1384 | 4645.39 | 31.6306 | 3757.57 | 25.5854 | 4028.36 | 27.4292 | 3789.62 | 25.8036 | 3970.99 | 27.0386
GEN-2024-138 | DIS-24-1 | 03 CENTRAL | SUNC | 300 | ER/NR | Wind | Setab 345 kV Substation | 781114 | 1 | 531465 | 4759.37 | 31.8063 | 3750.1 | 25.0615 | 4037.62 | 26.9829 | 3757.8 | 25.1129 | 4043.58 | 27.0228 | 4279.38 | 28.5986 | 4645.39 | 31.0446 | 3757.57 | 25.1114 | 4028.36 | 26.9211 | 3789.62 | 25.3256 | 3970.99 | 26.5377
GEN-2024-138 | DIS-24-1 | 03 CENTRAL | SUNC | 300 | ER/NR | Wind | Setab 345 kV Substation | 781117 | 1 | 531465 | 4759.37 | 32.4066 | 3750.1 | 25.5345 | 4037.62 | 27.4922 | 3757.8 | 25.5869 | 4043.58 | 27.5328 | 4279.38 | 29.1384 | 4645.39 | 31.6306 | 3757.57 | 25.5854 | 4028.36 | 27.4292 | 3789.62 | 25.8036 | 3970.99 | 27.0386
GEN-2024-139 | DIS-24-1 | 03 CENTRAL | NEETSW | 250 | ER/NR | Solar | Wolf Creek - Blackberry 345 kV Line | 781144 | 1 | 781140 | 11370.25 | 91.0523 | 9838.09 | N/A | 10896.45 | 87.2582 | 9841.59 | N/A | 10897.82 | 87.2691 | 9969.61 | N/A | 11240.05 | 90.0097 | 9885.95 | N/A | 10952.55 | 87.7074 | 9860.38 | N/A | 10905.7 | 87.3322
GEN-2024-139 | DIS-24-1 | 03 CENTRAL | NEETSW | 250 | ER/NR | Solar | Wolf Creek - Blackberry 345 kV Line | 781147 | 1 | 781140 | 11370.25 | 93.8108 | 9838.09 | N/A | 10896.45 | 89.9017 | 9841.59 | N/A | 10897.82 | 89.913 | 9969.61 | N/A | 11240.05 | 92.7366 | 9885.95 | N/A | 10952.55 | 90.3646 | 9860.38 | N/A | 10905.7 | 89.978
GEN-2024-140 | DIS-24-1 | 02 NEBRASKA | NPPD | 250 | ER/NR | Solar | Antelope - Hoskins 345 kV line | 781174 | 1 | 763443 | 7027.04 | 56.3588 | 5647.81 | N/A | 6044.82 | 48.4811 | 6428.78 | N/A | 6971.13 | 55.9104 | 5651.97 | N/A | 6095.71 | 48.8893 | 5638.65 | N/A | 6037.53 | 48.4227 | 5636.73 | N/A | 6032.43 | 48.3817
GEN-2024-140 | DIS-24-1 | 02 NEBRASKA | NPPD | 250 | ER/NR | Solar | Antelope - Hoskins 345 kV line | 781177 | 1 | 763443 | 7027.04 | 58.067 | 5647.81 | N/A | 6044.82 | 49.9506 | 6428.78 | N/A | 6971.13 | 57.605 | 5651.97 | N/A | 6095.71 | 50.3711 | 5638.65 | N/A | 6037.53 | 49.8903 | 5636.73 | N/A | 6032.43 | 49.8482
GEN-2024-141 | DIS-24-1 | 01 NORTH | BEPC | 424 | ER/NR | Wind | BASIN__-BE4 230 kV Substation | 781204 | 1 | 659199 | 8423.07 | 39.4708 | 7774.65 | 36.4323 | 8293.62 | 38.8642 | 7265.61 | 34.0469 | 7795.64 | 36.5307 | 7264.11 | 34.0399 | 7790.52 | 36.5067 | 7264.22 | 34.0404 | 7790.32 | 36.5057 | 7264.37 | 34.0411 | 7797.01 | 36.5371
GEN-2024-141 | DIS-24-1 | 01 NORTH | BEPC | 424 | ER/NR | Wind | BASIN__-BE4 230 kV Substation | 781207 | 1 | 659199 | 8423.07 | 39.9956 | 7774.65 | 36.9167 | 8293.62 | 39.3809 | 7265.61 | 34.4996 | 7795.64 | 37.0163 | 7264.11 | 34.4925 | 7790.52 | 36.992 | 7264.22 | 34.493 | 7790.32 | 36.9911 | 7264.37 | 34.4937 | 7797.01 | 37.0228
GEN-2024-142 | DIS-24-1 | 03 CENTRAL | WERE | 300 | ER/NR | Wind | Reno - Summit 345 kV Line | 781234 | 1 | 532998 | 7546.15 | 50.5104 | 6141.39 | 41.1076 | 6901.47 | 46.1952 | 6158.23 | 41.2203 | 6914.05 | 46.2794 | 6637.11 | 44.4257 | 7453.27 | 49.8887 | 6193.41 | 41.4558 | 6965.74 | 46.6254 | 6165.78 | 41.2708 | 6976.85 | 46.6998
GEN-2024-142 | DIS-24-1 | 03 CENTRAL | WERE | 300 | ER/NR | Wind | Reno - Summit 345 kV Line | 781237 | 1 | 532998 | 7546.15 | 51.4632 | 6141.39 | 41.883 | 6901.47 | 47.0666 | 6158.23 | 41.9979 | 6914.05 | 47.1524 | 6637.11 | 45.2637 | 7453.27 | 50.8298 | 6193.41 | 42.2378 | 6965.74 | 47.5049 | 6165.78 | 42.0493 | 6976.85 | 47.5807
GEN-2024-143 | DIS-24-1 | 05 SOUTHWEST | SPS | 250 | ER/NR | Wind | XIT Interchange 230 kV Substation | 781264 | 1 | 523221 | 2372.75 | 18.771 | 2021.49 | 15.9922 | 2263.41 | 17.906 | 2021.36 | 15.9911 | 2263.81 | 17.9092 | 2026.83 | 16.0344 | 2265.44 | 17.9221 | 2024.67 | 16.0173 | 2265.5 | 17.9226 | 2159.63 | 17.085 | 2355.44 | 18.6341
GEN-2024-143 | DIS-24-1 | 05 SOUTHWEST | SPS | 250 | ER/NR | Wind | XIT Interchange 230 kV Substation | 781267 | 1 | 523221 | 2372.75 | 19.1978 | 2021.49 | 16.3558 | 2263.41 | 18.3131 | 2021.36 | 16.3547 | 2263.81 | 18.3164 | 2026.83 | 16.399 | 2265.44 | 18.3295 | 2024.67 | 16.3815 | 2265.5 | 18.33 | 2159.63 | 17.4734 | 2355.44 | 19.0577
GEN-2024-144 | DIS-24-1 | 03 CENTRAL | SUNC | 300 | ER/NR | Wind | Setab 345 kV Substation | 781294 | 1 | 531465 | 4759.37 | 31.7636 | 3750.1 | 25.0279 | 4037.62 | 26.9467 | 3757.8 | 25.0793 | 4043.58 | 26.9865 | 4279.38 | 28.5602 | 4645.39 | 31.003 | 3757.57 | 25.0777 | 4028.36 | 26.8849 | 3789.62 | 25.2916 | 3970.99 | 26.5021
GEN-2024-144 | DIS-24-1 | 03 CENTRAL | SUNC | 300 | ER/NR | Wind | Setab 345 kV Substation | 781297 | 1 | 531465 | 4759.37 | 32.3628 | 3750.1 | 25.5 | 4037.62 | 27.455 | 3757.8 | 25.5523 | 4043.58 | 27.4956 | 4279.38 | 29.099 | 4645.39 | 31.5878 | 3757.57 | 25.5507 | 4028.36 | 27.3921 | 3789.62 | 25.7687 | 3970.99 | 27.002
GEN-2024-145 | DIS-24-1 | 05 SOUTHWEST | SPS | 250 | ER/NR | Wind | XIT Interchange 230 kV Substation | 781324 | 1 | 523221 | 2372.75 | 19.2564 | 2021.49 | 16.4057 | 2263.41 | 18.369 | 2021.36 | 16.4046 | 2263.81 | 18.3722 | 2026.83 | 16.449 | 2265.44 | 18.3855 | 2024.67 | 16.4315 | 2265.5 | 18.386 | 2159.63 | 17.5268 | 2355.44 | 19.1159
GEN-2024-145 | DIS-24-1 | 05 SOUTHWEST | SPS | 250 | ER/NR | Wind | XIT Interchange 230 kV Substation | 781327 | 1 | 523221 | 2372.75 | 19.694 | 2021.49 | 16.7785 | 2263.41 | 18.7864 | 2021.36 | 16.7774 | 2263.81 | 18.7898 | 2026.83 | 16.8228 | 2265.44 | 18.8033 | 2024.67 | 16.8049 | 2265.5 | 18.8038 | 2159.63 | 17.9251 | 2355.44 | 19.5503
GEN-2024-153 | DIS-24-1 | 05 SOUTHWEST | SPS | 250 | ER/NR | Solar | Bushland 230 kV Substation | 781564 | 1 | 524267 | 4439.36 | 39.0651 | 3901.45 | N/A | 4363.07 | 38.3938 | 3898.82 | N/A | 4363.21 | 38.395 | 3901.5 | N/A | 4365.1 | 38.4117 | 3909.27 | N/A | 4366.01 | 38.4197 | 4001.44 | N/A | 4450.98 | 39.1674
GEN-2024-153 | DIS-24-1 | 05 SOUTHWEST | SPS | 250 | ER/NR | Solar | Bushland 230 kV Substation | 781567 | 1 | 524267 | 4439.36 | 32.5562 | 3901.45 | N/A | 4363.07 | 31.9967 | 3898.82 | N/A | 4363.21 | 31.9977 | 3901.5 | N/A | 4365.1 | 32.0116 | 3909.27 | N/A | 4366.01 | 32.0183 | 4001.44 | N/A | 4450.98 | 32.6414
GEN-2024-154 | DIS-24-1 | 04 SOUTHEAST | AEP | 200 | ER/NR | Solar | Chisholm 345 kV Substation | 781594 | 1 | 511553 | 8454.49 | 42.2724 | 7366.96 | N/A | 8013.35 | 40.0667 | 7366.96 | N/A | 8016.8 | 40.084 | 7387.52 | N/A | 8039.57 | 40.1979 | 7557.16 | N/A | 8163.1 | 40.8155 | 7462.78 | N/A | 8016.49 | 40.0825
GEN-2024-157 | DIS-24-1 | 04 SOUTHEAST | AEP | 140 | ER/NR | Solar | Hobart - Martha 138 kV Line | 781684 | 1 | 781680 | 1742.34 | 27.0886 | 1578.52 | N/A | 1677.57 | 26.0816 | 1578.52 | N/A | 1677.62 | 26.0824 | 1577.98 | N/A | 1677.73 | 26.0841 | 1600.88 | N/A | 1724.71 | 26.8145 | 1580.79 | N/A | 1675.64 | 26.0516
GEN-2024-157 | DIS-24-1 | 04 SOUTHEAST | AEP | 140 | ER/NR | Solar | Hobart - Martha 138 kV Line | 781687 | 1 | 781680 | 1742.34 | 23.0225 | 1578.52 | N/A | 1677.57 | 22.1666 | 1578.52 | N/A | 1677.62 | 22.1673 | 1577.98 | N/A | 1677.73 | 22.1687 | 1600.88 | N/A | 1724.71 | 22.7895 | 1580.79 | N/A | 1675.64 | 22.1411
GEN-2024-158 | DIS-24-1 | 04 SOUTHEAST | AEP | 190 | ER/NR | Solar | Altus Jct - Snyder 138 kV Line | 781714 | 1 | 781710 | 1365.24 | 13.3064 | 1157.31 | N/A | 1238 | 12.0663 | 1157.31 | N/A | 1238.02 | 12.0665 | 1157.2 | N/A | 1238.07 | 12.067 | 1168.11 | N/A | 1354.16 | 13.1984 | 1158.98 | N/A | 1235.62 | 12.0431
GEN-2024-158 | DIS-24-1 | 04 SOUTHEAST | AEP | 190 | ER/NR | Solar | Altus Jct - Snyder 138 kV Line | 781717 | 1 | 781710 | 1365.24 | 15.6206 | 1157.31 | N/A | 1238 | 14.1648 | 1157.31 | N/A | 1238.02 | 14.165 | 1157.2 | N/A | 1238.07 | 14.1656 | 1168.11 | N/A | 1354.16 | 15.4938 | 1158.98 | N/A | 1235.62 | 14.1375
GEN-2024-159 | DIS-24-1 | 05 SOUTHWEST | SPS | 300 | ER/NR | Solar | Oasis - San Juan Mesa Wind 230 kV Line | 781744 | 1 | 524875 | 2938.95 | 19.3479 | 2502.33 | N/A | 2784.8 | 18.3331 | 2501.47 | N/A | 2784.84 | 18.3334 | 2501.79 | N/A | 2785.03 | 18.3346 | 2504.48 | N/A | 2785.28 | 18.3363 | 2565.45 | N/A | 2939.97 | 19.3546
GEN-2024-159 | DIS-24-1 | 05 SOUTHWEST | SPS | 300 | ER/NR | Solar | Oasis - San Juan Mesa Wind 230 kV Line | 781747 | 1 | 524875 | 2938.95 | 19.8444 | 2502.33 | N/A | 2784.8 | 18.8035 | 2501.47 | N/A | 2784.84 | 18.8038 | 2501.79 | N/A | 2785.03 | 18.8051 | 2504.48 | N/A | 2785.28 | 18.8068 | 2565.45 | N/A | 2939.97 | 19.8512
GEN-2024-161 | DIS-24-1 | 04 SOUTHEAST | AEP | 170 | ER/NR | Solar | Hobart - Martha 138 kV Line | 781804 | 1 | 781800 | 1391.24 | 7.9008 | 1271.65 | N/A | 1343.3 | 7.6286 | 1271.65 | N/A | 1343.33 | 7.6287 | 1271.34 | N/A | 1343.4 | 7.6291 | 1285.87 | N/A | 1380.47 | 7.8397 | 1273.21 | N/A | 1341.93 | 7.6208
GEN-2024-161 | DIS-24-1 | 04 SOUTHEAST | AEP | 170 | ER/NR | Battery/Storage | Hobart - Martha 138 kV Line | 781807 | 1 | 781800 | 1391.24 | 7.9322 | 1271.65 | N/A | 1343.3 | N/A | 1271.65 | N/A | 1343.33 | N/A | 1271.34 | N/A | 1343.4 | N/A | 1285.87 | N/A | 1380.47 | 7.8708 | 1273.21 | N/A | 1341.93 | N/A
GEN-2024-162 | DIS-24-1 | 02 NEBRASKA | NPPD | 110 | ER/NR | Solar | Twin Church 230 kV Substation | 781834 | 1 | 640386 | 4199.96 | 36.5723 | 3534.3 | N/A | 3704.24 | 32.2557 | 3575.81 | N/A | 4185.88 | 36.4497 | 3524.3 | N/A | 3699.15 | 32.2113 | 3522.92 | N/A | 3697.68 | 32.1985 | 3522.87 | N/A | 3697.47 | 32.1967
GEN-2024-162 | DIS-24-1 | 02 NEBRASKA | NPPD | 110 | ER/NR | Battery/Storage | Twin Church 230 kV Substation | 781837 | 1 | 640386 | 4199.96 | 36.8401 | 3534.3 | N/A | 3704.24 | N/A | 3575.81 | N/A | 4185.88 | 36.7166 | 3524.3 | N/A | 3699.15 | N/A | 3522.92 | N/A | 3697.68 | N/A | 3522.87 | N/A | 3697.47 | N/A
GEN-2024-164 | DIS-24-1 | 04 SOUTHEAST | OGE | 199 | ER/NR | Battery/Storage | Arbuckle 138 kV Substation | 781894 | 1 | 515117 | 3947.9 | 19.8387 | 3290.39 | N/A | 3495.78 | N/A | 3290.41 | N/A | 3495.77 | N/A | 3291.62 | N/A | 3496.32 | N/A | 3611.95 | N/A | 3861.09 | 19.4025 | 3295.24 | N/A | 3495.86 | N/A
GEN-2024-165 | DIS-24-1 | 04 SOUTHEAST | AEP | 500 | ER/NR | Solar | Pittsburg - Johnston County 345 kV line | 781924 | 1 | 781920 | 6236.59 | 84.9151 | 4639.49 | N/A | 5298.7 | 72.1451 | 4639.53 | N/A | 5298.69 | 72.145 | 4641.8 | N/A | 5299.85 | 72.1608 | 5125.11 | N/A | 5837.57 | 79.4822 | 4650.99 | N/A | 5298.94 | 72.1484
GEN-2024-165 | DIS-24-1 | 04 SOUTHEAST | AEP | 500 | ER/NR | Storage | Pittsburg - Johnston County 345 kV line | 781927 | 1 | 781920 | 6236.59 | 24.5228 | 4639.49 | N/A | 5298.7 | N/A | 4639.53 | N/A | 5298.69 | N/A | 4641.8 | N/A | 5299.85 | N/A | 5125.11 | N/A | 5837.57 | 22.9538 | 4650.99 | N/A | 5298.94 | N/A
GEN-2024-165 | DIS-24-1 | 04 SOUTHEAST | AEP | 500 | ER/NR | Solar | Pittsburg - Johnston County 345 kV line | 781930 | 1 | 781920 | 6236.59 | 84.9151 | 4639.49 | N/A | 5298.7 | 72.1451 | 4639.53 | N/A | 5298.69 | 72.145 | 4641.8 | N/A | 5299.85 | 72.1608 | 5125.11 | N/A | 5837.57 | 79.4822 | 4650.99 | N/A | 5298.94 | 72.1484
GEN-2024-165 | DIS-24-1 | 04 SOUTHEAST | AEP | 500 | ER/NR | Storage | Pittsburg - Johnston County 345 kV line | 781933 | 1 | 781920 | 6236.59 | 24.5228 | 4639.49 | N/A | 5298.7 | N/A | 4639.53 | N/A | 5298.69 | N/A | 4641.8 | N/A | 5299.85 | N/A | 5125.11 | N/A | 5837.57 | 22.9538 | 4650.99 | N/A | 5298.94 | N/A
GEN-2024-166 | DIS-24-1 | 03 CENTRAL | WERE | 275 | ER/NR | Storage | Murray Gill 138 kV Substation | 781954 | 1 | 533047 | 6325.71 | 22.5413 | 5519.42 | N/A | 5899.77 | N/A | 5512.77 | N/A | 5916.12 | N/A | 5573.72 | N/A | 6181.54 | 22.0276 | 5502.81 | N/A | 5831.48 | N/A | 5480.83 | N/A | 5725.42 | N/A
GEN-2024-166 | DIS-24-1 | 03 CENTRAL | WERE | 275 | ER/NR | Solar | Murray Gill 138 kV Substation | 781957 | 1 | 533047 | 6325.71 | 22.3309 | 5519.42 | N/A | 5899.77 | 20.8272 | 5512.77 | N/A | 5916.12 | 20.8849 | 5573.72 | N/A | 6181.54 | 21.8219 | 5502.81 | N/A | 5831.48 | 20.5862 | 5480.83 | N/A | 5725.42 | 20.2117
GEN-2024-167 | DIS-24-1 | 03 CENTRAL | WERE | 199 | ER/NR | Battery/Storage | Orrick 161 kV Substation | 781984 | 1 | 541244 | 3901.17 | 19.6039 | 3323.52 | N/A | 3757.27 | N/A | 3325.09 | N/A | 3757.67 | N/A | 3344.28 | N/A | 3799.21 | 19.0915 | 3326.54 | N/A | 3760.57 | N/A | 3326.85 | N/A | 3758.44 | N/A
GEN-2024-168 | DIS-24-1 | 02 NEBRASKA | NPPD | 200 | ER/NR | Solar | Geneva 115 kV Substation | 782014 | 1 | 640178 | 1942.09 | 9.8894 | 1777.63 | N/A | 1899.27 | 9.6714 | 1783.6 | N/A | 1914.85 | 9.7507 | 1749.04 | N/A | 1855.71 | 9.4496 | 1764.58 | N/A | 1880.24 | 9.5745 | 1773.25 | N/A | 1887.77 | 9.6128
GEN-2024-170 | DIS-24-1 | 03 CENTRAL | WERE | 280 | ER/NR | Battery/Storage | Pleasant Hill 345 kV Substation | 782074 | 1 | 541200 | 11670.22 | 86.4083 | 8312.28 | N/A | 11285.04 | N/A | 8318.78 | N/A | 11287 | N/A | 8409.95 | N/A | 11449.64 | 84.7751 | 8312.08 | N/A | 11290.39 | N/A | 8320.83 | N/A | 11286.48 | N/A
GEN-2024-170 | DIS-24-1 | 03 CENTRAL | WERE | 280 | ER/NR | Battery/Storage | Pleasant Hill 345 kV Substation | 782077 | 1 | 541200 | 11670.22 | 80.517 | 8312.28 | N/A | 11285.04 | N/A | 8318.78 | N/A | 11287 | N/A | 8409.95 | N/A | 11449.64 | 78.9952 | 8312.08 | N/A | 11290.39 | N/A | 8320.83 | N/A | 11286.48 | N/A
GEN-2024-171 | DIS-24-1 | 04 SOUTHEAST | GRDA | 250 | ER/NR | Battery/Storage | Tulsa North - Grand River Energy Center 345 kV Line | 782104 | 1 | 782100 | 14484.43 | 115.8754 | 11844.05 | N/A | 13888.39 | N/A | 11844.87 | N/A | 13887.87 | N/A | 11888.65 | N/A | 13932.38 | N/A | 12113.99 | N/A | 14172.4 | 113.3792 | 11861.39 | N/A | 13890.83 | N/A
GEN-2024-171 | DIS-24-1 | 04 SOUTHEAST | GRDA | 250 | ER/NR | Battery/Storage | Tulsa North - Grand River Energy Center 345 kV Line | 782107 | 1 | 782100 | 14484.43 | 115.8754 | 11844.05 | N/A | 13888.39 | N/A | 11844.87 | N/A | 13887.87 | N/A | 11888.65 | N/A | 13932.38 | N/A | 12113.99 | N/A | 14172.4 | 113.3792 | 11861.39 | N/A | 13890.83 | N/A
GEN-2024-173 | DIS-24-1 | 02 NEBRASKA | NPPD | 200 | ER/NR | Battery/Storage | Pawnee Lake 115 kV Substation | 782164 | 1 | 640316 | 2345.96 | 11.7298 | 2140.09 | N/A | 2268.77 | N/A | 2154.62 | N/A | 2293.13 | 11.4657 | 2137.58 | N/A | 2267.03 | N/A | 2137.62 | N/A | 2267.9 | N/A | 2139.26 | N/A | 2268.48 | N/A
GEN-2024-175 | DIS-24-1 | 03 CENTRAL | SPRM | 200 | ER/NR | Battery/Storage | Summit 161 kV Substation | 782224 | 1 | 549966 | 3819.83 | 19.0992 | 3007.51 | N/A | 3621.03 | N/A | 3007.73 | N/A | 3621.03 | N/A | 3003.67 | N/A | 3635.75 | 18.1788 | 2998.05 | N/A | 3619.34 | N/A | 3002.54 | N/A | 3621.77 | N/A
GEN-2024-176 | DIS-24-1 | 03 CENTRAL | WERE | 250 | ER/NR | Battery/Storage | Reno County 115 kV Substation | 782254 | 1 | 533416 | 6107.86 | 48.8629 | 4801.92 | N/A | 5831.29 | N/A | 4806.08 | N/A | 5836.41 | N/A | 4696.09 | N/A | 5550.21 | 44.4017 | 4490.5 | N/A | 5352.72 | N/A | 4638.61 | N/A | 5444.71 | N/A
GEN-2024-176 | DIS-24-1 | 03 CENTRAL | WERE | 250 | ER/NR | Battery/Storage | Reno County 115 kV Substation | 782257 | 1 | 533416 | 6107.86 | 48.8629 | 4801.92 | N/A | 5831.29 | N/A | 4806.08 | N/A | 5836.41 | N/A | 4696.09 | N/A | 5550.21 | 44.4017 | 4490.5 | N/A | 5352.72 | N/A | 4638.61 | N/A | 5444.71 | N/A
GEN-2024-177 | DIS-24-1 | 04 SOUTHEAST | AEP | 199 | ER/NR | Battery/Storage | Red Point 138 kV Substation | 782284 | 1 | 507751 | 2843.58 | 14.2893 | 2559.42 | N/A | 2646.85 | N/A | 2559.42 | N/A | 2646.85 | N/A | 2559.53 | N/A | 2646.88 | N/A | 2561.73 | N/A | 2799.57 | 14.0682 | 2559.66 | N/A | 2646.45 | N/A
GEN-2024-178 | DIS-24-1 | 04 SOUTHEAST | AEP | 199 | ER/NR | Battery/Storage | Pirkey 138 kV Substation | 782314 | 1 | 508562 | 11808.12 | 59.3373 | 4767.26 | N/A | 7871.85 | N/A | 4767.27 | N/A | 7871.84 | N/A | 4767.73 | N/A | 7872.12 | N/A | 4782.26 | N/A | 8223.58 | 41.3245 | 4768.46 | N/A | 7862.26 | N/A
GEN-2024-180 | DIS-24-1 | 04 SOUTHEAST | GRDA | 100 | ER/NR | Battery/Storage | Kerr Dam 161 kV Substation | 782374 | 1 | 512635 | 8541.2 | 85.412 | 6779.77 | N/A | 8279.61 | N/A | 6779.92 | N/A | 8279.57 | N/A | 6783.61 | N/A | 8286.17 | N/A | 6794.51 | N/A | 8487.48 | 84.8748 | 6780.3 | N/A | 8279.75 | N/A
GEN-2024-181 | DIS-24-1 | 03 CENTRAL | SPRM | 199 | ER/NR | Battery/Storage | Brookline 161 kV Substation | 782404 | 1 | 549969 | 7982.15 | 40.1113 | 5852.52 | N/A | 7675.48 | N/A | 5852.64 | N/A | 7675.52 | N/A | 5834.57 | N/A | 7721.94 | 38.8037 | 5816.87 | N/A | 7674.27 | N/A | 5831.57 | N/A | 7677.65 | N/A
GEN-2024-184 | DIS-24-1 | 04 SOUTHEAST | AEP | 199 | ER/NR | Battery/Storage | Atoka to Lehigh 138 kV Line | 782494 | 1 | 782490 | 1647.41 | 8.2784 | 1397.76 | N/A | 1486.34 | N/A | 1397.76 | N/A | 1486.34 | N/A | 1397.93 | N/A | 1486.39 | N/A | 1409.69 | N/A | 1594.6 | 8.0131 | 1398.3 | N/A | 1486.33 | N/A
GEN-2024-186 | DIS-24-1 | 05 SOUTHWEST | SPS | 199 | ER/NR | Battery/Storage | Roswell Interchange 115 kV Substation | 782554 | 1 | 527564 | 1118.98 | 5.623 | 1072.38 | N/A | 1100.47 | N/A | 1072.33 | N/A | 1100.51 | N/A | 1072.38 | N/A | 1100.51 | N/A | 1072.77 | N/A | 1100.54 | N/A | 1073.89 | N/A | 1107.03 | 5.563
GEN-2024-187 | DIS-24-1 | 04 SOUTHEAST | WFEC | 199 | ER/NR | Battery/Storage | Civit-Stratford 138 kV Line | 782584 | 1 | 782580 | 1454.57 | 7.3094 | 1374.64 | N/A | 1421.81 | N/A | 1374.64 | N/A | 1421.8 | N/A | 1374.79 | N/A | 1421.88 | N/A | 1385.23 | N/A | 1443.21 | 7.2523 | 1375.46 | N/A | 1421.8 | N/A
GEN-2024-189 | DIS-24-1 | 03 CENTRAL | ITCGP | 199 | ER/NR | Battery/Storage | ITC Great Plains Saddle 345 kV Substation | 782644 | 1 | 539816 | 8164.96 | 41.0299 | 6641.5 | N/A | 6638.23 | N/A | 6650.11 | N/A | 6646.4 | N/A | 7357.25 | N/A | 7889.63 | 39.6464 | 6689.67 | N/A | 6706.68 | N/A | 6691.59 | N/A | 6637.95 | N/A
GEN-2024-193 | DIS-24-1 | 03 CENTRAL | SUNC | 249.6 | ER/NR | Wind | Spearville - Buckner 345 kV Line | 782764 | 1 | 765911 | 7881.15 | 63.1502 | 6290.57 | 50.4052 | 6542.79 | 52.4262 | 6301.36 | 50.4917 | 6553.12 | 52.509 | 7048.88 | 56.4814 | 7675.21 | 61.5001 | 6323.49 | 50.669 | 6583.89 | 52.7555 | 6349.84 | 50.8801 | 6544.47 | 52.4397
GEN-2024-193 | DIS-24-1 | 03 CENTRAL | SUNC | 249.6 | ER/NR | Wind | Spearville - Buckner 345 kV Line | 782767 | 1 | 765911 | 7881.15 | 63.1502 | 6290.57 | 50.4052 | 6542.79 | 52.4262 | 6301.36 | 50.4917 | 6553.12 | 52.509 | 7048.88 | 56.4814 | 7675.21 | 61.5001 | 6323.49 | 50.669 | 6583.89 | 52.7555 | 6349.84 | 50.8801 | 6544.47 | 52.4397
GEN-2024-194 | DIS-24-1 | 03 CENTRAL | SUNC | 249.6 | ER/NR | Wind | Spearville - Holcomb 345 kV Line | 782794 | 1 | 765911 | 7881.15 | 63.1502 | 6290.57 | 50.4052 | 6542.79 | 52.4262 | 6301.36 | 50.4917 | 6553.12 | 52.509 | 7048.88 | 56.4814 | 7675.21 | 61.5001 | 6323.49 | 50.669 | 6583.89 | 52.7555 | 6349.84 | 50.8801 | 6544.47 | 52.4397
GEN-2024-194 | DIS-24-1 | 03 CENTRAL | SUNC | 249.6 | ER/NR | Wind | Spearville - Holcomb 345 kV Line | 782797 | 1 | 765911 | 7881.15 | 63.1502 | 6290.57 | 50.4052 | 6542.79 | 52.4262 | 6301.36 | 50.4917 | 6553.12 | 52.509 | 7048.88 | 56.4814 | 7675.21 | 61.5001 | 6323.49 | 50.669 | 6583.89 | 52.7555 | 6349.84 | 50.8801 | 6544.47 | 52.4397
GEN-2024-204 | DIS-24-1 | 04 SOUTHEAST | OGE | 100 | ER/NR | Battery/Storage | Brown 138 kV Substation | 783094 | 1 | 515157 | 2603.94 | 26.0394 | 1868.86 | N/A | 1994.04 | N/A | 1868.86 | N/A | 1994.04 | N/A | 1869.17 | N/A | 1994.15 | N/A | 1917.34 | N/A | 2345.84 | 23.4584 | 1870.45 | N/A | 1994.06 | N/A
GEN-2024-205 | DIS-24-1 | 03 CENTRAL | SUNC | 155 | ER/NR | Solar | St. John 115 kV Substation | 783124 | 1 | 539696 | 1026.22 | 6.4435 | 939.9 | N/A | 1003.15 | 6.2987 | 940.4 | N/A | 1003.34 | 6.2999 | 942.42 | N/A | 1009.29 | 6.3372 | 938.71 | N/A | 1001.95 | 6.2911 | 939.6 | N/A | 1001.06 | 6.2855
GEN-2024-205 | DIS-24-1 | 03 CENTRAL | SUNC | 155 | ER/NR | Battery/Storage | St. John 115 kV Substation | 783127 | 1 | 539696 | 1026.22 | 6.3134 | 939.9 | N/A | 1003.15 | N/A | 940.4 | N/A | 1003.34 | N/A | 942.42 | N/A | 1009.29 | 6.2092 | 938.71 | N/A | 1001.95 | N/A | 939.6 | N/A | 1001.06 | N/A
GEN-2024-206 | DIS-24-1 | 03 CENTRAL | City of Independence MO | 226.3 | ER/NR | Thermal | Blue Valley 161 kV Substation | 783154 | 1 | 548807 | 7406.15 | 163.6357 | 3969.23 | N/A | 4981.17 | N/A | 3971.09 | N/A | 4981.75 | N/A | 4013.41 | N/A | 5253.2 | N/A | 3988.68 | N/A | 5000.34 | N/A | 3978.61 | N/A | 4987.26 | N/A
GEN-2024-206 | DIS-24-1 | 03 CENTRAL | City of Independence MO | 226.3 | ER/NR | Thermal | Blue Valley 161 kV Substation | 783157 | 1 | 548807 | 7406.15 | 163.6357 | 3969.23 | N/A | 4981.17 | N/A | 3971.09 | N/A | 4981.75 | N/A | 4013.41 | N/A | 5253.2 | N/A | 3988.68 | N/A | 5000.34 | N/A | 3978.61 | N/A | 4987.26 | N/A
GEN-2024-206 | DIS-24-1 | 03 CENTRAL | City of Independence MO | 226.3 | ER/NR | Thermal | Blue Valley 161 kV Substation | 783160 | 1 | 548807 | 7406.15 | 163.6357 | 3969.23 | N/A | 4981.17 | N/A | 3971.09 | N/A | 4981.75 | N/A | 4013.41 | N/A | 5253.2 | N/A | 3988.68 | N/A | 5000.34 | N/A | 3978.61 | N/A | 4987.26 | N/A
GEN-2024-206 | DIS-24-1 | 03 CENTRAL | City of Independence MO | 226.3 | ER/NR | Thermal | Blue Valley 161 kV Substation | 783163 | 1 | 548807 | 7406.15 | 163.6357 | 3969.23 | N/A | 4981.17 | N/A | 3971.09 | N/A | 4981.75 | N/A | 4013.41 | N/A | 5253.2 | N/A | 3988.68 | N/A | 5000.34 | N/A | 3978.61 | N/A | 4987.26 | N/A
GEN-2024-206 | DIS-24-1 | 03 CENTRAL | City of Independence MO | 226.3 | ER/NR | Thermal | Blue Valley 161 kV Substation | 783166 | 1 | 548807 | 7406.15 | 163.6357 | 3969.23 | N/A | 4981.17 | N/A | 3971.09 | N/A | 4981.75 | N/A | 4013.41 | N/A | 5253.2 | N/A | 3988.68 | N/A | 5000.34 | N/A | 3978.61 | N/A | 4987.26 | N/A
GEN-2024-207 | DIS-24-1 | 03 CENTRAL | City of Independence MO | 778.6 | ER/NR | Thermal | Blue Valley - Blumil 161 kV Line | 783184 | 1 | 783180 | 5675.09 | 12.5807 | 3949.18 | N/A | 4941.15 | N/A | 3951.02 | N/A | 4941.72 | N/A | 3992.56 | N/A | 5209.76 | N/A | 3968.05 | N/A | 4959.66 | N/A | 3958.32 | N/A | 4947.03 | N/A
GEN-2024-207 | DIS-24-1 | 03 CENTRAL | City of Independence MO | 778.6 | ER/NR | Thermal | Blue Valley - Blumil 161 kV Line | 783187 | 1 | 783180 | 5675.09 | 17.3284 | 3949.18 | N/A | 4941.15 | N/A | 3951.02 | N/A | 4941.72 | N/A | 3992.56 | N/A | 5209.76 | N/A | 3968.05 | N/A | 4959.66 | N/A | 3958.32 | N/A | 4947.03 | N/A
GEN-2024-209 | DIS-24-1 | 03 CENTRAL | SUNC | 199 | ER/NR | Solar | Elm Creek - North Manhattan 230 kV Line | 783244 | 1 | 783240 | 2688.33 | 13.5092 | 2497.14 | N/A | 2634.16 | 13.237 | 2502.88 | N/A | 2637.75 | 13.255 | 2528.69 | N/A | 2661.02 | 13.372 | 2494.5 | N/A | 2632.98 | 13.2311 | 2496.04 | N/A | 2634.59 | 13.2391
GEN-2024-210 | DIS-24-1 | 03 CENTRAL | SUNC | 150 | ER/NR | Solar | St. Francis Tap 115 kV Substation | 783274 | 1 | 531370 | 434.56 | 2.8971 | 416.88 | N/A | 429.94 | 2.8663 | 417.04 | N/A | 430.04 | 2.8669 | 415.77 | N/A | 429.65 | 2.8643 | 412.5 | N/A | 424.96 | 2.8331 | 416.68 | N/A | 424.75 | 2.8317
GEN-2024-211 | DIS-24-1 | 02 NEBRASKA | OPPD | 303 | ER/NR | Thermal | Substation 3740 345 kV | 783303 | 1 | 645740 | 18658.95 | 61.5807 | 13281.12 | N/A | 16666.38 | N/A | 13418.26 | N/A | 17139.18 | N/A | 13370.11 | N/A | 16742.38 | N/A | 13278.32 | N/A | 16673.38 | N/A | 13274.41 | N/A | 16669.33 | N/A
GEN-2024-212 | DIS-24-1 | 02 NEBRASKA | OPPD | 303 | ER/NR | Thermal | Substation 3740 345 kV | 783333 | 1 | 645740 | 18658.95 | 61.5807 | 13281.12 | N/A | 16666.38 | N/A | 13418.26 | N/A | 17139.18 | N/A | 13370.11 | N/A | 16742.38 | N/A | 13278.32 | N/A | 16673.38 | N/A | 13274.41 | N/A | 16669.33 | N/A
GEN-2024-213 | DIS-24-1 | 02 NEBRASKA | OPPD | 360 | ER/NR | Thermal | Substation 3740 345 kV | 783363 | 1 | 645740 | 18658.95 | 51.8304 | 13281.12 | N/A | 16666.38 | N/A | 13418.26 | N/A | 17139.18 | N/A | 13370.11 | N/A | 16742.38 | N/A | 13278.32 | N/A | 16673.38 | N/A | 13274.41 | N/A | 16669.33 | N/A
GEN-2024-215 | DIS-24-1 | 03 CENTRAL | ITCGP | 300 | ER/NR | Solar | Elm Creek 345 kV Substation | 783424 | 1 | 539805 | 6999.08 | 22.787 | 5749.18 | N/A | 6353 | 20.6836 | 5810.47 | N/A | 6404.55 | 20.8514 | 6116.59 | N/A | 6717.12 | 21.869 | 5760.56 | N/A | 6368.13 | 20.7328 | 5755.16 | N/A | 6371.22 | 20.7429
GEN-2024-215 | DIS-24-1 | 03 CENTRAL | ITCGP | 300 | ER/NR | Battery/Storage | Elm Creek 345 kV Substation | 783427 | 1 | 539805 | 6999.08 | 22.198 | 5749.18 | N/A | 6353 | N/A | 5810.47 | N/A | 6404.55 | N/A | 6116.59 | N/A | 6717.12 | 21.3038 | 5760.56 | N/A | 6368.13 | N/A | 5755.16 | N/A | 6371.22 | N/A
GEN-2024-216 | DIS-24-1 | 01 NORTH | WAPA | 225 | ER/NR | Wind | Miles City 230 kV Substation | 783454 | 1 | 652411 | 1161.78 | 5.1635 | 968.8 | 4.3058 | 1149.53 | 5.109 | 919.72 | 4.0876 | 1108.89 | 4.9284 | 919.3 | 4.0858 | 1107.58 | 4.9226 | 919.31 | 4.0858 | 1107.55 | 4.9224 | 919.7 | 4.0876 | 1108.87 | 4.9283
GEN-2024-217 | DIS-24-1 | 03 CENTRAL | WERE | 250 | ER/NR | Battery/Storage | Sibley - Hawthorne 345 kV line | 783484 | 1 | 783480 | 11966.22 | 96.9891 | 8563.41 | N/A | 11420.84 | N/A | 8572.76 | N/A | 11424.85 | N/A | 8712.1 | N/A | 11606.43 | 94.0729 | 8567.44 | N/A | 11427.64 | N/A | 8573.65 | N/A | 11423.24 | N/A
GEN-2024-217 | DIS-24-1 | 03 CENTRAL | WERE | 250 | ER/NR | Battery/Storage | Sibley - Hawthorne 345 kV line | 783487 | 1 | 783480 | 11966.22 | 94.5027 | 8563.41 | N/A | 11420.84 | N/A | 8572.76 | N/A | 11424.85 | N/A | 8712.1 | N/A | 11606.43 | 91.6613 | 8567.44 | N/A | 11427.64 | N/A | 8573.65 | N/A | 11423.24 | N/A
GEN-2024-218 | DIS-24-1 | 03 CENTRAL | SUNC | 199 | ER/NR | Solar | Cimarron River 115 kV Substation | 783514 | 1 | 539652 | 1280.21 | 6.333 | 994.04 | N/A | 1202.99 | 5.951 | 994.17 | N/A | 1203.05 | 5.9513 | 1046.06 | N/A | 1255.56 | 6.211 | 994.85 | N/A | 1208.5 | 5.9782 | 1002.97 | N/A | 1199.45 | 5.9335
GEN-2024-218 | DIS-24-1 | 03 CENTRAL | SUNC | 199 | ER/NR | Battery/Storage | Cimarron River 115 kV Substation | 783517 | 1 | 539652 | 1280.21 | 6.3452 | 994.04 | N/A | 1202.99 | N/A | 994.17 | N/A | 1203.05 | N/A | 1046.06 | N/A | 1255.56 | 6.223 | 994.85 | N/A | 1208.5 | N/A | 1002.97 | N/A | 1199.45 | N/A
GEN-2024-219 | DIS-24-1 | 04 SOUTHEAST | OGE | 160 | ER/NR | Solar | Chigley - Oaklawn 138 kV Line | 783544 | 1 | 783540 | 2400.46 | 13.0517 | 2161.03 | N/A | 2246.66 | 12.2154 | 2161.04 | N/A | 2246.66 | 12.2154 | 2161.57 | N/A | 2246.89 | 12.2167 | 2269.6 | N/A | 2370.61 | 12.8894 | 2163.05 | N/A | 2246.7 | 12.2156
GEN-2024-219 | DIS-24-1 | 04 SOUTHEAST | OGE | 160 | ER/NR | Storage | Chigley - Oaklawn 138 kV Line | 783547 | 1 | 783540 | 2400.46 | 31.585 | 2161.03 | N/A | 2246.66 | N/A | 2161.04 | N/A | 2246.66 | N/A | 2161.57 | N/A | 2246.89 | N/A | 2269.6 | N/A | 2370.61 | 31.1922 | 2163.05 | N/A | 2246.7 | N/A
GEN-2024-220 | DIS-24-1 | 04 SOUTHEAST | AEP | 55 | ER/NR | Solar | Rodessa - Bloomberg 69 kV Line | 783574 | 1 | 783570 | 646.58 | 10.3123 | 617.1 | N/A | 633.45 | 10.1029 | 617.1 | N/A | 633.45 | 10.1029 | 617.11 | N/A | 633.45 | 10.1029 | 617.45 | N/A | 644 | 10.2711 | 617.12 | N/A | 633.38 | 10.1018
GEN-2024-220 | DIS-24-1 | 04 SOUTHEAST | AEP | 55 | ER/NR | Storage | Rodessa - Bloomberg 69 kV Line | 783576 | 1 | 783570 | 646.58 | 27.2244 | 617.1 | N/A | 633.45 | N/A | 617.1 | N/A | 633.45 | N/A | 617.11 | N/A | 633.45 | N/A | 617.45 | N/A | 644 | 27.1158 | 617.12 | N/A | 633.38 | N/A
GEN-2024-221 | DIS-24-1 | 05 SOUTHWEST | SPS | 400 | ER/NR | Wind | 345 kV Crossroads - Eddy County 345 kV Line | 783604 | 1 | 782910 | 5169.67 | 25.8483 | 4728.4 | 23.642 | 5118.67 | 25.5934 | 4727.85 | 23.6393 | 5119.02 | 25.5951 | 4728.29 | 23.6414 | 5120.01 | 25.6 | 4737.81 | 23.6891 | 5121.59 | 25.6079 | 4774.07 | 23.8703 | 5061.68 | 25.3084
GEN-2024-221 | DIS-24-1 | 05 SOUTHWEST | SPS | 400 | ER/NR | Wind | 345 kV Crossroads - Eddy County 345 kV Line | 783607 | 1 | 782910 | 5169.67 | 25.8483 | 4728.4 | 23.642 | 5118.67 | 25.5934 | 4727.85 | 23.6393 | 5119.02 | 25.5951 | 4728.29 | 23.6414 | 5120.01 | 25.6 | 4737.81 | 23.6891 | 5121.59 | 25.6079 | 4774.07 | 23.8703 | 5061.68 | 25.3084
GEN-2024-226 | DIS-24-1 | 04 SOUTHEAST | AEP | 300 | ER/NR | Solar | John W Turk Jr Power Plant 345 kV Substation | 783754 | 1 | 507455 | 5676.44 | 37.8429 | 4635.76 | N/A | 5359.8 | 35.732 | 4635.76 | N/A | 5359.8 | 35.732 | 4636.16 | N/A | 5359.88 | 35.7325 | 4661.24 | N/A | 5465.29 | 36.4353 | 4637.1 | N/A | 5354 | 35.6933
GEN-2024-226 | DIS-24-1 | 04 SOUTHEAST | AEP | 300 | ER/NR | Solar | John W Turk Jr Power Plant 345 kV Substation | 783757 | 1 | 507455 | 5676.44 | 37.8429 | 4635.76 | N/A | 5359.8 | 35.732 | 4635.76 | N/A | 5359.8 | 35.732 | 4636.16 | N/A | 5359.88 | 35.7325 | 4661.24 | N/A | 5465.29 | 36.4353 | 4637.1 | N/A | 5354 | 35.6933
GEN-2024-227 | DIS-24-1 | 04 SOUTHEAST | AEP | 200 | ER/NR | Battery/Storage | John W Turk Jr Power Plant 345 kV Substation | 783784 | 1 | 507455 | 5676.44 | 28.3822 | 4635.76 | N/A | 5359.8 | N/A | 4635.76 | N/A | 5359.8 | N/A | 4636.16 | N/A | 5359.88 | N/A | 4661.24 | N/A | 5465.29 | 27.3265 | 4637.1 | N/A | 5354 | N/A
GEN-2024-228 | DIS-24-1 | 03 CENTRAL | MIDW | 200 | ER/NR | Solar | Rice to Circle 230 kV Line | 783814 | 1 | 783810 | 2792.72 | 13.9636 | 2427.78 | N/A | 2705.38 | 13.5269 | 2425.58 | N/A | 2706.27 | 13.5313 | 2417.44 | N/A | 2695.5 | 13.4775 | 2391.77 | N/A | 2694.81 | 13.4741 | 2399.52 | N/A | 2685.21 | 13.4261
GEN-2024-229 | DIS-24-1 | 04 SOUTHEAST | AEP | 200 | ER/NR | Solar | Lawton East Side - Oklaunion North 345 kV | 783844 | 1 | 783840 | 3958.44 | 19.7922 | 3315.17 | N/A | 3583.55 | 17.9178 | 3315.15 | N/A | 3583.58 | 17.9179 | 3316.41 | N/A | 3584.93 | 17.9246 | 3404.89 | N/A | 3567.87 | 17.8393 | 3502.45 | N/A | 3523.87 | 17.6194
GEN-2024-230 | DIS-24-1 | 04 SOUTHEAST | AEP | 300 | ER/NR | Battery/Storage | Lawton East Side - Oklaunion North 345 kV | 783874 | 1 | 783840 | 3958.44 | 26.3896 | 3315.17 | N/A | 3583.55 | N/A | 3315.15 | N/A | 3583.58 | N/A | 3316.41 | N/A | 3584.93 | N/A | 3404.89 | N/A | 3567.87 | 23.7858 | 3502.45 | N/A | 3523.87 | N/A
GEN-2024-230 | DIS-24-1 | 04 SOUTHEAST | AEP | 300 | ER/NR | Battery/Storage | Lawton East Side - Oklaunion North 345 kV | 783877 | 1 | 783840 | 3958.44 | 26.3896 | 3315.17 | N/A | 3583.55 | N/A | 3315.15 | N/A | 3583.58 | N/A | 3316.41 | N/A | 3584.93 | N/A | 3404.89 | N/A | 3567.87 | 23.7858 | 3502.45 | N/A | 3523.87 | N/A
GEN-2024-231 | DIS-24-1 | 02 NEBRASKA | OPPD | 65 | ER/NR | Wind | S1399 5 161 kV Substation | 783904 | 1 | 646399 | 1758.2 | 27.9079 | 1691.16 | 26.8438 | 1740.3 | 27.6238 | 1692.98 | 26.8727 | 1748.73 | 27.7576 | 1690.74 | 26.8371 | 1735.9 | 27.554 | 1686.35 | 26.7675 | 1735.91 | 27.5541 | 1689.23 | 26.8132 | 1738.74 | 27.599
GEN-2024-231 | DIS-24-1 | 02 NEBRASKA | OPPD | 65 | ER/NR | Solar | S1399 5 161 kV Substation | 783907 | 1 | 646399 | 1758.2 | 512.1468 | 1691.16 | N/A | 1740.3 | 506.9327 | 1692.98 | N/A | 1748.73 | 509.3883 | 1690.74 | N/A | 1735.9 | 505.6511 | 1686.35 | N/A | 1735.91 | 505.654 | 1689.23 | N/A | 1738.74 | 506.4783
GEN-2024-232 | DIS-24-1 | 04 SOUTHEAST | AEP | 250 | ER/NR | Solar | Crockett - Rocky Creek 345 kV line | 783934 | 1 | 783930 | 3512.31 | 28.0985 | 2830.59 | N/A | 3423.03 | 27.3842 | 2830.59 | N/A | 3423.03 | 27.3842 | 2830.64 | N/A | 3425.94 | 27.4075 | 2829.1 | N/A | 3430.69 | 27.4455 | 2830.72 | N/A | 3422.71 | 27.3817
GEN-2024-232 | DIS-24-1 | 04 SOUTHEAST | AEP | 250 | ER/NR | Solar | Crockett - Rocky Creek 345 kV line | 783937 | 1 | 783930 | 3512.31 | 28.0985 | 2830.59 | N/A | 3423.03 | 27.3842 | 2830.59 | N/A | 3423.03 | 27.3842 | 2830.64 | N/A | 3425.94 | 27.4075 | 2829.1 | N/A | 3430.69 | 27.4455 | 2830.72 | N/A | 3422.71 | 27.3817
GEN-2024-234 | DIS-24-1 | 02 NEBRASKA | OPPD | 200 | ER/NR | Solar | Raun - Tekamah 161 kV line | 783994 | 1 | 646300 | 3224.52 | 16.1226 | 2964.8 | N/A | 3110.9 | 15.5545 | 3055.11 | N/A | 3209.04 | 16.0452 | 2963.57 | N/A | 3110.3 | 15.5515 | 2962.08 | N/A | 3109.88 | 15.5494 | 2962.03 | N/A | 3109.82 | 15.5491
GEN-2024-235 | DIS-24-1 | 04 SOUTHEAST | AEP | 250 | ER/NR | Wind | Sooner - Wekiwa 345 kV line | 784024 | 1 | 784020 | 7634.73 | 61.0778 | 6905.15 | 55.2412 | 7347.07 | 58.7766 | 6905.36 | 55.2429 | 7347.04 | 58.7763 | 6926.95 | 55.4156 | 7364.31 | 58.9145 | 7082.28 | 56.6582 | 7516.45 | 60.1316 | 6911.17 | 55.2894 | 7347.67 | 58.7814
GEN-2024-235 | DIS-24-1 | 04 SOUTHEAST | AEP | 250 | ER/NR | Wind | Sooner - Wekiwa 345 kV line | 784027 | 1 | 784020 | 7634.73 | 61.0778 | 6905.15 | 55.2412 | 7347.07 | 58.7766 | 6905.36 | 55.2429 | 7347.04 | 58.7763 | 6926.95 | 55.4156 | 7364.31 | 58.9145 | 7082.28 | 56.6582 | 7516.45 | 60.1316 | 6911.17 | 55.2894 | 7347.67 | 58.7814
GEN-2024-236 | DIS-24-1 | 04 SOUTHEAST | OGE | 241.4 | ER/NR | Wind | Seminole - Muskogee 345 kV line | 784054 | 1 | 516210 | 13005.64 | 53.8759 | 10306.71 | 42.6956 | 11885.05 | 49.2338 | 10306.88 | 42.6963 | 11885.01 | 49.2337 | 10315.38 | 42.7315 | 11888.71 | 49.249 | 10473.7 | 43.3873 | 12536.76 | 51.9336 | 10317.2 | 42.739 | 11885.08 | 49.234
GEN-2024-239 | DIS-24-1 | 04 SOUTHEAST | OGE | 200 | ER/NR | Battery/Storage | Cimarron 345 kV Substation | 784144 | 1 | 514901 | 24092.45 | 120.4622 | 16442.44 | N/A | 21268.14 | N/A | 16443.66 | N/A | 21267.81 | N/A | 16518.52 | N/A | 21344.81 | N/A | 17950.57 | N/A | 22547.57 | 112.7378 | 16563.87 | N/A | 21271.68 | N/A
GEN-2024-240 | DIS-24-1 | 04 SOUTHEAST | AEP | 300 | ER/NR | Wind | Neosho - Delaware 345 kV line | 784174 | 1 | 784170 | 6832.71 | 45.5514 | 5975.31 | 39.8354 | 6463.41 | 43.0894 | 5975.69 | 39.8379 | 6463.47 | 43.0898 | 5995.94 | 39.9729 | 6524.85 | 43.499 | 6103.46 | 40.6897 | 6606.25 | 44.0417 | 5983.81 | 39.8921 | 6463.69 | 43.0913
GEN-2024-240 | DIS-24-1 | 04 SOUTHEAST | AEP | 300 | ER/NR | Wind | Neosho - Delaware 345 kV line | 784177 | 1 | 784170 | 6832.71 | 45.5514 | 5975.31 | 39.8354 | 6463.41 | 43.0894 | 5975.69 | 39.8379 | 6463.47 | 43.0898 | 5995.94 | 39.9729 | 6524.85 | 43.499 | 6103.46 | 40.6897 | 6606.25 | 44.0417 | 5983.81 | 39.8921 | 6463.69 | 43.0913
GEN-2024-241 | DIS-24-1 | 04 SOUTHEAST | AEP | 100 | ER/NR | Solar | Lydia 345 kV Substation | 784204 | 1 | 508298 | 8704.63 | 87.0463 | 5513.92 | N/A | 7327.81 | 73.2781 | 5513.94 | N/A | 7327.81 | 73.2781 | 5515 | N/A | 7328.12 | 73.2812 | 5583.3 | N/A | 7643.19 | 76.4319 | 5517.58 | N/A | 7304.48 | 73.0448
GEN-2024-242 | DIS-24-1 | 04 SOUTHEAST | OGE | 250 | ER/NR | Battery/Storage | 515171 138 kV Substation | 784234 | 1 | 515171 | 3143.81 | 12.5752 | 2679.04 | N/A | 2825.51 | N/A | 2679.05 | N/A | 2825.51 | N/A | 2679.73 | N/A | 2825.87 | N/A | 2822.46 | N/A | 3002.72 | 12.0109 | 2683.44 | N/A | 2825.7 | N/A
GEN-2024-243 | DIS-24-1 | 04 SOUTHEAST | SWPA | 50.1 | ER/NR | Battery/Storage | Van Buren 161 kV Substation | 784264 | 1 | 505522 | 5479.35 | 109.3683 | 4205.77 | N/A | 4930.75 | N/A | 4205.78 | N/A | 4930.74 | N/A | 4206.28 | N/A | 4930.88 | N/A | 4207.09 | N/A | 5047.38 | 100.7461 | 4206.43 | N/A | 4930.75 | N/A
GEN-2024-244 | DIS-24-1 | 05 SOUTHWEST | SPS | 150 | ER/NR | Battery/Storage | Sooner 115 kV Substation | 784294 | 1 | 523084 | 1778.24 | 11.8549 | 1610.65 | N/A | 1616.51 | N/A | 1610.55 | N/A | 1616.98 | N/A | 1589.45 | N/A | 1552.68 | N/A | 1618.56 | N/A | 1622.41 | N/A | 1673.1 | N/A | 1670.6 | 11.1373
GEN-2024-245 | DIS-24-1 | 04 SOUTHEAST | OGE | 199 | ER/NR | Battery/Storage | Lincoln 138 kV Substation | 784324 | 1 | 515442 | 3706.11 | 18.6237 | 3207.7 | N/A | 3572.62 | N/A | 3207.73 | N/A | 3572.61 | N/A | 3209.74 | N/A | 3573.28 | N/A | 3243.82 | N/A | 3657.13 | 18.3775 | 3210.41 | N/A | 3572.6 | N/A
GEN-2024-246 | DIS-24-1 | 05 SOUTHWEST | SPS | 199 | ER/NR | Battery/Storage | North Loving 115 kV Substation | 784354 | 1 | 528182 | 4944.85 | 24.8485 | 4529.83 | N/A | 4896.55 | N/A | 4529.54 | N/A | 4897.87 | N/A | 4530.9 | N/A | 4898.33 | N/A | 4542.2 | N/A | 4901.01 | N/A | 4527.51 | N/A | 4357.29 | 21.8959
GEN-2024-247 | DIS-24-1 | 04 SOUTHEAST | GRDA | 456.6 | ER | Thermal | Stillwater Northtap 138 kV Substation | 784382 | 1 | 512731 | 2443.64 | 5.3518 | 2282.94 | N/A | 2388.55 | N/A | 2282.95 | N/A | 2388.55 | N/A | 2284.06 | N/A | 2389.86 | N/A | 2293.25 | N/A | 2409.66 | N/A | 2283.88 | N/A | 2388.45 | N/A
GEN-2024-249 | DIS-24-1 | 03 CENTRAL | WERE | 721.2 | ER/NR | Thermal | Jeffrey EC 345 kV Substation | 784443 | 1 | 532766 | 15782.41 | 21.8835 | 10522.14 | N/A | 15077.68 | N/A | 10553.77 | N/A | 15104.1 | N/A | 10762.55 | N/A | 15626.08 | N/A | 10535.61 | N/A | 15103.72 | N/A | 10538.21 | N/A | 15087.75 | N/A
GEN-2024-250 | DIS-24-1 | 04 SOUTHEAST | AEP | 199 | ER/NR | Battery/Storage | Pittsburgh 345 kV Substation | 784474 | 1 | 510907 | 10646.36 | 53.4993 | 7251.68 | N/A | 9485.76 | N/A | 7251.79 | N/A | 9485.72 | N/A | 7257.73 | N/A | 9488.75 | N/A | 7772.34 | N/A | 10094.47 | 50.726 | 7268.98 | N/A | 9484.69 | N/A
GEN-2024-251 | DIS-24-1 | 05 SOUTHWEST | SPS | 125 | ER/NR | Battery/Storage | Atoka 115 kV Substation | 784504 | 1 | 527786 | 1563.44 | 12.5075 | 1472.49 | N/A | 1559.12 | N/A | 1472.45 | N/A | 1559.24 | N/A | 1472.54 | N/A | 1559.23 | N/A | 1473.38 | N/A | 1559.31 | N/A | 1475.39 | N/A | 1489.81 | 11.9185
GEN-2024-252 | DIS-24-1 | 04 SOUTHEAST | OGE | 300 | ER/NR | Thermal | Cimmaron 345 kV Substation | 784534 | 1 | 514901 | 24092.45 | 119.5062 | 16442.44 | N/A | 21268.14 | N/A | 16443.66 | N/A | 21267.81 | N/A | 16518.52 | N/A | 21344.81 | N/A | 17950.57 | N/A | 22547.57 | N/A | 16563.87 | N/A | 21271.68 | N/A
GEN-2024-252 | DIS-24-1 | 04 SOUTHEAST | OGE | 300 | ER/NR | Storage | Cimmaron 345 kV Substation | 784537 | 1 | 514901 | 24092.45 | 234.0209 | 16442.44 | N/A | 21268.14 | N/A | 16443.66 | N/A | 21267.81 | N/A | 16518.52 | N/A | 21344.81 | N/A | 17950.57 | N/A | 22547.57 | 219.0148 | 16563.87 | N/A | 21271.68 | N/A
GEN-2024-253 | DIS-24-1 | 03 CENTRAL | WERE | 300 | ER/NR | Thermal | Stranger Creek - 87th Street 345 kV line | 784564 | 1 | 784560 | 12084.11 | 59.941 | 8531.52 | N/A | 11590.84 | N/A | 8544.72 | N/A | 11598.13 | N/A | 8815.64 | N/A | 11888.3 | N/A | 8520.97 | N/A | 11581.37 | N/A | 8543.05 | N/A | 11596.54 | N/A
GEN-2024-253 | DIS-24-1 | 03 CENTRAL | WERE | 300 | ER/NR | Storage | Stranger Creek - 87th Street 345 kV line | 784567 | 1 | 784560 | 12084.11 | 117.3784 | 8531.52 | N/A | 11590.84 | N/A | 8544.72 | N/A | 11598.13 | N/A | 8815.64 | N/A | 11888.3 | 115.4764 | 8520.97 | N/A | 11581.37 | N/A | 8543.05 | N/A | 11596.54 | N/A
GEN-2024-254 | DIS-24-1 | 04 SOUTHEAST | OGE | 300 | ER/NR | Thermal | Mathewson 345 kV Substation | 784594 | 1 | 515497 | 23717.71 | 117.6474 | 16244.37 | N/A | 20746.71 | N/A | 16245.84 | N/A | 20746.33 | N/A | 16332.61 | N/A | 20843.14 | N/A | 18020.91 | N/A | 22375.39 | N/A | 16353.12 | N/A | 20752.44 | N/A
GEN-2024-254 | DIS-24-1 | 04 SOUTHEAST | OGE | 300 | ER/NR | Storage | Mathewson 345 kV Substation | 784597 | 1 | 515497 | 23717.71 | 230.3809 | 16244.37 | N/A | 20746.71 | N/A | 16245.84 | N/A | 20746.33 | N/A | 16332.61 | N/A | 20843.14 | N/A | 18020.91 | N/A | 22375.39 | 217.3423 | 16353.12 | N/A | 20752.44 | N/A
GEN-2024-255 | DIS-24-1 | 04 SOUTHEAST | OGE | 300 | ER/NR | Thermal | Spring Creek 345 kV Substation | 784624 | 1 | 514881 | 14492.14 | 71.8856 | 10650.65 | N/A | 13486.34 | N/A | 10651.2 | N/A | 13486.22 | N/A | 10687.28 | N/A | 13516.9 | N/A | 11383.71 | N/A | 14067.23 | N/A | 10688.78 | N/A | 13487.85 | N/A
GEN-2024-255 | DIS-24-1 | 04 SOUTHEAST | OGE | 300 | ER/NR | Storage | Spring Creek 345 kV Substation | 784627 | 1 | 514881 | 14492.14 | 140.7687 | 10650.65 | N/A | 13486.34 | N/A | 10651.2 | N/A | 13486.22 | N/A | 10687.28 | N/A | 13516.9 | N/A | 11383.71 | N/A | 14067.23 | 136.6414 | 10688.78 | N/A | 13487.85 | N/A
GEN-2024-257 | DIS-24-1 | 03 CENTRAL | SUNC | 220 | ER/NR | Solar | Skellyville 115 kV Tap Substation | 784684 | 1 | 539756 | 479.86 | 2.1812 | 450.2 | N/A | 470.54 | 2.1388 | 450.27 | N/A | 470.57 | 2.139 | 450.87 | N/A | 471.79 | 2.1445 | 450.16 | N/A | 470.57 | 2.139 | 450.2 | N/A | 470.31 | 2.1378
GEN-2024-258 | DIS-24-1 | 03 CENTRAL | NEETSW | 300 | ER/NR | Wind | Wolf Creek - Blackberry 345 kV Line | 784714 | 1 | 784710 | 6466.39 | 44.1356 | 5823.85 | 39.75 | 6160.4 | 42.0471 | 5824.81 | 39.7565 | 6160.71 | 42.0492 | 5858.56 | 39.9869 | 6400.14 | 43.6834 | 5842.39 | 39.8765 | 6179.72 | 42.1789 | 5830.19 | 39.7933 | 6162.69 | 42.0627
GEN-2024-258 | DIS-24-1 | 03 CENTRAL | NEETSW | 300 | ER/NR | Wind | Wolf Creek - Blackberry 345 kV Line | 784717 | 1 | 784710 | 6466.39 | 42.1296 | 5823.85 | 37.9434 | 6160.4 | 40.136 | 5824.81 | 37.9496 | 6160.71 | 40.1381 | 5858.56 | 38.1695 | 6400.14 | 41.698 | 5842.39 | 38.0641 | 6179.72 | 40.2619 | 5830.19 | 37.9847 | 6162.69 | 40.151
GEN-2024-259 | DIS-24-1 | 03 CENTRAL | EMDE | 199.8 | ER/NR | Solar | Asbury 161 kV Substation | 784744 | 1 | 547476 | 3219.08 | 33.0081 | 2637.58 | N/A | 3058.36 | 31.3601 | 2638.54 | N/A | 3058.37 | 31.3602 | 2639.29 | N/A | 3176.34 | 32.5698 | 2638.4 | N/A | 3064.78 | 31.4259 | 2638.21 | N/A | 3058.14 | 31.3578
GEN-2024-259 | DIS-24-1 | 03 CENTRAL | EMDE | 199.8 | ER/NR | Storage | Asbury 161 kV Substation | 784747 | 1 | 547476 | 3219.08 | 13.2586 | 2637.58 | N/A | 3058.36 | N/A | 2638.54 | N/A | 3058.37 | N/A | 2639.29 | N/A | 3176.34 | 13.0826 | 2638.4 | N/A | 3064.78 | N/A | 2638.21 | N/A | 3058.14 | N/A
GEN-2024-260 | DIS-24-1 | 03 CENTRAL | WERE | 199.8 | ER/NR | Battery/Storage | East Town 161 kV Substation | 784774 | 1 | 541401 | 4837.04 | 24.2094 | 4080.96 | N/A | 4777.04 | N/A | 4086.1 | N/A | 4780.05 | N/A | 4129.92 | N/A | 4810.15 | 24.0748 | 4081.98 | N/A | 4777.16 | N/A | 4082.81 | N/A | 4777.64 | N/A
GEN-2024-261 | DIS-24-1 | 05 SOUTHWEST | LCEC | 150 | ER/NR | Solar | Hobbs - LCEC West 115 kV Line | 784804 | 1 | 784800 | 2039.21 | 12.777 | 1854.32 | N/A | 2020.97 | 12.6627 | 1854.27 | N/A | 2021.05 | 12.6632 | 1854.49 | N/A | 2021.03 | 12.6631 | 1855.16 | N/A | 2021.07 | 12.6633 | 1863.43 | N/A | 2031.35 | 12.7278
GEN-2024-261 | DIS-24-1 | 05 SOUTHWEST | LCEC | 150 | ER/NR | Battery/Storage | Hobbs - LCEC West 115 kV Line | 784807 | 1 | 784800 | 2039.21 | 12.4494 | 1854.32 | N/A | 2020.97 | N/A | 1854.27 | N/A | 2021.05 | N/A | 1854.49 | N/A | 2021.03 | N/A | 1855.16 | N/A | 2021.07 | N/A | 1863.43 | N/A | 2031.35 | 12.4014
GEN-2024-265 | DIS-24-1 | 05 SOUTHWEST | SPS | 155 | ER/NR | Solar | Bensing 115 kV Substation | 784924 | 1 | 528433 | 1652.13 | 10.0863 | 1502.81 | N/A | 1644.9 | 10.0421 | 1502.77 | N/A | 1644.96 | 10.0425 | 1502.97 | N/A | 1644.95 | 10.0424 | 1503.51 | N/A | 1644.98 | 10.0426 | 1506.83 | N/A | 1647.6 | 10.0586
GEN-2024-265 | DIS-24-1 | 05 SOUTHWEST | SPS | 155 | ER/NR | Battery/Storage | Bensing 115 kV Substation | 784927 | 1 | 528433 | 1652.13 | 9.5943 | 1502.81 | N/A | 1644.9 | N/A | 1502.77 | N/A | 1644.96 | N/A | 1502.97 | N/A | 1644.95 | N/A | 1503.51 | N/A | 1644.98 | N/A | 1506.83 | N/A | 1647.6 | 9.5679
GEN-2024-266 | DIS-24-1 | 05 SOUTHWEST | SPS | 500 | ER/NR | Solar | Potter Co - Hitchland 345 kV Line | 784954 | 1 | 784950 | 7640.78 | 45.022 | 6759 | N/A | 7394.18 | 43.569 | 6758.34 | N/A | 7394.61 | 43.5715 | 6785.58 | N/A | 7427.03 | 43.7625 | 6802.37 | N/A | 7425.22 | 43.7519 | 6967.87 | N/A | 7444.36 | 43.8647
GEN-2024-266 | DIS-24-1 | 05 SOUTHWEST | SPS | 500 | ER/NR | Battery/Storage | Potter Co - Hitchland 345 kV Line | 784957 | 1 | 784950 | 7640.78 | 56.7497 | 6759 | N/A | 7394.18 | N/A | 6758.34 | N/A | 7394.61 | N/A | 6785.58 | N/A | 7427.03 | N/A | 6802.37 | N/A | 7425.22 | N/A | 6967.87 | N/A | 7444.36 | 55.2908
GEN-2024-266 | DIS-24-1 | 05 SOUTHWEST | SPS | 500 | ER/NR | Solar | Potter Co - Hitchland 345 kV Line | 784960 | 1 | 784950 | 7640.78 | 45.022 | 6759 | N/A | 7394.18 | 43.569 | 6758.34 | N/A | 7394.61 | 43.5715 | 6785.58 | N/A | 7427.03 | 43.7625 | 6802.37 | N/A | 7425.22 | 43.7519 | 6967.87 | N/A | 7444.36 | 43.8647
GEN-2024-266 | DIS-24-1 | 05 SOUTHWEST | SPS | 500 | ER/NR | Battery/Storage | Potter Co - Hitchland 345 kV Line | 784961 | 1 | 784950 | 7640.78 | 56.7497 | 6759 | N/A | 7394.18 | N/A | 6758.34 | N/A | 7394.61 | N/A | 6785.58 | N/A | 7427.03 | N/A | 6802.37 | N/A | 7425.22 | N/A | 6967.87 | N/A | 7444.36 | 55.2908
GEN-2024-266 | DIS-24-1 | 05 SOUTHWEST | SPS | 500 | ER/NR | Battery/Storage | Potter Co - Hitchland 345 kV Line | 784963 | 1 | 784950 | 7640.78 | 56.7497 | 6759 | N/A | 7394.18 | N/A | 6758.34 | N/A | 7394.61 | N/A | 6785.58 | N/A | 7427.03 | N/A | 6802.37 | N/A | 7425.22 | N/A | 6967.87 | N/A | 7444.36 | 55.2908
GEN-2024-266 | DIS-24-1 | 05 SOUTHWEST | SPS | 500 | ER/NR | Solar | Potter Co - Hitchland 345 kV Line | 784966 | 1 | 784950 | 7640.78 | 45.022 | 6759 | N/A | 7394.18 | 43.569 | 6758.34 | N/A | 7394.61 | 43.5715 | 6785.58 | N/A | 7427.03 | 43.7625 | 6802.37 | N/A | 7425.22 | 43.7519 | 6967.87 | N/A | 7444.36 | 43.8647
GEN-2024-267 | DIS-24-1 | 04 SOUTHEAST | WFEC | 195 | ER/NR | Solar | Durantp4 - Sclmnjc4 138 kV Line | 784984 | 1 | 784980 | 1578.3 | 7.9079 | 1296.84 | N/A | 1370.15 | 6.865 | 1296.84 | N/A | 1370.15 | 6.865 | 1296.97 | N/A | 1370.19 | 6.8652 | 1316.92 | N/A | 1501.83 | 7.5248 | 1297.51 | N/A | 1370.15 | 6.865
GEN-2024-267 | DIS-24-1 | 04 SOUTHEAST | WFEC | 195 | ER/NR | Storage | Durantp4 - Sclmnjc4 138 kV Line | 784987 | 1 | 784980 | 1578.3 | 7.9079 | 1296.84 | N/A | 1370.15 | N/A | 1296.84 | N/A | 1370.15 | N/A | 1296.97 | N/A | 1370.19 | N/A | 1316.92 | N/A | 1501.83 | 7.5248 | 1297.51 | N/A | 1370.15 | N/A
GEN-2024-268 | DIS-24-1 | 04 SOUTHEAST | OGE | 390 | ER/NR | Solar | Keefton 345 kV Substation | 785014 | 1 | 516374 | 17000.82 | 87.1837 | 12798.18 | N/A | 15341.94 | 78.6766 | 12798.39 | N/A | 15341.89 | 78.6764 | 12809.09 | N/A | 15346.97 | 78.7024 | 12952.95 | N/A | 15954.3 | 81.8169 | 12807.61 | N/A | 15342.08 | 78.6773
GEN-2024-268 | DIS-24-1 | 04 SOUTHEAST | OGE | 390 | ER/NR | Solar | Keefton 345 kV Substation | 785017 | 1 | 516374 | 17000.82 | 87.1837 | 12798.18 | N/A | 15341.94 | 78.6766 | 12798.39 | N/A | 15341.89 | 78.6764 | 12809.09 | N/A | 15346.97 | 78.7024 | 12952.95 | N/A | 15954.3 | 81.8169 | 12807.61 | N/A | 15342.08 | 78.6773
GEN-2024-271 | DIS-24-1 | 05 SOUTHWEST | SPS | 250 | ER/NR | Solar | Chaves County - San Juan Wind 230 kV Line | 785104 | 1 | 785100 | 1614.85 | 12.802 | 1516.28 | N/A | 1586.63 | 12.5783 | 1516.17 | N/A | 1586.7 | 12.5789 | 1516.26 | N/A | 1586.71 | 12.579 | 1517.11 | N/A | 1586.79 | 12.5796 | 1519.21 | N/A | 1595.68 | 12.6501
GEN-2024-271 | DIS-24-1 | 05 SOUTHWEST | SPS | 250 | ER/NR | Solar | Chaves County - San Juan Wind 230 kV Line | 785107 | 1 | 785100 | 1614.85 | 12.4363 | 1516.28 | N/A | 1586.63 | 12.2189 | 1516.17 | N/A | 1586.7 | 12.2195 | 1516.26 | N/A | 1586.71 | 12.2196 | 1517.11 | N/A | 1586.79 | 12.2202 | 1519.21 | N/A | 1595.68 | 12.2886
GEN-2024-271 | DIS-24-1 | 05 SOUTHWEST | SPS | 250 | ER/NR | Battery/Storage | Chaves County - San Juan Wind 230 kV Line | 785110 | 1 | 785100 | 1614.85 | 23.7674 | 1516.28 | N/A | 1586.63 | N/A | 1516.17 | N/A | 1586.7 | N/A | 1516.26 | N/A | 1586.71 | N/A | 1517.11 | N/A | 1586.79 | N/A | 1519.21 | N/A | 1595.68 | 23.4852
GEN-2024-271 | DIS-24-1 | 05 SOUTHWEST | SPS | 250 | ER/NR | Battery/Storage | Chaves County - San Juan Wind 230 kV Line | 785113 | 1 | 785100 | 1614.85 | 25.0878 | 1516.28 | N/A | 1586.63 | N/A | 1516.17 | N/A | 1586.7 | N/A | 1516.26 | N/A | 1586.71 | N/A | 1517.11 | N/A | 1586.79 | N/A | 1519.21 | N/A | 1595.68 | 24.79
GEN-2024-272 | DIS-24-1 | 03 CENTRAL | SUNC | 199 | ER/NR | Solar | Sawyer 115 kV Substation | 785134 | 1 | 539649 | 949.06 | 9.3044 | 875.31 | N/A | 924.5 | 9.0636 | 875.47 | N/A | 924.6 | 9.0646 | 877.97 | N/A | 929.3 | 9.1107 | 875.53 | N/A | 925.11 | 9.0696 | 875.43 | N/A | 923.86 | 9.0574
GEN-2024-272 | DIS-24-1 | 03 CENTRAL | SUNC | 199 | ER/NR | Solar | Sawyer 115 kV Substation | 785137 | 1 | 539649 | 949.06 | 9.3044 | 875.31 | N/A | 924.5 | 9.0636 | 875.47 | N/A | 924.6 | 9.0646 | 877.97 | N/A | 929.3 | 9.1107 | 875.53 | N/A | 925.11 | 9.0696 | 875.43 | N/A | 923.86 | 9.0574
GEN-2024-272 | DIS-24-1 | 03 CENTRAL | SUNC | 199 | ER/NR | Battery/Storage | Sawyer 115 kV Substation | 785140 | 1 | 539649 | 949.06 | 18.0423 | 875.31 | N/A | 924.5 | N/A | 875.47 | N/A | 924.6 | N/A | 877.97 | N/A | 929.3 | 17.6666 | 875.53 | N/A | 925.11 | N/A | 875.43 | N/A | 923.86 | N/A
GEN-2024-272 | DIS-24-1 | 03 CENTRAL | SUNC | 199 | ER/NR | Battery/Storage | Sawyer 115 kV Substation | 785143 | 1 | 539649 | 949.06 | 18.0423 | 875.31 | N/A | 924.5 | N/A | 875.47 | N/A | 924.6 | N/A | 877.97 | N/A | 929.3 | 17.6666 | 875.53 | N/A | 925.11 | N/A | 875.43 | N/A | 923.86 | N/A
GEN-2024-273 | DIS-24-1 | 05 SOUTHWEST | SPS | 16.214 | ER/NR | Solar | Pearl 115 kV Substation | 785164 | 1 | 528392 | 6406.56 | 395.1496 | 5461.82 | N/A | 6326.61 | 390.2184 | 5461.34 | N/A | 6330.06 | 390.4312 | 5462.75 | N/A | 6328.72 | 390.3485 | 5474.01 | N/A | 6329.43 | 390.3923 | 5496.44 | N/A | 6162.99 | 380.1265
GEN-2024-274 | DIS-24-1 | 03 CENTRAL | SUNC | 175 | ER/NR | Solar | Harper - Anthony 138 kV Line | 785194 | 1 | 785190 | 1439.01 | 8.2229 | 1406 | N/A | 1423.84 | 8.1362 | 1405.03 | N/A | 1425.82 | 8.1475 | 1409.28 | N/A | 1427.38 | 8.1565 | 1406.57 | N/A | 1421.13 | 8.1207 | 1404.41 | N/A | 1405.74 | 8.0328
GEN-2024-276 | DIS-24-1 | 03 CENTRAL | WERE | 150 | ER/NR | Battery/Storage | Tecumseh Hill - Swissvale 230kV Line | 785254 | 1 | 785250 | 4518.98 | 30.1265 | 3999.84 | N/A | 4450.94 | N/A | 4002.73 | N/A | 4454.83 | N/A | 4022.5 | N/A | 4490.81 | 29.9387 | 3985.22 | N/A | 4446.27 | N/A | 3996.72 | N/A | 4451.15 | N/A
GEN-2024-277 | DIS-24-1 | 03 CENTRAL | WERE | 150 | ER/NR | Battery/Storage | Tecumseh Hill - Swissvale 230kV Line | 785284 | 1 | 785250 | 4518.98 | 30.1265 | 3999.84 | N/A | 4450.94 | N/A | 4002.73 | N/A | 4454.83 | N/A | 4022.5 | N/A | 4490.81 | 29.9387 | 3985.22 | N/A | 4446.27 | N/A | 3996.72 | N/A | 4451.15 | N/A
GEN-2024-278 | DIS-24-1 | 05 SOUTHWEST | SPS | 264.3 | ER/NR | Wind | Eddy County - Crossroads 345 kV Line | 785314 | 1 | 785310 | 4319.14 | 31.9936 | 3965.43 | 29.3736 | 4284.92 | 31.7401 | 3965.08 | 29.371 | 4285.53 | 31.7447 | 3965.57 | 29.3746 | 4285.88 | 31.7473 | 3972.18 | 29.4236 | 4286.87 | 31.7546 | 3993.07 | 29.5783 | 4217.37 | 31.2398
GEN-2024-278 | DIS-24-1 | 05 SOUTHWEST | SPS | 264.3 | ER/NR | Battery/Storage | Eddy County - Crossroads 345 kV Line | 785317 | 1 | 785310 | 4319.14 | 63.9873 | 3965.43 | N/A | 4284.92 | N/A | 3965.08 | N/A | 4285.53 | N/A | 3965.57 | N/A | 4285.88 | N/A | 3972.18 | N/A | 4286.87 | N/A | 3993.07 | N/A | 4217.37 | 62.4796
GEN-2024-278 | DIS-24-1 | 05 SOUTHWEST | SPS | 264.3 | ER/NR | Wind | Eddy County - Crossroads 345 kV Line | 785320 | 1 | 785310 | 4319.14 | 31.9936 | 3965.43 | 29.3736 | 4284.92 | 31.7401 | 3965.08 | 29.371 | 4285.53 | 31.7447 | 3965.57 | 29.3746 | 4285.88 | 31.7473 | 3972.18 | 29.4236 | 4286.87 | 31.7546 | 3993.07 | 29.5783 | 4217.37 | 31.2398
GEN-2024-278 | DIS-24-1 | 05 SOUTHWEST | SPS | 264.3 | ER/NR | Battery/Storage | Eddy County - Crossroads 345 kV Line | 785323 | 1 | 785310 | 4319.14 | 63.9873 | 3965.43 | N/A | 4284.92 | N/A | 3965.08 | N/A | 4285.53 | N/A | 3965.57 | N/A | 4285.88 | N/A | 3972.18 | N/A | 4286.87 | N/A | 3993.07 | N/A | 4217.37 | 62.4796
GEN-2024-280 | DIS-24-1 | 05 SOUTHWEST | SPS | 350 | ER/NR | Solar | Andrews County 345 kV Substation | 785374 | 1 | 528604 | 9804.6 | 54.842 | 8032.25 | N/A | 9621.42 | 53.8174 | 8031.3 | N/A | 9631.98 | 53.8765 | 8034.2 | N/A | 9626.93 | 53.8482 | 8057.24 | N/A | 9626.89 | 53.848 | 8102.39 | N/A | 9360.05 | 52.3554
GEN-2024-280 | DIS-24-1 | 05 SOUTHWEST | SPS | 350 | ER/NR | Battery/Storage | Andrews County 345 kV Substation | 785377 | 1 | 528604 | 9804.6 | 54.6135 | 8032.25 | N/A | 9621.42 | N/A | 8031.3 | N/A | 9631.98 | N/A | 8034.2 | N/A | 9626.93 | N/A | 8057.24 | N/A | 9626.89 | N/A | 8102.39 | N/A | 9360.05 | 52.1373
GEN-2024-280 | DIS-24-1 | 05 SOUTHWEST | SPS | 350 | ER/NR | Solar | Andrews County 345 kV Substation | 785380 | 1 | 528604 | 9804.6 | 54.842 | 8032.25 | N/A | 9621.42 | 53.8174 | 8031.3 | N/A | 9631.98 | 53.8765 | 8034.2 | N/A | 9626.93 | 53.8482 | 8057.24 | N/A | 9626.89 | 53.848 | 8102.39 | N/A | 9360.05 | 52.3554
GEN-2024-280 | DIS-24-1 | 05 SOUTHWEST | SPS | 350 | ER/NR | Battery/Storage | Andrews County 345 kV Substation | 785383 | 1 | 528604 | 9804.6 | 55.9454 | 8032.25 | N/A | 9621.42 | N/A | 8031.3 | N/A | 9631.98 | N/A | 8034.2 | N/A | 9626.93 | N/A | 8057.24 | N/A | 9626.89 | N/A | 8102.39 | N/A | 9360.05 | 53.4088
GEN-2024-281 | DIS-24-1 | 05 SOUTHWEST | SPS | 250 | ER/NR | Solar | Jal - Teague 115 kV Line | 785404 | 1 | 785400 | 1778.5 | 13.8512 | 1715.73 | N/A | 1772.21 | 13.8023 | 1715.69 | N/A | 1772.65 | 13.8057 | 1715.83 | N/A | 1772.49 | 13.8044 | 1716.87 | N/A | 1772.45 | 13.8041 | 1718.36 | N/A | 1759.82 | 13.7058
GEN-2024-281 | DIS-24-1 | 05 SOUTHWEST | SPS | 250 | ER/NR | Battery/Storage | Jal - Teague 115 kV Line | 785407 | 1 | 785400 | 1778.5 | 13.9813 | 1715.73 | N/A | 1772.21 | N/A | 1715.69 | N/A | 1772.65 | N/A | 1715.83 | N/A | 1772.49 | N/A | 1716.87 | N/A | 1772.45 | N/A | 1718.36 | N/A | 1759.82 | 13.8344
GEN-2024-281 | DIS-24-1 | 05 SOUTHWEST | SPS | 250 | ER/NR | Solar | Jal - Teague 115 kV Line | 785410 | 1 | 785400 | 1778.5 | 13.8512 | 1715.73 | N/A | 1772.21 | 13.8023 | 1715.69 | N/A | 1772.65 | 13.8057 | 1715.83 | N/A | 1772.49 | 13.8044 | 1716.87 | N/A | 1772.45 | 13.8041 | 1718.36 | N/A | 1759.82 | 13.7058
GEN-2024-281 | DIS-24-1 | 05 SOUTHWEST | SPS | 250 | ER/NR | Battery/Storage | Jal - Teague 115 kV Line | 785413 | 1 | 785400 | 1778.5 | 13.9813 | 1715.73 | N/A | 1772.21 | N/A | 1715.69 | N/A | 1772.65 | N/A | 1715.83 | N/A | 1772.49 | N/A | 1716.87 | N/A | 1772.45 | N/A | 1718.36 | N/A | 1759.82 | 13.8344
GEN-2024-282 | DIS-24-1 | 01 NORTH | WAPA | 150 | ER/NR | Solar | Maurine - New Underwood 230 kV Line | 785434 | 1 | 785430 | 1186.7 | 15.8227 | 1133.66 | N/A | 1175.86 | 15.6781 | 1004.84 | N/A | 1011.81 | 13.4908 | 989.02 | N/A | 995.52 | 13.2736 | 988.82 | N/A | 994.84 | 13.2645 | 1004.09 | N/A | 1011.19 | 13.4825
GEN-2024-282 | DIS-24-1 | 01 NORTH | WAPA | 150 | ER/NR | Solar | Maurine - New Underwood 230 kV Line | 785437 | 1 | 785430 | 1186.7 | 15.8227 | 1133.66 | N/A | 1175.86 | 15.6781 | 1004.84 | N/A | 1011.81 | 13.4908 | 989.02 | N/A | 995.52 | 13.2736 | 988.82 | N/A | 994.84 | 13.2645 | 1004.09 | N/A | 1011.19 | 13.4825
GEN-2024-283 | DIS-24-1 | 01 NORTH | WAPA | 150 | ER/NR | Solar | Maurine - New Underwood 230 kV Line | 785464 | 1 | 785430 | 1186.7 | 15.8227 | 1133.66 | N/A | 1175.86 | 15.6781 | 1004.84 | N/A | 1011.81 | 13.4908 | 989.02 | N/A | 995.52 | 13.2736 | 988.82 | N/A | 994.84 | 13.2645 | 1004.09 | N/A | 1011.19 | 13.4825
GEN-2024-283 | DIS-24-1 | 01 NORTH | WAPA | 150 | ER/NR | Solar | Maurine - New Underwood 230 kV Line | 785467 | 1 | 785430 | 1186.7 | 15.8227 | 1133.66 | N/A | 1175.86 | 15.6781 | 1004.84 | N/A | 1011.81 | 13.4908 | 989.02 | N/A | 995.52 | 13.2736 | 988.82 | N/A | 994.84 | 13.2645 | 1004.09 | N/A | 1011.19 | 13.4825
GEN-2024-284 | DIS-24-1 | 01 NORTH | BEPC | 199 | ER/NR | Solar | Antelope Valley - Broadland 345 kV Line | 785494 | 1 | 785490 | 2108.51 | 10.5955 | 2064.8 | N/A | 2105.85 | 10.5822 | 2046.06 | N/A | 2090.14 | 10.5032 | 2044.06 | N/A | 2089.04 | 10.4977 | 2043.96 | N/A | 2088.99 | 10.4974 | 2044.19 | N/A | 2089.07 | 10.4978
GEN-2024-285 | DIS-24-1 | 01 NORTH | BEPC | 250 | ER/NR | Wind | Crocker 345 kV Substation | 785524 | 1 | 659165 | 3683.1 | 29.077 | 3473.29 | 27.4206 | 3641.92 | 28.7519 | 3430.26 | 27.0809 | 3648.06 | 28.8004 | 3429.2 | 27.0726 | 3647.61 | 28.7968 | 3429.14 | 27.0721 | 3647.59 | 28.7967 | 3430.03 | 27.0791 | 3647.62 | 28.7969
GEN-2024-285 | DIS-24-1 | 01 NORTH | BEPC | 250 | ER/NR | Wind | Crocker 345 kV Substation | 785527 | 1 | 659165 | 3683.1 | 29.8631 | 3473.29 | 28.1619 | 3641.92 | 29.5292 | 3430.26 | 27.813 | 3648.06 | 29.5789 | 3429.2 | 27.8044 | 3647.61 | 29.5753 | 3429.14 | 27.8039 | 3647.59 | 29.5751 | 3430.03 | 27.8111 | 3647.62 | 29.5754
GEN-2024-286 | DIS-24-1 | 04 SOUTHEAST | OGE | 136 | ER | Thermal | AES 5 161 kV Substation | 785554 | 1 | 515262 | 3461.16 | 50.8994 | 3175.06 | N/A | 3340.71 | N/A | 3175.06 | N/A | 3340.71 | N/A | 3175.3 | N/A | 3340.74 | N/A | 3175.41 | N/A | 3384.29 | N/A | 3175.55 | N/A | 3340.71 | N/A
GEN-2024-286 | DIS-24-1 | 04 SOUTHEAST | OGE | 136 | ER | Thermal | AES 5 161 kV Substation | 785557 | 1 | 515262 | 3461.16 | 50.8994 | 3175.06 | N/A | 3340.71 | N/A | 3175.06 | N/A | 3340.71 | N/A | 3175.3 | N/A | 3340.74 | N/A | 3175.41 | N/A | 3384.29 | N/A | 3175.55 | N/A | 3340.71 | N/A
GEN-2024-287 | DIS-24-1 | 03 CENTRAL | NEETSW | 199.8 | ER/NR | Solar | Wolf Creek - Blackberry 345 kV Line | 785584 | 1 | 785580 | 6296.15 | 31.5123 | 5615.86 | N/A | 5938.3 | 29.7212 | 5616.55 | N/A | 5938.51 | 29.7223 | 5640.96 | N/A | 6204.72 | 31.0547 | 5635.98 | N/A | 5959.95 | 29.8296 | 5621.16 | N/A | 5940.24 | 29.7309
GEN-2024-288 | DIS-24-1 | 03 CENTRAL | SUNC | 130 | ER/NR | Solar | Elm Creek - Tobias 345 kV Line | 785614 | 1 | 785610 | 6332.66 | 48.7128 | 5356.49 | N/A | 5766.02 | 44.354 | 5424.28 | N/A | 5824.58 | 44.8045 | 5633.82 | N/A | 6035.8 | 46.4292 | 5365.88 | N/A | 5779.11 | 44.4547 | 5361.27 | N/A | 5780.78 | 44.4675
GEN-2024-289 | DIS-24-1 | 03 CENTRAL | WERE | 350 | ER/NR | Solar | Archie - Clinton 161 kV Line | 785644 | 1 | 785640 | 3506.16 | 20.2578 | 3007.23 | N/A | 3339.27 | 19.2936 | 3007.84 | N/A | 3339.35 | 19.294 | 3015.71 | N/A | 3484.85 | 20.1347 | 3007.94 | N/A | 3341.28 | 19.3052 | 3009.21 | N/A | 3339.88 | 19.2971
GEN-2024-289 | DIS-24-1 | 03 CENTRAL | WERE | 350 | ER/NR | Solar | Archie - Clinton 161 kV Line | 785647 | 1 | 785640 | 3506.16 | 19.8174 | 3007.23 | N/A | 3339.27 | 18.8741 | 3007.84 | N/A | 3339.35 | 18.8746 | 3015.71 | N/A | 3484.85 | 19.697 | 3007.94 | N/A | 3341.28 | 18.8855 | 3009.21 | N/A | 3339.88 | 18.8776
GEN-2024-291 | DIS-24-1 | 04 SOUTHEAST | OGE | 250 | ER/NR | Wind | Canadian River 345 kV Substation | 785704 | 1 | 515422 | 7351.89 | 58.8151 | 6102.02 | 48.8162 | 6923.62 | 55.389 | 6102.08 | 48.8166 | 6923.6 | 55.3888 | 6105.7 | 48.8456 | 6924.98 | 55.3998 | 6279.99 | 50.2399 | 7176.61 | 57.4129 | 6109.6 | 48.8768 | 6923.41 | 55.3873
GEN-2024-291 | DIS-24-1 | 04 SOUTHEAST | OGE | 250 | ER/NR | Wind | Canadian River 345 kV Substation | 785707 | 1 | 515422 | 7351.89 | 58.8151 | 6102.02 | 48.8162 | 6923.62 | 55.389 | 6102.08 | 48.8166 | 6923.6 | 55.3888 | 6105.7 | 48.8456 | 6924.98 | 55.3998 | 6279.99 | 50.2399 | 7176.61 | 57.4129 | 6109.6 | 48.8768 | 6923.41 | 55.3873
GEN-2024-293 | DIS-24-1 | 04 SOUTHEAST | OGE | 248 | ER | Thermal | Muskoge7 345 kV Substation | 785764 | 1 | 515224 | 20061.18 | 80.8919 | 14702.94 | N/A | 18481.37 | N/A | 14703.21 | N/A | 18481.31 | N/A | 14716.74 | N/A | 18488.35 | N/A | 14888.34 | N/A | 19249.57 | N/A | 14714.12 | N/A | 18481.57 | N/A
GEN-2024-294 | DIS-24-1 | 04 SOUTHEAST | GRDA | 500 | ER/NR | Solar | Tulsa North - Igloo Valley 345 kV line | 785794 | 1 | 785790 | 12768.21 | 25.0824 | 11055.59 | N/A | 12422.05 | 24.4024 | 11056.59 | N/A | 12420.88 | 24.4001 | 11097.15 | N/A | 12463.27 | 24.4834 | 11198.62 | N/A | 12602.61 | 24.7571 | 11073.12 | N/A | 12425.12 | 24.4084
GEN-2024-294 | DIS-24-1 | 04 SOUTHEAST | GRDA | 500 | ER/NR | Storage | Tulsa North - Igloo Valley 345 kV line | 785797 | 1 | 785790 | 12768.21 | 50.5327 | 11055.59 | N/A | 12422.05 | N/A | 11056.59 | N/A | 12420.88 | N/A | 11097.15 | N/A | 12463.27 | N/A | 11198.62 | N/A | 12602.61 | 49.8774 | 11073.12 | N/A | 12425.12 | N/A
GEN-2024-295 | DIS-24-1 | 05 SOUTHWEST | SPS | 115 | ER/NR | Battery/Storage | S Loving 115 kV Substation | 785824 | 1 | 528192 | 2950.56 | 25.657 | 2797.12 | N/A | 2933.09 | N/A | 2797.01 | N/A | 2933.56 | N/A | 2797.55 | N/A | 2933.76 | N/A | 2802.04 | N/A | 2934.81 | N/A | 2798.55 | N/A | 2755.3 | 23.9591
GEN-2024-296 | DIS-24-1 | 04 SOUTHEAST | OGE | 167 | ER/NR | Solar | Muskogee - Pittsburg 345 kV Line | 785854 | 1 | 785850 | 7381.7 | 44.2018 | 6261.62 | N/A | 6994.76 | 41.8848 | 6261.69 | N/A | 6994.74 | 41.8847 | 6265.31 | N/A | 6996.1 | 41.8928 | 6404.68 | N/A | 7222.71 | 43.2498 | 6268.3 | N/A | 6994.63 | 41.884
GEN-2024-297 | DIS-24-1 | 04 SOUTHEAST | OGE | 167 | ER/NR | Solar | Muskogee - Pittsburg 345 kV Line | 785884 | 1 | 785850 | 7381.7 | 44.2018 | 6261.62 | N/A | 6994.76 | 41.8848 | 6261.69 | N/A | 6994.74 | 41.8847 | 6265.31 | N/A | 6996.1 | 41.8928 | 6404.68 | N/A | 7222.71 | 43.2498 | 6268.3 | N/A | 6994.63 | 41.884
GEN-2024-298 | DIS-24-1 | 04 SOUTHEAST | OGE | 167 | ER/NR | Solar | Muskogee - Pittsburg 345 kV Line | 785914 | 1 | 785850 | 7381.7 | 44.2018 | 6261.62 | N/A | 6994.76 | 41.8848 | 6261.69 | N/A | 6994.74 | 41.8847 | 6265.31 | N/A | 6996.1 | 41.8928 | 6404.68 | N/A | 7222.71 | 43.2498 | 6268.3 | N/A | 6994.63 | 41.884
GEN-2024-299 | DIS-24-1 | 04 SOUTHEAST | OGE | 744 | ER | Thermal | AES 5 345 kV Substation | 785944 | 1 | 515012 | 7060.72 | 28.4706 | 6427.72 | N/A | 6825.9 | N/A | 6427.74 | N/A | 6825.89 | N/A | 6428.97 | N/A | 6826.31 | N/A | 6440.36 | N/A | 6892.62 | N/A | 6428.82 | N/A | 6825.91 | N/A
GEN-2024-299 | DIS-24-1 | 04 SOUTHEAST | OGE | 744 | ER | Thermal | AES 5 345 kV Substation | 785947 | 1 | 515012 | 7060.72 | 28.4706 | 6427.72 | N/A | 6825.9 | N/A | 6427.74 | N/A | 6825.89 | N/A | 6428.97 | N/A | 6826.31 | N/A | 6440.36 | N/A | 6892.62 | N/A | 6428.82 | N/A | 6825.91 | N/A
GEN-2024-299 | DIS-24-1 | 04 SOUTHEAST | OGE | 744 | ER | Thermal | AES 5 345 kV Substation | 785950 | 1 | 515012 | 7060.72 | 28.4706 | 6427.72 | N/A | 6825.9 | N/A | 6427.74 | N/A | 6825.89 | N/A | 6428.97 | N/A | 6826.31 | N/A | 6440.36 | N/A | 6892.62 | N/A | 6428.82 | N/A | 6825.91 | N/A
GEN-2024-303 | DIS-24-1 | 05 SOUTHWEST | SPS | 500 | ER/NR | Solar | Crossroads 345 kV Substation | 786064 | 1 | 527656 | 11096.62 | 21.4668 | 9429.77 | N/A | 10857.55 | 21.0044 | 9427.42 | N/A | 10856.99 | 21.0033 | 9428.23 | N/A | 10863.31 | 21.0155 | 9466.71 | N/A | 10871.01 | 21.0304 | 9633.93 | N/A | 10721.3 | 20.7408
GEN-2024-303 | DIS-24-1 | 05 SOUTHWEST | SPS | 500 | ER/NR | Battery/Storage | Crossroads 345 kV Substation | 786067 | 1 | 527656 | 11096.62 | 21.6858 | 9429.77 | N/A | 10857.55 | N/A | 9427.42 | N/A | 10856.99 | N/A | 9428.23 | N/A | 10863.31 | N/A | 9466.71 | N/A | 10871.01 | N/A | 9633.93 | N/A | 10721.3 | 20.9523
GEN-2024-304 | DIS-24-1 | 05 SOUTHWEST | SPS | 500 | ER/NR | Solar | Crossroads 345 kV Substation | 786094 | 1 | 527656 | 11096.62 | 21.7408 | 9429.77 | N/A | 10857.55 | 21.2724 | 9427.42 | N/A | 10856.99 | 21.2713 | 9428.23 | N/A | 10863.31 | 21.2837 | 9466.71 | N/A | 10871.01 | 21.2988 | 9633.93 | N/A | 10721.3 | 21.0054
GEN-2024-304 | DIS-24-1 | 05 SOUTHWEST | SPS | 500 | ER/NR | Battery/Storage | Crossroads 345 kV Substation | 786097 | 1 | 527656 | 11096.62 | 21.8221 | 9429.77 | N/A | 10857.55 | N/A | 9427.42 | N/A | 10856.99 | N/A | 9428.23 | N/A | 10863.31 | N/A | 9466.71 | N/A | 10871.01 | N/A | 9633.93 | N/A | 10721.3 | 21.084
GEN-2024-305 | DIS-24-1 | 04 SOUTHEAST | AEP | 50 | ER/NR | Battery/Storage | Superior - Jefferson 69 kV Line | 786124 | 1 | 786120 | 689.46 | 13.7892 | 641.58 | N/A | 659.39 | N/A | 641.58 | N/A | 659.39 | N/A | 641.59 | N/A | 659.39 | N/A | 641.82 | N/A | 685.66 | 13.7132 | 641.6 | N/A | 659.34 | N/A
GEN-2024-306 | DIS-24-1 | 05 SOUTHWEST | SPS | 150 | ER/NR | Battery/Storage | Taylor Switching Station 115 kV Substation | 786154 | 1 | 528413 | 3233.46 | 21.5564 | 2728.87 | N/A | 3201.67 | N/A | 2728.75 | N/A | 3201.95 | N/A | 2729.21 | N/A | 3201.86 | N/A | 2730.99 | N/A | 3201.97 | N/A | 2740.44 | N/A | 3215.07 | 21.4338
GEN-2024-308 | DIS-24-1 | 04 SOUTHEAST | WFEC | 199 | ER/NR | Wind | Okeene - Mooreland 138 kV line | 786214 | 1 | 786210 | 4512.09 | 43.5951 | 3306.43 | 31.9462 | 4081.05 | 39.4304 | 3306.53 | 31.9471 | 4081.11 | 39.431 | 3311.17 | 31.992 | 4089.09 | 39.5081 | 3694.59 | 35.6965 | 4476.01 | 43.2465 | 3311.53 | 31.9955 | 4082.04 | 39.44
GEN-2024-308 | DIS-24-1 | 04 SOUTHEAST | WFEC | 199 | ER/NR | Wind | Okeene - Mooreland 138 kV line | 786217 | 1 | 786210 | 4512.09 | 43.5951 | 3306.43 | 31.9462 | 4081.05 | 39.4304 | 3306.53 | 31.9471 | 4081.11 | 39.431 | 3311.17 | 31.992 | 4089.09 | 39.5081 | 3694.59 | 35.6965 | 4476.01 | 43.2465 | 3311.53 | 31.9955 | 4082.04 | 39.44
GEN-2024-308 | DIS-24-1 | 04 SOUTHEAST | WFEC | 199 | ER/NR | Storage | Okeene - Mooreland 138 kV line | 786220 | 1 | 786210 | 4512.09 | 43.3855 | 3306.43 | N/A | 4081.05 | N/A | 3306.53 | N/A | 4081.11 | N/A | 3311.17 | N/A | 4089.09 | N/A | 3694.59 | N/A | 4476.01 | 43.0386 | 3311.53 | N/A | 4082.04 | N/A
GEN-2024-310 | DIS-24-1 | 05 SOUTHWEST | SPS | 75 | ER | Battery/Storage | Eddy - Chaves 230 kV line | 786274 | 1 | 786270 | 1691.07 | 43.3608 | 1616.89 | N/A | 1686.9 | N/A | 1616.83 | N/A | 1687.03 | N/A | 1616.93 | N/A | 1687.02 | N/A | 1617.9 | N/A | 1687.11 | N/A | 1620.55 | N/A | 1658.9 | 42.5359
GEN-2024-310 | DIS-24-1 | 05 SOUTHWEST | SPS | 75 | ER | Battery/Storage | Eddy - Chaves 230 kV line | 786277 | 1 | 786270 | 1691.07 | 46.9742 | 1616.89 | N/A | 1686.9 | N/A | 1616.83 | N/A | 1687.03 | N/A | 1616.93 | N/A | 1687.02 | N/A | 1617.9 | N/A | 1687.11 | N/A | 1620.55 | N/A | 1658.9 | 46.0806
GEN-2024-311 | DIS-24-1 | 05 SOUTHWEST | SPS | 225 | ER/NR | Solar | Eddy - Chaves 230 kV line | 786304 | 1 | 786270 | 1691.07 | 29.5937 | 1616.89 | N/A | 1686.9 | 29.5207 | 1616.83 | N/A | 1687.03 | 29.523 | 1616.93 | N/A | 1687.02 | 29.5228 | 1617.9 | N/A | 1687.11 | 29.5244 | 1620.55 | N/A | 1658.9 | 29.0307
GEN-2024-311 | DIS-24-1 | 05 SOUTHWEST | SPS | 225 | ER/NR | Solar | Eddy - Chaves 230 kV line | 786307 | 1 | 786270 | 1691.07 | 29.5937 | 1616.89 | N/A | 1686.9 | 29.5207 | 1616.83 | N/A | 1687.03 | 29.523 | 1616.93 | N/A | 1687.02 | 29.5228 | 1617.9 | N/A | 1687.11 | 29.5244 | 1620.55 | N/A | 1658.9 | 29.0307
GEN-2024-311 | DIS-24-1 | 05 SOUTHWEST | SPS | 225 | ER/NR | Solar | Eddy - Chaves 230 kV line | 786310 | 1 | 786270 | 1691.07 | 29.5937 | 1616.89 | N/A | 1686.9 | 29.5207 | 1616.83 | N/A | 1687.03 | 29.523 | 1616.93 | N/A | 1687.02 | 29.5228 | 1617.9 | N/A | 1687.11 | 29.5244 | 1620.55 | N/A | 1658.9 | 29.0307
GEN-2024-311 | DIS-24-1 | 05 SOUTHWEST | SPS | 225 | ER/NR | Solar | Eddy - Chaves 230 kV line | 786313 | 1 | 786270 | 1691.07 | 31.5669 | 1616.89 | N/A | 1686.9 | 31.4891 | 1616.83 | N/A | 1687.03 | 31.4915 | 1616.93 | N/A | 1687.02 | 31.4913 | 1617.9 | N/A | 1687.11 | 31.493 | 1620.55 | N/A | 1658.9 | 30.9664
GEN-2024-312 | DIS-24-1 | 04 SOUTHEAST | SWPA | 50 | ER/NR | Solar | Clarksville Ozark 161 kV line | 786334 | 1 | 786330 | 2075.85 | 41.517 | 1525.93 | N/A | 1932.86 | 38.6572 | 1525.93 | N/A | 1932.86 | 38.6572 | 1525.97 | N/A | 1932.87 | 38.6574 | 1525.51 | N/A | 1951.86 | 39.0372 | 1525.99 | N/A | 1932.86 | 38.6572
GEN-2024-316 | DIS-24-1 | 04 SOUTHEAST | AEP | 300 | ER/NR | Solar | Pittsburg - Valliant 345 kV Line | 786454 | 1 | 786450 | 7470.28 | 49.8019 | 5096.26 | N/A | 6301.87 | 42.0125 | 5096.29 | N/A | 6301.86 | 42.0124 | 5097.97 | N/A | 6302.48 | 42.0165 | 5242.49 | N/A | 6565.76 | 43.7717 | 5102.48 | N/A | 6297.3 | 41.982
GEN-2024-316 | DIS-24-1 | 04 SOUTHEAST | AEP | 300 | ER/NR | Solar | Pittsburg - Valliant 345 kV Line | 786457 | 1 | 786450 | 7470.28 | 49.8019 | 5096.26 | N/A | 6301.87 | 42.0125 | 5096.29 | N/A | 6301.86 | 42.0124 | 5097.97 | N/A | 6302.48 | 42.0165 | 5242.49 | N/A | 6565.76 | 43.7717 | 5102.48 | N/A | 6297.3 | 41.982
GEN-2024-317 | DIS-24-1 | 05 SOUTHWEST | SPS | 300 | ER/NR | Solar | Dragon 345 kV Substation | 786484 | 1 | 762467 | 3771.04 | 25.1403 | 3386.02 | N/A | 3538.47 | 23.5898 | 3385.96 | N/A | 3538.81 | 23.5921 | 3389.23 | N/A | 3542.28 | 23.6152 | 3417.77 | N/A | 3558.73 | 23.7249 | 3414.73 | N/A | 3703.55 | 24.6903
GEN-2024-317 | DIS-24-1 | 05 SOUTHWEST | SPS | 300 | ER/NR | Solar | Dragon 345 kV Substation | 786487 | 1 | 762467 | 3771.04 | 25.1403 | 3386.02 | N/A | 3538.47 | 23.5898 | 3385.96 | N/A | 3538.81 | 23.5921 | 3389.23 | N/A | 3542.28 | 23.6152 | 3417.77 | N/A | 3558.73 | 23.7249 | 3414.73 | N/A | 3703.55 | 24.6903
GEN-2024-318 | DIS-24-1 | 04 SOUTHEAST | AEP | 199 | ER/NR | Battery/Storage | Tulsa North - American Airlines 138 kV Line | 786514 | 1 | 786510 | 5270.02 | 52.0516 | 4702.69 | N/A | 5175.86 | N/A | 4702.79 | N/A | 5175.82 | N/A | 4708.12 | N/A | 5179.85 | N/A | 4736.08 | N/A | 5217.33 | 51.5312 | 4704.58 | N/A | 5175.99 | N/A
GEN-2024-318 | DIS-24-1 | 04 SOUTHEAST | AEP | 199 | ER/NR | Battery/Storage | Tulsa North - American Airlines 138 kV Line | 786517 | 1 | 786510 | 5270.02 | 53.911 | 4702.69 | N/A | 5175.86 | N/A | 4702.79 | N/A | 5175.82 | N/A | 4708.12 | N/A | 5179.85 | N/A | 4736.08 | N/A | 5217.33 | 53.372 | 4704.58 | N/A | 5175.99 | N/A
GEN-2024-319 | DIS-24-1 | 03 CENTRAL | KACY | 199 | ER/NR | Battery/Storage | Metro 5 161 kV Substation | 786544 | 1 | 546742 | 7338.81 | 72.4849 | 5409.28 | N/A | 7080.62 | N/A | 5412.74 | N/A | 7081.63 | N/A | 5470.78 | N/A | 7145.76 | 70.5782 | 5420.73 | N/A | 7121.57 | N/A | 5433.95 | N/A | 7088.83 | N/A
GEN-2024-319 | DIS-24-1 | 03 CENTRAL | KACY | 199 | ER/NR | Battery/Storage | Metro 5 161 kV Substation | 786547 | 1 | 546742 | 7338.81 | 75.0743 | 5409.28 | N/A | 7080.62 | N/A | 5412.74 | N/A | 7081.63 | N/A | 5470.78 | N/A | 7145.76 | 73.0994 | 5420.73 | N/A | 7121.57 | N/A | 5433.95 | N/A | 7088.83 | N/A
GEN-2024-320 | DIS-24-1 | 03 CENTRAL | WERE | 199 | ER/NR | Battery/Storage | Jaggard 115 kV Substation | 786574 | 1 | 533243 | 3468.38 | 34.257 | 3117.82 | N/A | 3426.42 | N/A | 3119.3 | N/A | 3426.94 | N/A | 3128.95 | N/A | 3449.33 | 34.0688 | 3095.07 | N/A | 3414.27 | N/A | 3111.29 | N/A | 3424.45 | N/A
GEN-2024-320 | DIS-24-1 | 03 CENTRAL | WERE | 199 | ER/NR | Battery/Storage | Jaggard 115 kV Substation | 786577 | 1 | 533243 | 3468.38 | 35.4807 | 3117.82 | N/A | 3426.42 | N/A | 3119.3 | N/A | 3426.94 | N/A | 3128.95 | N/A | 3449.33 | 35.2858 | 3095.07 | N/A | 3414.27 | N/A | 3111.29 | N/A | 3424.45 | N/A
GEN-2024-321 | DIS-24-1 | 04 SOUTHEAST | OGE | 493 | ER/NR | Thermal | Seminole 345 kV Substation | 786604 | 1 | 515045 | 25623.06 | 103.9475 | 16429.62 | N/A | 23503.4 | N/A | 16430.58 | N/A | 23502.58 | N/A | 16484.49 | N/A | 23551.25 | N/A | 17401.49 | N/A | 24391.67 | N/A | 16534.46 | N/A | 23503.36 | N/A
GEN-2024-321 | DIS-24-1 | 04 SOUTHEAST | OGE | 493 | ER/NR | Thermal | Seminole 345 kV Substation | 786607 | 1 | 515045 | 25623.06 | 103.9475 | 16429.62 | N/A | 23503.4 | N/A | 16430.58 | N/A | 23502.58 | N/A | 16484.49 | N/A | 23551.25 | N/A | 17401.49 | N/A | 24391.67 | N/A | 16534.46 | N/A | 23503.36 | N/A
GEN-2024-322 | DIS-24-1 | 03 CENTRAL | MIDW | 75 | ER/NR | Battery/Storage | Redlin - Beach3 115 kV line | 786634 | 1 | 786630 | 766.57 | 10.2209 | 727.98 | N/A | 762.8 | N/A | 728.54 | N/A | 763.22 | N/A | 707.99 | N/A | 735.01 | 9.8001 | 716.77 | N/A | 729.13 | N/A | 719.87 | N/A | 729.19 | N/A
GEN-2024-323 | DIS-24-1 | 04 SOUTHEAST | ITCGP | 356.8 | ER | Thermal | ITC Hugo 7 345 kV Substation | 786664 | 1 | 521157 | 7599.69 | 42.5992 | 4764.52 | N/A | 6305.83 | N/A | 4764.55 | N/A | 6305.82 | N/A | 4765.88 | N/A | 6306.36 | N/A | 4900.76 | N/A | 6690.3 | N/A | 4770.7 | N/A | 6301.49 | N/A
GEN-2024-323 | DIS-24-1 | 04 SOUTHEAST | ITCGP | 356.8 | ER | Thermal | ITC Hugo 7 345 kV Substation | 786667 | 1 | 521157 | 7599.69 | 42.5992 | 4764.52 | N/A | 6305.83 | N/A | 4764.55 | N/A | 6305.82 | N/A | 4765.88 | N/A | 6306.36 | N/A | 4900.76 | N/A | 6690.3 | N/A | 4770.7 | N/A | 6301.49 | N/A
GEN-2024-324 | DIS-24-1 | 05 SOUTHWEST | SPS | 160 | ER/NR | Battery/Storage | Samson 115 kV Substation | 786694 | 1 | 527546 | 1059.23 | 6.6202 | 1022.84 | N/A | 1041.92 | N/A | 1022.8 | N/A | 1041.95 | N/A | 1022.84 | N/A | 1041.95 | N/A | 1023.2 | N/A | 1041.98 | N/A | 1024.21 | N/A | 1048.92 | 6.5558
GEN-2024-325 | DIS-24-1 | 05 SOUTHWEST | SPS | 150 | ER/NR | Battery/Storage | Sierra 115 kV Substation | 786724 | 1 | 527533 | 1104.3 | 7.362 | 1058.51 | N/A | 1086.29 | N/A | 1058.46 | N/A | 1086.32 | N/A | 1058.5 | N/A | 1086.33 | N/A | 1058.89 | N/A | 1086.36 | N/A | 1059.98 | N/A | 1092.68 | 7.2845
GEN-2024-326 | DIS-24-1 | 01 NORTH | WAPA | 225 | ER/NR | Battery/Storage | Belfield 230 kV Substation | 786754 | 1 | 652425 | 3842.18 | 17.0764 | 3459.66 | N/A | 3763.72 | 16.7276 | 3256.08 | N/A | 3593.92 | N/A | 3254.21 | N/A | 3588.87 | N/A | 3254.25 | N/A | 3588.78 | N/A | 3255.87 | N/A | 3594.08 | N/A
GEN-2024-327 | DIS-24-1 | 01 NORTH | CPEC | 200 | ER/NR | Battery/Storage | Berthold 115 kV Substation | 786784 | 1 | 655641 | 1212.13 | 6.0607 | 1195.94 | N/A | 1196.17 | 5.9809 | 1174.87 | N/A | 1179.29 | N/A | 1174.95 | N/A | 1178.81 | N/A | 1174.99 | N/A | 1178.77 | N/A | 1174.89 | N/A | 1179.24 | N/A
GEN-2024-328 | DIS-24-1 | 01 NORTH | BEPC | 250 | ER/NR | Battery/Storage | Little Missouri 230 kV Substation | 786814 | 1 | 659265 | 1399.37 | 5.5975 | 1279.7 | N/A | 1389.06 | 5.5562 | 1146.44 | N/A | 1263.47 | N/A | 1144.88 | N/A | 1258.14 | N/A | 1144.87 | N/A | 1258.09 | N/A | 1146.36 | N/A | 1263.44 | N/A
GEN-2024-329 | DIS-24-1 | 01 NORTH | MWEC | 200 | ER/NR | Battery/Storage | Pleasant Valley 115 kV Substation | 786844 | 1 | 655902 | 1617.78 | 8.0889 | 1512.14 | N/A | 1558.2 | 7.791 | 1472.89 | N/A | 1526.53 | N/A | 1473.16 | N/A | 1525.46 | N/A | 1473.26 | N/A | 1525.28 | N/A | 1472.97 | N/A | 1526.3 | N/A
GEN-2024-330 | DIS-24-1 | 03 CENTRAL | WERE | 225 | ER/NR | Battery/Storage | Midian 138 kV Substation | 786874 | 1 | 532990 | 2985.57 | 13.2692 | 2815.94 | N/A | 2932.71 | N/A | 2820.37 | N/A | 2933.27 | N/A | 2828.08 | N/A | 2943.38 | 13.0817 | 2777.56 | N/A | 2877.82 | N/A | 2806.9 | N/A | 2882.67 | N/A
GEN-2024-331 | DIS-24-1 | 01 NORTH | BEPC | 300 | ER/NR | Battery/Storage | Round Up 345 kV Substation | 786904 | 1 | 659384 | 6437.9 | 21.4597 | 5391.98 | N/A | 6210.04 | 20.7001 | 5203.38 | N/A | 6039.84 | N/A | 5202.54 | N/A | 6036.84 | N/A | 5202.68 | N/A | 6036.58 | N/A | 5202.94 | N/A | 6039.64 | N/A
GEN-2024-332 | DIS-24-1 | 04 SOUTHEAST | OGE | 150 | ER/NR | Battery/Storage | Discovery 138 kV Substation | 786934 | 1 | 514962 | 6653.52 | 44.3568 | 5526.43 | N/A | 6431.41 | N/A | 5526.53 | N/A | 6431.38 | N/A | 5532.38 | N/A | 6434.05 | N/A | 5646.37 | N/A | 6492.38 | 43.2825 | 5536.86 | N/A | 6431.7 | N/A
GEN-2024-333 | DIS-24-1 | 04 SOUTHEAST | OGE | 100 | ER/NR | Battery/Storage | Kelley Avenue 138 kV | 786964 | 1 | 514501 | 7111.59 | 71.1159 | 5743.1 | N/A | 6882.19 | N/A | 5743.21 | N/A | 6882.16 | N/A | 5750.69 | N/A | 6885.69 | N/A | 5889.42 | N/A | 6953.94 | 69.5394 | 5754.05 | N/A | 6882.59 | N/A
GEN-2024-334 | DIS-24-1 | 04 SOUTHEAST | OGE | 124 | ER/NR | Thermal | Ranch Road 345 kV Substation | 786994 | 1 | 515576 | 8022.43 | 129.394 | 6814.04 | N/A | 7191.01 | N/A | 6814.42 | N/A | 7191.45 | N/A | 6932.2 | N/A | 7310.05 | N/A | 7270.81 | N/A | 7870.88 | N/A | 6825.16 | N/A | 7195.67 | N/A
GEN-2024-334 | DIS-24-1 | 04 SOUTHEAST | OGE | 124 | ER/NR | Thermal | Ranch Road 345 kV Substation | 786997 | 1 | 515576 | 8022.43 | 129.394 | 6814.04 | N/A | 7191.01 | N/A | 6814.42 | N/A | 7191.45 | N/A | 6932.2 | N/A | 7310.05 | N/A | 7270.81 | N/A | 7870.88 | N/A | 6825.16 | N/A | 7195.67 | N/A
GEN-2024-336 | DIS-24-1 | 05 SOUTHWEST | SPS | 300 | ER/NR | Solar | Ink Basin 230 kV Substation | 787054 | 1 | 527028 | 4770 | 31.1969 | 3720.64 | N/A | 4672.01 | 30.556 | 3720.25 | N/A | 4672.45 | 30.5589 | 3721.63 | N/A | 4672.47 | 30.559 | 3725.64 | N/A | 4673.03 | 30.5627 | 3764.89 | N/A | 4719.7 | 30.8679
GEN-2024-336 | DIS-24-1 | 05 SOUTHWEST | SPS | 300 | ER/NR | Storage | Ink Basin 230 kV Substation | 787057 | 1 | 527028 | 4770 | 29.9262 | 3720.64 | N/A | 4672.01 | N/A | 3720.25 | N/A | 4672.45 | N/A | 3721.63 | N/A | 4672.47 | N/A | 3725.64 | N/A | 4673.03 | N/A | 3764.89 | N/A | 4719.7 | 29.6106
GEN-2024-336 | DIS-24-1 | 05 SOUTHWEST | SPS | 300 | ER/NR | Solar | Ink Basin 230 kV Substation | 787060 | 1 | 527028 | 4770 | 31.1969 | 3720.64 | N/A | 4672.01 | 30.556 | 3720.25 | N/A | 4672.45 | 30.5589 | 3721.63 | N/A | 4672.47 | 30.559 | 3725.64 | N/A | 4673.03 | 30.5627 | 3764.89 | N/A | 4719.7 | 30.8679
GEN-2024-336 | DIS-24-1 | 05 SOUTHWEST | SPS | 300 | ER/NR | Storage | Ink Basin 230 kV Substation | 787063 | 1 | 527028 | 4770 | 30.3729 | 3720.64 | N/A | 4672.01 | N/A | 3720.25 | N/A | 4672.45 | N/A | 3721.63 | N/A | 4672.47 | N/A | 3725.64 | N/A | 4673.03 | N/A | 3764.89 | N/A | 4719.7 | 30.0526
GEN-2024-337 | DIS-24-1 | 04 SOUTHEAST | OGE | 250 | ER/NR | Solar | Sunnyside - Pooleville 138 kV line | 787084 | 1 | 787080 | 1954.75 | 9.6044 | 1724.86 | N/A | 1771.97 | 8.7064 | 1724.86 | N/A | 1771.97 | 8.7064 | 1725.12 | N/A | 1772.11 | 8.707 | 1840.44 | N/A | 1901.77 | 9.3441 | 1726.73 | N/A | 1772.07 | 8.7068
GEN-2024-337 | DIS-24-1 | 04 SOUTHEAST | OGE | 250 | ER/NR | Storage | Sunnyside - Pooleville 138 kV line | 787087 | 1 | 787080 | 1954.75 | 39.095 | 1724.86 | N/A | 1771.97 | N/A | 1724.86 | N/A | 1771.97 | N/A | 1725.12 | N/A | 1772.11 | N/A | 1840.44 | N/A | 1901.77 | 38.0354 | 1726.73 | N/A | 1772.07 | N/A
GEN-2024-338 | DIS-24-1 | 04 SOUTHEAST | AEP | 350 | ER/NR | Solar | Pittsburg - Johnston County 345 kV line | 787114 | 1 | 787110 | 6368.48 | 36.3913 | 4576.53 | N/A | 5185.49 | 29.6314 | 4576.56 | N/A | 5185.48 | 29.6313 | 4578.73 | N/A | 5186.69 | 29.6382 | 5175.55 | N/A | 5872.51 | 33.5572 | 4589.28 | N/A | 5185.95 | 29.634
GEN-2024-338 | DIS-24-1 | 04 SOUTHEAST | AEP | 350 | ER/NR | Solar | Pittsburg - Johnston County 345 kV line | 787117 | 1 | 787110 | 6368.48 | 36.3913 | 4576.53 | N/A | 5185.49 | 29.6314 | 4576.56 | N/A | 5185.48 | 29.6313 | 4578.73 | N/A | 5186.69 | 29.6382 | 5175.55 | N/A | 5872.51 | 33.5572 | 4589.28 | N/A | 5185.95 | 29.634
GEN-2024-339 | DIS-24-1 | 03 CENTRAL | WERE | 300 | ER/NR | Battery/Storage | Stranger Creek 115 kV Substation | 787144 | 1 | 533268 | 7431.46 | 48.9533 | 5996.74 | N/A | 7228.66 | N/A | 6003.96 | N/A | 7232.4 | N/A | 6132.67 | N/A | 7350.15 | 48.4177 | 5973.31 | N/A | 7220.87 | N/A | 6000.42 | N/A | 7230.92 | N/A
GEN-2024-339 | DIS-24-1 | 03 CENTRAL | WERE | 300 | ER/NR | Battery/Storage | Stranger Creek 115 kV Substation | 787147 | 1 | 533268 | 7431.46 | 50.1472 | 5996.74 | N/A | 7228.66 | N/A | 6003.96 | N/A | 7232.4 | N/A | 6132.67 | N/A | 7350.15 | 49.5985 | 5973.31 | N/A | 7220.87 | N/A | 6000.42 | N/A | 7230.92 | N/A
GEN-2024-340 | DIS-24-1 | 04 SOUTHEAST | AEP | 1400 | ER/NR | Thermal | Riverside â€“ Redbud 345 kV line | 787174 | 1 | 787170 | 6262.83 | 15.3466 | 5518.11 | N/A | 6158.92 | N/A | 5518.21 | N/A | 6158.9 | N/A | 5523.91 | N/A | 6161.41 | N/A | 5617.72 | N/A | 6231.61 | N/A | 5523.65 | N/A | 6159.06 | N/A
GEN-2024-340 | DIS-24-1 | 04 SOUTHEAST | AEP | 1400 | ER/NR | Thermal | Riverside â€“ Redbud 345 kV line | 787177 | 1 | 787170 | 6262.83 | 21.4547 | 5518.11 | N/A | 6158.92 | N/A | 5518.21 | N/A | 6158.9 | N/A | 5523.91 | N/A | 6161.41 | N/A | 5617.72 | N/A | 6231.61 | N/A | 5523.65 | N/A | 6159.06 | N/A
GEN-2024-340 | DIS-24-1 | 04 SOUTHEAST | AEP | 1400 | ER/NR | Thermal | Riverside â€“ Redbud 345 kV line | 787180 | 1 | 787170 | 6262.83 | 15.3466 | 5518.11 | N/A | 6158.92 | N/A | 5518.21 | N/A | 6158.9 | N/A | 5523.91 | N/A | 6161.41 | N/A | 5617.72 | N/A | 6231.61 | N/A | 5523.65 | N/A | 6159.06 | N/A
GEN-2024-340 | DIS-24-1 | 04 SOUTHEAST | AEP | 1400 | ER/NR | Thermal | Riverside â€“ Redbud 345 kV line | 787183 | 1 | 787170 | 6262.83 | 21.4547 | 5518.11 | N/A | 6158.92 | N/A | 5518.21 | N/A | 6158.9 | N/A | 5523.91 | N/A | 6161.41 | N/A | 5617.72 | N/A | 6231.61 | N/A | 5523.65 | N/A | 6159.06 | N/A
GEN-2024-341 | DIS-24-1 | 04 SOUTHEAST | AEP | 1045 | ER/NR | Thermal | Pittsburgh 345 kV Substation | 787204 | 1 | 510907 | 10646.36 | 40.7516 | 7251.68 | N/A | 9485.76 | N/A | 7251.79 | N/A | 9485.72 | N/A | 7257.73 | N/A | 9488.75 | N/A | 7772.34 | N/A | 10094.47 | N/A | 7268.98 | N/A | 9484.69 | N/A
GEN-2024-341 | DIS-24-1 | 04 SOUTHEAST | AEP | 1045 | ER/NR | Thermal | Pittsburgh 345 kV Substation | 787207 | 1 | 510907 | 10646.36 | 40.7516 | 7251.68 | N/A | 9485.76 | N/A | 7251.79 | N/A | 9485.72 | N/A | 7257.73 | N/A | 9488.75 | N/A | 7772.34 | N/A | 10094.47 | N/A | 7268.98 | N/A | 9484.69 | N/A
GEN-2024-341 | DIS-24-1 | 04 SOUTHEAST | AEP | 1045 | ER/NR | Thermal | Pittsburgh 345 kV Substation | 787210 | 1 | 510907 | 10646.36 | 40.7516 | 7251.68 | N/A | 9485.76 | N/A | 7251.79 | N/A | 9485.72 | N/A | 7257.73 | N/A | 9488.75 | N/A | 7772.34 | N/A | 10094.47 | N/A | 7268.98 | N/A | 9484.69 | N/A
GEN-2024-341 | DIS-24-1 | 04 SOUTHEAST | AEP | 1045 | ER/NR | Thermal | Pittsburgh 345 kV Substation | 787213 | 1 | 510907 | 10646.36 | 40.7516 | 7251.68 | N/A | 9485.76 | N/A | 7251.79 | N/A | 9485.72 | N/A | 7257.73 | N/A | 9488.75 | N/A | 7772.34 | N/A | 10094.47 | N/A | 7268.98 | N/A | 9484.69 | N/A
GEN-2024-343 | DIS-24-1 | 04 SOUTHEAST | AEP | 470.5 | ER/NR | Thermal | LeBrock 345 kV Substation | 787264 | 1 | 508572 | 14154 | 60.1658 | 5025.76 | N/A | 9682.34 | N/A | 5025.77 | N/A | 9682.34 | N/A | 5026.25 | N/A | 9682.91 | N/A | 5041.83 | N/A | 10082.56 | N/A | 5027.04 | N/A | 9668.39 | N/A
GEN-2024-343 | DIS-24-1 | 04 SOUTHEAST | AEP | 470.5 | ER/NR | Thermal | LeBrock 345 kV Substation | 787266 | 1 | 508572 | 14154 | 60.1658 | 5025.76 | N/A | 9682.34 | N/A | 5025.77 | N/A | 9682.34 | N/A | 5026.25 | N/A | 9682.91 | N/A | 5041.83 | N/A | 10082.56 | N/A | 5027.04 | N/A | 9668.39 | N/A
GEN-2024-344 | DIS-24-1 | 04 SOUTHEAST | OGE/AEP | 200 | ER/NR | Wind | Riverside - Redbud Switch 345 kV Line | 787294 | 1 | 787290 | 9991.03 | 49.9552 | 5767.54 | 28.8377 | 6539.39 | 32.697 | 5767.65 | 28.8382 | 6539.37 | 32.6968 | 5774.33 | 28.8716 | 6542.42 | 32.7121 | 5893.92 | 29.4696 | 6619.7 | 33.0985 | 5774.51 | 28.8726 | 6539.57 | 32.6979
GEN-2024-345 | DIS-24-1 | 04 SOUTHEAST | AEP | 600 | ER/NR | Wind | Delaware 345 kV Substation | 787324 | 1 | 510380 | 7009.53 | 34.799 | 6106.23 | 30.3146 | 6636.71 | 32.9481 | 6106.58 | 30.3163 | 6636.76 | 32.9484 | 6125.84 | 30.4119 | 6691.88 | 33.222 | 6252.79 | 31.0422 | 6804 | 33.7786 | 6114.09 | 30.3536 | 6636.96 | 32.9494
GEN-2024-345 | DIS-24-1 | 04 SOUTHEAST | AEP | 600 | ER/NR | Wind | Delaware 345 kV Substation | 787327 | 1 | 510380 | 7009.53 | 34.799 | 6106.23 | 30.3146 | 6636.71 | 32.9481 | 6106.58 | 30.3163 | 6636.76 | 32.9484 | 6125.84 | 30.4119 | 6691.88 | 33.222 | 6252.79 | 31.0422 | 6804 | 33.7786 | 6114.09 | 30.3536 | 6636.96 | 32.9494
GEN-2024-345 | DIS-24-1 | 04 SOUTHEAST | AEP | 600 | ER/NR | Wind | Delaware 345 kV Substation | 787330 | 1 | 510380 | 7009.53 | 35.5556 | 6106.23 | 30.9736 | 6636.71 | 33.6644 | 6106.58 | 30.9754 | 6636.76 | 33.6647 | 6125.84 | 31.0731 | 6691.88 | 33.9443 | 6252.79 | 31.717 | 6804 | 34.513 | 6114.09 | 31.0135 | 6636.96 | 33.6657
GEN-2024-346 | DIS-24-1 | 04 SOUTHEAST | AEP | 220 | ER/NR | Wind | Coffeyville Tap - North Barlettsville 138 kV Line | 787354 | 1 | 787350 | 2239.85 | 18.9078 | 2017.62 | 17.0318 | 2210.8 | 18.6625 | 2017.48 | 17.0306 | 2210.8 | 18.6625 | 2019.48 | 17.0475 | 2217.82 | 18.7218 | 2024.75 | 17.092 | 2223.94 | 18.7734 | 2018.26 | 17.0372 | 2210.68 | 18.6615
GEN-2024-346 | DIS-24-1 | 04 SOUTHEAST | AEP | 220 | ER/NR | Wind | Coffeyville Tap - North Barlettsville 138 kV Line | 787357 | 1 | 787350 | 2239.85 | 22.0592 | 2017.62 | 19.8706 | 2210.8 | 21.7731 | 2017.48 | 19.8692 | 2210.8 | 21.7731 | 2019.48 | 19.8889 | 2217.82 | 21.8423 | 2024.75 | 19.9408 | 2223.94 | 21.9025 | 2018.26 | 19.8769 | 2210.68 | 21.7719
GEN-2024-351 | DIS-24-1 | 05 SOUTHWEST | SPS | 199 | ER/NR | Solar | Cooper Ranch 115 kV Substation | 787504 | 1 | 528554 | 1876.55 | 18.1836 | 1759.18 | N/A | 1869.86 | 18.1188 | 1759.14 | N/A | 1870.14 | 18.1215 | 1759.28 | N/A | 1870 | 18.1202 | 1760.18 | N/A | 1870 | 18.1202 | 1762.68 | N/A | 1864.28 | 18.0647
GEN-2024-351 | DIS-24-1 | 05 SOUTHWEST | SPS | 199 | ER/NR | Battery/Storage | Cooper Ranch 115 kV Substation | 787507 | 1 | 528554 | 1876.55 | 17.7291 | 1759.18 | N/A | 1869.86 | N/A | 1759.14 | N/A | 1870.14 | N/A | 1759.28 | N/A | 1870 | N/A | 1760.18 | N/A | 1870 | N/A | 1762.68 | N/A | 1864.28 | 17.6131
GEN-2024-351 | DIS-24-1 | 05 SOUTHWEST | SPS | 199 | ER/NR | Solar | Cooper Ranch 115 kV Substation | 787510 | 1 | 528554 | 1876.55 | 18.8106 | 1759.18 | N/A | 1869.86 | 18.7436 | 1759.14 | N/A | 1870.14 | 18.7464 | 1759.28 | N/A | 1870 | 18.745 | 1760.18 | N/A | 1870 | 18.745 | 1762.68 | N/A | 1864.28 | 18.6876
GEN-2024-351 | DIS-24-1 | 05 SOUTHWEST | SPS | 199 | ER/NR | Battery/Storage | Cooper Ranch 115 kV Substation | 787513 | 1 | 528554 | 1876.55 | 18.123 | 1759.18 | N/A | 1869.86 | N/A | 1759.14 | N/A | 1870.14 | N/A | 1759.28 | N/A | 1870 | N/A | 1760.18 | N/A | 1870 | N/A | 1762.68 | N/A | 1864.28 | 18.0045
GEN-2024-352 | DIS-24-1 | 03 CENTRAL | WERE | 199 | ER/NR | Battery/Storage | Sibley 345 kV Substation | 787534 | 1 | 541201 | 12787.78 | 64.2602 | 9173.02 | N/A | 12189.01 | N/A | 9183.12 | N/A | 12193.42 | N/A | 9330.82 | N/A | 12401.37 | 62.3184 | 9176.57 | N/A | 12196.41 | N/A | 9183.42 | N/A | 12191.39 | N/A
GEN-2024-355 | DIS-24-1 | 05 SOUTHWEST | SPS | 199 | ER/NR | Battery/Storage | Lubbock South 230 kV Substation | 787624 | 1 | 526269 | 6353.7 | 63.8563 | 3386.19 | N/A | 6183.26 | N/A | 3385.36 | N/A | 6183.32 | N/A | 3384.58 | N/A | 6183.9 | N/A | 3390.59 | N/A | 6185.63 | N/A | 3484.7 | N/A | 6198.62 | 62.2977
GEN-2024-355 | DIS-24-1 | 05 SOUTHWEST | SPS | 199 | ER/NR | Battery/Storage | Lubbock South 230 kV Substation | 787627 | 1 | 526269 | 6353.7 | 63.8563 | 3386.19 | N/A | 6183.26 | N/A | 3385.36 | N/A | 6183.32 | N/A | 3384.58 | N/A | 6183.9 | N/A | 3390.59 | N/A | 6185.63 | N/A | 3484.7 | N/A | 6198.62 | 62.2977
GEN-2024-359 | DIS-24-1 | 01 NORTH | WAPA | 100 | ER/NR | Battery/Storage | Belfield 345 kV Substation | 787744 | 1 | 652424 | 4119.32 | 41.1932 | 3659.22 | N/A | 4025.55 | 40.2555 | 3490.35 | N/A | 3887.92 | N/A | 3488.99 | N/A | 3884.19 | N/A | 3489.04 | N/A | 3884.08 | N/A | 3490.14 | N/A | 3887.99 | N/A
GEN-2024-360 | DIS-24-1 | 04 SOUTHEAST | OGE | 160 | ER/NR | Solar | Seminole - Maud 138 kV Line | 787774 | 1 | 787770 | 5259.48 | 31.9523 | 4682.54 | N/A | 5050 | 30.6797 | 4682.6 | N/A | 5049.98 | 30.6796 | 4685.72 | N/A | 5051.35 | 30.6879 | 4767.31 | N/A | 5118.11 | 31.0935 | 4689.09 | N/A | 5050.06 | 30.6801
GEN-2024-360 | DIS-24-1 | 04 SOUTHEAST | OGE | 160 | ER/NR | Storage | Seminole - Maud 138 kV Line | 787777 | 1 | 787770 | 5259.48 | 31.9861 | 4682.54 | N/A | 5050 | N/A | 4682.6 | N/A | 5049.98 | N/A | 4685.72 | N/A | 5051.35 | N/A | 4767.31 | N/A | 5118.11 | 31.1264 | 4689.09 | N/A | 5050.06 | N/A
GEN-2024-361 | DIS-24-1 | 04 SOUTHEAST | OGE | 80 | ER/NR | Solar | Spring Valley - Warwick 138 kV line | 787804 | 1 | 787800 | 2124.42 | 25.2258 | 1897.23 | N/A | 1979.79 | 23.5085 | 1897.24 | N/A | 1979.79 | 23.5085 | 1897.93 | N/A | 1980.1 | 23.5122 | 1906.46 | N/A | 2086.44 | 24.7749 | 1897.86 | N/A | 1979.73 | 23.5078
GEN-2024-361 | DIS-24-1 | 04 SOUTHEAST | OGE | 80 | ER/NR | Storage | Spring Valley - Warwick 138 kV line | 787806 | 1 | 787800 | 2124.42 | 25.1688 | 1897.23 | N/A | 1979.79 | N/A | 1897.24 | N/A | 1979.79 | N/A | 1897.93 | N/A | 1980.1 | N/A | 1906.46 | N/A | 2086.44 | 24.7188 | 1897.86 | N/A | 1979.73 | N/A
GEN-2024-362 | DIS-24-1 | 04 SOUTHEAST | AEP | 140 | ER/NR | Solar | Leonard 138 kV Substation | 787834 | 1 | 511575 | 2374.8 | 16.3257 | 2215.21 | N/A | 2347.2 | 16.136 | 2215.22 | N/A | 2347.2 | 16.136 | 2215.6 | N/A | 2347.55 | 16.1384 | 2237.68 | N/A | 2361.2 | 16.2322 | 2217.24 | N/A | 2347.17 | 16.1357
GEN-2024-362 | DIS-24-1 | 04 SOUTHEAST | AEP | 140 | ER/NR | Battery/Storage | Leonard 138 kV Substation | 787837 | 1 | 511575 | 2374.8 | 16.3296 | 2215.21 | N/A | 2347.2 | N/A | 2215.22 | N/A | 2347.2 | N/A | 2215.6 | N/A | 2347.55 | N/A | 2237.68 | N/A | 2361.2 | 16.2361 | 2217.24 | N/A | 2347.17 | N/A
GEN-2024-364 | DIS-24-1 | 05 SOUTHWEST | SPS | 300 | ER/NR | Solar | Bushland 230 kV Substation | 787894 | 1 | 524267 | 4439.36 | 29.1929 | 3901.45 | N/A | 4363.07 | 28.6912 | 3898.82 | N/A | 4363.21 | 28.6921 | 3901.5 | N/A | 4365.1 | 28.7045 | 3909.27 | N/A | 4366.01 | 28.7105 | 4001.44 | N/A | 4450.98 | 29.2693
GEN-2024-364 | DIS-24-1 | 05 SOUTHWEST | SPS | 300 | ER/NR | Storage | Bushland 230 kV Substation | 787897 | 1 | 524267 | 4439.36 | 28.9524 | 3901.45 | N/A | 4363.07 | N/A | 3898.82 | N/A | 4363.21 | N/A | 3901.5 | N/A | 4365.1 | N/A | 3909.27 | N/A | 4366.01 | N/A | 4001.44 | N/A | 4450.98 | 29.0282
GEN-2024-364 | DIS-24-1 | 05 SOUTHWEST | SPS | 300 | ER/NR | Solar | Bushland 230 kV Substation | 787900 | 1 | 524267 | 4439.36 | 29.1929 | 3901.45 | N/A | 4363.07 | 28.6912 | 3898.82 | N/A | 4363.21 | 28.6921 | 3901.5 | N/A | 4365.1 | 28.7045 | 3909.27 | N/A | 4366.01 | 28.7105 | 4001.44 | N/A | 4450.98 | 29.2693
GEN-2024-364 | DIS-24-1 | 05 SOUTHWEST | SPS | 300 | ER/NR | Storage | Bushland 230 kV Substation | 787903 | 1 | 524267 | 4439.36 | 28.9524 | 3901.45 | N/A | 4363.07 | N/A | 3898.82 | N/A | 4363.21 | N/A | 3901.5 | N/A | 4365.1 | N/A | 3909.27 | N/A | 4366.01 | N/A | 4001.44 | N/A | 4450.98 | 29.0282
GEN-2024-365 | DIS-24-1 | 05 SOUTHWEST | SPS | 200 | ER/NR | Wind | Hobbs - Yoakum 345 kV Line | 787924 | 1 | 787920 | 6679.06 | 33.3953 | 5388.28 | 26.9414 | 6439.44 | 32.1972 | 5387.61 | 26.9381 | 6441.41 | 32.2071 | 5389.35 | 26.9468 | 6441.13 | 32.2056 | 5400.75 | 27.0038 | 6442.81 | 32.2141 | 5477.71 | 27.3885 | 6491.15 | 32.4557
GEN-2024-366 | DIS-24-1 | 05 SOUTHWEST | SPS | 200 | ER/NR | Wind | Hobbs - Yoakum 345 kV Line | 787954 | 1 | 787920 | 6679.06 | 33.3953 | 5388.28 | 26.9414 | 6439.44 | 32.1972 | 5387.61 | 26.9381 | 6441.41 | 32.2071 | 5389.35 | 26.9468 | 6441.13 | 32.2056 | 5400.75 | 27.0038 | 6442.81 | 32.2141 | 5477.71 | 27.3885 | 6491.15 | 32.4557
GEN-2024-367 | DIS-24-1 | 04 SOUTHEAST | AEP | 250 | ER/NR | Battery/Storage | Lawton East Side 345 kV Substation | 787984 | 1 | 511468 | 9280.84 | 37.1234 | 6149.55 | N/A | 7572.06 | N/A | 6149.59 | N/A | 7572.17 | N/A | 6153.02 | N/A | 7577.71 | N/A | 6627.76 | N/A | 8478.6 | 33.9144 | 6276.95 | N/A | 7547.9 | N/A
GEN-2024-368 | DIS-24-1 | 05 SOUTHWEST | SPS | 250 | ER/NR | Battery/Storage | Bowers 115 kV Substation | 788014 | 1 | 523748 | 1416.74 | 5.667 | 1431.74 | N/A | 1407.55 | N/A | 1431.69 | N/A | 1410.28 | N/A | 1433.03 | N/A | 1404.73 | N/A | 1431.44 | N/A | 1404.27 | N/A | 1431.7 | N/A | 1393.81 | 5.5752
GEN-2024-369 | DIS-24-1 | 04 SOUTHEAST | AEP | 250 | ER/NR | Battery/Storage | Cornville 138 kV Substation | 788044 | 1 | 511449 | 4135.94 | 16.5438 | 3471.22 | N/A | 4014.24 | N/A | 3471.24 | N/A | 4014.25 | N/A | 3470.16 | N/A | 4014.93 | N/A | 3537.04 | N/A | 4086.41 | 16.3456 | 3476.76 | N/A | 4013.79 | N/A
GEN-2024-370 | DIS-24-1 | 03 CENTRAL | WERE | 250 | ER/NR | Battery/Storage | Smithville 161 kV Substation | 788074 | 1 | 541204 | 6925.61 | 27.7024 | 5322.72 | N/A | 6585.85 | N/A | 5328.11 | N/A | 6588.29 | N/A | 5406.35 | N/A | 6656.28 | 26.6251 | 5329.34 | N/A | 6591.58 | N/A | 5330.64 | N/A | 6588.02 | N/A
GEN-2024-371 | DIS-24-1 | 05 SOUTHWEST | SPS | 250 | ER/NR | Battery/Storage | Maddox 115 kV Substation | 788104 | 1 | 528355 | 6605.07 | 26.4203 | 4632.34 | N/A | 6471.71 | N/A | 4632.03 | N/A | 6472.96 | N/A | 4633.06 | N/A | 6472.52 | N/A | 4638.43 | N/A | 6472.87 | N/A | 4662.49 | N/A | 6524.28 | 26.0971
GEN-2024-372 | DIS-24-1 | 02 NEBRASKA | OPPD | 250 | ER/NR | Battery/Storage | S1247 161 kV Substation | 788134 | 1 | 646247 | 7070.65 | 28.2826 | 5889.36 | N/A | 6798.26 | N/A | 5928.36 | N/A | 6880.8 | 27.5232 | 5895.15 | N/A | 6801.58 | N/A | 5885.87 | N/A | 6797.81 | N/A | 5885.48 | N/A | 6797.5 | N/A
GEN-2024-373 | DIS-24-1 | 04 SOUTHEAST | WFEC | 120 | ER/NR | Solar | Unger - West Bank Tap 138 kV Line | 788164 | 1 | 788160 | 1353.83 | 11.2035 | 1134.02 | N/A | 1237.57 | 10.2414 | 1134.03 | N/A | 1237.57 | 10.2414 | 1134.1 | N/A | 1237.59 | 10.2416 | 1143.88 | N/A | 1323.89 | 10.9557 | 1134.41 | N/A | 1237.52 | 10.241
GEN-2024-373 | DIS-24-1 | 04 SOUTHEAST | WFEC | 120 | ER/NR | Storage | Unger - West Bank Tap 138 kV Line | 788167 | 1 | 788160 | 1353.83 | 10.7183 | 1134.02 | N/A | 1237.57 | N/A | 1134.03 | N/A | 1237.57 | N/A | 1134.1 | N/A | 1237.59 | N/A | 1143.88 | N/A | 1323.89 | 10.4813 | 1134.41 | N/A | 1237.52 | N/A
GEN-2024-374 | DIS-24-1 | 02 NEBRASKA | BEPC | 225 | ER/NR | Solar | Stegall 345 kV Substation | 788194 | 1 | 659135 | 2759.04 | 24.5248 | 2648.16 | N/A | 2742.85 | 24.3809 | 2635.88 | N/A | 2727.96 | 24.2485 | 2626.35 | N/A | 2719.61 | 24.1743 | 2624.52 | N/A | 2718.32 | 24.1628 | 2627.6 | N/A | 2720.02 | 24.178
GEN-2024-374 | DIS-24-1 | 02 NEBRASKA | BEPC | 225 | ER/NR | Solar | Stegall 345 kV Substation | 788197 | 1 | 659135 | 2759.04 | 24.5248 | 2648.16 | N/A | 2742.85 | 24.3809 | 2635.88 | N/A | 2727.96 | 24.2485 | 2626.35 | N/A | 2719.61 | 24.1743 | 2624.52 | N/A | 2718.32 | 24.1628 | 2627.6 | N/A | 2720.02 | 24.178
GEN-2024-375 | DIS-24-1 | 03 CENTRAL | WERE | 100 | ER/NR | Battery/Storage | Malta Bend - Norton 161 kV Line | 788224 | 1 | 788220 | 1651.14 | 16.5114 | 1271.79 | N/A | 1336.45 | N/A | 1271.68 | N/A | 1336.47 | N/A | 1273.02 | N/A | 1390.4 | 13.904 | 1273.07 | N/A | 1337.15 | N/A | 1271.22 | N/A | 1336.11 | N/A
GEN-2024-376 | DIS-24-1 | 04 SOUTHEAST | ETEC | 142.183 | ER/NR | Solar | Hemphill 138 kV Substation | 788254 | 1 | 509106 | 880.44 | 6.1923 | 857.48 | N/A | 877.54 | 6.1719 | 857.48 | N/A | 877.54 | 6.1719 | 857.48 | N/A | 877.55 | 6.172 | 857.58 | N/A | 878.28 | 6.1771 | 857.49 | N/A | 877.53 | 6.1718
GEN-2024-377 | DIS-24-1 | 04 SOUTHEAST | AEP | 1350 | ER/NR | Thermal | Pirkey 345 kV Substation | 788284 | 1 | 508563 | 13294.14 | 27.1467 | 5313.94 | N/A | 9984.1 | N/A | 5313.95 | N/A | 9984.1 | N/A | 5314.52 | N/A | 9984.65 | N/A | 5332.7 | N/A | 10474.23 | N/A | 5315.43 | N/A | 9967.13 | N/A
GEN-2024-377 | DIS-24-1 | 04 SOUTHEAST | AEP | 1350 | ER/NR | Thermal | Pirkey 345 kV Substation | 788287 | 1 | 508563 | 13294.14 | 27.1467 | 5313.94 | N/A | 9984.1 | N/A | 5313.95 | N/A | 9984.1 | N/A | 5314.52 | N/A | 9984.65 | N/A | 5332.7 | N/A | 10474.23 | N/A | 5315.43 | N/A | 9967.13 | N/A
GEN-2024-377 | DIS-24-1 | 04 SOUTHEAST | AEP | 1350 | ER/NR | Thermal | Pirkey 345 kV Substation | 788290 | 1 | 508563 | 13294.14 | 35.8747 | 5313.94 | N/A | 9984.1 | N/A | 5313.95 | N/A | 9984.1 | N/A | 5314.52 | N/A | 9984.65 | N/A | 5332.7 | N/A | 10474.23 | N/A | 5315.43 | N/A | 9967.13 | N/A
GEN-2024-379 | DIS-24-1 | 04 SOUTHEAST | AEP | 1350 | ER/NR | Thermal | Longwood - El Dorado 345 kV Line | 788343 | 1 | 788340 | 6835.5 | 13.9581 | 5899.95 | N/A | 6606.84 | N/A | 5899.96 | N/A | 6606.83 | N/A | 5900.65 | N/A | 6607.09 | N/A | 5912.18 | N/A | 6723.2 | N/A | 5901.47 | N/A | 6603.33 | N/A
GEN-2024-379 | DIS-24-1 | 04 SOUTHEAST | AEP | 1350 | ER/NR | Thermal | Longwood - El Dorado 345 kV Line | 788345 | 1 | 788340 | 6835.5 | 18.4459 | 5899.95 | N/A | 6606.84 | N/A | 5899.96 | N/A | 6606.83 | N/A | 5900.65 | N/A | 6607.09 | N/A | 5912.18 | N/A | 6723.2 | N/A | 5901.47 | N/A | 6603.33 | N/A
GEN-2024-379 | DIS-24-1 | 04 SOUTHEAST | AEP | 1350 | ER/NR | Thermal | Longwood - El Dorado 345 kV Line | 788347 | 1 | 788340 | 6835.5 | 13.9581 | 5899.95 | N/A | 6606.84 | N/A | 5899.96 | N/A | 6606.83 | N/A | 5900.65 | N/A | 6607.09 | N/A | 5912.18 | N/A | 6723.2 | N/A | 5901.47 | N/A | 6603.33 | N/A