## Executive Summary
Executive Summary: DISIS-2024-001 Phase 1 of Power Flow
Pursuant to the Southwest Power Pool (SPP) Open Access Transmission Tariff (OATT), SPP has conducted this Definitive Interconnection System Impact Study (DISIS) for generation interconnection requests received during the DISIS Queue Cluster Window which closed on March 01, 2025. The primary objective of this DISIS is to identify the system constraints, transient instabilities, and over-dutied equipment associated with connecting the generation to the area transmission system. The Impact Study and other subsequent Interconnection Studies are designed to identify required Transmission Owner Interconnection Facilities, Network Upgrades and other Direct Assignment Facilities needed to inject power into the grid at each specific point of interconnection. The study analysis for the generation interconnection requests included in this DISIS are displayed in this workbook. This workbook provides a convenient method to sort and analyze required study data. The DISIS Manual Version 4.4 posted on https://spp.org/engineering/generator-interconnection contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual or contact gistudies@spp.org for more information about the study process. DISIS-2024-001 Phase 1 includes study requests in the following cluster groups: (01 NORTH, 02 NEBRASKA, 03 CENTRAL, 04 SOUTHEAST, 05 SOUTHWEST, WECC)
DISIS Manual Version 4.4
https://spp.org/media/2400/gi-manual-business-practice_7250_20251017.pdf
This DISIS analyzes the impact of interconnecting new generation for total of:
67,186.76 MW
The standard cost of interconnecting all requests included in this DISIS is estimated at:
Total Network Upgrade $28,700,995,615.66 Steady State Network Upgrade $25,288,345,783.24 Interconnection Costs: $3,412,649,832.42
Models Used in Steady State Study
2025 ITP Series, WECC Models
Winter: 2029 WECC Winter: 2031
Summer: 2026, 2029 WECC Summer: 2026, 2031
Light: 2029
By: SPP Generator Interconnection Department
Published: April 1, 2026
Costs for Solar/Battery Requests were allocated using the 29SP (summer peak) model.
Costs for Wind Requests were allocated using the 29L (light load) model.
Short Circuit Ratio calculation is provided per group. A value of “N/A” means the request was offline for that scenario.
All analysis was performed iteratively. A “Mitigation Iteration” column is included in the report to indicate the iteration in which each upgrade was identified.
Iterations are defined in study order as follows: ‘SI‑NC’ = system‑intact non‑convergence; ‘N0’ = first contingency non‑convergence iteration; ‘N1’ = second contingency non‑convergence iteration; ‘T0’ = first thermal iteration; ‘T1’ and ‘T2’ = follow‑up thermal iterations; ‘V’ = voltage.
System‑intact network upgrades used to resolve non‑convergence were selected through automation, with a preference for reinforcing existing facilities via parallel circuits.
Non‑converged contingencies were mitigated using parallel‑circuiting of the contingent elements.
Thermal and voltage upgrades were selected using automated methods consistent with previous DISIS Phase 1 manual review and mitigation selection whitepaper. (Link)
Network upgrades were not reviewed by SPP or Transmission Owners for viability or optimality.
A formal Contingent Facilities analysis was not performed. A list of approved upgrades included in the models, including those from the 2025ITP portfolio and prior-queued DISIS projects, is included in the 'Included Upgrades' tab.
Certain 26SP‑only constraints were assigned no cost when year‑29 element ratings would resolve them. These represent contingent facilities and will be reported in detail in Phase 2.
Interconnection costs were provided by Transmission Owners.
Good‑faith estimates leveraging SPP’s 2025 ITP Conceptual Cost Estimates were used.

## Requests
Gen Number | Group | Queue | Fuel Type | MW Amount | Service | Area | Substation or Line
ASGI-2024-001 | 01 NORTH | DIS-24-1 | Thermal | 17.1 | ER | WAPA | Pine Lake 12.47 kV
ASGI-2024-002 | 05 SOUTHWEST | DIS-24-1 | Hybrid | 30 | ER | SPS | GridLiance's Cougar 69 kV Substation
ASGI-2024-003 | 03 CENTRAL | DIS-24-1 | Solar | 79.8 | ER/NR | SUNC | Rolla 115 kV Substation
ASGI-2024-006 | 03 CENTRAL | DIS-24-1 | Solar | 100 | ER/NR | KCPL | Y-road 115 kV switching station
ASGI-2024-007 | 03 CENTRAL | DIS-24-1 | Thermal | 47.99 | ER/NR | KCPL | Marshall Miami 13.2 kV Substation
ASGI-2024-008 | 03 CENTRAL | DIS-24-1 | Thermal | 86 | ER/NR | KCPL | Marshall Miami 161 kV Substation
ASGI-2024-012 | WECC | DIS-24-1 | Solar | 300 | ER/NR | WAPA | South Huntley 230 kV Substation
ASGI-2024-020 | 03 CENTRAL | DIS-24-1 | Thermal | 131.58 | ER/NR | WERE | Johns-Manville 115 kV Substation
ASGI-2024-023 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 120 | ER/NR | AEPW | Hope NW - Fulton 115 kV Line
ASGI-2024-024 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 79 | ER/NR | KCPL | Alabama St 161 kV Substation
GEN-2024-003 | 04 SOUTHEAST | DIS-24-1 | Thermal | 102.2 | ER | AEPW | Fitzhugh 161kV
GEN-2024-007 | 03 CENTRAL | DIS-24-1 | Hybrid | 80 | ER/NR | MIDW | Seward 115 kV Substation
GEN-2024-013 | 04 SOUTHEAST | DIS-24-1 | Thermal | 496 | ER/NR | OKGE | Norman Hills 345 kV
GEN-2024-015 | 05 SOUTHWEST | DIS-24-1 | Hybrid | 280 | ER/NR | SPS | Sundown-Amaco-Yoakum 230 kV Substation
GEN-2024-016 | 03 CENTRAL | DIS-24-1 | Wind | 300 | ER/NR | MIDW | Post Rock - Macon 345 kV Line
GEN-2024-017 | 02 NEBRASKA | DIS-24-1 | Thermal | 62 | ER/NR | NPPD | Olive Creek 345 kV Substation
GEN-2024-018 | 02 NEBRASKA | DIS-24-1 | Thermal | 31 | ER/NR | NPPD | New Beatrice Power Station 345 kV
GEN-2024-019 | 02 NEBRASKA | DIS-24-1 | Thermal | 62 | ER/NR | NPPD | New Beatrice Power Station 345 kV Substation
GEN-2024-020 | 02 NEBRASKA | DIS-24-1 | Thermal | 390 | ER/NR | NPPD | Olive Creek 345 kV Substation
GEN-2024-021 | 02 NEBRASKA | DIS-24-1 | Thermal | 540 | ER/NR | NPPD | Olive Creek 345 kV Substation
GEN-2024-022 | 02 NEBRASKA | DIS-24-1 | Thermal | 390 | ER/NR | NPPD | New Beatrice Power Station 345 kV
GEN-2024-023 | 02 NEBRASKA | DIS-24-1 | Thermal | 270 | ER/NR | NPPD | New Beatrice Power Station 345 kV
GEN-2024-025 | 04 SOUTHEAST | DIS-24-1 | Solar | 300 | ER/NR | AEPW | Lydia 345 kV Substation
GEN-2024-029 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 150 | ER/NR | OKGE | Crescent 138 kV Substation
GEN-2024-030 | 03 CENTRAL | DIS-24-1 | Solar | 150 | ER/NR | SUNC | Santa Fe 115 kV Substation
GEN-2024-032 | 03 CENTRAL | DIS-24-1 | Solar | 250 | ER/NR | SUNC | Hugoton 115 kV Substation
GEN-2024-034 | 01 NORTH | DIS-24-1 | Battery/Storage | 175 | ER/NR | WAPA | Forman 115 kV Substation
GEN-2024-035 | 01 NORTH | DIS-24-1 | Hybrid | 270 | ER/NR | WAPA | Groton 345 kV Substation
GEN-2024-038 | 02 NEBRASKA | DIS-24-1 | Solar | 300 | ER/NR | OPPD | Cooper - S12080 161 kV line
GEN-2024-039 | 02 NEBRASKA | DIS-24-1 | Solar | 250 | ER/NR | OPPD | Humboldt - S1280 161 kV line
GEN-2024-040 | 02 NEBRASKA | DIS-24-1 | Solar | 174 | ER/NR | OPPD | S3458 to Cooper 345 kV line
GEN-2024-041 | 05 SOUTHWEST | DIS-24-1 | Wind | 250 | ER/NR | SPS | Tuco - Whirlwind 345 kV Line
GEN-2024-042 | 05 SOUTHWEST | DIS-24-1 | Wind | 250 | ER/NR | SPS | Tuco - Whirlwind 345 kV line
GEN-2024-043 | 05 SOUTHWEST | DIS-24-1 | Wind | 250 | ER/NR | SPS | Crossroads - Tolk 345 kV Line
GEN-2024-044 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 36 | ER/NR | AEPW | Hosston - Plain Dealing 69 kV Line
GEN-2024-045 | 05 SOUTHWEST | DIS-24-1 | Solar | 345 | ER/NR | SPS | Hitchland - Moore 230kV line
GEN-2024-046 | 05 SOUTHWEST | DIS-24-1 | Solar | 345 | ER/NR | SPS | Hitchland-Moore 230 kV line
GEN-2024-050 | 05 SOUTHWEST | DIS-24-1 | Hybrid | 300 | ER/NR | SPS | Olson 230 kV Substation
GEN-2024-051 | 02 NEBRASKA | DIS-24-1 | Battery/Storage | 170 | ER/NR | LES | Waverly 115 kV Substation
GEN-2024-052 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 42 | ER/NR | WFEC | Unger - West Bank Tap 138 kV Line
GEN-2024-054 | 03 CENTRAL | DIS-24-1 | Solar | 120 | ER/NR | KCPL | Overton - Sedalia East 161 kV line
GEN-2024-055 | 03 CENTRAL | DIS-24-1 | Solar | 175 | ER/NR | KCPL | Butler - Nevada 161 kV line
GEN-2024-056 | 04 SOUTHEAST | DIS-24-1 | Solar | 120 | ER/NR | OKGE | Cow Creek - Morrison 138 kV line
GEN-2024-058 | 04 SOUTHEAST | DIS-24-1 | Wind | 200 | ER/NR | GRDA | Farmland - Delaware 138 kV line
GEN-2024-061 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 200 | ER/NR | WERE | Creswell 138 kV Substation
GEN-2024-062 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 230 | ER/NR | WFEC | Dover SW 138 kV Substation
GEN-2024-063 | 05 SOUTHWEST | DIS-24-1 | Solar | 256 | ER/NR | SPS | Plant X 230 kV Substation
GEN-2024-065 | 02 NEBRASKA | DIS-24-1 | Battery/Storage | 150 | ER/NR | NPPD | FREMONT7 115 kV Substation
GEN-2024-067 | 03 CENTRAL | DIS-24-1 | Solar | 380 | ER/NR | SUNC | Cirrus 345 kV Substation
GEN-2024-068 | 04 SOUTHEAST | DIS-24-1 | Solar | 300 | ER/NR | AEPW | Lydia - Welsh 345 kV Line
GEN-2024-069 | 03 CENTRAL | DIS-24-1 | Hybrid | 228 | ER/NR | WERE | Franklin 69 kV Substation
GEN-2024-071 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 75 | ER/NR | AEPW | West Atlanta - Atlanta 69 kV Line
GEN-2024-072 | 03 CENTRAL | DIS-24-1 | Solar | 160 | ER/NR | SUNC | Beloit 115 kV Substation
GEN-2024-073 | 05 SOUTHWEST | DIS-24-1 | Hybrid | 500 | ER/NR | SPS | Crossroads - Hobbs 345 kV Substation
GEN-2024-074 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 200 | ER/NR | KCPL | Duncan Road 161 kV Substation
GEN-2024-076 | 03 CENTRAL | DIS-24-1 | Solar | 130 | ER/NR | WERE | Neosho - LaCygne 345 kV Line
GEN-2024-077 | 05 SOUTHWEST | DIS-24-1 | Solar | 300 | ER/NR | SPS | Pringle 230 kV Substation
GEN-2024-078 | 05 SOUTHWEST | DIS-24-1 | Solar | 300 | ER/NR | SPS | Pringle 230 kV Substation
GEN-2024-079 | 05 SOUTHWEST | DIS-24-1 | Solar | 250 | ER/NR | SPS | San Juan 230 kV Substation
GEN-2024-080 | 05 SOUTHWEST | DIS-24-1 | Solar | 250 | ER/NR | SPS | San Juan 230 kV Substation
GEN-2024-081 | 01 NORTH | DIS-24-1 | Thermal | 745 | ER | WAPA | Springbrook - Tande 345 kV Line
GEN-2024-082 | 01 NORTH | DIS-24-1 | Thermal | 745 | ER | WAPA | Springbrook - Tande 345 kV Line
GEN-2024-083 | 04 SOUTHEAST | DIS-24-1 | Solar | 250 | ER/NR | WFEC | Hugo 345 kV Substation
GEN-2024-084 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 167 | ER/NR | EMDE | Reeds Spring - Aurora 161 kV Line
GEN-2024-085 | 03 CENTRAL | DIS-24-1 | Solar | 160 | ER/NR | SUNC | Otis 115 kV Substation
GEN-2024-088 | 03 CENTRAL | DIS-24-1 | Thermal | 144.999 | ER/NR | SPRM | McCartney 161 kV Substation
GEN-2024-089 | 05 SOUTHWEST | DIS-24-1 | Wind | 195 | ER | SPS | Pleasant Hills 230 kV Substation
GEN-2024-090 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 100 | ER/NR | KCPL | Smithville 161 kV Substation
GEN-2024-091 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 100 | ER/NR | EMDE | 145 JOPLIN WEST 7TH 161 kV Substation
GEN-2024-092 | 05 SOUTHWEST | DIS-24-1 | Battery/Storage | 199.5 | ER/NR | SPS | Portales 115 kV Substation
GEN-2024-099 | 05 SOUTHWEST | DIS-24-1 | Solar | 300 | ER/NR | SPS | Newhart 230 kV Substation
GEN-2024-102 | 03 CENTRAL | DIS-24-1 | Wind | 400.5 | ER/NR | SUNC | Holcomb 345 kV Substation
GEN-2024-109 | 05 SOUTHWEST | DIS-24-1 | Wind | 400.5 | ER/NR | SPS | Tolk - Crossroads 345 kV line
GEN-2024-113 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 300 | ER/NR | OKGE | Muskogee - Ft. Smith 345 kV Line
GEN-2024-114 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 199 | ER/NR | SWPA | Jonesboro - Independence County 161 kV Line
GEN-2024-117 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 150 | ER/NR | AEPW | Coffeyville Tap - North Bartlesville 138kV Line
GEN-2024-118 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 199 | ER/NR | AEPW | East 11th Street 138kV Substation
GEN-2024-119 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 199 | ER/NR | WFEC | Lexington 138 kV Substation
GEN-2024-120 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 199 | ER/NR | OKGE | JNS KAMO 138 kV Substation
GEN-2024-121 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 199 | ER/NR | WERE | Jarbalo 115 kV Substation
GEN-2024-122 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 160 | ER/NR | AEPW | Lieberman - IPC Jefferson 138 kV Line
GEN-2024-123 | 04 SOUTHEAST | DIS-24-1 | Solar | 120 | ER/NR | AEPW | Center - Tenaha 138 kV Line
GEN-2024-124 | 05 SOUTHWEST | DIS-24-1 | Hybrid | 420 | ER/NR | SPS | Crossroads-Hobbs-Roadrunner 345 kV Line
GEN-2024-125 | 03 CENTRAL | DIS-24-1 | Solar | 400 | ER/NR | WERE | Neosho Ridge - Caney River 345 kV Line
GEN-2024-128 | 04 SOUTHEAST | DIS-24-1 | Thermal | 690 | ER/NR | OKGE | Gracemont - Lawton 345 kV Line
GEN-2024-129 | 03 CENTRAL | DIS-24-1 | Thermal | 910 | ER/NR | WERE | Caney River - Neosho 345 kV Line
GEN-2024-132 | 04 SOUTHEAST | DIS-24-1 | Thermal | 1300 | ER/NR | OKGE | Hugo (71 miles) - Sunnyside (42 miles) 345 kV Line
GEN-2024-134 | 04 SOUTHEAST | DIS-24-1 | Wind | 250 | ER/NR | OKGE | Degrasse 345 kV Substation
GEN-2024-135 | 04 SOUTHEAST | DIS-24-1 | Wind | 250 | ER/NR | OKGE | Degrasse 345 kV Substation
GEN-2024-136 | 03 CENTRAL | DIS-24-1 | Solar | 400 | ER/NR | SUNC | Setab 345 kV Substation
GEN-2024-137 | 03 CENTRAL | DIS-24-1 | Wind | 296.5 | ER/NR | SUNC | Setab 345 kV Substation
GEN-2024-138 | 03 CENTRAL | DIS-24-1 | Wind | 296.5 | ER/NR | SUNC | Setab 345 kV Substation
GEN-2024-139 | 03 CENTRAL | DIS-24-1 | Solar | 246.08 | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line
GEN-2024-140 | 02 NEBRASKA | DIS-24-1 | Solar | 245.7 | ER/NR | NPPD | Antelope - Hoskins 345 kV line
GEN-2024-141 | 01 NORTH | DIS-24-1 | Wind | 424 | ER/NR | WAPA | BASIN__-BE4 230 kV Substation
GEN-2024-142 | 03 CENTRAL | DIS-24-1 | Wind | 296.03 | ER/NR | WERE | Reno - Summit 345 kV Line
GEN-2024-143 | 05 SOUTHWEST | DIS-24-1 | Wind | 250 | ER/NR | SPS | XIT Interchange 230 kV Substation
GEN-2024-144 | 03 CENTRAL | DIS-24-1 | Wind | 296.9 | ER/NR | SUNC | Setab 345 kV Substation
GEN-2024-145 | 05 SOUTHWEST | DIS-24-1 | Wind | 243.7 | ER/NR | SPS | XIT Interchange 230 kV Substation
GEN-2024-153 | 05 SOUTHWEST | DIS-24-1 | Solar | 250 | ER/NR | SPS | Bushland 230 kV Substation
GEN-2024-154 | 04 SOUTHEAST | DIS-24-1 | Solar | 200 | ER/NR | AEPW | Chisholm 345 kV Substation
GEN-2024-157 | 04 SOUTHEAST | DIS-24-1 | Solar | 140 | ER/NR | AEPW | Hobart - Martha 138 kV Line
GEN-2024-158 | 04 SOUTHEAST | DIS-24-1 | Solar | 190 | ER/NR | AEPW | Altus Jct - Snyder 138 kV Line
GEN-2024-159 | 05 SOUTHWEST | DIS-24-1 | Solar | 300 | ER/NR | SPS | Oasis - San Juan Mesa Wind 230 kV Line
GEN-2024-161 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 170 | ER/NR | AEPW | Hobart - Martha 138 kV Line
GEN-2024-162 | 02 NEBRASKA | DIS-24-1 | Hybrid | 110 | ER/NR | NPPD | Twin Church 230 kV Substation
GEN-2024-164 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 199 | ER/NR | OKGE | Arbuckle 138 kV Substation
GEN-2024-165 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 500 | ER/NR | OKGE | Pittsburg - Johnston County 345 kV line
GEN-2024-166 | 03 CENTRAL | DIS-24-1 | Hybrid | 275 | ER/NR | WERE | Murray Gill 138 kV Substation
GEN-2024-167 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 199 | ER/NR | KCPL | Orrick 161 kV Substation
GEN-2024-168 | 02 NEBRASKA | DIS-24-1 | Solar | 196.38 | ER/NR | NPPD | Geneva 115 kV Substation
GEN-2024-170 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 280 | ER/NR | KCPL | Pleasant Hill 345 kV Substation
GEN-2024-171 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 250 | ER/NR | AEPW | Tulsa North - Grand River Energy Center 345 kV Line
GEN-2024-173 | 02 NEBRASKA | DIS-24-1 | Battery/Storage | 200 | ER/NR | NPPD | Pawnee Lake 115 kV Substation
GEN-2024-175 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 200 | ER/NR | SPRM | Summit 161 kV Substation
GEN-2024-176 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 250 | ER/NR | WERE | Reno County 115 kV Substation
GEN-2024-177 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 199 | ER/NR | AEPW | Red Point 138 kV Substation
GEN-2024-178 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 199 | ER/NR | AEPW | Pirkey 138 kV Substation
GEN-2024-180 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 100 | ER/NR | GRDA | Kerr Dam 161 kV Substation
GEN-2024-181 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 199 | ER/NR | SPRM | Brookline 161 kV Substation
GEN-2024-184 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 199 | ER/NR | AEPW | Atoka to Lehigh 138 kV Line
GEN-2024-186 | 05 SOUTHWEST | DIS-24-1 | Battery/Storage | 199 | ER/NR | SPS | Roswell Interchange 115 kV Substation
GEN-2024-187 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 199 | ER/NR | WFEC | Civit-Stratford 138 kV Line
GEN-2024-189 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 199 | ER/NR | SUNC | ITC Great Plains Saddle 345 kV Substation
GEN-2024-193 | 03 CENTRAL | DIS-24-1 | Wind | 249.6 | ER/NR | SUNC | Spearville - Buckner 345 kV Line
GEN-2024-194 | 03 CENTRAL | DIS-24-1 | Wind | 249.6 | ER/NR | SUNC | Spearville - Holcomb 345 kV Line
GEN-2024-204 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 100 | ER/NR | OKGE | Brown 138 kV Substation
GEN-2024-205 | 03 CENTRAL | DIS-24-1 | Hybrid | 155 | ER/NR | SUNC | St. John 115 kV Substation
GEN-2024-206 | 03 CENTRAL | DIS-24-1 | Thermal | 226.3 | ER/NR | INDN | Blue Valley 161 kV Substation
GEN-2024-207 | 03 CENTRAL | DIS-24-1 | Thermal | 778.6 | ER/NR | INDN | Blue Valley - Blumil 161 kV Line
GEN-2024-209 | 03 CENTRAL | DIS-24-1 | Solar | 199 | ER/NR | SUNC | Elm Creek - North Manhattan 230 kV Line
GEN-2024-210 | 03 CENTRAL | DIS-24-1 | Solar | 150 | ER/NR | SUNC | St. Francis Tap 115 kV Substation
GEN-2024-211 | 02 NEBRASKA | DIS-24-1 | Thermal | 303 | ER/NR | OPPD | Substation 3740 345 kV
GEN-2024-212 | 02 NEBRASKA | DIS-24-1 | Thermal | 303 | ER/NR | OPPD | Substation 3740 345 kV
GEN-2024-213 | 02 NEBRASKA | DIS-24-1 | Thermal | 360 | ER/NR | OPPD | Substation 3740 345 kV
GEN-2024-215 | 03 CENTRAL | DIS-24-1 | Hybrid | 300 | ER/NR | SUNC | Elm Creek 345 kV Substation
GEN-2024-216 | 01 NORTH | DIS-24-1 | Wind | 225 | ER/NR | WAPA | Miles City 230 kV Substation
GEN-2024-217 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 250 | ER/NR | KCPL | Sibley - Hawthorne 345 kV line
GEN-2024-218 | 03 CENTRAL | DIS-24-1 | Hybrid | 199 | ER/NR | SUNC | Cimarron River 115 kV Substation
GEN-2024-219 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 160 | ER/NR | OKGE | Chigley - Oaklawn 138 kV Line
GEN-2024-220 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 55 | ER/NR | AEPW | Rodessa - Bloomberg 69 kV Line
GEN-2024-221 | 05 SOUTHWEST | DIS-24-1 | Wind | 400 | ER/NR | SPS | 345 kV Crossroads - Eddy County 345 kV Line
GEN-2024-226 | 04 SOUTHEAST | DIS-24-1 | Solar | 300 | ER/NR | AEPW | John W Turk Jr Power Plant 345 kV Substation
GEN-2024-227 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 200 | ER/NR | AEPW | John W Turk Jr Power Plant 345 kV Substation
GEN-2024-228 | 03 CENTRAL | DIS-24-1 | Solar | 200 | ER/NR | WERE | Rice to Circle 230 kV Line
GEN-2024-229 | 04 SOUTHEAST | DIS-24-1 | Solar | 200 | ER/NR | AEPW | Lawton East Side - Oklaunion North 345 kV
GEN-2024-230 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 300 | ER/NR | AEPW | Lawton East Side - Oklaunion North 345 kV
GEN-2024-231 | 02 NEBRASKA | DIS-24-1 | Hybrid | 65 | ER/NR | OPPD | S1399 5 161 kV Substation
GEN-2024-232 | 04 SOUTHEAST | DIS-24-1 | Solar | 250 | ER/NR | AEPW | Crockett - Rocky Creek 345 kV line
GEN-2024-234 | 02 NEBRASKA | DIS-24-1 | Solar | 200 | ER/NR | OPPD | Raun - Tekamah 161 kV line
GEN-2024-235 | 04 SOUTHEAST | DIS-24-1 | Wind | 250 | ER/NR | AEPW | Sooner - Wekiwa 345 kV line
GEN-2024-236 | 04 SOUTHEAST | DIS-24-1 | Wind | 241.4 | ER/NR | OKGE | Seminole - Muskogee 345 kV line
GEN-2024-239 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 200 | ER/NR | OKGE | Cimarron 345 kV Substation
GEN-2024-240 | 04 SOUTHEAST | DIS-24-1 | Wind | 300 | ER/NR | AEPW | Neosho - Delaware 345 kV line
GEN-2024-241 | 04 SOUTHEAST | DIS-24-1 | Solar | 100 | ER/NR | AEPW | Lydia 345 kV Substation
GEN-2024-242 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 250 | ER/NR | OKGE | 515171 138 kV Substation
GEN-2024-243 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 50.1 | ER/NR | SWPA | Van Buren 161 kV Substation
GEN-2024-244 | 05 SOUTHWEST | DIS-24-1 | Battery/Storage | 150 | ER/NR | SPS | Sooner 115 kV Substation
GEN-2024-245 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 199 | ER/NR | OKGE | Lincoln 138 kV Substation
GEN-2024-246 | 05 SOUTHWEST | DIS-24-1 | Battery/Storage | 199 | ER/NR | SPS | North Loving 115 kV Substation
GEN-2024-247 | 04 SOUTHEAST | DIS-24-1 | Thermal | 456.6 | ER | GRDA | Stillwater Northtap 138 kV Substation
GEN-2024-249 | 03 CENTRAL | DIS-24-1 | Thermal | 721.2 | ER/NR | WERE | Jeffrey EC 345 kV Substation
GEN-2024-250 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 199 | ER/NR | AEPW | Pittsburgh 345 kV Substation
GEN-2024-251 | 05 SOUTHWEST | DIS-24-1 | Battery/Storage | 125 | ER/NR | SPS | Atoka 115 kV Substation
GEN-2024-252 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 300 | ER/NR | OKGE | Cimmaron 345 kV Substation
GEN-2024-253 | 03 CENTRAL | DIS-24-1 | Hybrid | 300 | ER/NR | WERE | Stranger Creek - 87th Street 345 kV line
GEN-2024-254 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 300 | ER/NR | OKGE | Mathewson 345 kV Substation
GEN-2024-255 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 300 | ER/NR | OKGE | Spring Creek 345 kV Substation
GEN-2024-257 | 03 CENTRAL | DIS-24-1 | Solar | 220 | ER/NR | SUNC | Skellyville 115 kV Tap Substation
GEN-2024-258 | 03 CENTRAL | DIS-24-1 | Wind | 300 | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line
GEN-2024-259 | 03 CENTRAL | DIS-24-1 | Hybrid | 199.8 | ER/NR | WERE | Asbury 161 kV Substation
GEN-2024-260 | 03 CENTRAL | DIS-24-1 | Storage | 199.8 | ER/NR | KCPL | East Town 161 kV Substation
GEN-2024-261 | 05 SOUTHWEST | DIS-24-1 | Hybrid | 150 | ER/NR | SPS | Hobbs - LCEC West 115 kV Line
GEN-2024-265 | 05 SOUTHWEST | DIS-24-1 | Hybrid | 155 | ER/NR | SPS | Bensing 115 kV Substation
GEN-2024-266 | 05 SOUTHWEST | DIS-24-1 | Hybrid | 500 | ER/NR | SPS | Potter Co - Hitchland 345 kV Line
GEN-2024-267 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 195 | ER/NR | WFEC | Durantp4 - Sclmnjc4 138 kV Line
GEN-2024-268 | 04 SOUTHEAST | DIS-24-1 | Solar | 390 | ER/NR | OKGE | Keefton 345 kV Substation
GEN-2024-271 | 05 SOUTHWEST | DIS-24-1 | Hybrid | 250 | ER/NR | SPS | Chaves County - San Juan Wind 230 kV Line
GEN-2024-272 | 03 CENTRAL | DIS-24-1 | Hybrid | 199 | ER/NR | SUNC | Sawyer 115 kV Substation
GEN-2024-273 | 05 SOUTHWEST | DIS-24-1 | Solar | 16.214 | ER/NR | SPS | Pearl 115 kV Substation
GEN-2024-274 | 03 CENTRAL | DIS-24-1 | Solar | 175 | ER/NR | SUNC | Harper - Anthony 138 kV Line
GEN-2024-276 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 150 | ER/NR | WERE | Tecumseh Hill - Swissvale 230kV Line
GEN-2024-277 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 150 | ER/NR | WERE | Tecumseh Hill - Swissvale 230kV Line
GEN-2024-278 | 05 SOUTHWEST | DIS-24-1 | Hybrid | 264.3 | ER/NR | SPS | Eddy County - Crossroads 345 kV Line
GEN-2024-280 | 05 SOUTHWEST | DIS-24-1 | Hybrid | 350 | ER/NR | SPS | Andrews County 345 kV Substation
GEN-2024-281 | 05 SOUTHWEST | DIS-24-1 | Hybrid | 250 | ER/NR | SPS | Jal - Teague 115 kV Line
GEN-2024-282 | 01 NORTH | DIS-24-1 | Solar | 150 | ER/NR | WAPA | Maurine - New Underwood 230 kV Line
GEN-2024-283 | 01 NORTH | DIS-24-1 | Solar | 150 | ER/NR | WAPA | Maurine - New Underwood 230 kV Line
GEN-2024-284 | 01 NORTH | DIS-24-1 | Solar | 199 | ER/NR | WAPA | Antelope Valley - Broadland 345 kV Line
GEN-2024-285 | 01 NORTH | DIS-24-1 | Wind | 250 | ER/NR | WAPA | Crocker 345 kV Substation
GEN-2024-286 | 04 SOUTHEAST | DIS-24-1 | Thermal | 136 | ER | OKGE | AES 5 161 kV Substation
GEN-2024-287 | 03 CENTRAL | DIS-24-1 | Solar | 199.8 | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line
GEN-2024-288 | 03 CENTRAL | DIS-24-1 | Solar | 130 | ER/NR | SUNC | Elm Creek - Tobias 345 kV Line
GEN-2024-289 | 03 CENTRAL | DIS-24-1 | Solar | 350 | ER/NR | KCPL | Archie - Clinton 161 kV Line
GEN-2024-291 | 04 SOUTHEAST | DIS-24-1 | Wind | 250 | ER/NR | OKGE | Canadian River 345 kV Substation
GEN-2024-293 | 04 SOUTHEAST | DIS-24-1 | Thermal | 248 | ER | OKGE | Muskoge7 345 kV Substation
GEN-2024-294 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 500 | ER/NR | AEPW | Tulsa North - Igloo Valley 345 kV line
GEN-2024-295 | 05 SOUTHWEST | DIS-24-1 | Battery/Storage | 115 | ER/NR | SPS | S Loving 115 kV Substation
GEN-2024-296 | 04 SOUTHEAST | DIS-24-1 | Solar | 167 | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line
GEN-2024-297 | 04 SOUTHEAST | DIS-24-1 | Solar | 167 | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line
GEN-2024-298 | 04 SOUTHEAST | DIS-24-1 | Solar | 167 | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line
GEN-2024-299 | 04 SOUTHEAST | DIS-24-1 | Thermal | 744 | ER | OKGE | AES 5 345 kV Substation
GEN-2024-303 | 05 SOUTHWEST | DIS-24-1 | Hybrid | 500 | ER/NR | SPS | Crossroads 345 kV Substation
GEN-2024-304 | 05 SOUTHWEST | DIS-24-1 | Hybrid | 500 | ER/NR | SPS | Crossroads 345 kV Substation
GEN-2024-305 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 50 | ER/NR | AEPW | Superior - Jefferson 69 kV Line
GEN-2024-306 | 05 SOUTHWEST | DIS-24-1 | Battery/Storage | 150 | ER/NR | SPS | Taylor Switching Station 115 kV Substation
GEN-2024-308 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 199 | ER/NR | WFEC | Okeene - Mooreland 138 kV line
GEN-2024-310 | 05 SOUTHWEST | DIS-24-1 | Battery/Storage | 75 | ER | SPS | Eddy - Chaves 230 kV line
GEN-2024-311 | 05 SOUTHWEST | DIS-24-1 | Solar | 225 | ER/NR | SPS | Eddy - Chaves 230 kV line
GEN-2024-312 | 04 SOUTHEAST | DIS-24-1 | Solar | 50 | ER/NR | SWPA | Clarksville Ozark 161 kV line
GEN-2024-316 | 04 SOUTHEAST | DIS-24-1 | Solar | 300 | ER/NR | AEPW | Pittsburg - Valliant 345 kV Line
GEN-2024-317 | 05 SOUTHWEST | DIS-24-1 | Solar | 300 | ER/NR | SPS | Dragon 345 kV Substation
GEN-2024-318 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 199 | ER/NR | AEPW | Tulsa North - American Airlines 138 kV Line
GEN-2024-319 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 199 | ER/NR | KACY | Metro 5 161 kV Substation
GEN-2024-320 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 199 | ER/NR | WERE | Jaggard 115 kV Substation
GEN-2024-321 | 04 SOUTHEAST | DIS-24-1 | Thermal | 493 | ER/NR | OKGE | Seminole 345 kV Substation
GEN-2024-322 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 75 | ER/NR | MIDW | Redlin - Beach3 115 kV line
GEN-2024-323 | 04 SOUTHEAST | DIS-24-1 | Thermal | 356.8 | ER | WFEC | ITC Hugo 7 345 kV Substation
GEN-2024-324 | 05 SOUTHWEST | DIS-24-1 | Battery/Storage | 160 | ER/NR | SPS | Samson 115 kV Substation
GEN-2024-325 | 05 SOUTHWEST | DIS-24-1 | Battery/Storage | 150 | ER/NR | SPS | Sierra 115 kV Substation
GEN-2024-326 | 01 NORTH | DIS-24-1 | Battery/Storage | 225 | ER/NR | WAPA | Belfield 230 kV Substation
GEN-2024-327 | 01 NORTH | DIS-24-1 | Battery/Storage | 200 | ER/NR | WAPA | Berthold 115 kV Substation
GEN-2024-328 | 01 NORTH | DIS-24-1 | Battery/Storage | 250 | ER/NR | WAPA | Little Missouri 230 kV Substation
GEN-2024-329 | 01 NORTH | DIS-24-1 | Battery/Storage | 200 | ER/NR | WAPA | Pleasant Valley 115 kV Substation
GEN-2024-330 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 225 | ER/NR | WERE | Midian 138 kV Substation
GEN-2024-331 | 01 NORTH | DIS-24-1 | Battery/Storage | 300 | ER/NR | WAPA | Round Up 345 kV Substation
GEN-2024-332 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 150 | ER/NR | OKGE | Discovery 138 kV Substation
GEN-2024-333 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 100 | ER/NR | OKGE | Kelley Avenue 138 kV
GEN-2024-334 | 04 SOUTHEAST | DIS-24-1 | Thermal | 124 | ER/NR | OKGE | Ranch Road 345 kV Substation
GEN-2024-336 | 05 SOUTHWEST | DIS-24-1 | Hybrid | 300 | ER/NR | SPS | Ink Basin 230 kV Substation
GEN-2024-337 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 250 | ER/NR | OKGE | Sunnyside - Pooleville 138 kV line
GEN-2024-338 | 04 SOUTHEAST | DIS-24-1 | Solar | 350 | ER/NR | OKGE | Pittsburg - Johnston County 345 kV line
GEN-2024-339 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 300 | ER/NR | WERE | Stranger Creek 115 kV Substation
GEN-2024-340 | 04 SOUTHEAST | DIS-24-1 | Thermal | 1400 | ER/NR | OKGE | Riverside – Redbud 345 kV line
GEN-2024-341 | 04 SOUTHEAST | DIS-24-1 | Thermal | 1045 | ER/NR | AEPW | Pittsburgh 345 kV Substation
GEN-2024-343 | 04 SOUTHEAST | DIS-24-1 | Thermal | 470.5 | ER/NR | AEPW | LeBrock 345 kV Substation
GEN-2024-344 | 04 SOUTHEAST | DIS-24-1 | Wind | 200 | ER/NR | OKGE | Riverside - Redbud Switch 345 kV Line
GEN-2024-345 | 04 SOUTHEAST | DIS-24-1 | Wind | 600.001 | ER/NR | AEPW | Delaware 345 kV Substation
GEN-2024-346 | 04 SOUTHEAST | DIS-24-1 | Wind | 220 | ER/NR | AEPW | Coffeyville Tap - North Barlettsville 138 kV Line
GEN-2024-351 | 05 SOUTHWEST | DIS-24-1 | Hybrid | 199 | ER/NR | SPS | Cooper Ranch 115 kV Substation
GEN-2024-352 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 199 | ER/NR | KCPL | Sibley 345 kV Substation
GEN-2024-355 | 05 SOUTHWEST | DIS-24-1 | Battery/Storage | 199 | ER/NR | SPS | Lubbock South 230 kV Substation
GEN-2024-359 | 01 NORTH | DIS-24-1 | Battery/Storage | 100 | ER/NR | WAPA | Belfield 345 kV Substation
GEN-2024-360 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 160 | ER/NR | OKGE | Seminole - Maud 138 kV Line
GEN-2024-361 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 80 | ER/NR | OKGE | Spring Valley - Warwick 138 kV line
GEN-2024-362 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 140 | ER/NR | AEPW | Leonard 138 kV Substation
GEN-2024-364 | 05 SOUTHWEST | DIS-24-1 | Hybrid | 300 | ER/NR | SPS | Bushland 230 kV Substation
GEN-2024-365 | 05 SOUTHWEST | DIS-24-1 | Wind | 200 | ER/NR | SPS | Hobbs - Yoakum 345 kV Line
GEN-2024-366 | 05 SOUTHWEST | DIS-24-1 | Wind | 200 | ER/NR | SPS | Hobbs - Yoakum 345 kV Line
GEN-2024-367 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 250 | ER/NR | AEPW | Lawton East Side 345 kV Substation
GEN-2024-368 | 05 SOUTHWEST | DIS-24-1 | Battery/Storage | 250 | ER/NR | SPS | Bowers 115 kV Substation
GEN-2024-369 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 250 | ER/NR | AEPW | Cornville 138 kV Substation
GEN-2024-370 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 250 | ER/NR | KCPL | Smithville 161 kV Substation
GEN-2024-371 | 05 SOUTHWEST | DIS-24-1 | Battery/Storage | 250 | ER/NR | SPS | Maddox 115 kV Substation
GEN-2024-372 | 02 NEBRASKA | DIS-24-1 | Battery/Storage | 250 | ER/NR | OPPD | S1247 161 kV Substation
GEN-2024-373 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 120 | ER/NR | WFEC | Unger - West Bank Tap 138 kV Line
GEN-2024-374 | 02 NEBRASKA | DIS-24-1 | Solar | 225 | ER/NR | WAPA | Stegall 345 kV Substation
GEN-2024-375 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 100 | ER/NR | KCPL | Malta Bend - Norton 161 kV Line
GEN-2024-376 | 04 SOUTHEAST | DIS-24-1 | Solar | 142.183 | ER/NR | AEPW | Hemphill 138 kV Substation
GEN-2024-377 | 04 SOUTHEAST | DIS-24-1 | Thermal | 1350.001 | ER/NR | AEPW | Pirkey 345 kV Substation
GEN-2024-379 | 04 SOUTHEAST | DIS-24-1 | Thermal | 1350.001 | ER/NR | AEPW | Longwood - El Dorado 345 kV Line
ASGI-2010-010 | 05 SOUTHWEST | DIS-10-1 | Gas | 42.195 | ER | SPS
ASGI-2010-020 | 05 SOUTHWEST | DIS-10-2 | Wind | 30 | ER | SPS
ASGI-2010-021 | 05 SOUTHWEST | DIS-10-2 | Wind | 15 | ER | SPS
ASGI-2011-001 | 05 SOUTHWEST | DIS-10-2 | Wind | 27.3 | ER | SPS
ASGI-2011-002 | 05 SOUTHWEST | DIS-11-1 | Wind | 20 | ER | SPS
ASGI-2011-003 | 05 SOUTHWEST | DIS-11-1 | Wind | 10 | ER | SPS
ASGI-2011-004 | 05 SOUTHWEST | DIS-11-2 | Wind | 19.8 | ER | SPS
ASGI-2012-002 | 05 SOUTHWEST | DIS-16-1 | Wind | 18.15 | ER | SPS | FEC 69kV line
ASGI-2012-006 | 03 CENTRAL | DIS-16-1 | Steam | 22.5 | ER | SUNC
ASGI-2013-001 | 05 SOUTHWEST | DIS-13-1 | Wind | 11.5 | ER | SPS
ASGI-2013-002 | 05 SOUTHWEST | DIS-16-1 | Wind | 18.4 | ER | SPS
ASGI-2013-003 | 05 SOUTHWEST | DIS-16-1 | Wind | 18.4 | ER | SPS
ASGI-2013-004 | 03 CENTRAL | DIS-16-1 | Gas | 36.6 | ER | SUNC | Garden City 115kV substation, bus 531445
ASGI-2013-005 | 05 SOUTHWEST | DIS-16-1 | Wind | 1.65 | ER | SPS
ASGI-2015-001 | 03 CENTRAL | DIS-16-1 | Thermal | 6.13 | ER | SUNC | Ninnescah 115kV
ASGI-2016-003 | 03 CENTRAL | DIS-16-1 | Diesel | 12 | ER | KCPL | Paola 161kV
ASGI-2016-004 | 05 SOUTHWEST | DIS-16-1 | Wind | 10 | ER | SPS | Palo Buro 115kV substation
ASGI-2016-005NWE205 | 01 NORTH | DIS-16-1 | Wind | 20 | ER | WAPA
ASGI-2016-007NWE208 | 01 NORTH | DIS-16-1 | Wind | 20 | ER | WAPA
ASGI-2016-010 | 05 SOUTHWEST | DIS-16-2 | Wind | 90 | ER | SPS | Powell Corner 115kV Substation
ASGI-2016-011 | 04 SOUTHEAST | DIS-16-2-PQ | Thermal | 7.407 | ER | SWPA
ASGI-2016-012 | 04 SOUTHEAST | DIS-16-2-PQ | Thermal | 61.725 | ER | SWPA
ASGI-2016-013 | 04 SOUTHEAST | DIS-16-2-PQ | Thermal | 4.938 | ER | WFEC
ASGI-2017-013 | 01 NORTH | DIS-18-1 | Wind | 40 | ER | WAPA | Wosley Substation 69kV
ASGI-2018-003 | 03 CENTRAL | DIS-18-1 | Solar | 20 | ER | KCPL | Tap Appleton - Rockbille 34.5kV
ASGI-2018-006 | 03 CENTRAL | DIS-18-1 | Solar | 20 | ER | KCPL | Tap Metz-Dederick Junction 34.5kV
ASGI-2018-007 | 03 CENTRAL | DIS-18-1 | Solar | 20 | ER | KCPL | Tap Salisbury - Glasgow 34.5kV
ASGI-2018-010 | 03 CENTRAL | DIS-18-1 | Solar | 35 | ER | KCPL | Tap Wal-Mart-Rock Creek 34.5kV
ASGI-2018-011 | 03 CENTRAL | DIS-18-1 | Solar | 35 | ER | KCPL | Tap Rock Creek-Lane 34.5kV
ASGI-2020-001 | 03 CENTRAL | DIS-20-1 | Solar | 35 | ER | KCPL
ASGI-2020-003 | 03 CENTRAL | DIS-20-1 | Solar | 35 | ER | KCPL
ASGI-2021-001 | 05 SOUTHWEST | DIS-21-1 | Solar | 50 | ER/NR | SPS
ASGI-2021-003 | 05 SOUTHWEST | DIS-21-1 | Solar | 40 | ER/NR | SPS
ASGI-2023-001 | 05 SOUTHWEST | DIS-23-1 | Solar | 20 | ER/NR | SPS | Chevron Green 115 kV Substation
BEPCAyrshire | 01 NORTH | DIS-17-1-PQ | Wind | 21 | ER | BEPC
BEPCGerled | 01 NORTH | DIS-17-1-PQ | Wind | 10.5 | ER | BEPC
BEPCHummel | 01 NORTH | DIS-17-1-PQ | Wind | 10.5 | ER | BEPC
BEPCNDPW0 | 01 NORTH | DIS-17-1-PQ | Wind | 7.5 | ER | BEPC
BEPCNDPW1 | 01 NORTH | DIS-17-1 | Wind | 5 | ER | BEPC
GEN-2002-008IS | 01 NORTH | DIS-15-2-PQ | Wind | 40.5 | ER/NR | BEPC
GEN-2002-009IS | 01 NORTH | DIS-15-2-PQ | Wind | 40.5 | ER/NR | BEPC
GEN-2003-022_GEN-2004-020_GEN-2016-051 | 04 SOUTHEAST | DIS-16-1 | Wind | 156.8 | ER | AEPW
GEN-2004-008_GEN-2011-011 | 03 CENTRAL | DIS-11-1 | Coal | 900 | ER | KCPL
GEN-2004-017_GEN-2014-028 | 03 CENTRAL | DIS-14-2 | CT/ST | 300 | ER/NR | EMDE
GEN-2005-003IS | 01 NORTH | DIS-16-1 | Wind | 100 | ER/NR | BEPC
GEN-2005-008IS | 01 NORTH | DIS-16-1 | Wind | 50 | ER/NR | BEPC
GEN-2006-001IS | 01 NORTH | DIS-15-2-PQ | Wind | 10 | ER/NR | XEL
GEN-2006-002IS | 01 NORTH | DIS-16-1 | Wind | 53 | ER/NR | WAPA
GEN-2006-006IS | 01 NORTH | DIS-15-2-PQ | Wind | 10 | ER/NR | XEL
GEN-2006-010_GEN-2013-011 | 04 SOUTHEAST | DIS-16-1 | Coal | 650 | ER | AEPW
GEN-2006-015IS | 01 NORTH | DIS-16-1 | Wind | 50 | ER/NR | BEPC
GEN-2006-031 | 03 CENTRAL | DIS-13-2 | Gas | 75.6 | ER | MIDW | Knoll 115kV
GEN-2006-044N | 02 NEBRASKA | DIS-09-1 | Wind | 40.5 | ER | OPPD | North Petersburg 115kV
GEN-2007-013IS | 01 NORTH | DIS-16-1 | Wind | 100 | ER/NR | BEPC
GEN-2007-014IS | 01 NORTH | DIS-16-1 | Wind | 50 | ER/NR | BEPC
GEN-2007-015IS | 01 NORTH | DIS-15-2-PQ | Wind | 102 | ER/NR | BEPC
GEN-2007-017IS | 02 NEBRASKA | DIS-15-2-PQ | Wind | 202 | ER/NR | OPPD
GEN-2007-018IS | 02 NEBRASKA | DIS-15-2-PQ | Wind | 198 | ER/NR | OPPD
GEN-2007-020IS | 01 NORTH | DIS-16-1 | Wind | 16 | ER/NR | BEPC
GEN-2007-043_GEN-2016-131_GEN-2023-SR18 | 04 SOUTHEAST | DIS-16-2 | Wind | 202.5 | ER | OKGE
GEN-2008-008IS | 01 NORTH | DIS-16-1 | Wind | 5 | ER/NR | WAPA
GEN-2008-023 | 04 SOUTHEAST | DIS-09-1 | Wind | 150 | ER | AEPW | Hobart Junction 138kV
GEN-2008-037 | 04 SOUTHEAST | DIS-10-1 | Wind | 99 | ER | WFEC | Tap Washita - Blue Canyon Wind 138kV
GEN-2008-079 | 03 CENTRAL | DIS-09-1 | Wind | 98.9 | ER | SUNC | Crooked Creek 115kV
GEN-2008-123N | 02 NEBRASKA | DIS-10-1 | Wind | 89.66 | ER | NPPD | Tap Pauline - Hildreth (Rosemont) 115kV
GEN-2009-001IS | 01 NORTH | DIS-16-1 | Wind | 200 | ER/NR | BEPC
GEN-2009-008 | 03 CENTRAL | DIS-10-1 | Wind | 198.69 | ER | MIDW | South Hays 230kV
GEN-2009-018IS | 01 NORTH | DIS-16-1 | Wind | 100 | ER | BEPC
GEN-2009-020AIS | 01 NORTH | DIS-16-1 | Wind | 80 | ER/NR | WAPA
GEN-2009-025 | 04 SOUTHEAST | DIS-09-1 | Wind | 59.8 | ER | OKGE | TAP Deer Creek – Sinclair 69kV
GEN-2009-026IS | 01 NORTH | DIS-16-1 | Wind | 110 | ER/NR | BEPC
GEN-2010-001IS | 01 NORTH | DIS-15-2-PQ | Wind | 99 | ER/NR | BEPC
GEN-2010-003 | 03 CENTRAL | DIS-10-1 | Wind | 99.5 | ER | WERE | Waverly 345kV
GEN-2010-003IS | 01 NORTH | DIS-16-1 | Wind | 34 | ER/NR | BEPC
GEN-2010-005 | 03 CENTRAL | DIS-10-1 | Wind | 299.2 | ER | WERE | Viola 345kV
GEN-2010-036 | 03 CENTRAL | DIS-10-2 | Hydro | 4.6 | ER | WERE | 6th Street 115kV
GEN-2010-036PQ | 03 CENTRAL | DIS-10-2 | Hydro | 2.7 | ER | WERE
GEN-2010-055 | 04 SOUTHEAST | DIS-16-1 | Gas | 4.5 | ER | AEPW | Wekiwa 138kV
GEN-2010-057 | 03 CENTRAL | DIS-11-1 | Wind | 201 | ER/NR | MIDW | Rice County 230kV
GEN-2011-008 | 03 CENTRAL | DIS-11-1 | Wind | 600 | ER | SUNC | Clark County 345kV
GEN-2011-010 | 04 SOUTHEAST | DIS-11-1 | Wind | 100.8 | ER | OKGE | Minco 345kV
GEN-2011-014 | 05 SOUTHWEST | DIS-11-1 | Wind | 198 | ER | OKGE | Beaver County-Woodward EHV Dbl Ckt (Badger) 345kV
GEN-2011-018 | 02 NEBRASKA | DIS-16-1 | Wind | 73.6 | ER/NR | NPPD | Steele City 115kV
GEN-2011-019 | 04 SOUTHEAST | DIS-16-1 | Wind | 175 | ER/NR | OKGE | Woodward EHV 345kV
GEN-2011-020 | 04 SOUTHEAST | DIS-16-1 | Wind | 165.6 | ER/NR | OKGE | Woodward EHV 345kV
GEN-2011-025_GEN-2023-SR9 | 05 SOUTHWEST | DIS-11-1 | Wind | 79.96 | ER | SPS
GEN-2011-027 | 02 NEBRASKA | DIS-16-1 | Wind | 120 | ER/NR | NPPD | Wakefield 230kV
GEN-2011-040 | 04 SOUTHEAST | DIS-16-1 | Wind | 111 | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV
GEN-2011-045 | 05 SOUTHWEST | DIS-16-1 | NG CT | 205 | ER | SPS | Jones 230kV
GEN-2011-046 | 05 SOUTHWEST | DIS-16-1 | Diesel CT | 23 | ER | SPS | Tucumcari 115kV
GEN-2011-050 | 04 SOUTHEAST | DIS-11-2 | Wind | 108 | ER | AEPW | Tap Rush Springs - Marlow 138kV
GEN-2011-056 | 02 NEBRASKA | DIS-16-1 | Hydro | 3.6 | ER | NPPD | Jeffrey 115kV
GEN-2011-056A | 02 NEBRASKA | DIS-11-2 | Hydro | 3.6 | ER | NPPD | John 1 115kV
GEN-2011-056APQ | 02 NEBRASKA | DIS-11-2 | Hydro | 20 | ER | NPPD
GEN-2011-056B | 02 NEBRASKA | DIS-11-2 | Hydro | 4.5 | ER | NPPD | John 2 115kV
GEN-2011-056BPQ | 02 NEBRASKA | DIS-11-2 | Hydro | 22 | ER | NPPD
GEN-2011-056PQ | 02 NEBRASKA | DIS-11-2 | Hydro | 20 | ER | NPPD
GEN-2011-057 | 03 CENTRAL | DIS-11-2 | Wind | 150 | ER | WERE | Creswell 138kV
GEN-2012-001 | 05 SOUTHWEST | DIS-12-1 | Wind | 61.2 | ER | SPS | Tap Grassland - Borden County 230 kv
GEN-2012-004 | 04 SOUTHEAST | DIS-16-1 | Wind | 40.8 | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV
GEN-2012-007 | 03 CENTRAL | DIS-16-1 | Gas | 120 | ER/NR | SUNC | Rubart 115kV
GEN-2012-020 | 05 SOUTHWEST | DIS-12-2 | Wind | 478 | ER | SPS | TUCO 230kV
GEN-2012-021 | 02 NEBRASKA | DIS-12-2 | Gas | 4.8 | ER | LES | Terry Bundy Generating Station 115kV
GEN-2012-024 | 03 CENTRAL | DIS-16-1 | Wind | 180 | ER | SUNC | Clark County 345kV
GEN-2012-028 | 04 SOUTHEAST | DIS-12-2 | Wind | 74 | ER | WFEC | Gotebo 69kV
GEN-2012-032 | 04 SOUTHEAST | DIS-12-2 | Wind | 299 | ER | OKGE | Rose Hill-(Ranch Road) Sooner (Open Sky) 345kV
GEN-2012-033_GEN-2015-062_GEN-2023-SR13 | 04 SOUTHEAST | DIS-16-1 | Wind | 103.32 | ER | OKGE
GEN-2012-041 | 04 SOUTHEAST | DIS-16-1 | CT | 121.5 | ER | OMPA | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV
GEN-2013-002_GEN-2013-019 | 02 NEBRASKA | DIS-16-1 | Wind | 124.2 | ER/NR | NPPD
GEN-2013-007 | 04 SOUTHEAST | DIS-13-1 | Wind | 100 | ER/NR | OKGE | Tap Prices Falls - Carter 138kV
GEN-2013-008 | 02 NEBRASKA | DIS-16-1 | Wind | 1.2 | ER | NPPD | Steele City 115kV
GEN-2013-009IS | 01 NORTH | DIS-16-1 | Wind | 19.5 | ER | WAPA
GEN-2013-012 | 04 SOUTHEAST | DIS-16-1 | Gas | 147 | ER | OKGE | Redbud 345kV
GEN-2013-022 | 05 SOUTHWEST | DIS-13-2 | Solar | 25 | ER/NR | SPS | Norton 115kV Switching Station
GEN-2013-027 | 05 SOUTHWEST | DIS-14-2 | Wind | 148.4 | ER/NR | SPS | Tolk - Yoakum 230kV
GEN-2013-028 | 04 SOUTHEAST | DIS-16-1 | Gas | 538 | ER | GRDA | Tap N Tulsa - GRDA 1 345kV
GEN-2013-029 | 04 SOUTHEAST | DIS-13-2 | Wind | 299 | ER | OKGE | Renfrow 345kV
GEN-2013-032 | 02 NEBRASKA | DIS-13-2 | Wind | 202.5 | ER | NPPD | Antelope 115kV
GEN-2013-033 | 03 CENTRAL | DIS-13-2 | Gas | 28 | ER/NR | MIDW | Goodman Energy Center 115kV
GEN-2014-001 | 03 CENTRAL | DIS-16-1 | Wind | 200.6 | ER | WERE | Tap Wichita - Emporia Energy Center 345kV
GEN-2014-001IS | 01 NORTH | DIS-16-1 | Wind | 103.24 | ER | WAPA | Sulphur 115kV
GEN-2014-002 | 04 SOUTHEAST | DIS-16-1 | Wind | 10.53 | ER | OKGE | Tatonga 345kV
GEN-2014-005 | 04 SOUTHEAST | DIS-16-1 | Wind | 5.7 | ER | OKGE | Minco 345kV
GEN-2014-006IS | 01 NORTH | DIS-16-1 | Gas | 125 | ER/NR | BEPC
GEN-2014-010IS | 01 NORTH | DIS-16-1 | Wind | 150 | ER/NR | BEPC
GEN-2014-013 | 02 NEBRASKA | DIS-16-1 | Wind | 73.5 | ER/NR | LES | Meadow Grove 230kV
GEN-2014-014IS | 01 NORTH | DIS-16-1 | Wind | 150 | ER/NR | BEPC
GEN-2014-020 | 04 SOUTHEAST | DIS-16-1 | Wind | 100 | ER/NR | AEPW | Tuttle 138kV
GEN-2014-021 | 03 CENTRAL | DIS-16-1 | Wind | 300 | ER/NR | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV
GEN-2014-031 | 02 NEBRASKA | DIS-14-2 | Wind | 35.8 | ER/NR | GRIS | Meadow Grove 230kV
GEN-2014-032 | 02 NEBRASKA | DIS-16-1 | Wind | 10.2 | ER/NR | NPPD | Meadow Grove 230kV
GEN-2014-033 | 05 SOUTHWEST | DIS-14-2 | Solar | 70 | ER | SPS | Chaves County 115kV
GEN-2014-034 | 05 SOUTHWEST | DIS-14-2 | Solar | 70 | ER | SPS | Chaves County 115kV
GEN-2014-035 | 05 SOUTHWEST | DIS-16-1 | Solar | 30 | ER | SPS | Chaves County 115kV
GEN-2014-040 | 05 SOUTHWEST | DIS-16-1 | Wind | 320 | ER | SPS | Castro 115kV
GEN-2014-056_GEN-2015-057 | 04 SOUTHEAST | DIS-16-1 | Wind | 350 | ER | OKGE
GEN-2014-057 | 04 SOUTHEAST | DIS-14-2 | Wind | 249.9 | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV
GEN-2014-064 | 04 SOUTHEAST | DIS-16-1 | Wind | 248.4 | ER | OKGE | Otter 138kV
GEN-2015-001 | 04 SOUTHEAST | DIS-15-1 | Wind | 200 | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV
GEN-2015-005 | 03 CENTRAL | DIS-16-1 | Wind | 200.1 | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV
GEN-2015-007 | 02 NEBRASKA | DIS-15-1 | Wind | 160 | ER | NPPD | Hoskins 345kV
GEN-2015-013 | 04 SOUTHEAST | DIS-16-1 | Solar | 120 | ER/NR | WFEC | Snyder 138kV
GEN-2015-014_GEN-2023-SR12 | 05 SOUTHWEST | DIS-15-1 | Wind | 150 | ER | SPS
GEN-2015-015 | 04 SOUTHEAST | DIS-15-1 | Wind | 154.56 | ER/NR | OKGE | Tap Medford Tap – Coyote 138kV
GEN-2015-016 | 03 CENTRAL | DIS-16-1 | Wind | 200 | ER/NR | KCPL | Tap Marmaton - Centerville 161kV
GEN-2015-021 | 03 CENTRAL | DIS-15-1 | Solar | 20 | ER/NR | SUNC | Johnson Corner 115kV
GEN-2015-023 | 02 NEBRASKA | DIS-16-1 | Wind | 300.7 | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV
GEN-2015-034 | 04 SOUTHEAST | DIS-16-1 | Wind | 200 | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV
GEN-2015-036 | 04 SOUTHEAST | DIS-16-1 | Wind | 303.6 | ER | OKGE | Johnston County 345kV
GEN-2015-041 | 05 SOUTHWEST | DIS-16-1 | CT | 5 | ER | SPS | TUCO 345kV
GEN-2015-045 | 04 SOUTHEAST | DIS-16-1 | Battery/Storage | 10.3 | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV
GEN-2015-046 | 01 NORTH | DIS-16-1 | Wind | 300 | ER | BEPC | Tande 345kV
GEN-2015-048 | 04 SOUTHEAST | DIS-16-1 | Wind | 200 | ER | OKGE | Cleo Corner 138kV
GEN-2015-052 | 03 CENTRAL | DIS-16-1 | Wind | 300 | ER | WERE | Open Sky-Rose Hill 345kV
GEN-2015-063 | 04 SOUTHEAST | DIS-16-1 | Wind | 300 | ER | OKGE | Woodring-Matthewson 345kV
GEN-2015-064 | 03 CENTRAL | DIS-16-1 | Wind | 197.8 | ER | SUNC | Mingo 115kV
GEN-2015-065 | 03 CENTRAL | DIS-15-2 | Wind | 202.4 | ER | SUNC | Mingo 345kV
GEN-2015-066 | 04 SOUTHEAST | DIS-16-1 | Wind | 219.96 | ER | OKGE | Sooner - Cleveland 345kV
GEN-2015-082 | 05 SOUTHWEST | DIS-16-1 | Wind | 200 | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV
GEN-2015-088 | 02 NEBRASKA | DIS-16-1 | Wind | 300 | ER/NR | NPPD | Tobias 345kV Substation
GEN-2015-089 | 01 NORTH | DIS-16-1 | Wind | 200 | ER | BEPC | Utica 230 kV Substation
GEN-2015-090 | 03 CENTRAL | DIS-16-1 | Wind | 220 | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV
GEN-2015-096 | 01 NORTH | DIS-16-1 | Wind | 150 | ER | BEPC | Brady 230kV substation
GEN-2016-003 | 04 SOUTHEAST | DIS-16-1 | Wind | 248.4 | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV
GEN-2016-004 | 01 NORTH | DIS-16-1 | Wind | 202 | ER/NR | BEPC | Basin Electric 230 kV
GEN-2016-009 | 03 CENTRAL | DIS-16-1 | Steam Turbine | 29 | ER | OKGE | Osage 69 kV Sub
GEN-2016-013 | 03 CENTRAL | DIS-16-1 | CT | 10 | ER | EMDE | LaRussell Energy Center 161kV
GEN-2016-014 | 03 CENTRAL | DIS-16-1 | CT | 10 | ER | EMDE | LaRussell Energy Center 161kV
GEN-2016-017 | 01 NORTH | DIS-16-1 | Wind | 250.24 | ER | BEPC | Chappelle Creek 345kV
GEN-2016-020 | 04 SOUTHEAST | DIS-16-1 | WIND | 148.4 | ER | WFEC | Moreland 138kV Substation
GEN-2016-021 | 02 NEBRASKA | DIS-16-1 | WIND | 298.47 | ER | NPPD | Hoskins 345kV
GEN-2016-022 | 04 SOUTHEAST | DIS-16-1 | Wind | 151.8 | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV
GEN-2016-028 | 04 SOUTHEAST | DIS-16-1 | Wind | 100 | ER | AEPW | Clayton 138 kV Sub
GEN-2016-030_GEN-2020-SR2 | 04 SOUTHEAST | DIS-16-1 | Solar | 100 | ER/NR | OKGE
GEN-2016-031 | 04 SOUTHEAST | DIS-16-1 | Wind | 1.5 | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV
GEN-2016-032 | 04 SOUTHEAST | DIS-16-1 | Wind | 200 | ER/NR | OKGE | Crescent Substation 138 kV
GEN-2016-036 | 01 NORTH | DIS-16-2 | Wind | 44.6 | ER | WAPA | Granite Falls 115kV substation
GEN-2016-037 | 04 SOUTHEAST | DIS-17-1 | Wind | 300 | ER | AEPW | Chisholm-Gracemont 345kV
GEN-2016-043 | 02 NEBRASKA | DIS-16-1 | Wind | 230 | ER | NPPD | Hoskins 345kV
GEN-2016-045 | 04 SOUTHEAST | DIS-16-1 | Wind | 499.1 | ER | OKGE | Mathewson 345kV
GEN-2016-046 | 03 CENTRAL | DIS-16-1 | Wind | 299 | ER | SUNC | Clark County-Ironwood 345kV
GEN-2016-047_PQOKGEMustang | 04 SOUTHEAST | DIS-16-1 | CT | 134 | ER | OKGE
GEN-2016-050 | 02 NEBRASKA | DIS-16-1 | Wind | 250.7 | ER | NPPD | Axtell – Post Rock 345 kV
GEN-2016-057 | 04 SOUTHEAST | DIS-16-1 | Wind | 499.1 | ER | OKGE | Mathewson 345kV
GEN-2016-061 | 04 SOUTHEAST | DIS-16-1 | Wind | 250.7 | ER | OKGE | Sooner-Woodring 345 kV line
GEN-2016-067 | 03 CENTRAL | DIS-16-1 | Wind | 73.6 | ER | SUNC | Mingo 345kV
GEN-2016-068 | 04 SOUTHEAST | DIS-16-1 | Wind | 250 | ER | OKGE | Woodring 345kV
GEN-2016-071 | 04 SOUTHEAST | DIS-16-1 | Wind | 64.6 | ER | OKGE | Middleton Tap 138kV Substation
GEN-2016-074 | 02 NEBRASKA | DIS-16-2 | Wind | 200 | ER | NPPD | Sweetwater 345kV
GEN-2016-075 | 02 NEBRASKA | DIS-16-1 | Wind | 50 | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV
GEN-2016-087 | 01 NORTH | DIS-16-2 | Wind | 98.9 | ER | WAPA | Campbell County 230 kV line
GEN-2016-091 | 04 SOUTHEAST | DIS-16-2 | Wind | 303.6 | ER | AEPW | Gracemont-Lawton East Side 345kV
GEN-2016-094 | 01 NORTH | DIS-16-2 | Wind | 200 | ER | BEPC | Tap Ft Thompson - Oahe 230kV Line (Single Circuit)
GEN-2016-095 | 04 SOUTHEAST | DIS-16-2 | Wind | 200 | ER/NR | AEPW | Gracemont-Lawton East Side 345kV
GEN-2016-097 | 04 SOUTHEAST | DIS-16-2 | Wind | 100 | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV
GEN-2016-102 | 04 SOUTHEAST | DIS-16-2 | Wind | 147.5 | ER/NR | OKGE | Blue River 138kV
GEN-2016-111 | 03 CENTRAL | DIS-16-2 | Wind | 302 | ER | WERE | Reno - Summit 345kV
GEN-2016-115 | 03 CENTRAL | DIS-16-2 | Wind | 300 | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV
GEN-2016-118 | 04 SOUTHEAST | DIS-16-2 | Wind | 288 | ER | WFEC | Dover Switchyard 138 kV Line
GEN-2016-119 | 04 SOUTHEAST | DIS-16-2 | Wind | 600 | ER | OKGE | Spring Creek-Sooner 345kV
GEN-2016-121 | 05 SOUTHWEST | DIS-16-2 | Solar | 110 | ER | SPS | Roadrunner 115kV
GEN-2016-123_GEN-2016-124_GEN-2016-125 | 05 SOUTHWEST | DIS-16-2 | Wind | 522 | ER | SPS
GEN-2016-126 | 04 SOUTHEAST | DIS-16-2 | Wind | 172.5 | ER/NR | OKGE | Arbuckle 138kV substation
GEN-2016-128 | 04 SOUTHEAST | DIS-16-2 | Wind | 176 | ER | OKGE | Woodring 345kV
GEN-2016-130 | 01 NORTH | DIS-16-2 | Wind | 202 | ER | BEPC | Leland Olds 345 kV
GEN-2016-132 | 04 SOUTHEAST | DIS-16-2 | Wind | 6.1 | ER | AEPW | Sweetwater 230kV
GEN-2016-133_GEN-2016-134_GEN-2016-137_GEN-2016-138 | 04 SOUTHEAST | DIS-16-2 | Wind | 750 | ER | AEPW
GEN-2016-139 | 04 SOUTHEAST | DIS-16-2 | Wind | 100 | ER | AEPW | Riverside 345kV Substation
GEN-2016-141 | 04 SOUTHEAST | DIS-16-2 | Wind | 350 | ER | AEPW | Riverside 345kV Substation
GEN-2016-142 | 04 SOUTHEAST | DIS-16-2 | Wind | 350 | ER | AEPW | Riverside 345kV Substation
GEN-2016-145 | 04 SOUTHEAST | DIS-16-2 | Wind | 175 | ER | AEPW | Riverside 345kV Substation
GEN-2016-146 | 04 SOUTHEAST | DIS-16-2 | Wind | 175 | ER | AEPW | Riverside 345kV Substation
GEN-2016-147 | 02 NEBRASKA | DIS-16-2 | Solar | 40 | ER | NPPD | Sidney 115 kV Sub
GEN-2016-149 | 03 CENTRAL | DIS-16-2 | Wind | 302 | ER | WERE | Stranger Creek 345kV
GEN-2016-150 | 03 CENTRAL | DIS-16-2 | Wind | 302 | ER | WERE | Stranger Creek 345kV
GEN-2016-151_GEN-2023-SR4 | 01 NORTH | DIS-16-2 | Wind | 202 | ER | BEPC
GEN-2016-153_GEN-2021-SR8 | 03 CENTRAL | DIS-16-2 | Wind | 134 | ER | WERE
GEN-2016-160 | 03 CENTRAL | DIS-16-2 | Battery/Storage | 20 | ER/NR | MIDW | Post Rock 230kV
GEN-2016-167 | 04 SOUTHEAST | DIS-16-2 | Solar | 73.5 | ER/NR | AEPW | Lieberman - North Benton 138 kV Line
GEN-2016-174 | 03 CENTRAL | DIS-16-2 | Wind | 302 | ER | WERE | Stranger Creek 345kV
GEN-2016-176 | 03 CENTRAL | DIS-16-2 | Wind | 302 | ER | WERE | Stranger Creek 345kV
GEN-2016-177 | 05 SOUTHWEST | DIS-16-2 | Gas Turbine | 17 | ER | SPS | XTO-Cornell 115 kV station
GEN-2017-004 | 03 CENTRAL | DIS-17-1 | Wind | 201.6 | ER | SUNC | Elm Creek - Summit 345 kV
GEN-2017-005 | 03 CENTRAL | DIS-17-1 | Wind | 190 | ER | WERE | Marmaton - Litchfield 161 kV
GEN-2017-009 | 03 CENTRAL | DIS-17-1 | Wind | 302 | ER | WERE | Neosho - Caney River 345 kV
GEN-2017-010 | 01 NORTH | DIS-17-1 | Wind | 200.1 | ER | BEPC | Rhame 230 kV Sub
GEN-2017-011 | 04 SOUTHEAST | DIS-17-1 | Solar | 151.8 | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV
GEN-2017-014 | 01 NORTH | DIS-17-1 | Wind | 300 | ER | WAPA | Philip Tap 230 kV
GEN-2017-018 | 03 CENTRAL | DIS-17-1 | Solar | 189 | ER/NR | SUNC | Thistle 345 kV sub
GEN-2017-022 | 03 CENTRAL | DIS-17-1 | Solar | 65 | ER/NR | WERE | Altoona- NE Parson 138kV
GEN-2017-023 | 04 SOUTHEAST | DIS-17-1 | Solar | 85 | ER/NR | WFEC | Hugo Power Plant 138 kV Sub
GEN-2017-027 | 04 SOUTHEAST | DIS-17-1 | Wind | 140 | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV
GEN-2017-033 | 05 SOUTHWEST | DIS-17-1 | Wind | 200 | ER | AEPW | Oklaunion 345 kV sub
GEN-2017-036 | 04 SOUTHEAST | DIS-17-1 | Solar | 100 | ER | WFEC | Snyder - Cache 138 kV
GEN-2017-040 | 04 SOUTHEAST | DIS-17-1 | Solar | 200.1 | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV
GEN-2017-047 | 05 SOUTHWEST | DIS-17-1 | Wind | 102 | ER/NR | SPS | Bull Creek 115 kV substation
GEN-2017-048 | 01 NORTH | DIS-17-1 | Wind | 300 | ER | BEPC | Neset 230 kV Substation
GEN-2017-057 | 04 SOUTHEAST | DIS-17-1 | Solar | 72.5 | ER | AEPW | Hosston 69kV
GEN-2017-060 | 03 CENTRAL | DIS-17-1 | Wind | 149.4 | ER | EMDE | LaRussell Energy Center 161kV
GEN-2017-061 | 04 SOUTHEAST | DIS-17-1 | Solar | 101.5 | ER | GRDA | GRDA1 to CLARMR 5 161kV line
GEN-2017-068 | 03 CENTRAL | DIS-17-1 | Solar | 103.5 | ER/NR | WERE | Gordon Evans 138kV Substation
GEN-2017-071_GEN-2017-072_GEN-2024-SR5 | 04 SOUTHEAST | DIS-17-1 | Solar | 176.9 | ER | OKGE
GEN-2017-073 | 04 SOUTHEAST | DIS-17-1 | Solar | 72.5 | ER | GRDA | Dry Gulch 161kV sub
GEN-2017-074 | 04 SOUTHEAST | DIS-17-1 | Solar | 72.5 | ER | AEPW | Pryor Junction 138kV sub
GEN-2017-075 | 04 SOUTHEAST | DIS-17-1 | Solar | 200 | ER | OKGE | Hugo-Sunnyside 345 kV
GEN-2017-077 | 04 SOUTHEAST | DIS-17-1 | Solar | 124.7 | ER | AEPW | Explorer Claremore Tap COOYYAH4
GEN-2017-082 | 03 CENTRAL | DIS-17-1 | Wind | 149.4 | ER | EMDE | Asbury Plant 161 kV
GEN-2017-086 | 03 CENTRAL | DIS-17-1 | Wind | 150 | ER | WERE | Viola 345kV
GEN-2017-092 | 04 SOUTHEAST | DIS-17-1 | Solar | 200 | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV
GEN-2017-094 | 01 NORTH | DIS-17-1 | Wind | 200 | ER | WAPA | Fort Thompson-Huron 230 kV
GEN-2017-097 | 01 NORTH | DIS-17-1 | Solar | 128 | ER | WAPA | Underwood 115 kV Sub
GEN-2017-100 | 05 SOUTHWEST | DIS-17-1 | Solar | 102.6 | ER/NR | SPS | Texas County 115kV
GEN-2017-105 | 02 NEBRASKA | DIS-17-2 | Wind | 75 | ER/NR | OPPD | Tekamah - Raun 161 kV Line
GEN-2017-108 | 03 CENTRAL | DIS-17-2 | Solar | 400 | ER/NR | KCPL | Stillwell - Clinton 161kV Line
GEN-2017-117 | 04 SOUTHEAST | DIS-17-2 | Battery/Storage | 19.8 | ER/NR | WFEC | El Reno SW 138kV
GEN-2017-119 | 03 CENTRAL | DIS-17-2 | Wind | 180 | ER | SUNC | Elm Creek 345kV substation
GEN-2017-120 | 03 CENTRAL | DIS-17-2 | Wind | 260 | ER | WERE | Abilene Energy Center-Northview 115kV
GEN-2017-121 | 03 CENTRAL | DIS-17-2 | Wind | 200 | ER/NR | WERE | Sumner 138kV
GEN-2017-133 | 04 SOUTHEAST | DIS-17-2 | Wind | 200 | ER/NR | OKGE | Arcadia 345kV
GEN-2017-134 | 04 SOUTHEAST | DIS-17-2 | Wind | 250 | ER/NR | OKGE | Arcadia 345kV
GEN-2017-137 | 04 SOUTHEAST | DIS-17-2 | Wind | 295 | ER/NR | OKGE | Arcadia 345kV
GEN-2017-140 | 04 SOUTHEAST | DIS-17-2 | Solar | 160 | ER/NR | AEPW | Clarksville 345kV Switching Station
GEN-2017-141 | 04 SOUTHEAST | DIS-17-2 | Solar | 241.7 | ER/NR | AEPW | Clarksville 345kV Switching Station
GEN-2017-144 | 02 NEBRASKA | DIS-17-2 | Wind | 200 | ER | NPPD | Holt County 345kV
GEN-2017-146 | 05 SOUTHWEST | DIS-17-2 | Wind | 151.8 | ER | SPS | Deaf Smith-Plant X 230kV
GEN-2017-149 | 04 SOUTHEAST | DIS-17-2 | Wind | 258 | ER/NR | OKGE | Johnson County 345kV Substation
GEN-2017-150 | 04 SOUTHEAST | DIS-17-2 | Solar | 250 | ER/NR | OKGE | Minco 345kV
GEN-2017-151 | 05 SOUTHWEST | DIS-17-2 | Wind | 300 | ER | SPS | TUCO-Oklaunion 345kV
GEN-2017-158 | 05 SOUTHWEST | DIS-17-2 | Wind | 265 | ER | SPS | Tolk 230kV Substation
GEN-2017-164 | 04 SOUTHEAST | DIS-17-2 | Solar | 250 | ER/NR | OKGE | Woodring 345kV Substation
GEN-2017-171 | 04 SOUTHEAST | DIS-17-2 | Solar | 150 | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV
GEN-2017-172 | 04 SOUTHEAST | DIS-17-2 | Solar | 50 | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV
GEN-2017-173 | 04 SOUTHEAST | DIS-17-2 | Solar | 50 | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV
GEN-2017-175 | 01 NORTH | DIS-17-2 | Wind | 270 | ER | WAPA | Vfodnes-Utica Jct. 230kV
GEN-2017-178 | 04 SOUTHEAST | DIS-17-2 | Battery/Storage | 52 | ER/NR | OKGE | Woodring 345kV Substation
GEN-2017-181 | 02 NEBRASKA | DIS-17-2 | Wind | 300 | ER/NR | NPPD | Tobias 345kV Substation
GEN-2017-182 | 02 NEBRASKA | DIS-17-2 | Wind | 128 | ER/NR | NPPD | Tobias 345kV Substation
GEN-2017-183 | 03 CENTRAL | DIS-17-2 | Wind | 400 | ER/NR | KCPL | Nashua-St. Joe 345kV
GEN-2017-184 | 03 CENTRAL | DIS-17-2 | Solar | 400 | ER/NR | KCPL | Nashua-St. Joe 345kV
GEN-2017-187 | 05 SOUTHWEST | DIS-17-2 | Solar | 150 | ER | SPS | Flatland 115 kV Substation
GEN-2017-188 | 03 CENTRAL | DIS-17-2 | Solar | 130 | ER | EMDE | Asbury 161 kV
GEN-2017-195 | 03 CENTRAL | DIS-17-2 | Solar | 500.4 | ER/NR | KCPL | West Gardner 345kV
GEN-2017-196 | 03 CENTRAL | DIS-17-2 | Battery/Storage | 128 | ER/NR | KCPL | West Gardner 345kV
GEN-2017-198 | 02 NEBRASKA | DIS-17-2 | Battery/Storage | 11.64 | ER | OPPD | Jones St. No 1201 69kV substation
GEN-2017-201 | 02 NEBRASKA | DIS-17-2 | Wind | 250 | ER/NR | NPPD | Hoskins 345kV Substation
GEN-2017-210 | 02 NEBRASKA | DIS-17-2 | Storage | 310 | ER | NPPD | McCool 345kV Substation
GEN-2017-214 | 01 NORTH | DIS-17-2 | Wind | 100 | ER/NR | WAPA | Logan 230kV Substation
GEN-2017-215 | 01 NORTH | DIS-17-2 | Wind | 100 | ER/NR | WAPA | Logan 230kV Substation
GEN-2017-220 | 03 CENTRAL | DIS-17-2 | Solar | 201.6 | ER/NR | WERE | Buffalo Flats 345kV Substation
GEN-2017-221 | 03 CENTRAL | DIS-17-2 | Battery/Storage | 152 | ER/NR | WERE | Buffalo Flats 345kV Substation
GEN-2017-222 | 01 NORTH | DIS-17-2 | Wind | 180 | ER | WAPA | Denison 230kV Substation
GEN-2017-226 | 03 CENTRAL | DIS-17-2 | Solar | 201.6 | ER/NR | WERE | Gordon Evans 138kV Substation
GEN-2017-227 | 03 CENTRAL | DIS-17-2 | Storage | 201.6 | ER/NR | WERE | Gordon Evans 138kV Substation
GEN-2017-230_GEN-2024-SR3 | 04 SOUTHEAST | DIS-17-2 | Solar | 72.5 | ER/NR | OKGE
GEN-2017-231_GEN-2024-SR2 | 04 SOUTHEAST | DIS-17-2 | Solar | 72.5 | ER/NR | OKGE
GEN-2017-232 | 04 SOUTHEAST | DIS-17-2 | Solar | 52.2 | ER/NR | OKGE | Brown 138kV Substation
GEN-2017-233 | 04 SOUTHEAST | DIS-17-2 | Wind | 215 | ER/NR | OKGE | Minco 345kV
GEN-2017-234 | 02 NEBRASKA | DIS-17-2 | Wind | 115 | ER | NPPD | Spalding to North Loup 115kV
GEN-2017-239 | 05 SOUTHWEST | DIS-17-2 | Solar | 300 | ER | SPS | Mahoney 230kV Substation
GEN-2018-003 | 04 SOUTHEAST | DIS-18-1 | Solar | 150 | ER/NR | AEPW | North Boston-Bann 138kV Line
GEN-2018-004 | 05 SOUTHWEST | DIS-18-1 | Solar | 74.99 | ER | SPS | T14 Circuit 115kV line
GEN-2018-009 | 03 CENTRAL | DIS-18-1 | Wind | 150 | ER | SUNC | Cimarron 115kV Substation
GEN-2018-011 | 04 SOUTHEAST | DIS-18-1 | Battery/Storage | 74.1 | ER/NR | WFEC | Dover 138 kV Switching Station
GEN-2018-013 | 03 CENTRAL | DIS-18-1 | Wind | 74.1 | ER | WERE | Abilene Energy Center-Northview 115kV Line
GEN-2018-015 | 05 SOUTHWEST | DIS-18-1 | Solar | 252 | ER/NR | SPS | Tuco-Oklaunion 345kV Line
GEN-2018-024 | 04 SOUTHEAST | DIS-17-1 | Battery/Storage | 100 | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV
GEN-2018-025 | 02 NEBRASKA | DIS-18-1 | Battery/Storage | 200 | ER | OPPD | Fort Calhoun 345kV Substation
GEN-2018-026 | 04 SOUTHEAST | DIS-18-1 | Battery/Storage | 100 | ER | OKGE | Mustang 138kV Substation
GEN-2018-027 | 04 SOUTHEAST | DIS-18-1 | Battery/Storage | 100 | ER | OKGE | Tulsa Power Station 138kV Substation
GEN-2018-028 | 04 SOUTHEAST | DIS-18-1 | Battery/Storage | 200 | ER | AEPW | Tulsa North 138kV Substation
GEN-2018-029 | 04 SOUTHEAST | DIS-18-1 | Battery/Storage | 100 | ER | OKGE | Horseshoe Lake 138kV Substation
GEN-2018-031 | 03 CENTRAL | DIS-18-1 | Battery/Storage | 50 | ER | KCPL | Blue Valley 161kV Substation
GEN-2018-033 | 02 NEBRASKA | DIS-18-1 | Battery/Storage | 200 | ER | OPPD | Cass County 345kV Substation
GEN-2018-037 | 02 NEBRASKA | DIS-18-1 | Battery/Storage | 100 | ER | OPPD | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV
GEN-2018-043 | 02 NEBRASKA | DIS-18-1 | Solar | 500 | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break
GEN-2018-048 | 04 SOUTHEAST | DIS-18-1 | Solar | 300 | ER | OKGE | Pecan Creek 345kV Substation
GEN-2018-049 | 03 CENTRAL | DIS-18-1 | Solar | 120 | ER | SUNC | Thistle 345kV Substation
GEN-2018-050 | 04 SOUTHEAST | DIS-18-1 | Solar | 200 | ER | AEPW | Longwood 345kV Substation
GEN-2018-052 | 05 SOUTHWEST | DIS-18-1 | Battery/Storage | 70 | ER | SPS | Roadrunner 115kV Substation
GEN-2018-055 | 04 SOUTHEAST | DIS-18-1 | Solar | 252 | ER/NR | AEPW | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie)
GEN-2018-057 | 03 CENTRAL | DIS-18-1 | Solar | 203.4 | ER/NR | WERE | Gordon Evans 138kV
GEN-2018-060 | 02 NEBRASKA | DIS-18-1 | Wind | 50 | ER/NR | NPPD | Axtell-Post Rock 345 kV
GEN-2018-064 | 04 SOUTHEAST | DIS-18-2_19-1 | Solar | 80 | ER/NR | GRDA | Tonnece Substation 69kV
GEN-2018-067 | 01 NORTH | DIS-18-2_19-1 | Wind | 255 | ER | BEPC | 115kV Strandahl sub
GEN-2018-069 | 01 NORTH | DIS-18-2_19-1 | Wind | 125 | ER/NR | WAPA | WAPA-UGP Mingusville 230kV
GEN-2018-071 | 04 SOUTHEAST | DIS-18-2_19-1 | Battery/Storage | 151 | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line
GEN-2018-072 | 04 SOUTHEAST | DIS-18-2_19-1 | Battery/Storage | 151 | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line
GEN-2018-074 | 01 NORTH | DIS-18-2_19-1 | Wind | 72 | ER | WAPA | Denison 230kV Substation
GEN-2018-079 | 04 SOUTHEAST | DIS-18-2_19-1 | Solar | 148 | ER | AEPW | Farmland-Delaware 138kV line
GEN-2018-082 | 04 SOUTHEAST | DIS-18-2_19-1 | Wind | 215 | ER | AEPW | Pittsburg 345kV Substation
GEN-2018-089 | 05 SOUTHWEST | DIS-18-2_19-1 | Wind | 196 | ER | SPS | Newhart 230kV Substation
GEN-2018-099 | 05 SOUTHWEST | DIS-18-2_19-1 | Wind | 300 | ER | SPS | Tolk 230kV Substation
GEN-2018-106 | 04 SOUTHEAST | DIS-18-2_19-1 | Solar | 165 | ER | AEPW | Longwood 345kV substation
GEN-2018-108 | 03 CENTRAL | DIS-18-2_19-1 | Battery/Storage | 95 | ER | SUNC | Thistle 345kV substation
GEN-2018-115 | 04 SOUTHEAST | DIS-18-2_19-1 | Solar | 250 | ER/NR | AEPW | Lawton East Side 345kV/138kv Substation
GEN-2018-125 | 02 NEBRASKA | DIS-18-2_19-1 | Wind | 231 | ER/NR | NPPD | New switching station on Gentleman to Sweetwater 345kV line
GEN-2018-128 | 03 CENTRAL | DIS-18-2_19-1 | Wind | 200.22 | ER/NR | OKGE | Renfrow-Viola 345 kV
GEN-2018-131 | 02 NEBRASKA | DIS-18-2_19-1 | Solar | 221.4 | ER/NR | NPPD | Antelope - Hoskins 345 kV
GEN-2018-132 | 02 NEBRASKA | DIS-18-2_19-1 | Solar | 201.6 | ER/NR | NPPD | Antelope - Hoskins 345 kV
GEN-2019-001 | 03 CENTRAL | DIS-18-2_19-1 | Wind | 25 | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV
GEN-2019-002 | 04 SOUTHEAST | DIS-18-2_19-1 | Battery/Storage | 100 | ER | GRDA | Maid 161kV substation
GEN-2019-003 | 05 SOUTHWEST | DIS-18-2_19-1 | Solar | 150 | ER/NR | SPS | Roosevelt 230kV Substation
GEN-2019-009 | 02 NEBRASKA | DIS-18-2_19-1 | Solar | 100 | ER | OPPD | S1263 Brock 161kV substation
GEN-2019-011 | 05 SOUTHWEST | DIS-18-2_19-1 | Battery/Storage | 207 | ER/NR | SPS | Yoakum 345kV Substation
GEN-2019-012 | 04 SOUTHEAST | DIS-18-2_19-1 | Battery/Storage | 200 | ER/NR | OKGE | Woodward 345kV substation
GEN-2019-016 | 03 CENTRAL | DIS-18-2_19-1 | Solar | 200 | ER | EMDE | Dadeville 161kV Substation
GEN-2019-018 | 03 CENTRAL | DIS-18-2_19-1 | Thermal | 15.56 | ER/NR | MIDW | Saxman 115kV substation
GEN-2019-019 | 01 NORTH | DIS-18-2_19-1 | Thermal | 15.15 | ER/NR | BEPC | Siouxland 69kV
GEN-2019-021 | 05 SOUTHWEST | DIS-18-2_19-1 | Solar | 50 | ER/NR | SPS | Roosevelt 230kV Substation
GEN-2019-023 | 01 NORTH | DIS-18-2_19-1 | Wind | 110 | ER/NR | BEPC | WAPA-UGP Mingusville 230kV
GEN-2019-030 | 03 CENTRAL | DIS-18-2_19-1 | Wind | 252 | ER/NR | SUNC | Spearville to Clark County 345 kV line
GEN-2019-037 | 01 NORTH | DIS-18-2_19-1 | Solar | 150 | ER/NR | BEPC | Leland Olds 345kV substation
GEN-2019-039 | 02 NEBRASKA | DIS-18-2_19-1 | Solar | 174.5 | ER/NR | NPPD | Columbus Southeast-Rising City 115kV
GEN-2019-041 | 02 NEBRASKA | DIS-18-2_19-1 | Solar | 78 | ER/NR | NPPD | 115kV Monolith Substation
GEN-2019-044 | 03 CENTRAL | DIS-18-2_19-1 | Solar | 100 | ER | SUNC | North Fort Dodge 115kV Substation
GEN-2019-045 | 04 SOUTHEAST | DIS-18-2_19-1 | Solar | 155 | ER | OKGE | DeGrasse 138kV Substation
GEN-2019-053 | 03 CENTRAL | DIS-18-2_19-1 | Battery/Storage | 50 | ER/NR | SUNC | Great Bend-Spearville 230kV line
GEN-2019-054 | 03 CENTRAL | DIS-18-2_19-1 | Solar | 150 | ER/NR | SUNC | Great Bend- Circle 230kV line
GEN-2019-055 | 03 CENTRAL | DIS-18-2_19-1 | Solar | 150 | ER/NR | SUNC | Great Bend-Spearville 230kV line
GEN-2019-058 | 03 CENTRAL | DIS-18-2_19-1 | Solar | 150 | ER/NR | SUNC | Clark County 345kV substation
GEN-2019-063 | 03 CENTRAL | DIS-18-2_19-1 | Battery/Storage | 50 | ER/NR | SUNC | Clark County 345kV substation
GEN-2019-065 | 04 SOUTHEAST | DIS-18-2_19-1 | Battery/Storage | 180 | ER | AEPW | Overton-Northwest Henderson 138kV
GEN-2019-068 | 03 CENTRAL | DIS-18-2_19-1 | Battery/Storage | 50 | ER/NR | SUNC | Great Bend - Circle 230kV line
GEN-2020-003 | 03 CENTRAL | DIS-20-1 | Thermal | 58 | ER/NR | WERE | East Substation 69 kV
GEN-2020-007 | 03 CENTRAL | DIS-20-1 | Solar | 650 | ER/NR | KCPL | Evergy La Cygne to Wolf Creek 345kV Substation
GEN-2020-008 | 03 CENTRAL | DIS-20-1 | Solar | 250 | ER | SPS | Corporation Carpenter 345kV Substation
GEN-2020-010 | 04 SOUTHEAST | DIS-20-1 | Solar | 140 | ER/NR | WFEC | Seiling-Taloga Substations 138kV
GEN-2020-011 | 02 NEBRASKA | DIS-20-1 | Solar | 320 | ER/NR | NPPD | Axtell 345 kV Substation
GEN-2020-012 | 04 SOUTHEAST | DIS-20-1 | Solar | 113 | ER/NR | AEPW | Snyder – Altus Jct. 138kV
GEN-2020-013 | 02 NEBRASKA | DIS-20-1 | Solar | 215 | ER/NR | NPPD | Orleans-Holdrege Substation 115kV
GEN-2020-014 | 01 NORTH | DIS-20-1 | Thermal | 45 | ER/NR | WAPA | Lonesome Creek 115kV
GEN-2020-020 | 04 SOUTHEAST | DIS-20-1 | Solar | 201.6 | ER/NR | AEPW | Tap the 345 kV Northwest Texarkana - Valliant line
GEN-2020-025 | 02 NEBRASKA | DIS-20-1 | Thermal | 255 | ER | OPPD | Substation 1363; 161kV Substation
GEN-2020-028 | 02 NEBRASKA | DIS-20-1 | Thermal | 255 | ER | OPPD | Substation 1363; 161kV Substation
GEN-2020-031 | 02 NEBRASKA | DIS-20-1 | Thermal | 272.7 | ER | OPPD | Substation 1363; 161kV Substation
GEN-2020-038 | 02 NEBRASKA | DIS-20-1 | Thermal | 272.7 | ER | OPPD | Substation 3740; 345kV
GEN-2020-043 | 02 NEBRASKA | DIS-20-1 | Thermal | 56.52 | ER | OPPD | Between Substation 1209 and 1252; 161kV
GEN-2020-044 | 02 NEBRASKA | DIS-20-1 | Thermal | 56.52 | ER | OPPD | Between Substation 1209 and 1252; 161kV
GEN-2020-045 | 02 NEBRASKA | DIS-20-1 | Thermal | 56.52 | ER | OPPD | Between Substation 1209 and 1252; 161kV
GEN-2020-054 | 04 SOUTHEAST | DIS-20-1 | Solar | 298 | ER/NR | AEPW | Lydia 345 kV Station
GEN-2020-057 | 03 CENTRAL | DIS-20-1 | Battery/Storage | 424.5 | ER/NR | KCPL | Atlantic 345 kV Substation
GEN-2020-058 | 03 CENTRAL | DIS-20-1 | Solar | 424.5 | ER/NR | KCPL | Atlantic 345 kV Substation
GEN-2020-060 | 05 SOUTHWEST | DIS-20-1 | Battery/Storage | 200 | ER | SPS | Lubbock East Substation 230 kV
GEN-2020-061 | 03 CENTRAL | DIS-20-1 | Thermal | 29 | ER/NR | KCPL | Pleasant Hill 345/161/69 kV Substation
GEN-2020-064 | 03 CENTRAL | DIS-20-1 | Thermal | 64 | ER/NR | EMDE | 4544 Stateline CC 161kV Substation
GEN-2020-065 | 05 SOUTHWEST | DIS-20-1 | Thermal | 1003 | ER | SPS | Hobbs-Andrews 345 kV Line
GEN-2020-067 | 05 SOUTHWEST | DIS-20-1 | Wind | 352.5 | ER | SPS | Tuco to Yoakum 345kV line
GEN-2020-069 | 02 NEBRASKA | DIS-20-1 | Wind | 52.85 | ER/NR | NPPD | Cody to Valentine 115kV line
GEN-2020-072 | 03 CENTRAL | DIS-20-1 | Solar | 150 | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV line
GEN-2020-073 | 03 CENTRAL | DIS-20-1 | Solar | 150 | ER/NR | KCPL | SE Ottawa to Pleasant Valley 161kV
GEN-2020-078 | 02 NEBRASKA | DIS-20-1 | Solar | 100 | ER/NR | OPPD | Substation 1226 to Substation 1237, 161kV Tap
GEN-2020-079 | 03 CENTRAL | DIS-20-1 | Solar | 225 | ER/NR | EMDE | Riverton-Neosho 161kV line
GEN-2020-081 | 04 SOUTHEAST | DIS-20-1 | Battery/Storage | 200 | ER/NR | AEPW | Tenaska Switching Substation 345kV
GEN-2020-083 | 01 NORTH | DIS-20-1 | Solar | 74.5 | ER/NR | WAPA | Fairview 115kV Substation
GEN-2020-084 | 02 NEBRASKA | DIS-20-1 | Solar | 350 | ER/NR | OPPD | Raun - Fort Calhoun 345 kV
GEN-2020-087 | 04 SOUTHEAST | DIS-20-1 | Solar | 500 | ER/NR | AEPW | Cimmarron to Lawton 345 kV Line
GEN-2020-088 | 03 CENTRAL | DIS-20-1 | Solar | 150 | ER/NR | EMDE | La Russell 161 kV Substation
GEN-2020-090 | 03 CENTRAL | DIS-20-1 | Battery/Storage | 204.3 | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Substation
GEN-2020-091 | 01 NORTH | DIS-20-1 | Solar | 150 | ER/NR | WAPA | Patent Gate Substation 345 kV
GEN-2020-092 | 04 SOUTHEAST | DIS-20-1 | Solar | 100 | ER/NR | AEPW | Pryor Junction - Midwest Carbide 138kV line
GEN-2020-094 | 02 NEBRASKA | DIS-20-1 | Solar | 250 | ER/NR | OPPD | Neb. City - 103rd & Rokeby 345 kV
GEN-2021-001 | 04 SOUTHEAST | DIS-21-1 | Battery/Storage | 100 | ER/NR | OKGE | 138kV Brown Substation
GEN-2021-005 | 03 CENTRAL | DIS-21-1 | Battery/Storage | 350 | ER/NR | WERE | Summit 345 kV substation in Saline County, KS
GEN-2021-006 | 03 CENTRAL | DIS-21-1 | Battery/Storage | 300 | ER/NR | WERE | Neosho 345kV substation in Labette County, KS
GEN-2021-008 | 01 NORTH | DIS-21-1 | Solar | 200 | ER/NR | BEPC | 345kV Bus at BEPC Patent Gate Substation, McKenzie County, ND
GEN-2021-016 | 04 SOUTHEAST | DIS-21-1 | Wind | 250 | ER | AEPW | Sunnyside-Johnston 345 kV
GEN-2021-017 | 03 CENTRAL | DIS-21-1 | Wind | 37.5 | ER | SUNC | Elm Creek 345 kV interconnection substation
GEN-2021-018 | 04 SOUTHEAST | DIS-21-1 | Solar | 231 | ER | OKGE | Sooner 345 kV
GEN-2021-019 | 04 SOUTHEAST | DIS-21-1 | Battery/Storage | 74.9 | ER/NR | OKGE | Sooner 345 kV
GEN-2021-021 | 03 CENTRAL | DIS-21-1 | Wind | 150 | ER | SPS | Carpenter 345 kV Substation
GEN-2021-023 | 04 SOUTHEAST | DIS-21-1 | Solar | 306.18 | ER | WERE | Wild Plains 345kV Substation
GEN-2021-025 | 04 SOUTHEAST | DIS-21-1 | Wind | 203.04 | ER | WFEC | Western Farmers 138kV Mooreland Substation
GEN-2021-027 | 02 NEBRASKA | DIS-21-1 | Solar | 102.06 | ER | NPPD | Olive Creek 115 kV Substation
GEN-2021-029 | 03 CENTRAL | DIS-21-1 | Battery/Storage | 253.8 | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line
GEN-2021-030 | 03 CENTRAL | DIS-21-1 | Solar | 510.3 | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line
GEN-2021-033 | 04 SOUTHEAST | DIS-21-1 | Solar | 204.12 | ER | OKGE | Branch 161kV Substation
GEN-2021-034 | 02 NEBRASKA | DIS-21-1 | Solar | 113 | ER | LES | Rokeby 115 kV Substation
GEN-2021-035 | 03 CENTRAL | DIS-21-1 | Solar | 113 | ER | SUNC | Tap Sunflower Santana 115kV Transmission Line
GEN-2021-036 | 04 SOUTHEAST | DIS-21-1 | Solar | 204.12 | ER/NR | AEPW | Craig to Patterson 138 kV Transmission Line
GEN-2021-038 | 04 SOUTHEAST | DIS-21-1 | Battery/Storage | 200 | ER/NR | AEPW | Welsh 345kV Substation
GEN-2021-039 | 02 NEBRASKA | DIS-21-1 | Battery/Storage | 100 | ER | OPPD | New 161kV substation looping in OPPD 161kV lines S1211 to S1220 and S1211 to S1299
GEN-2021-040 | 02 NEBRASKA | DIS-21-1 | Battery/Storage | 200 | ER | OPPD | OPPD District, Cass County Power Plant Substation, 345kV Bus
GEN-2021-041 | 04 SOUTHEAST | DIS-21-1 | Battery/Storage | 100 | ER/NR | OKGE | Mustang 138kV Substation
GEN-2021-042 | 03 CENTRAL | DIS-21-1 | Battery/Storage | 50 | ER/NR | KCPL | Independence Power & Light, Blue Valley Substation, 161kV Bus
GEN-2021-043 | 02 NEBRASKA | DIS-21-1 | Battery/Storage | 250 | ER | LES | 8000 SW 12th (Rokeby) Station, 115kV Bus
GEN-2021-047 | 04 SOUTHEAST | DIS-21-1 | Solar | 250 | ER | GRDA | Tulsa (Bus #509852) - Igloo (Bus #513596) 345kV line
GEN-2021-048 | 02 NEBRASKA | DIS-21-1 | Battery/Storage | 75 | ER/NR | LES | Wagener 115kV Substation
GEN-2021-049 | 02 NEBRASKA | DIS-21-1 | Solar | 225 | ER/NR | LES | Wagener 115kV Substation
GEN-2021-052 | 04 SOUTHEAST | DIS-21-1 | Battery/Storage | 75 | ER | OKGE | Pecan Creek 345kV substation
GEN-2021-053 | 04 SOUTHEAST | DIS-21-1 | Solar | 300 | ER | OKGE | Pecan Creek 345 kV Substation
GEN-2021-056 | 03 CENTRAL | DIS-21-1 | Wind | 300 | ER | WERE | Viola 345kV Substation
GEN-2021-057 | 02 NEBRASKA | DIS-21-1 | Wind | 300 | ER | NPPD | Antelope 345kV substation
GEN-2021-063 | 04 SOUTHEAST | DIS-21-1 | Solar | 155 | ER/NR | AEPW | Craig JCT 138kV
GEN-2021-064 | 04 SOUTHEAST | DIS-21-1 | Solar | 100 | ER/NR | AEPW | Carnegie South 138kV
GEN-2021-068 | 03 CENTRAL | DIS-21-1 | Wind | 249.6 | ER | SUNC | SUNC Spearville - Holcomb 345kV
GEN-2021-069 | 03 CENTRAL | DIS-21-1 | Wind | 249.6 | ER | SUNC | SUNC Spearville - Holcomb 345kV
GEN-2021-070 | 03 CENTRAL | DIS-21-1 | Wind | 504 | ER | SUNC | SUNC Spearville - Holcomb 345kV
GEN-2021-076 | 03 CENTRAL | DIS-21-1 | Solar | 113 | ER/NR | MIDW | ITC Post Rock 345 kV Substation
GEN-2021-077 | 03 CENTRAL | DIS-21-1 | Solar | 95 | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV
GEN-2021-088 | 04 SOUTHEAST | DIS-21-1 | Battery/Storage | 100 | ER/NR | OKGE | Cedar Lane - Canadian 138 kV Transmission Line
GEN-2021-090 | 05 SOUTHWEST | DIS-21-1 | Solar | 400 | ER/NR | SPS | Yoakum 345kV Substation
GEN-2021-096 | 03 CENTRAL | DIS-21-1 | Solar | 500 | ER/NR | WERE | Wolf Creek - Benton 345 kV
GEN-2021-101 | 03 CENTRAL | DIS-21-1 | Solar | 159 | ER/NR | WERE | Evergy's Midland Substation 115kV bus
GEN-2021-103 | 03 CENTRAL | DIS-21-1 | Battery/Storage | 150 | ER/NR | WERE | Evergy's Atlantic Substation115kV bus
GEN-2021-107 | 03 CENTRAL | DIS-21-1 | Solar | 201.6 | ER | WERE | Evergy 345kV Jeffrey Energy Center
GEN-2021-108 | 02 NEBRASKA | DIS-21-1 | Solar | 182.25 | ER/NR | OPPD | OPPD 345KV Cass County Substation
GEN-2022-004 | 03 CENTRAL | DIS-22-1 | Solar | 33 | ER/NR | WERE | Murray Gill 138 kV Substation
GEN-2022-006 | 03 CENTRAL | DIS-22-1 | Solar | 200 | ER/NR | WERE | Neosho - N345 161 kV Substation
GEN-2022-007 | 03 CENTRAL | DIS-22-1 | Solar | 135 | ER/NR | WERE | Lang - Reading 115 kV Transmission Line
GEN-2022-009 | 01 NORTH | DIS-22-1 | Thermal | 125 | ER | BEPC | Judson Substation 345 kV
GEN-2022-010 | 01 NORTH | DIS-22-1 | Thermal | 250 | ER | BEPC | Judson Substation 345 kV
GEN-2022-012 | 04 SOUTHEAST | DIS-22-1 | Battery/Storage | 100 | ER/NR | OKGE | Woodward 345 kV Substation
GEN-2022-013 | 03 CENTRAL | DIS-22-1 | Solar | 300 | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line
GEN-2022-015 | 03 CENTRAL | DIS-22-1 | Solar | 270 | ER/NR | SUNC | Tap of Mingo - Red Willow 345 kV Line
GEN-2022-016 | 04 SOUTHEAST | DIS-22-1 | Solar | 288 | ER/NR | OKGE | Woodward 345kV Substation
GEN-2022-017 | 04 SOUTHEAST | DIS-22-1 | Battery/Storage | 150 | ER/NR | OKGE | Woodward 345kV Substation
GEN-2022-024 | 03 CENTRAL | DIS-22-1 | Battery/Storage | 200 | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line
GEN-2022-038 | 04 SOUTHEAST | DIS-22-1 | Solar | 180 | ER | AEPW | Longwood to Scottville 138 kV line
GEN-2022-054 | 03 CENTRAL | DIS-22-1 | Solar | 200 | ER | WERE | Wolf Creek - Blackberry 345 kV Tap
GEN-2022-055 | 04 SOUTHEAST | DIS-22-1 | Solar | 200 | ER | WFEC | Sunshine North to Anadarko 138 kV
GEN-2022-065 | 03 CENTRAL | DIS-22-1 | Solar | 145 | ER/NR | SUNC | tap on Arthur Mullergreen-Spearville 230 kV line
GEN-2022-071 | 04 SOUTHEAST | DIS-22-1 | Solar | 90.824 | ER/NR | AEPW | Talawanda to Canadian River 138 kV Line Tap
GEN-2022-073 | 03 CENTRAL | DIS-22-1 | Battery/Storage | 300 | ER/NR | KCPL | Nashua-Smithville 161kV
GEN-2022-075 | 03 CENTRAL | DIS-22-1 | Solar | 175 | ER/NR | MIDW | Tap on the Spearville - Post Rock 345kV line
GEN-2022-083 | 01 NORTH | DIS-22-1 | Thermal | 250 | ER | BEPC | Judson Substation 345 kV
GEN-2022-098 | 04 SOUTHEAST | DIS-22-1 | Solar | 200 | ER/NR | OKGE | Bison 345kV Substation
GEN-2022-100 | 03 CENTRAL | DIS-22-1 | Solar | 80 | ER/NR | KCPL | Overton - Sedalia East 161 kV Substation
GEN-2022-102 | 03 CENTRAL | DIS-22-1 | Battery/Storage | 100 | ER/NR | KCPL | Liberty West 161 kV
GEN-2022-104 | 04 SOUTHEAST | DIS-22-1 | Solar | 113.078 | ER/NR | WFEC | Brown - South Coleman Junction 138kV line
GEN-2022-111 | 04 SOUTHEAST | DIS-22-1 | Solar | 150 | ER/NR | AEPW | Wilkes 345 kV Substation
GEN-2022-130 | 04 SOUTHEAST | DIS-22-1 | Battery/Storage | 200 | ER/NR | OKGE | Battlefield BESS 161kV
GEN-2022-136 | 04 SOUTHEAST | DIS-22-1 | Battery/Storage | 180 | ER | WFEC | Colbert 138 kV Substation
GEN-2022-139 | 04 SOUTHEAST | DIS-22-1 | Battery/Storage | 300 | ER | AEPW | Pirkey 345kV Substation
GEN-2022-142 | 03 CENTRAL | DIS-22-1 | Battery/Storage | 200 | ER | KCPL | Shoal Creek 161 kV Substation
GEN-2022-143 | 04 SOUTHEAST | DIS-22-1 | Battery/Storage | 200 | ER | OKGE | Caney Creek 138 kV Substation
GEN-2022-144 | 03 CENTRAL | DIS-22-1 | Battery/Storage | 200 | ER | KCPL | Blue Mills BESS 161kV Substation
GEN-2022-145 | 04 SOUTHEAST | DIS-22-1 | Battery/Storage | 180 | ER | AEPW | Weatherford Jct. to Hinton 138 kV line
GEN-2022-147 | 05 SOUTHWEST | DIS-22-1 | Thermal | 203 | ER | SPS | Tuco 345kV
GEN-2022-154 | 04 SOUTHEAST | DIS-22-1 | Battery/Storage | 100 | ER | WFEC | Canadian Switch 138 kV Substation
GEN-2022-155 | 04 SOUTHEAST | DIS-22-1 | Battery/Storage | 200 | ER | OKGE | Horseshoe Lake 138 kV Substation
GEN-2022-156 | 04 SOUTHEAST | DIS-22-1 | Battery/Storage | 100 | ER | GRDA | Silver City 138 kV Substation
GEN-2022-161 | 03 CENTRAL | DIS-22-1 | Wind | 360 | ER | WERE | Burns 345kV Substation
GEN-2022-176 | 04 SOUTHEAST | DIS-22-1 | Wind | 215 | ER/NR | AEPW | Northeastern - Delaware 345 kV transmission line
GEN-2022-214 | 03 CENTRAL | DIS-22-1 | Solar | 239 | ER | WERE | Gill - Viola 138 kV Line Break
GEN-2022-235 | 04 SOUTHEAST | DIS-22-1 | Battery/Storage | 150 | ER/NR | WFEC | El Reno SW 138 kV
GEN-2022-238 | 04 SOUTHEAST | DIS-22-1 | Battery/Storage | 150 | ER/NR | OKGE | Maud 138 kV substation
GEN-2023-015 | 03 CENTRAL | DIS-23-1 | Solar | 330 | ER/NR | SPS | Finney-Carpenter 345 KV line
GEN-2023-033 | 03 CENTRAL | DIS-23-1 | Storage | 200 | ER/NR | KCPL | Liberty South 161 kV Substation
GEN-2023-034 | 03 CENTRAL | DIS-23-1 | Solar | 130 | ER/NR | WERE | Clear Water - Waco 138 kV line
GEN-2023-035 | 04 SOUTHEAST | DIS-23-1 | Solar | 200 | ER/NR | WFEC | Cleveland - Amber Tap 138 kV Line
GEN-2023-037 | 03 CENTRAL | DIS-23-1 | Storage | 200 | ER/NR | KACY | Nearman 161 kV Substation
GEN-2023-038 | 04 SOUTHEAST | DIS-23-1 | Solar | 200 | ER/NR | OKGE | Lula 138 kV Substation
GEN-2023-055 | 04 SOUTHEAST | DIS-23-1 | Storage | 100 | ER/NR | GRDA | Kerr Grove 161 kV
GEN-2023-057 | 04 SOUTHEAST | DIS-23-1 | Storage | 150 | ER/NR | GRDA | Pawnee Switch 138 kV
GEN-2023-059 | 04 SOUTHEAST | DIS-23-1 | Solar | 200 | ER/NR | AEPW | Tap Rockhill to South Shreveport 138 kV line
GEN-2023-061 | 03 CENTRAL | DIS-23-1 | Storage | 100 | ER/NR | SWPA | Carthage 161 kV Substation
GEN-2023-063 | 04 SOUTHEAST | DIS-23-1 | Solar | 135 | ER/NR | AEPW | Catoosa - Owasso 88th 138 kV line
GEN-2023-064 | 04 SOUTHEAST | DIS-23-1 | Solar | 200 | ER/NR | SWPA | RS Kerr-Stigler 161 kV line
GEN-2023-069 | 04 SOUTHEAST | DIS-23-1 | Solar | 100 | ER/NR | WFEC | Tupelo - Atoka 138 kV Line
GEN-2023-077 | 02 NEBRASKA | DIS-23-1 | Thermal | 255 | ER | OPPD | Substation 3740 345 kV
GEN-2023-078 | 02 NEBRASKA | DIS-23-1 | Thermal | 255 | ER | OPPD | Substation 3740 345 kV
GEN-2023-079 | 02 NEBRASKA | DIS-23-1 | Thermal | 272.7 | ER | OPPD | Substation 3740 345 kV
GEN-2023-088 | 04 SOUTHEAST | DIS-23-1 | Wind | 117 | ER/NR | WFEC | Pharaoh 138 kV Substation
GEN-2023-092 | 04 SOUTHEAST | DIS-23-1 | Solar | 125 | ER/NR | WFEC | Unger - Frogville 138 kV line
GEN-2023-099 | 03 CENTRAL | DIS-23-1 | Solar | 300 | ER | WERE | Jeffery Energy Center 345 kV Substation
GEN-2023-102 | 04 SOUTHEAST | DIS-23-1 | Solar | 475 | ER/NR | OKGE | Degrasse 345 kV Substation
GEN-2023-104 | 04 SOUTHEAST | DIS-23-1 | Solar | 100 | ER/NR | WFEC | Mooreland - Noel 138 kV Line
GEN-2023-107 | 03 CENTRAL | DIS-23-1 | Wind | 300 | ER | SUNC | Setab 345 kV
GEN-2023-120 | 05 SOUTHWEST | DIS-23-1 | Solar | 130 | ER | SPS | Kress 115 kV Substation
GEN-2023-132 | 04 SOUTHEAST | DIS-23-1 | Solar | 150 | ER/NR | SWPA | Jonesboro - Independence 161 kV
GEN-2023-135 | 04 SOUTHEAST | DIS-23-1 | Solar | 52 | ER/NR | AEPW | Lydia 345kV substation
GEN-2023-153 | 02 NEBRASKA | DIS-23-1 | Solar | 120 | ER/NR | NPPD | Grant 115 kV Substation
GEN-2023-161 | 04 SOUTHEAST | DIS-23-1 | Storage | 74.9 | ER/NR | OKGE | Roman Nose 138 kV Substation
GEN-2023-170 | 03 CENTRAL | DIS-23-1 | Storage | 150 | ER | KCPL | Salisbury 161 kV Substation
GEN-2023-171 | 03 CENTRAL | DIS-23-1 | Storage | 150 | ER/NR | INDN | Sub M 161 kV Substation
GEN-2023-172 | 03 CENTRAL | DIS-23-1 | Wind | 200 | ER/NR | SUNC | Holcomb 345 kV
GEN-2023-173 | 03 CENTRAL | DIS-23-1 | Wind | 100 | ER/NR | SUNC | Holcomb 345 kV
GEN-2023-177 | 04 SOUTHEAST | DIS-23-1 | Solar | 200 | ER/NR | OKGE | Paoli - Seminole 138 kV line tap
GEN-2023-193 | 04 SOUTHEAST | DIS-23-1 | Solar | 175 | ER/NR | AEPW | Pirkey - Whitney 138 kV Line
GEN-2023-199 | 02 NEBRASKA | DIS-23-1 | Solar | 250 | ER/NR | NPPD | Twin Church 230 kV Substation
GEN-2023-204 | 04 SOUTHEAST | DIS-23-1 | Thermal | 914.6 | ER | AEPW | Welsh-Lydia 345kV Line
GEN-2023-205 | 04 SOUTHEAST | DIS-23-1 | Solar | 180 | ER/NR | AEPW | McAlester City - Weleetka 138 kV line
GEN-2023-206 | 04 SOUTHEAST | DIS-23-1 | Storage | 50 | ER/NR | OKGE | Battlefield BESS 161 kV Substation
GEN-2023-210 | 04 SOUTHEAST | DIS-23-1 | Solar | 191 | ER/NR | WFEC | Prague - Chernicky 138 kV Line
GEN-2023-220 | 03 CENTRAL | DIS-23-1 | Solar | 250 | ER/NR | WERE | Emporia Energy Center - Swissvale 345 kV Line
GEN-2023-221 | 03 CENTRAL | DIS-23-1 | Solar | 250 | ER/NR | WERE | Emporia Energy Center - Swissvale 345 kV Line
GEN-2023-222 | 02 NEBRASKA | DIS-23-1 | Thermal | 478 | ER/NR | NPPD | New Beatrice Power Station 345 kV
GEN-2023-223 | 02 NEBRASKA | DIS-23-1 | Thermal | 239 | ER/NR | NPPD | New Beatrice Power Station 345 kV
GEN-2023-224 | 02 NEBRASKA | DIS-23-1 | Thermal | 478 | ER | NPPD | Olive Creek 345 kV Substation
GEN-2023-225 | 02 NEBRASKA | DIS-23-1 | Thermal | 217 | ER | NPPD | Olive Creek 345 kV Substation
GEN-2023-229 | 04 SOUTHEAST | DIS-23-1 | Wind | 230 | ER/NR | AEPW | Southwestern Power Station 138 kV Substation (SWS4)
GEN-2023-230 | 04 SOUTHEAST | DIS-23-1 | Solar | 150 | ER/NR | WAPA | Red Pointe 138 kV Substation
GEN-2023-241 | 04 SOUTHEAST | DIS-23-1 | Solar | 93 | ER | AEPW | Winnsboro 138 kV Substation
IR24 | 02 NEBRASKA | DIS-17-2-PQ | Wind | 57 | ER/NR | ALTW
IR32 | 02 NEBRASKA | DIS-17-2-PQ | Wind | 56 | ER/NR | ALTW
J1846 | 01 NORTH | DIS-22-1-PQ | Battery/Storage | 200 | ER/NR | XEL
J1867 | 04 SOUTHEAST | DIS-22-1-PQ | Wind | 200 | ER/NR | ALTW
J1889 | 02 NEBRASKA | DIS-22-1-PQ | Solar | 60 | ER/NR | ALTW
J1898 | 01 NORTH | DIS-22-1-PQ | Battery/Storage | 200 | ER/NR | XEL
J1998 | 02 NEBRASKA | DIS-22-1-PQ | Wind | 66 | ER/NR | ALTW
J2027 | 01 NORTH | DIS-22-1-PQ | Solar | 150 | ER/NR | GRE
J2031 | 02 NEBRASKA | DIS-22-1-PQ | Wind | 100 | ER/NR | ALTW
J2053 | 01 NORTH | DIS-22-1-PQ | Wind | 151.47 | ER/NR | XEL
J2068 | 01 NORTH | DIS-22-1-PQ | Solar | 75 | ER/NR | XEL
J2078 | 02 NEBRASKA | DIS-22-1-PQ | Solar | 200 | ER/NR | ALTW
J2080 | 01 NORTH | DIS-22-1-PQ | Wind | 200 | ER/NR | MP
J2087 | 01 NORTH | DIS-22-1-PQ | Solar | 125 | ER/NR | XEL
J2097 | 01 NORTH | DIS-22-1-PQ | Wind | 100 | ER/NR | MP
J2104 | 01 NORTH | DIS-22-1-PQ | Wind | 230.01 | ER/NR | XEL
J2120 | 02 NEBRASKA | DIS-22-1-PQ | Battery/Storage | 100 | ER/NR | ALTW
J2122 | 02 NEBRASKA | DIS-22-1-PQ | Wind | 33 | ER/NR | ALTW
J2157 | 01 NORTH | DIS-22-1-PQ | Wind | 100 | ER/NR | MP
J2219 | 01 NORTH | DIS-22-1-PQ | Battery/Storage | 180 | ER/NR | DPC
J2227 | 01 NORTH | DIS-22-1-PQ | Solar | 80.1 | ER/NR | DPC
J2250 | 01 NORTH | DIS-22-1-PQ | Wind | 200 | ER/NR | OTP
J2268 | 02 NEBRASKA | DIS-22-1-PQ | Solar | 370 | ER/NR | ALTW
J2276 | 01 NORTH | DIS-22-1-PQ | Solar | 39.5 | ER/NR | OTP
J2309 | 01 NORTH | DIS-22-1-PQ | Solar | 100 | ER/NR | XEL
MPC00100 | 01 NORTH | DIS-15-2-PQ | Wind | 99 | ER | OTP
MPC00200 | 01 NORTH | DIS-15-2-PQ | Wind | 60 | ER | OTP
MPC00300 | 01 NORTH | DIS-15-2-PQ | Wind | 40.5 | ER | OTP
MPC00500 | 01 NORTH | DIS-15-2-PQ | Wind | 327.9 | ER/NR | OTP
MPC00500GRE | 01 NORTH | DIS-15-2-PQ | Wind | 51 | ER/NR | GRE
MPC01200 | 01 NORTH | DIS-15-2-PQ | Wind | 49.5 | ER | OTP
MPC01300 | 01 NORTH | DIS-15-2-PQ | Coal | 493 | ER/NR | OTP
MPC02100 | 01 NORTH | DIS-15-2-PQ | Wind | 99.25 | ER | OTP
MPC03600 | 01 NORTH | DIS-18-1-PQ | Solar | 167.2 | ER | OTP
MPC03700 | 01 NORTH | DIS-18-1-PQ | Solar | 127.9 | ER | OTP
MPC03800 | 01 NORTH | DIS-18-1-PQ | Wind | 230 | ER/NR | OTP
MPC03900 | 01 NORTH | DIS-18-1-PQ | Wind | 140 | ER/NR | OTP
MPC04000 | 01 NORTH | DIS-18-1-PQ | Wind | 284 | ER/NR | OTP
MPC04500 | 01 NORTH | DIS-22-PQ | Wind | 250 | ER/NR | OTP
NPPDSpringview | 02 NEBRASKA | DIS-17-1-PQ | Wind | 3 | ER | NPPD
PQOKGEMustang | 04 SOUTHEAST | DIS-16-1 | CT | 287 | ER | OKGE
SPSLeaCounty | 05 SOUTHWEST | DIS-17-1-PQ | Solar | 5.5 | ER | SPS
SWPANixaSolar | 03 CENTRAL | DIS-17-1-PQ | Solar | 7.9 | ER | SWPA
WAPAMPSWind | 01 NORTH | DIS-17-1-PQ | Wind | 1.5 | ER | WAPA
WAPATitanWind | 01 NORTH | DIS-17-1-PQ | Wind | 25 | ER | WAPA
FORT DODGE 4_GEN-2023-SR28 | 03 CENTRAL | Surplus | Solar | 175 | ER | SUNC
GEN-2001-014 | 04 SOUTHEAST | PQ | Wind | 94.5 | ER | WFEC | Ft Supply 138kV
GEN-2001-026 | 04 SOUTHEAST | PQ | Wind | 74.25 | ER | WFEC | Washita 138kV
GEN-2001-030 | 03 CENTRAL | PQ | CT | 50 | ER | EMDE | LaRussell Energy Center 161kV
GEN-2001-037_GEN-2023-SR16 | 04 SOUTHEAST | PQ | Wind | 102 | ER | OKGE
GEN-2001-039A | 03 CENTRAL | PQ | Wind | 104 | ER | SUNC | Shooting Star Tap 115kV
GEN-2001-039M | 03 CENTRAL | PQ | Wind | 100 | ER | SUNC | Central Plains Tap 115kV
GEN-2001-040 | 03 CENTRAL | PQ | CT | 50 | ER | EMDE | LaRussell Energy Center 161kV
GEN-2002-005 | 04 SOUTHEAST | PQ | Wind | 123 | ER | WFEC | Red Hills Tap 138kV
GEN-2002-009 | 05 SOUTHWEST | PQ | Wind | 67.2 | ER | SPS | Hansford 115kV
GEN-2002-022 | 05 SOUTHWEST | PQ | Wind | 239.2 | ER | SPS | Bushland 230kV
GEN-2002-025A_GEN-2004-014 | 03 CENTRAL | PQ | Wind | 252.5 | ER | SUNC
GEN-2003-004_GEN-2004-023_GEN-2005-003 | 04 SOUTHEAST | PQ | Wind | 151.2 | ER | WFEC
GEN-2003-005_GEN-2011-037 | 04 SOUTHEAST | PQ | Wind | 105.6 | ER | WFEC
GEN-2003-006A | 03 CENTRAL | PQ | Wind | 201 | ER | SUNC | Elm Creek 230kV
GEN-2003-019 | 03 CENTRAL | PQ | Wind | 249.3 | ER | MIDW | Smoky Hills Tap 230kV
GEN-2003-020_GEN-2016-070 | 05 SOUTHWEST | PQ | Wind | 165.3 | ER | SPS
GEN-2003-021N_GEN-2023-SR1 | 02 NEBRASKA | PQ | Wind | 75 | ER/NR | NPPD
GEN-2004-015_GEN-2012-034 | 05 SOUTHWEST | PQ | CT | 157 | ER | SPS
GEN-2004-023N | 02 NEBRASKA | PQ | Coal | 75 | ER | NPPD | Columbus Co 115kV
GEN-2005-008 | 04 SOUTHEAST | PQ | Wind | 120 | ER | OKGE | Woodward 138kV
GEN-2005-012 | 03 CENTRAL | PQ | Wind | 248.4 | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV
GEN-2005-013 | 03 CENTRAL | PQ | Wind | 199.8 | ER | WERE | Caney River 345kV
GEN-2006-002 | 04 SOUTHEAST | PQ | Wind | 100.8 | ER | AEPW | Sweetwater 230kV
GEN-2006-008 | 04 SOUTHEAST | PQ | Thermal | 550 | ER | AEPW | Arsenal Hill 138kV
GEN-2006-018 | 05 SOUTHWEST | PQ | CT | 168.1 | ER | SPS | TUCO 230kV
GEN-2006-020N | 02 NEBRASKA | PQ | Wind | 42 | ER | NPPD | Bloomfield 115kV
GEN-2006-020S | 05 SOUTHWEST | PQ | Wind | 20 | ER | SPS | DWS Frisco 115kV
GEN-2006-021 | 03 CENTRAL | PQ | Wind | 94 | ER | SUNC | Flat Ridge Tap 138kV
GEN-2006-024S | 04 SOUTHEAST | PQ | Wind | 18.9 | ER | WFEC | Buffalo Bear Tap 69kV
GEN-2006-035 | 04 SOUTHEAST | PQ | Wind | 132 | ER | AEPW | Sweetwater 230kV
GEN-2006-037N1 | 02 NEBRASKA | PQ | Wind | 75 | ER | NPPD | Broken Bow 115kV
GEN-2006-038N005 | 02 NEBRASKA | PQ | Wind | 80 | ER | NPPD | Broken Bow 115kV
GEN-2006-038N019 | 02 NEBRASKA | PQ | Wind | 80 | ER | NPPD | Petersburg North 115kV
GEN-2006-043 | 04 SOUTHEAST | PQ | Wind | 99 | ER | AEPW | Sweetwater 230kV
GEN-2006-044 | 05 SOUTHWEST | PQ | Wind | 370 | ER | SPS | Hitchland 345kV
GEN-2006-046 | 04 SOUTHEAST | PQ | Wind | 129.6 | ER | OKGE | Dewey 138kV
GEN-2007-011N08 | 02 NEBRASKA | PQ | Wind | 81 | ER | NPPD | Bloomfield 115kV
GEN-2007-021 | 04 SOUTHEAST | ICS1 | Wind | 198.9 | ER | OKGE | Tatonga 345kV
GEN-2007-040 | 03 CENTRAL | PQ | Wind | 131.1 | ER | SUNC | Buckner 345kV
GEN-2007-044_GEN-2014-003_GEN-2023-SR5 | 04 SOUTHEAST | ICS1 | Wind | 315 | ER | OKGE
GEN-2007-046 | 05 SOUTHWEST | ICS1 | Wind | 200 | ER | SPS | Hitchland 115kV
GEN-2007-050 | 04 SOUTHEAST | ICS1 | Wind | 151.8 | ER | OKGE | Woodward EHV 138kV
GEN-2007-052 | 04 SOUTHEAST | PQ | Gas | 150 | ER | WFEC | Anadarko 138kV
GEN-2007-062 | 04 SOUTHEAST | PQ | Wind | 424 | ER | OKGE | Woodward EHV 345kV
GEN-2008-003 | 04 SOUTHEAST | PQ | Wind | 101.2 | ER | OKGE | Woodward EHV 138kV
GEN-2008-013 | 04 SOUTHEAST | ICS1 | Wind | 300 | ER | OKGE | Hunter 345kV
GEN-2008-018 | 03 CENTRAL | ICS1 | Wind | 250 | ER | SPS | Finney 345kV
GEN-2008-044_GEN-2010-011 | 04 SOUTHEAST | PQ | Wind | 227.5 | ER | OKGE
GEN-2008-047 | 05 SOUTHWEST | PQ | Wind | 263.13 | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV
GEN-2008-086N02 | 02 NEBRASKA | PQ | Wind | 201 | ER | OPPD | Meadow Grove 230kV
GEN-2008-092 | 03 CENTRAL | PQ | Wind | 200.5 | ER | MIDW | Post Rock 230kV
GEN-2008-119O | 02 NEBRASKA | PQ | Wind | 60 | ER | OPPD | S1399 161kV
GEN-2008-124 | 03 CENTRAL | PQ | Wind | 200.1 | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV
GEN-2008-129 | 03 CENTRAL | PQ | CT | 72 | ER | KCPL | Pleasant Hill 161kV
GEN-2009-020_GEN-2014-025 | 03 CENTRAL | PQ | Wind | 50.72 | ER | MIDW
GEN-2010-001 | 05 SOUTHWEST | PQ | Wind | 300 | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV
GEN-2010-009 | 03 CENTRAL | PQ | Wind | 165.6 | ER | SUNC | Buckner 345kV
GEN-2010-014_GEN-2011-022_GEN-2023-SR8 | 05 SOUTHWEST | PQ | Wind | 657.8 | ER | SPS
GEN-2010-040 | 04 SOUTHEAST | PQ | Wind | 300 | ER | OKGE | Cimarron 345kV
GEN-2010-051 | 02 NEBRASKA | PQ | Wind | 200 | ER | NPPD | Wakefield 230kV
GEN-2022-GR1 | 04 SOUTHEAST | Replacement | Thermal | 513 | ER | AEPW | Pirkey 138 kV
GEN-2023-GR1 | 04 SOUTHEAST | Replacement | Thermal | 97.488 | ER | WFEC | Anadarko Power Plant 69 kV
GEN-2023-GR2 | 04 SOUTHEAST | Replacement | Thermal | 94.242 | ER | OKGE | Tinker Air Force Base 138kV
GEN-2023-GR3 | 05 SOUTHWEST | Replacement | Wind | 80 | ER/NR | SPS | Norton 115 kV
GEN-2023-GR4 | 05 SOUTHWEST | Replacement | Solar | 72 | ER | SPS | Cunningham 115kV
GEN-2023-GR5 | 05 SOUTHWEST | Replacement | Solar | 150 | ER | SPS | Plant X 115 kV Substation
HAWCT_GEN-2021-SR9 | 03 CENTRAL | Surplus | Solar | 96.75 | ER/NR | KCPL
J476 | 03 CENTRAL | ICS1 | Wind | 246 | ER/NR | MEC
J569 | 01 NORTH | ICS1 | Wind | 100 | ER/NR | XEL
LlanoEstacadoWhiteDeer | 05 SOUTHWEST | PQ | Wind | 80 | ER | SPS
NPPDColumbusHydro | 02 NEBRASKA | PQ | Hydro | 45 | ER | NPPD
NPPDOrd | 02 NEBRASKA | PQ | Heat | 10.8 | ER | NPPD
SPSDumas19thSt | 05 SOUTHWEST | PQ | Wind | 20 | ER | SPS
SPSEtter | 05 SOUTHWEST | PQ | Wind | 20 | ER | SPS
SPSHopi | 05 SOUTHWEST | PQ | Solar | 10 | ER | SPS
SPSJal | 05 SOUTHWEST | PQ | Solar | 10 | ER | SPS
SPSLeaRoad | 05 SOUTHWEST | PQ | Solar | 10 | ER | SPS
SPSMonument | 05 SOUTHWEST | PQ | Solar | 10 | ER | SPS
SPSMooreE | 05 SOUTHWEST | PQ | Wind | 17.5 | ER | SPS
SPSOcotillo | 05 SOUTHWEST | PQ | Solar | 10 | ER | SPS
SPSSherman | 05 SOUTHWEST | PQ | Wind | 20 | ER | SPS
Sunray | 05 SOUTHWEST | PQ | Wind | 34.5 | ER | SPS
WAPASEAMSFtRandallHydro | 02 NEBRASKA | PQ | Hydro | 360 | ER | WAPA
WAPASEAMSGavinsPointHydro | 02 NEBRASKA | PQ | Hydro | 102 | ER | WAPA

## Revision History
Revision History
Date | Author | Change Description
2026-03-13 | SPP | Phase 1 Draft Posting
2026-04-01 | SPP | Phase 1 Draft Posting#2
2026-04-08 | SPP | Phase 1 Final Posting

## Included Upgrades
Upgrade Type | Study Type | Assigned Study | Upgrade Name
Contingent | Steady State | 2023 ITP PORTFOLIO | Line - Mathewson 345 kV - Redbud 345 kV
Contingent | Steady State | 2023 ITP PORTFOLIO | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Contingent | Steady State | 2023 ITP PORTFOLIO | Device - Broadland 345 kV Reactor
Contingent | Steady State | 2023 ITP PORTFOLIO | Device - Groton 345 kV Reactor
Contingent | Steady State | 2024 ITP PORTFOLIO | Antelope - Holt County 345 kV Ckt 1 New Line
Contingent | Steady State | 2024 ITP PORTFOLIO | Beckham County - Potter 345 kV New Line
Contingent | Steady State | 2024 ITP PORTFOLIO | Belfield - Maurine - New Underwood - Laramie River 345 kV New Line
Contingent | Steady State | 2024 ITP PORTFOLIO | Buffalo Flats - Delaware 345 kV New Line
Contingent | Steady State | 2024 ITP PORTFOLIO | Crane Creek - Robinson Lake 115 kV New Line
Contingent | Steady State | 2024 ITP PORTFOLIO | Delaware - Monett 345 kV Ckt 1 New Line
Contingent | Steady State | 2024 ITP PORTFOLIO | Elm Creek - Tobias 345 kV New Line
Contingent | Steady State | 2024 ITP PORTFOLIO | Finstad - Logan 345 kV New Line, Leland Olds - Logan 345 kV Voltage Conversion
Contingent | Steady State | 2024 ITP PORTFOLIO | Holcomb - Sidney 345 kV Ckt 1 New Line
Contingent | Steady State | 2024 ITP PORTFOLIO | Muskogee - Tahlequah 161 kV Rebuild, Muskogee - Fort Smith 345 kV Conversion/New Line
Contingent | Steady State | 2024 ITP PORTFOLIO | Nashua 345/161 kV Ckt 1 New Line
Contingent | Steady State | 2024 ITP PORTFOLIO | Patent Gate - Pioneer 345 kV Ckt 1 New Line
Contingent | Steady State | 2024 ITP PORTFOLIO | Roadrunner 345/115 kV Ckt 3 Transformer
Contingent | Steady State | 2024 ITP PORTFOLIO | S3458 - S3740 345 kV Ckt 2 New Line
Contingent | Steady State | 2024 ITP PORTFOLIO | Spring Brook - Twelve Mile 345 kV Ckt 1 New Line
Contingent | Steady State | 2024 ITP PORTFOLIO | Tulsa North 345/138 kV Ckt 2 Transformer
Contingent | Steady State | 2024 ITP PORTFOLIO | W Banks 345/115 kV Transformer
Contingent | Steady State | 2025 ITP PORTFOLIO | Trosper - Reno 138 kV Line Rebuild
Contingent | Steady State | 2025 ITP PORTFOLIO | Lindahls - Simpson 115 kV Terminal Upgrade
Contingent | Steady State | 2025 ITP PORTFOLIO | Horseshoe Lake - Dunjee - Reno 138 kV Line Reconductor
Contingent | Steady State | 2025 ITP PORTFOLIO | Whitten - Jal 115 kV Line Rebuild
Contingent | Steady State | 2025 ITP PORTFOLIO | Hobbs South - Switch 4J44 115 kV Line Rebuild Switch 4J44 - Hobbs West S.W. Sta. 115 kV Line Rebuild
Contingent | Steady State | 2025 ITP PORTFOLIO | Patentgate - Pioneer 345 kV Line Tap
Contingent | Steady State | 2025 ITP PORTFOLIO | TWA - North Congress 161 kV Line Rebuild
Contingent | Steady State | 2025 ITP PORTFOLIO | NE 10th - Reno 138 kV Line Rebuild
Contingent | Steady State | 2025 ITP PORTFOLIO | Diamond Tap - Carthage 69 kV Line Rebuild
Contingent | Steady State | 2025 ITP PORTFOLIO | Horseshoe Lake - Midway 138 kV New Line
Contingent | Steady State | 2025 ITP PORTFOLIO | Memorial - Bryant 138 kV Terminal Upgrade Acorn - Jones Tap - Horseshoe Lake 138 kV Terminal Upgrade Stonewall - Remington - NE 30th - Reno 138 kV Voltage Conversion Kelly Ave. - Remington - Green Pastures - Horseshoe Lake 138 kV Voltage Conversion NE 30th 138 kV Convert Substation Green Pastures 138 kV Convert Substation
Contingent | Steady State | 2025 ITP PORTFOLIO | Stilwell 161 kV Breaker Replacements
Contingent | Steady State | 2025 ITP PORTFOLIO | Joplin 161 kV Breaker Replacement
Contingent | Steady State | 2025 ITP PORTFOLIO | Beckville - Bearcat Tap - Henderson REC - Poynter 69 kV Line Rebuild
Contingent | Steady State | 2025 ITP PORTFOLIO | Knoll - North Hays 115 kV Line Rebuild
Contingent | Steady State | 2025 ITP PORTFOLIO | Smokey Hills - Summit 230 kV Line Rebuild
Contingent | Steady State | 2025 ITP PORTFOLIO | Craig - Lenexa South 161 kV Line Rebuild
Contingent | Steady State | 2025 ITP PORTFOLIO | St. Joseph Maryville - Midway - Avenue City 161 kV Line Rebuild
Contingent | Steady State | 2025 ITP PORTFOLIO | FARMRAC - Ripley - Argo 69 kV Line Rebuild Chapel Hill to Adora Closed Loop
Contingent | Steady State | 2025 ITP PORTFOLIO | Buford - DeKalb 69 kV Line Tap
Contingent | Steady State | 2025 ITP PORTFOLIO | Center - Center South 138 kV Line Tap
Contingent | Steady State | 2025 ITP PORTFOLIO | Valliant Weyco - Valliant 138 kV Second Circuit
Contingent | Steady State | 2025 ITP PORTFOLIO | Lone Oak - Tuskahoma - Talihina 138 kV New Line
Contingent | Steady State | 2025 ITP PORTFOLIO | Emmet - Hope North 115 kV Close Normally Open Line
Contingent | Steady State | 2025 ITP PORTFOLIO | Adora - Pilgrims Pride 69 kV New Line
Contingent | Steady State | 2025 ITP PORTFOLIO | Choctaw 138 kV New Capacitor
Contingent | Steady State | 2025 ITP PORTFOLIO | Lindsay Water Flood - Choctaw 138 kV New Line
Contingent | Steady State | 2025 ITP PORTFOLIO | Darco - Nesbitt 138 kV New Line Lake O The Pines - Nesbitt 138 kV Voltage Conversion
Contingent | Steady State | 2025 ITP PORTFOLIO | Nichols - Hill-Wilson 69 kV Close in Normally Open Line Hill-Wilson - D.O. Aldridge 69 kV Upgrade Terminal Equipment D.O. Aldridge - Scroggins 69 kV Upgrade Terminal Equipment
Contingent | Steady State | 2025 ITP PORTFOLIO | Battle Axe - Wolfcamp Tap 115 kV Double-Circuit New Line Battle Axe - Ponderosa - Dollarhide 115 kV New Line
Contingent | Steady State | 2025 ITP PORTFOLIO | Hobbs - Kiowa 345 kV Line Tap Lea National 345/115 kV New Transformer
Contingent | Steady State | 2025 ITP PORTFOLIO | Kiowa - Road Runner 345 kV Line Tap Sand Dunes 345/115 kV New Transformer
Contingent | Steady State | 2025 ITP PORTFOLIO | Muskogee - Ft. Smith 345 kV New Line Muskogee - Oktaha 345 kV Line Tap Muskogee - Keefton 345 kV New Line Pecan Crk. - Keefton 345 kV New Line Keefton 345 kV New Substation
Contingent | Steady State | 2025 ITP PORTFOLIO | Axtell 115/345 kV New Transformer
Contingent | Steady State | 2025 ITP PORTFOLIO | Altamont Switching - Katy 69 kV Line Rebuild Katy 69 kV Convert Substation
Contingent | Steady State | 2025 ITP PORTFOLIO | Duncan - Duncan Tap 138 kV Line Rebuild Duncan Eastside - Duncan Tap 138 kV Line Rebuild Duncan Eastside - Duncan Eastside 138 kV Line Rebuild Rush Springs Tap - Marlow 138 kV Line Rebuild Marlow - Duncan Eastside 138 kV Line Rebuild
Contingent | Steady State | 2025 ITP PORTFOLIO | Camp County POD - Ebenezer 138 kV New Line Ebenezer - Pittsburg 138 kV New Line Gilmer - Pittsburg 138 kV New Line Ebenezer 138 kV Convert Substation Pittsburg 138 kV Convert Substation Pittsburg 69 kV New Substation Pittsburg 138/69 kV New Transformer
Contingent | Steady State | 2025 ITP PORTFOLIO | Lake Hawkins - Piney Wood 138 kV New Line Little Mound - Gilmer 138 kV Voltage Conversion Little Mound - Piney Wood 138 kV New Line Little Mound 138 kV Convert Substation Piney Wood 138 kV Convert Substation Little Mound 138/69 kV New Transformer
Contingent | Steady State | 2025 ITP PORTFOLIO | URECC-Gum Springs - URECC-Hallsville 138 kV New Line Diana East - Diana 138 kV New Line Diana - NoonDay 138 kV Line Retermination NTEC-Hallsville - Noonday 138 kV Line Rebuild
Contingent | Steady State | 2025 ITP PORTFOLIO | Lake Murvaul - Tenaska Gateway 138 kV New Line Murvaul Tap Switch - Lake Murvaul 138 kV CKt 1 Line Reconductor Tenaska Gateway 138 kV New Substation Tenaska Gateway 138/345 kV New Transformer
Contingent | Steady State | 2025 ITP PORTFOLIO | Sawmill - Turnertown 69 kV New Line Modify Hard Tap at North Laneville 69 kV substation Modify Hard Tap at Fears Corner 69 kV substation
Contingent | Steady State | 2025 ITP PORTFOLIO | Baldwin - Baldwin 69 kV New Line Cross Roads - Leigh 69 kV Line Switch-out
Contingent | Steady State | 2025 ITP PORTFOLIO | Stanley - Huxley 69 kV New Line
Contingent | Steady State | 2025 ITP PORTFOLIO | Liberty City - Kilgore 138 kV New Line Big Sandy - Mt. Eara Tap 138 kV Voltage Conversion Mt. Eara - Mt. Eara Tap 138 kV Voltage Conversion Mt. Eara - Kilgore 138 kV Voltage Conversion Mt. Eara 138 kV Convert Substation Mt. Eara Tap 138 kV Convert Substation Kilgore 138 kV New Substation Kilgore 69/138 kV New Transformer
Contingent | Steady State | 2025 ITP PORTFOLIO | Lone Oak - Chisholm Creek 138 kV New Line
Contingent | Steady State | 2025 ITP PORTFOLIO | North Hays - Chetolah 115 kV New Line
Contingent | Steady State | 2025 ITP PORTFOLIO | Aurora - White 115 kV New Line Aurora Industrial - BMU East 115 kV New Line BMU Brookings East - BMU Brookings West 115 kV Line Switch-in White 345/115 kV New Transformer
Contingent | Steady State | 2025 ITP PORTFOLIO | Maddox - Pearl 115 kV Line Rebuild
Contingent | Steady State | 2025 ITP PORTFOLIO | Lamb Co. 69/115 kV New Transformer
Contingent | Steady State | 2025 ITP PORTFOLIO | Plains Int 115/69 kV New Transformer
Contingent | Steady State | 2025 ITP PORTFOLIO | Crosstown - Blue Valley Station 161 kV New Line
Contingent | Steady State | 2025 ITP PORTFOLIO | Columbus Southeast - Columbus 115 kV Line Rebuild
Contingent | Steady State | 2025 ITP PORTFOLIO | Ft. Thompson 345/230 kV New Transformer
Contingent | Steady State | 2025 ITP PORTFOLIO | Quincy - Milwaukee 115 kV New Line
Contingent | Steady State | 2025 ITP PORTFOLIO | Lubbock South - Wolfforth 230 kV Line Rebuild
Contingent | Steady State | 2025 ITP PORTFOLIO | Pruek - Osage 69 kV Line Rebuild
Contingent | Steady State | 2025 ITP PORTFOLIO | Spring Brook - Tande 345 kV Line Tap West Bank South 345 kV New Substation Farmvale Tap 115/345 kV New Transformer
Contingent | Steady State | 2025 ITP PORTFOLIO | KCI - Ferrelview 161 kV Line Rebuild KCI - Platte City 161 kV Line Rebuild Ferrelview - TWA 161 kV Line Rebuild Roanridge - North Congress 161 kV Line Rebuild Roanridge - First Creek 161 kV Line Rebuild
Contingent | Steady State | 2025 ITP PORTFOLIO | Harisburg - Dayton 115 kV Line Rebuild Virgil Fodness- La Valley 115 kV Line Rebuild La Valley - Dayton 115 kV Line Rebuild
Contingent | Steady State | 2025 ITP PORTFOLIO | Hobbs - Millen 115 kV Line Rebuild Taylor S.W. Sta. - Hobbs N.E. 115 kV Line Rebuild Millen - Hobbs N.E. 115 kV Line Rebuild
Contingent | Steady State | 2025 ITP PORTFOLIO | Anita Tap - Anita 161 kV Line Switch-out Anita Tap - Creston 161 kV Line Switch-out Anita Tap - Exira 161 kV Line Switch-out Anita - Creston 161 kV New Line Anita - Exira 161 kV New Line
Contingent | Steady State | 2025 ITP PORTFOLIO | 166th Street - Jaggard Jct. 115 kV Terminal Upgrade 166th Street - Jarbalo Jct. 115 kV Terminal Upgrade Jaggard Jct. - Pentagon 115 kV Terminal Upgrade Pentagon - 53rd & Mund 115 kV Terminal Upgrade
Contingent | Steady State | 2025 ITP PORTFOLIO | Belfield - Roundup 345 kV New Line
Contingent | Steady State | 2025 ITP PORTFOLIO | Diana East 345/138 kV New Transformer Southwest Shreveport 345/138 kV New Transformer AEP Southwest Shreveport 345 kV New STATCOM Southwest Shreveport 345 kV New STATCOM Diana 345 kV New STATCOM AEP Diana 345 kV New STATCOM
Contingent | Steady State | 2025 ITP PORTFOLIO | Anthem - Seminole 765 kV New Line Anthem 765 kV New Substation Anthem 765 kV New Reactor Anthem 345/765 kV New Transformer
Contingent | Steady State | 2025 ITP PORTFOLIO | Oklaunion - Crawfish Draw 345 kV New Line Border - Crawfish Draw 345 kV New Line Tuco - Crawfish Draw 345 kV New Line Crawfish Draw 345 kV New Substation Crawfish Draw 765 kV New Substation Oklaunion 345 kV New Reactor Border 345 kV New Reactor Crawfish Draw 345 kV New Reactor Crawfish Draw 765 kV New Reactor Phantom 765 kV New Reactor Crawfish Draw 345/765 kV New Transformer
Contingent | Steady State | 2025 ITP PORTFOLIO | Southwest Shreveport - Seminole 765 kV New Line Southwest Shreveport 765 kV New Substation Seminole 765 kV New Substation Southwest Shreveport 765 kV New Reactor Seminole 765 kV New Reactor Southwest Shreveport 345/765 kV New Transformer Seminole 345/765 kV New Transformer
Contingent | Steady State | 2025 ITP PORTFOLIO | Woodward - Crawfish Draw 765 kV New Line Woodward 765 kV New Substation Woodward 345 kV New Reactor Woodward 765 kV New Reactor Woodward 345/765 kV New Transformer
Contingent | Steady State | 2025 ITP PORTFOLIO | Quahada 115 kV New Capacitor
Contingent | Steady State | 2025 ITP PORTFOLIO | Lynch Tap - Pearl 115 kV Line Rebuild
Contingent | Steady State | 2025 ITP PORTFOLIO | Twist 115 kV New Capacitor
Contingent | Steady State | 2025 ITP PORTFOLIO | Hobbs 230/345 kV New Transformer
Contingent | Steady State | 2025 ITP PORTFOLIO | Enron Tap - Lea National 115 kV Line Rebuild
Contingent | Steady State | 2025 ITP PORTFOLIO | Phantom - Wood Draw 115 kV Line Rebuild
Contingent | Steady State | 2025 ITP PORTFOLIO | North Loving - China Draw 345 kV Line Tap Sendero 345/115 kV New Transformer
Contingent | Steady State | 2025 ITP PORTFOLIO | Phantom 345/115 kV New Transformer
Contingent | Steady State | 2025 ITP PORTFOLIO | Anthem 345/138 kV New Transformer
Contingent | Steady State | 2025 ITP PORTFOLIO | Dardanelle Dam - Clarksville 161 kV Terminal Upgrade
Contingent | Steady State | 2025 ITP PORTFOLIO | J.G. Walker - Cathey 69 kV Close in Normally Open Line Nichols 69 kV New Capacitor
Contingent | Steady State | 2025 ITP PORTFOLIO | Road Runner - Whitten - Andrews 345 kV New Line
Contingent | Steady State | 2025 ITP PORTFOLIO | Sage Brush - Road Runner 115 kV New Line Sage Brush - Pearl 115 kV New Line
Contingent | Steady State | 2025 ITP PORTFOLIO | Potash Junction 230/345 kV New Transformer
Contingent | Steady State | 2025 ITP PORTFOLIO | Sand Dunes - Red Bluff 115 kV Line Rebuild Jal - Dollarhide 115 kV Line Rebuild
Contingent | Steady State | 2025 ITP PORTFOLIO | Sage Brush - Cardinal 115 kV Line Tap Lea Road - Ward 115 kV Line Tap
Contingent | Steady State | 2025 ITP PORTFOLIO | Zia Hills 115 kV New Capacitor
Contingent | Steady State | 2025 ITP PORTFOLIO | Carpenter 345 kV New Capacitor
Contingent | Steady State | 2025 ITP PORTFOLIO | Jarred Williamson - V.B. Shaw Tap 69 kV Line Switch-in
Contingent | Steady State | 2025 ITP PORTFOLIO | Fiesta 115 kV New Capacitor
Contingent | Steady State | 2025 ITP PORTFOLIO | Potter Co - Harrington 230 kV New Line
Contingent | Steady State | 2025 ITP PORTFOLIO | Harrington - Rolling Hills 230 kV New Line
Contingent | Steady State | 2025 ITP PORTFOLIO | Potter Co 345/230 kV New Transformer
Contingent | Steady State | 2025 ITP PORTFOLIO | Quahada - Lea National 115 kV New Line
Contingent | Steady State | 2025 ITP PORTFOLIO | Castro Co. 115 kV New Capacitor
Contingent | Steady State | 2025 ITP PORTFOLIO | PCA - Potash Junction 115 kV Voltage Conversion
Contingent | Steady State | 2025 ITP PORTFOLIO | Hoskins 230/345 kV New Transformer
Contingent | Steady State | 2025 ITP PORTFOLIO | Farmers - Amarillo South 115 kV Line Rebuild
Contingent | Steady State | 2025 ITP PORTFOLIO | Clinton - Stilwell 345 kV Double-Circuit New Line
Contingent | Steady State | 2025 ITP PORTFOLIO | Randall Co. Intg. 115/230 kV New Transformer
Contingent | Steady State | 2025 ITP PORTFOLIO | Murphy - Quincy 115 kV Line Rebuild
Contingent | Steady State | 2025 ITP PORTFOLIO | Deaf Smith 115/230 kV New Transformer
Contingent | Steady State | 2025 ITP PORTFOLIO | Amarillo South 230/115 kV New Transformer
Contingent | Steady State | 2025 ITP PORTFOLIO | Amarillo S.E. - Randall Co. Intg. 115 kV Line Rebuild Amarillo S.E. - Randall Co. Intg. 115 kV New Line
Contingent | Steady State | 2025 ITP PORTFOLIO | Potter Co 115 kV New Capacitor
Contingent | Steady State | AFFECTED SYSTEM UPGRADE | GIA-61 ERIS REBUILD CRESTON-MARYVILLE 161 KV
Contingent | Steady State | DISIS-2016-002-4 RESTUDY UPGRADE | DISIS-2016-002 UPGRADE: REBUILD_DOVER-HENESSEY-138KV (NTC 210556).IDV
Contingent | Steady State | DISIS-2016-002-4 RESTUDY UPGRADE | DISIS-2016-002 UPGRADE: REBUILD_BUCKEYE_XFMR.IDV
Contingent | Steady State | DISIS-2016-002-4 RESTUDY UPGRADE | DISIS-2016-002 UPGRADE: ADD_OKLAUNION_200MVAR_REACTIVE_EQUIP_345_KV.IDV
Contingent | Steady State | DISIS-2016-002-4 RESTUDY UPGRADE | DISIS-2016-002 UPGRADE: BUILD_DEAFSMITH_100MVAR_REACTIVE_EQUIP_115_KV.IDV
Contingent | Steady State | DISIS-2017-001 UPGRADE | DISIS-2017-001 UPGRADE: REBUILD_NESET-TIOGA-230KV.IDV
Contingent | Steady State | DISIS-2017-001 UPGRADE | DISIS-2017-001 UPGRADE: REPLACE_BROADLAND345-230KV_XFMR.IDV
Contingent | Steady State | DISIS-2017-002 Restudy 2S UPGRADE | Denison to Boyer 69kV Terminal Upgrade
Contingent | Steady State | DISIS-2017-002 Restudy 2S UPGRADE | Replace Mark Moore 345/115 kV Transformer
Contingent | Steady State | DISIS-2017-002 Restudy 2S UPGRADE | Partly rebuild the Elm Creek to North Manhattan 230 kV line
Contingent | Steady State | DISIS-2017-002 Restudy 2S UPGRADE | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line
Contingent | Steady State | DISIS-2017-002 Restudy 2S UPGRADE | Terminal Upgrades at Archie 161kV
Contingent | Steady State | DISIS-2017-002 Restudy 2S UPGRADE | Terminal upgrades at Clinton (owned by AECI)
Contingent | Steady State | DISIS-2017-002 Restudy 2S UPGRADE | Terminal upgrades on the Roanridge to Nashua 161 kV line 1
Contingent | Steady State | DISIS-2017-002 Restudy 2S UPGRADE | SPA Brown to Brown 138 kV Equipment Upgrade
Contingent | Steady State | DISIS-2018-001 Restudy 2 UPGRADE | Delaware Tap to T.S.E. 138 kV Rebuild
Contingent | Steady State | DISIS-2018-001 Restudy 2 UPGRADE | N North Boston to GEN-2018-003-TAP 138 kV Rebuild
Contingent | Steady State | DISIS-2018-002/2019-001 Restudy 2S UPGRADE | Build a new 69 kV tap station cutting off DENISON8 - MANNINGTAP 8 and K338 - K318 circuits
Contingent | Steady State | DISIS-2018-002/2019-001 Restudy 2S UPGRADE | Build Strandahl to Black Tail 115 kV line
Contingent | Steady State | DISIS-2018-002/2019-001 Restudy 2S UPGRADE | Rebuild Mont to STRNDAHL Line_115kV
Contingent | Steady State | DISIS-2018-002/2019-001 Restudy 2S UPGRADE | Rebuild the circuit from K338 to the new 69 kV tap station
Contingent | Steady State | DISIS-2018-002/2019-001 Restudy 2S UPGRADE | Rebuild the circuit from WAPA Denison to the new 69 kV tap station
Contingent | Steady State | DISIS-2018-002/2019-001 Restudy 2S UPGRADE | Rebuild the DENISON8 to J6BOYER_-NI8 69kV Line 1
Contingent | Steady State | DISIS-2018-002/2019-001 Restudy 2S UPGRADE | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line
Contingent | Steady State | DISIS-2018-002/2019-001 Restudy 2S UPGRADE | Rebuild the K335AMAI-NI8 to J6BOYER_-NI8 69kV Line 1
Contingent | Steady State | DISIS-2018-002/2019-001 Restudy 2S UPGRADE | Rebuild Columbus SE to G19-039-TAP 115 kV
Contingent | Steady State | DISIS-2018-002/2019-001 Restudy 2S UPGRADE | Rebuild Rising to G19-039-TAP 115 kV
Contingent | Steady State | DISIS-2020-001 Restudy 2S UPGRADE | Rebuild the HOLDREG7 to G20-013-TAP 115kV line 1
Contingent | Steady State | DISIS-2020-001 Restudy 2S UPGRADE | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Contingent | Steady State | DISIS-2020-001 Restudy 2S UPGRADE | Rebuild the CRAIG 5 to LENEXA 5 161 kV line 2
Contingent | Steady State | DISIS-2020-001 Restudy 2S UPGRADE | Rebuild the MARTCIT5 to REDEL 5 161 kV line 1
Contingent | Steady State | DISIS-2020-001 Restudy 2S UPGRADE | Rebuild the SHWNMSN5 to LENEXA 5 161 kV line 1
Contingent | Steady State | DISIS-2020-001 Restudy 2S UPGRADE | Rebuild the STILWEL5 to REDEL 5 161 kV line 1
Contingent | Steady State | DISIS-2020-001 Restudy 2S UPGRADE | Build New Andrews to Road Runner 345 kV Line
Contingent | Steady State | DISIS-2020-001 Restudy 2S UPGRADE | Hobbs to Andrews Voltage Conversion
Contingent | Steady State | DISIS-2020-001 Restudy 2S UPGRADE | Sidewinder to Andrews 345 kV Lidar Clearance Correction
Contingent | Steady State | DISIS-2020-001 Restudy 2S UPGRADE | Sidewinder to Hobbs 345 kV Lidar Clearance Correction
Contingent | Steady State | DISIS-2021-001 Restudy 1 UPGRADE | Build New Beckham to Potter 345 kV Line Ckt 2
Contingent | Steady State | DISIS-2021-001 Restudy 1 UPGRADE | Rebuild LE-TATMGOAB2 to LE-MCDONALD2 69kV line 1
Contingent | Steady State | DISIS-2021-001 Restudy 1 UPGRADE | Rebuild LE-MCDONALD2 to LE-TATUM_SW2 69kV line 1
Contingent | Steady State | DISIS-2021-001 Restudy 1 UPGRADE | Rebuild LE-LOVINTON2 to LE-TATMGOAB2 69kV line 1
Contingent | Steady State | DISIS-2021-001 Restudy 1 UPGRADE | Build New Border to Beckham 345 kV Line Ckt 2
Contingent | Steady State | DISIS-2021-001 Restudy 1 UPGRADE | Upgrade the existing Tuco 345/230 kV Transformer 1
Contingent | Steady State | DISIS-2021-001 Restudy 1 UPGRADE | Upgrade the existing Elk City 230/138kV Transformer 1
Contingent | Steady State | DISIS-2021-001 Restudy 1 UPGRADE | Rebuild LE-LEWIS 2 to A21-003-TAP 69kV line NO
Contingent | Steady State | DISIS-2021-001 Restudy 1 UPGRADE | Build a second 345/115kV transformer at Antelope
Contingent | Steady State | DISIS-2021-001 Restudy 1 UPGRADE | Rebuild AXTELL7 to KEARNEY7 115 kV line 1
Contingent | Steady State | DISIS-2021-001 Restudy 1 UPGRADE | 5SEDALA to SEDALIA5 161 kV Ckt 1 Terminal Upgrade
Contingent | Steady State | DISIS-2021-001 Restudy 1 UPGRADE | Build a new 50 MVAR cap bank at Viola 138 kV
Contingent | Steady State | DISIS-2021-001 Restudy 1 UPGRADE | Build a new AXTELL 345/115 kV Transformer 2
Contingent | Steady State | DISIS-2021-001 Restudy 1 UPGRADE | Build a new North Hays to Chelotalah 115 kV line 1
Contingent | Steady State | DISIS-2021-001 Restudy 1 UPGRADE | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Contingent | Steady State | DISIS-2021-001 Restudy 1 UPGRADE | MIDLADN3 to MIDLADS3 115 kV Bus Tie Upgrade
Contingent | Steady State | DISIS-2021-001 Restudy 1 UPGRADE | NMANHT6 to ELMCREK6 230 kV Ckt 1 Terminal Upgrade
Contingent | Steady State | DISIS-2021-001 Restudy 1 UPGRADE | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Contingent | Steady State | DISIS-2021-001 Restudy 1 UPGRADE | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Contingent | Steady State | DISIS-2021-001 Restudy 1 UPGRADE | Switch out Axtell to G16-050-TAP 345 kV line reactor at Axtell (50 MVAR)
Contingent | Steady State | DISIS-2021-001 Restudy 1 UPGRADE | Brown Substation Expansion
Contingent | Steady State | DISIS-2021-001 Restudy 1 UPGRADE | Rebuild DEQUEEN2 to DEQUEEN 2 69 kV line 1
Contingent | Steady State | DISIS-2021-001 Restudy 1 UPGRADE | Rebuild NOELSW4 to ROSEVLY4 138 kV line 1
Contingent | Steady State | DISIS-2021-001 Restudy 1 UPGRADE | Rebuild ROSEVLY4 to MOORLND4 138 kV line 1
Contingent | Steady State | DISIS-2021-001 Restudy 1 UPGRADE | Rebuild SOUTHRD4 to ROMNOSE4 138 kV line 1
Contingent | Steady State | DISIS-2021-001 Restudy 1 UPGRADE | Rebuild SW5th4 to CLASSEN4 138 kV line 1
Contingent | Steady State | DISIS-2021-001 Restudy 1 UPGRADE | Reconfigure Little City to Brown 138 kV Line
Contingent | Steady State | DISIS-2021-001 Restudy 1 UPGRADE | Upgrade Terminal Equipment at ROSEHIL and G15052_T
Contingent | Steady State | DISIS-2021-001 Restudy 1 UPGRADE | Build a second Yoakum 345/230 kV Transformer 2
Contingent | Steady State | DISIS-2022-001 Restudy 1 UPGRADE | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1
Contingent | Steady State | DISIS-2022-001 Restudy 1 UPGRADE | Rebuild the RIV4525 to G20-079-TAP 161kV Line 1
Contingent | Steady State | DISIS-2022-001 Restudy 1 UPGRADE | CANEYCK4 to TEXOMAJ4 138kV Line Rebuild
Contingent | Steady State | DISIS-2022-001 Restudy 1 UPGRADE | JEFFRSN4 to WILKES 4 138kV Line Rebuild
Contingent | Steady State | DISIS-2022-001 Restudy 1 UPGRADE | JENSEN 4 to EL RENO4 138kV Line Rebuild
Contingent | Steady State | DISIS-2022-001 Restudy 1 UPGRADE | KRSEY1_4 to COLBERT4 138kV Line Reconductor
Contingent | Steady State | DISIS-2022-001 Restudy 1 UPGRADE | Rebuild the LSSOUTH4 to WILKES 4 138kV Line 1
Contingent | Steady State | DISIS-2022-001 Restudy 1 UPGRADE | Rebuild the WELSH 7 to WILKES 7 345kV Line 1
Contingent | Steady State | DISIS-2022-001 Restudy 1 UPGRADE | Rebuild the WOODWRD4 to WINDFRM4 138kV Line 1
Contingent | Steady State | DISIS-2022-001 Restudy 1 UPGRADE | Replace the LONGWD 7 to LONGWD 4 345kV Transformer 1
Contingent | Steady State | DISIS-2022-001 Restudy 1 UPGRADE | WTH_SE 138/69 kV Transformer Replacement
Contingent | Steady State | DISIS-2022-001 Restudy 1 UPGRADE | Tuco Int 345/230 kV Transformer Replacement
Contingent | Steady State | DISIS-2023-001 Restudy 1 UPGRADE | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1
Contingent | Steady State | DISIS-2023-001 Restudy 1 UPGRADE | Build a new Beatrice Power Station 345/115 kV to DAYKIN 345 kV line 1
Contingent | Steady State | DISIS-2023-001 Restudy 1 UPGRADE | Build Second Red Willow 345/115 kV Transformer
Contingent | Steady State | DISIS-2023-001 Restudy 1 UPGRADE | Build the Daykin 345 kV Substation
Contingent | Steady State | DISIS-2023-001 Restudy 1 UPGRADE | Rebuild the existing LOWELL7 to MINDEN7 115 kV line
Contingent | Steady State | DISIS-2023-001 Restudy 1 UPGRADE | Rebuild the existing 5HEBER.N# to GREERSF5 161 kV line
Contingent | Steady State | DISIS-2023-001 Restudy 1 UPGRADE | Lula 138 kV Substation Reconfiguration
Contingent | Steady State | JTIQ UPGRADE | Raun – S3452 345 kV
Contingent | Steady State | JTIQ UPGRADE | Sibley - 345 kV Bus Reconfiguration
Contingent | Steady State | JTIQ UPGRADE | Lyons Co.– Lakefield 345 kV
Contingent | Steady State | JTIQ UPGRADE | Auburn – Hoyt 345 kV
Contingent | Steady State | JTIQ UPGRADE | Bison – Hankinson – Big Stone South 345 kV

## Constraints Summary
Group | Service Type | Constraint Type | Constraints | Season | Mitigation Iteration | Most Severe Contingency | Rating Type | Rating (MVA) | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | [7 empty] | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | [7 empty] | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | [7 empty] | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | [7 empty] | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | [7 empty] | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | [7 empty] | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | [7 empty] | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | [7 empty] | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | [7 empty] | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | [7 empty] | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | [7 empty] | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | [7 empty] | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | [7 empty] | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | [7 empty] | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | [7 empty] | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29L | N0 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | [7 empty] | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | [7 empty] | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | [7 empty] | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | [7 empty] | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | [7 empty] | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29L | N0 | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | [7 empty] | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | [7 empty] | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | [7 empty] | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | [7 empty] | Add line 659131 LARAMIE_-MB3 345 800120 UNDERWOOD 2 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 532871 CIRCLE6 230 783810 G24-228-TAP 230 1 | [7 empty] | Add line 532871 CIRCLE 6 230 783810 G24-228-TAP 230 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 532871 CIRCLE6 230 783810 G24-228-TAP 230 1 | [7 empty] | Add line 532871 CIRCLE 6 230 783810 G24-228-TAP 230 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 532871 CIRCLE6 230 783810 G24-228-TAP 230 1 | [7 empty] | Add line 532871 CIRCLE 6 230 783810 G24-228-TAP 230 P2
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | [7 empty] | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | [7 empty] | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | [7 empty] | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P12:345:WERE:RENO-WICH-345:EHV: | [7 empty] | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P42:345:SPS:CARPENTER-OR335:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P12:345:WERE:HOYT-JEC-345:EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P23:345:ITCGP:SV_BRK388:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:230:MIDW-WERE:SMOKYHL6-SUMMIT6:::HV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P23:345:SUNC:HLC_BRK188:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 539760 BARBER3 115 539674 BARBER4 138 539917 'BARBER-1 ' 13 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P42:345:OKGE:SB_RARD7313:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P55:345:OPPD:S3458 3::FN13:EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P21:115:MIDW:ST.JOHN-HUNTSVILLE:::HV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P42:345:SPS:FINNEY_OR70:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 640065 AXTELL3 345 640527 MACON3 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:SUNC:SB_BRK482:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P23:345:SUNC:SB_BRK482:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P55:345:OPPD:S3458 3::FN13:EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:345:WERE:HOYT-JEC-345:EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P42:345:NPPD:BKR-AXT-3306:::: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P12:115:SUNC:SAINTJOHN-SAINTJOHN(MIDWEST):::HV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P55:345:OPPD:S3740 3::FN13:EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 640065 AXTELL3 345 640312 PAULINE3 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:SUNC:HLC_BRK188:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 539679 GRTBEND6 230 763862 G19-054-TAP 230 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:ITCGP:SV_BRK388:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P42:345:NPPD:BKR-AXT-3308:::: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P42:345:NPPD:BKR-MOR-3312:::: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 539638 FLATRDG4 138 539674 BARBER4 138 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P42:345:NPPD:BKR-MOR-3310:::: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 530618 HUNTSVL3 115 530724 CENTENNIAL3 115 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P42:345:OKGE:SB_RARD7381:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P42:345:OKGE:SB_OPKY7308:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:115:MIDW:ST.JOHN-CIRCLE:::HV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:SUNC:SB_BRK482:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P42:345:NPPD:BKR-TOB-3304:::: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P42:345:OKGE:SB_DGSE7385:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:WERE:JEC-345-16:EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 531510 HARBNGR3 115 531512 HARBNGR7 345 531511 'HARBNGR-1 ' 13 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 532871 CIRCLE6 230 763862 G19-054-TAP 230 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P42:345:OKGE:SB_RARD7383:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P12:345:OKGE:BKRBKR3572:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:SUNC:HLC_BRK282:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 533412 ARKVALJ3 115 533413 CIRCLE3 115 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P42:345:SPS:CARPENTER-OR335:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:ITCGP:SV_BRK388:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:115-345:SUNC:MO_BRK188:::HV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 531510 HARBNGR3 115 531512 HARBNGR7 345 531511 'HARBNGR-1 ' 13 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29L | N0 | P23:345:SUNC:HLC_BRK188:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 2 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P42:345:NPPD:BKR-GGS-3322:::: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P21:115:MIDW:HUNTSVILLE-ARK VLY JCT:::HV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:SUNC:HLC_BRK282:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P23:345:WERE:WICH-345-50:EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 531405 WALKMYR3 115 531481 HUGOTON3 115 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P12:138:SUNC:BARBER-FLATRIDGE::539638-539674(1):HV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P42:345:OKGE:SB_SOER7383:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P42:345:OKGE:SB_DGSE7313:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P42:345:NPPD:BKR-AXT-3306:::: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P23:345:SUNC:HLC_BRK282:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:SUNC:BU_BRK688:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 539760 BARBER3 115 539674 BARBER4 138 539917 'BARBER-1 ' 13 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P42:345:NPPD:BKR-GGS-3322:::: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:138:SUNC:BARBER-FLATRIDGE::539638-539674(1):HV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 530724 CENTENNIAL3 115 533412 ARKVALJ3 115 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | 275521 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 531405 WALKMYR3 115 531481 HUGOTON3 115 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P42:345:NPPD:BKR-AXT-3306:::: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 530618 HUNTSVL3 115 530724 CENTENNIAL3 115 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P55:345:OPPD:S3458 3::FN13:EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P21:115:MIDW:HUNTSVILLE-ARK VLY JCT:::HV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29L | N0 | P23:345:SUNC:SB_BRK482:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 640065 AXTELL3 345 640374 SWEETW3 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P23:345:WERE:JEC-345-16:EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:115:SUNC:SAINTJOHN-SAINTJOHN(MIDWEST):::HV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 640065 AXTELL3 345 640527 MACON3 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P42:345:OKGE:SB_RARD7311:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P12:115:MIDW:ST.JOHN-CIRCLE:::HV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 539638 FLATRDG4 138 539674 BARBER4 138 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P42:345:OKGE:SB_DGSE7313:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P12:345:OKGE:BKRBKR3571:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 523961 POTTER_CO7 345 784950 G24-266_TAP 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P42:345:NPPD:BKR-AXT-3308:::: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | 275521 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29L | N0 | P23:345:SUNC:HLC_BRK282:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | 275516 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:115-345:SUNC:MO_BRK188:::HV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 533412 ARKVALJ3 115 533413 CIRCLE3 115 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P42:345:NPPD:BKR-GGS-3322:::: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P23:115-345:SUNC:MO_BRK188:::HV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P42:345:SPS:FINNEY_OR70:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P42:345:OKGE:SB_OPKY7388:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 531365 BIRDCTY3 115 531487 MCDONLD3 115 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:115:WERE:CIRC-MWE-115:HV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 530724 CENTENNIAL3 115 533412 ARKVALJ3 115 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P42:345:NPPD:BKR-MOR-3306:::: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P42:345:SPS:CARPENTER-OR335:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P12:115:WERE:CIRC-MWE-115:HV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P42:345:OKGE:SB_DGSE7385:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P42:345:NPPD:BKR-SW-3304:::: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:SUNC:HLC_BRK188:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 640065 AXTELL3 345 640527 MACON3 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 2 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | 275516 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | [7 empty] | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | [7 empty] | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | [7 empty] | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | [7 empty] | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | [7 empty] | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | [7 empty] | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | [7 empty] | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | [7 empty] | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | [7 empty] | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | [7 empty] | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | [7 empty] | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | [7 empty] | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | [7 empty] | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | [7 empty] | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:345:WERE:VIOL-WICH-345:EHV: | [7 empty] | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:345:WERE:VIOL-WICH-345:EHV: | [7 empty] | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | [7 empty] | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:345:WERE:RENO-WICH-345:EHV: | [7 empty] | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:345:WERE:RENO-WICH-345:EHV: | [7 empty] | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 505418 JONESBO5 161 774620 G23-132-TAP 161 1 | [7 empty] | Add line 505418 JONESBO5 161 774620 G23-132-TAP 161 P2
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 505418 JONESBO5 161 774620 G23-132-TAP 161 1 | [7 empty] | Add line 505418 JONESBO5 161 774620 G23-132-TAP 161 P2
04ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 505418 JONESBO5 161 774620 G23-132-TAP 161 1 | [7 empty] | Add line 505418 JONESBO5 161 774620 G23-132-TAP 161 P2
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:SUNC:BU_BRK688:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 509241 CROCKET7 345 783930 G24-232-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:345:WERE:WAVS-WOLF-345:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 510380 DELWARE7 345 580555 MONETT345 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:345:WERE:EMPR-MORR-345:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 640065 AXTELL3 345 640527 MACON3 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | 266352_a | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P55:345:OPPD:S3458 3::FN13:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P42:345:NPPD:BKR-AXT-3306:::: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:WERE:EMPR-345-300:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P42:345:SPS:CARPENTER-OR335:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 542972 HAWTH7 345 783480 G24-217-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 640065 AXTELL3 345 640527 MACON3 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:WERE:N345-345-20:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P51:13:WERE:EMPEC 7:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:SUNC:SB_BRK482:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P55:345:OPPD:S3458 3::FN13:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P52:345:WERE:BURNS 7:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P42:345:OKGE:SB_GRIN7382:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P42:345:SPS:CARPENTER-OR335:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 506935 FLINTCR7 345 580555 MONETT345 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:SUNC:HLC_BRK188:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:WERE:EMPR-345-210:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:115-345:SUNC:MO_BRK188:::HV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P42:345:OKGE:SB_GRIN7312:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | 266352_a | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 510380 DELWARE7 345 580555 MONETT345 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P51:13:WERE:EMPEC 7:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 541198 PECULR7 345 541200 PHILL7 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:SUNC:HLC_BRK188:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:GRDA:TONNECE CB9580:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P42:345:OKGE:SB_GRIN7312:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:ITCGP:SV_BRK388:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:345:WERE:EMPR-MORR-345:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P42:345:OKGE:SB_GRIN7382:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:SUNC:HLC_BRK282:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P42:345:NPPD:BKR-AXT-3306:::: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:WERE:WAVS-BKRS:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:SUNC:HLC_BRK282:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 541201 SIBLEY7 345 783480 G24-217-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:ITCGP:SV_BRK388:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:SUNC:BU_BRK488:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P52:345:WERE:BURNS 7:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:345:AEPW-GRDA:FLINTCR7:TONECE7::: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:WERE:N345-345-20:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:345:WERE:JEC-MORR-345:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:WERE:EMPR-345-210:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:345:WERE:HOYT-JEC-345:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P42:345:SPS:FINNEY_OR70:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:WERE:WAVS-BKRS:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:WERE:EMPR-345-300:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:345:WERE:HOYT-JEC-345:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:WERE:WICH-345-116:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:WERE:JEC-345-16:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:GRDA:TONNECE CB9580:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:WERE:JEC-345-20:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P42:345:SPS:FINNEY_OR70:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:WERE:WICH-345-50:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:WERE:WICH-345-116:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:WERE:EMPR-345-330:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 541200 PHILL7 345 541201 SIBLEY7 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:345:WERE:WAVS-WOLF-345:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:WERE:WICH-345-50:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P51:13:WERE:EMPEC 7:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 580555 MONETT345 345 800102 NBRAN345 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:WERE:EMPR-345-330:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:345:WERE:SWIS-WGAR-345:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P42:345:NPPD:BKR-GGS-3322:::: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P42:345:OKGE:SB_DGSE7313:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P42:345:OKGE:SB_DGSE7313:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:115-345:SUNC:MO_BRK188:::HV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:WERE:JEC-345-20:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:WERE:JEC-345-16:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:SUNC:SB_BRK482:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | [7 empty] | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | [7 empty] | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
05ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | [7 empty] | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | [7 empty] | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | [7 empty] | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | [7 empty] | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | [7 empty] | Add 880 MVAR switched shunt at SWSHRV9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | [7 empty] | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 523221 XIT_INTG6 230 523869 CHAN+TASCOS6 230 1 | [7 empty] | Add line 523221 XIT_INTG 6 230 523869 CHAN+TASCOS6 230 P2
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | [7 empty] | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | [7 empty] | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
05ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 1 | [7 empty] | Add line 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 P2
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | [7 empty] | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | [7 empty] | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | [7 empty] | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | [7 empty] | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | [7 empty] | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | [7 empty] | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | [7 empty] | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
05ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | [7 empty] | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | [7 empty] | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | [7 empty] | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | [7 empty] | Add 960 MVAR switched shunt at MINCO 9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | [7 empty] | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | [7 empty] | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | [7 empty] | Add 960 MVAR switched shunt at MINCO 9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | [7 empty] | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | [7 empty] | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
05ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | [7 empty] | Add 960 MVAR switched shunt at MINCO 9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | [7 empty] | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | [7 empty] | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | [7 empty] | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
05ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | [7 empty] | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 523869 CHAN+TASCOS6 230 523959 POTTER_CO6 230 1 | [7 empty] | Add line 523869 CHAN+TASCOS6 230 523959 POTTER_CO 6 230 P2
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:345:WERE:VIOL-WICH-345:EHV: | [7 empty] | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:345:WERE:VIOL-WICH-345:EHV: | [7 empty] | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | [7 empty] | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | [7 empty] | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | [7 empty] | Add 960 MVAR switched shunt at MINCO 9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | [7 empty] | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | [7 empty] | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | [7 empty] | Add 960 MVAR switched shunt at MINCO 9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | [7 empty] | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
05ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | [7 empty] | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | [7 empty] | Add 960 MVAR switched shunt at MINCO 9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | [7 empty] | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | [7 empty] | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P42:345:OKGE:SB_MICO7381:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P42:345:OKGE:SB_REOW7319:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P42:345:SPS:FINNEY_OR70:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P42:345:OKGE:SB_BOER:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P52:345:AEPW:NR4TERRYRD7:::: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:ITCGP:SV_BRK388:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:345:OKGE:BKRBKR4890:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:OKGE:IF_MICO7302:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P42:345:OKGE:SB_GRNT7313:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P23:345:SUNC:HLC_BRK188:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P42:345:SPS:HITCHLAND-1R15:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P42:345:OKGE:SB_BOER:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P42:345:SPS:FINNEY_OR70:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:115-345:SUNC:MO_BRK188:::HV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P42:345:OKGE:SB_GRNT7313:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:SUNC:HLC_BRK282:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P42:345:OKGE:SB_MICO7381:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 523267 PRINGLE6 230 523979 HARRNG_EST6 230 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P42:345:OKGE:SB_GRNT7381:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:SUNC:SB_BRK482:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P45:345:OKGE:SB_MICO_NOBF:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:OKGE:IF_MICO7302:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P42:345:OKGE:SB_DGSE7385:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P42:345:SPS:HITCHLAND-1R15:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P42:345:SPS:CARPENTER-OR335:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P42:345:OKGE:SB_DGSE7385:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P42:345:SPS:KIOWA-J20-4R45:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P45:345:OKGE:SB_MICO_NOBF:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 523267 PRINGLE6 230 523979 HARRNG_EST6 230 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P23:345:SUNC:HLC_BRK282:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:345:OKGE:BKRBKR4890:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:SUNC:SB_BRK482:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:345:OKGE:BKRBKR3670:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P42:345:OKGE:SB_MICO7311:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:SUNC:HLC_BRK188:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P42:345:SPS:FINNEY_OR70:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P42:345:OKGE:SB_DGSE7313:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P42:345:OKGE:SB_BOER:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P42:345:OKGE:SB_DGSE7313:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P42:345:OKGE:SB_MICO7311:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P42:345:OKGE:SB_GRNT7381:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | P42:345:SPS:CARPENTER-OR335:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:WERE:WICH-345-116:EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:SUNC:HLC_BRK282:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:WERE:WICH-345-116:EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:SUNC:HLC_BRK188:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:115-345:SUNC:MO_BRK188:::HV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:345:OKGE:BKRBKR3670:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P42:345:SPS:CARPENTER-OR335:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | MULTIGEN523979 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P42:345:OKGE:SB_GRNT7381:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N1 | Single 652424 BELFELD3 345 800121 MAURINE2 345 1 | [7 empty] | Add line 652424 BELFELD3 345 800121 MAURINE 2 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N1 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | [7 empty] | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N1 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | [7 empty] | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N1 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | [7 empty] | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29L | N1 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | [7 empty] | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N1 | Single 532871 CIRCLE6 230 783810 G24-228-TAP 230 1 | [7 empty] | Add line 532871 CIRCLE 6 230 783810 G24-228-TAP 230 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N1 | Single 532871 CIRCLE6 230 783810 G24-228-TAP 230 1 | [7 empty] | Add line 532871 CIRCLE 6 230 783810 G24-228-TAP 230 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N1 | Single 532871 CIRCLE6 230 783810 G24-228-TAP 230 1 | [7 empty] | Add line 532871 CIRCLE 6 230 783810 G24-228-TAP 230 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N1 | P23:345:SUNC:HLC_BRK282:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29L | N1 | P23:345:SUNC:HLC_BRK282:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N1 | P42:345:SPS:CARPENTER-OR335:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N1 | P23:345:SUNC:HLC_BRK188:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N1 | P23:345:SUNC:HLC_BRK282:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N1 | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N1 | P23:345:SUNC:HLC_BRK282:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N1 | P23:345:SUNC:HLC_BRK188:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N1 | P23:345:SUNC:HLC_BRK188:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N1 | P51:13:WERE:EMPEC 7:EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N1 | Single 523221 XIT_INTG6 230 523869 CHAN+TASCOS6 230 1 | [7 empty] | Add line 523221 XIT_INTG 6 230 523869 CHAN+TASCOS6 230 P2
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N1 | Single 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 1 | [7 empty] | Add line 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 P2
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N1 | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | [7 empty] | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N1 | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | [7 empty] | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N2 | P12:345.0:UMZ:# N-1 #:: LINE BELFELD3-CHARL_CK-BE3-1 :EHV: | [7 empty] | Add line 652424 BELFELD3 345 659183 CHARL_CK-BE3 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N2 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | [7 empty] | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N2 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | [7 empty] | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N2 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | [7 empty] | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29L | N2 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | [7 empty] | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29L | N2 | P23:345:SUNC:HLC_BRK282:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N2 | P23:345:SUNC:HLC_BRK282:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N2 | P42:345:SPS:CARPENTER-OR335:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N2 | P23:345:SUNC:HLC_BRK188:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N2 | P23:345:SUNC:HLC_BRK282:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N2 | P23:345:SUNC:HLC_BRK188:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N2 | P23:345:SUNC:HLC_BRK282:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N2 | P23:345:SUNC:HLC_BRK188:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N2 | Single 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 1 | [7 empty] | Add line 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 P2
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N2 | Single 523869 CHAN+TASCOS6 230 523959 POTTER_CO6 230 1 | [7 empty] | Add line 523869 CHAN+TASCOS6 230 523959 POTTER_CO 6 230 P2
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N2 | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | [7 empty] | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N2 | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | [7 empty] | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N3 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | [7 empty] | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N3 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | [7 empty] | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N3 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | [7 empty] | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29L | N3 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | [7 empty] | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N3 | P23:345:SUNC:HLC_BRK282:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N3 | P23:345:SUNC:HLC_BRK282:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N3 | P23:345:SUNC:HLC_BRK188:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N3 | P23:345:SUNC:HLC_BRK188:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N3 | P42:345:SPS:CARPENTER-OR335:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29L | N3 | P23:345:SUNC:HLC_BRK282:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N3 | P23:345:SUNC:HLC_BRK282:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N3 | P23:345:SUNC:HLC_BRK188:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N3 | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | [7 empty] | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N4 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | [7 empty] | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N4 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | [7 empty] | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N4 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | [7 empty] | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N4 | P23:345:SUNC:HLC_BRK282:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N4 | P23:345:SUNC:HLC_BRK188:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N4 | P23:345:SUNC:HLC_BRK282:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N4 | P23:345:SUNC:HLC_BRK188:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N4 | P42:345:SPS:CARPENTER-OR335:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N4 | P23:345:SUNC:HLC_BRK282:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N4 | P23:345:SUNC:HLC_BRK188:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N5 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | [7 empty] | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N5 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | [7 empty] | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N5 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | [7 empty] | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N5 | P23:345:SUNC:HLC_BRK188:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N5 | P23:345:SUNC:HLC_BRK282:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N5 | P23:345:SUNC:HLC_BRK188:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N5 | P23:345:SUNC:HLC_BRK282:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP | N5 | P23:345:SUNC:HLC_BRK282:::EHV: | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29WP | N5 | P42:345:SPS:CARPENTER-OR335:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N5 | P23:345:SUNC:HLC_BRK188:::EHV: | [7 empty] | None
00ALL | ERIS | Thermal | 300141 4STILWTR 138 512731 NORTHTP4 138 1 | 29WP | T0 | P12:138:GRDA:KINZEGR4-NORTHTP4:::HV: | B | 191 | -13.1054 | 168.7371 |  |  |  | Rebuild line 300141 4STILWTR 138 512731 NORTHTP4 138 1
00ALL | ERIS | Thermal | 300141 4STILWTR 138 512731 NORTHTP4 138 1 | 29SP | T0 | P12:138:GRDA:KINZEGR4-NORTHTP4:::HV: | B | 191 | -17.4154 | 153.353 |  |  |  | Rebuild line 300141 4STILWTR 138 512731 NORTHTP4 138 1
00ALL | ERIS | Thermal | 300141 4STILWTR 138 512731 NORTHTP4 138 1 | 26SP | T0 | P12:138:GRDA:KINZEGR4-NORTHTP4:::HV: | B | 191 | -17.164 | 136.0367 |  |  |  | Rebuild line 300141 4STILWTR 138 512731 NORTHTP4 138 1
00ALL | ERIS | Thermal | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | 29SP | T0 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 227 | 36.7346 | 155.015 |  |  |  | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
00ALL | ERIS | Thermal | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | 26SP | T0 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 227 | 31.0414 | 136.1107 |  |  |  | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
00ALL | ERIS | Thermal | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | 29WP | T0 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 277 | 12.1449 | 105.6658 |  |  |  | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
00ALL | ERIS | Thermal | 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | 29WP | T0 | Single 508809 LONGWD7 345 788340 G24-379-TAP 345 1 | B | 1195 | -1.8024 | 102.3428 |  |  |  | Rebuild line 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1
00ALL | ERIS | Thermal | 507727 FLOURNY4 138 507732 GENMOTR4 138 1 | 29SP | T0 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 188 | 92.3986 | 137.8049 |  |  |  | Rebuild line 507727 FLOURNY4 138 507732 GENMOTR4 138 1
00ALL | ERIS | Thermal | 507727 FLOURNY4 138 507732 GENMOTR4 138 1 | 26SP | T0 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 188 | 79.2873 | 115.8898 |  |  |  | Rebuild line 507727 FLOURNY4 138 507732 GENMOTR4 138 1
00ALL | ERIS | Thermal | 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | 26SP | T0 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 188 | 106.8978 | 143.8893 |  |  |  | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1
00ALL | ERIS | Thermal | 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | 29SP | T0 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 287 | 78.1869 | 107.7922 |  |  |  | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1
00ALL | ERIS | Thermal | 507732 GENMOTR4 138 507759 SW SHV 4 138 1 | 29SP | T0 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 188 | 91.9423 | 137.2847 |  |  |  | Rebuild line 507732 GENMOTR4 138 507759 SW SHV 4 138 1
00ALL | ERIS | Thermal | 507732 GENMOTR4 138 507759 SW SHV 4 138 1 | 26SP | T0 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 188 | 78.7052 | 115.2421 |  |  |  | Rebuild line 507732 GENMOTR4 138 507759 SW SHV 4 138 1
00ALL | ERIS | Thermal | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | 29SP | T0 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | B | 162 | 48.1063 | 106.4047 |  |  |  | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
00ALL | ERIS | Thermal | 508808 LONGWD 4 138 3WXFMR 520:LONGWOOD 345 1 | 29SP | T0 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | B | 580 | 51.9063 | 111.3979 |  |  |  | Add 3-winding transformer 508808 LONGWD 4 138 508809 LONGWD 7 345 508819 LONGW1-1 13 M2
00ALL | ERIS | Thermal | 508808 LONGWD 4 138 3WXFMR 520:LONGWOOD 345 1 | 26SP | T0 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | B | 580 | 42.8409 | 105.0961 |  |  |  | Add 3-winding transformer 508808 LONGWD 4 138 508809 LONGWD 7 345 508819 LONGW1-1 13 M2
00ALL | ERIS | Thermal | 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | 26SP | T0 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 188 | 108.7952 | 145.7927 |  |  |  | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1
00ALL | ERIS | Thermal | 508809 LONGWD 7 345 3WXFMR 520:LONGWOOD 345 1 | 29SP | T0 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 580 | 83.2764 | 113.0091 |  |  |  | Add 3-winding transformer 508808 LONGWD 4 138 508809 LONGWD 7 345 508819 LONGW1-1 13 M2
00ALL | ERIS | Thermal | 508809 LONGWD 7 345 3WXFMR 520:LONGWOOD 345 1 | 26SP | T0 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | B | 580 | 45.0133 | 106.6696 |  |  |  | Add 3-winding transformer 508808 LONGWD 4 138 508809 LONGWD 7 345 508819 LONGW1-1 13 M2
00ALL | ERIS | Thermal | 508809 LONGWD 7 345 788340 G24-379-TAP 345 1 | 29WP | T0 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | B | 1195 | -1.6404 | 101.1416 |  |  |  | Rebuild line 508809 LONGWD 7 345 788340 G24-379-TAP 345 1
00ALL | ERIS | Thermal | 509048 MURVAULTP 138 509049 MURVAUL4 138 P | 29WP | T0 | P12:345:EES:TENRUSK7!:CROCKET7%:1:EHV: | B | 233 | 84.8977 | 104.21 |  |  |  | Rebuild line 509048 MURVAULTP 138 509049 MURVAUL4 138 P
00ALL | ERIS | Thermal | 509048 MURVAULTP 138 509049 MURVAUL4 138 P | 29SP | T0 | P23:345:EES::7ROCKYCRK%:1:EHV: | B | 233 | 85.7162 | 101.396 |  |  |  | Rebuild line 509048 MURVAULTP 138 509049 MURVAUL4 138 P
00ALL | ERIS | Thermal | 509049 MURVAUL4 138 712002 TENASK4 138 P | 29WP | T0 | P12:345:EES:TENRUSK7!:CROCKET7%:1:EHV: | B | 233 | 91.4371 | 110.7322 |  |  |  | Rebuild line 509049 MURVAUL4 138 712002 TENASK4 138 P
00ALL | ERIS | Thermal | 509049 MURVAUL4 138 712002 TENASK4 138 P | 29SP | T0 | P23:345:EES::7ROCKYCRK%:1:EHV: | B | 233 | 91.3502 | 107.0477 |  |  |  | Rebuild line 509049 MURVAUL4 138 712002 TENASK4 138 P
00ALL | ERIS | Thermal | 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | 29WP | T0 | Single 514909 REDBUD7 345 787290 G24-344-TAP 345 1 | B | 1143 | -6.0022 | 115.8125 |  |  |  | Rebuild line 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1
00ALL | ERIS | Thermal | 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | 29SP | T0 | Single 514909 REDBUD7 345 787290 G24-344-TAP 345 1 | B | 1055 | -6.5009 | 126.4054 |  |  |  | Rebuild line 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1
00ALL | ERIS | Thermal | 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | 26SP | T0 | Single 514909 REDBUD7 345 787290 G24-344-TAP 345 1 | B | 1055 | -6.5055 | 113.4867 |  |  |  | Rebuild line 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1
00ALL | ERIS | Thermal | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 29WP | T0 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | B | 956 | 14.4424 | 129.1811 |  |  |  | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
00ALL | ERIS | Thermal | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 29SP | T0 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | B | 956 | 43.6457 | 140.016 |  |  |  | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
00ALL | ERIS | Thermal | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 26SP | T0 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | B | 956 | 37.4569 | 121.7088 |  |  |  | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
00ALL | ERIS | Thermal | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 29SP | T0 | P42:345:OKGE:SB_GRNT7381:::EHV: | B | 191 | 14.3408 | 100.9272 |  |  |  | Rebuild line 511425 TUTCONT4 138 514898 CIMARON4 138 1
00ALL | ERIS | Thermal | 511467 L.E.S.-4 138 3WXFMR 520:LES 5 345 2 | 29SP | T0 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | B | 515 | 48.2369 | 100.1834 |  |  |  | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
00ALL | ERIS | Thermal | 511468 L.E.S.-7 345 3WXFMR 520:LES 5 345 2 | 29SP | T0 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | B | 515 | 49.6364 | 100.0358 |  |  |  | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
00ALL | ERIS | Thermal | 512710 KINZEGR4 138 512731 NORTHTP4 138 1 | 29WP | T0 | P12:138:GRDA:4STILWTR-NORTHTP4:::HV: | B | 191 | -13.9735 | 161.3788 |  |  |  | Rebuild line 512710 KINZEGR4 138 512731 NORTHTP4 138 1
00ALL | ERIS | Thermal | 512710 KINZEGR4 138 512731 NORTHTP4 138 1 | 29SP | T0 | P12:138:GRDA:4STILWTR-NORTHTP4:::HV: | B | 191 | -16.5743 | 145.5572 |  |  |  | Rebuild line 512710 KINZEGR4 138 512731 NORTHTP4 138 1
00ALL | ERIS | Thermal | 512710 KINZEGR4 138 512731 NORTHTP4 138 1 | 26SP | T0 | P12:138:GRDA:4STILWTR-NORTHTP4:::HV: | B | 191 | -16.317 | 129.599 |  |  |  | Rebuild line 512710 KINZEGR4 138 512731 NORTHTP4 138 1
00ALL | ERIS | Thermal | 514808 JOHNCO 4 138 3WXFMR 524:524:JOHNCOT3 345 3 | 29SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 478 | 27.5083 | 109.5361 |  |  |  | Add 3-winding transformer 514808 JOHNCO 4 138 514809 JOHNCO 7 345 514810 JOHNCO11 13 M2
00ALL | ERIS | Thermal | 514808 JOHNCO 4 138 3WXFMR 524:524:JOHNCOT3 345 3 | 26SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 478 | 28.6847 | 101.6309 |  |  |  | Add 3-winding transformer 514808 JOHNCO 4 138 514809 JOHNCO 7 345 514810 JOHNCO11 13 M2
00ALL | ERIS | Thermal | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 | 29SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 222 | 60.9597 | 115.4138 |  |  |  | Rebuild line 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1
00ALL | ERIS | Thermal | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 | 26SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 222 | 59.0428 | 100.1915 |  |  |  | Rebuild line 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1
00ALL | ERIS | Thermal | 514809 JOHNCO 7 345 3WXFMR 524:524:JOHNCOT3 345 3 | 29SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 478 | 27.339 | 109.5361 |  |  |  | Add 3-winding transformer 514808 JOHNCO 4 138 514809 JOHNCO 7 345 514810 JOHNCO11 13 M2
00ALL | ERIS | Thermal | 514809 JOHNCO 7 345 3WXFMR 524:524:JOHNCOT3 345 3 | 26SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 478 | 28.6917 | 101.6309 |  |  |  | Add 3-winding transformer 514808 JOHNCO 4 138 514809 JOHNCO 7 345 514810 JOHNCO11 13 M2
00ALL | ERIS | Thermal | 514909 REDBUD 7 345 787290 G24-344-TAP 345 1 | 29WP | T0 | Single 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1143 | -5.2076 | 112.7493 |  |  |  | Rebuild line 514909 REDBUD 7 345 787290 G24-344-TAP 345 1
00ALL | ERIS | Thermal | 514909 REDBUD 7 345 787290 G24-344-TAP 345 1 | 29SP | T0 | Single 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1055 | -5.6241 | 122.9793 |  |  |  | Rebuild line 514909 REDBUD 7 345 787290 G24-344-TAP 345 1
00ALL | ERIS | Thermal | 514909 REDBUD 7 345 787290 G24-344-TAP 345 1 | 26SP | T0 | Single 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1055 | -5.6388 | 110.9705 |  |  |  | Rebuild line 514909 REDBUD 7 345 787290 G24-344-TAP 345 1
00ALL | ERIS | Thermal | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | 29WP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 191 | 39.411 | 113.1788 |  |  |  | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1
00ALL | ERIS | Thermal | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | 29SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 191 | 65.7916 | 128.8052 |  |  |  | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1
00ALL | ERIS | Thermal | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | 26SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 191 | 63.5048 | 111.1423 |  |  |  | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1
00ALL | ERIS | Thermal | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 | 29SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 222 | 60.1357 | 114.5605 |  |  |  | Rebuild line 515121 MILLCKT4 138 515122 SXMLCKT4 138 1
00ALL | ERIS | Thermal | 515235 PECANCK7 345 516374 KEEFTON7 345 1 | 29SP | T0 | P22:345:EES:MUSKOGE7!:::EHV: | B | 1195 | 49.1408 | 105.7048 |  |  |  | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1
00ALL | ERIS | Thermal | 515336 VBI 2 69 3WXFMR 524:524:VBI2 161 2 | 29SP | T0 | System Intact | A | 76 | 104.2625 | 108.7425 |  |  |  | Rebuild 3-winding transformer 515336 VBI 2 69 515339 VBI 5 161 515769 VBI 1 13 2
00ALL | ERIS | Thermal | 515339 VBI 5 161 3WXFMR 524:524:VBI2 161 2 | 29SP | T0 | System Intact | A | 76 | 104.2625 | 108.7425 |  |  |  | Rebuild 3-winding transformer 515336 VBI 2 69 515339 VBI 5 161 515769 VBI 1 13 2
00ALL | ERIS | Thermal | 515800 GRACMNT7 345 3WXFMR 524:524:GRACMNT3 345 3 | 29WP | T0 | P42:345:OKGE:SB_GRNT7381:::EHV: | B | 478 | 15.6026 | 108.2719 |  |  |  | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2
00ALL | ERIS | Thermal | 515800 GRACMNT7 345 3WXFMR 524:524:GRACMNT3 345 3 | 29SP | T0 | P42:345:OKGE:SB_GRNT7381:::EHV: | B | 478 | 32.8239 | 111.1711 |  |  |  | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2
00ALL | ERIS | Thermal | 515802 GRACMNT4 138 3WXFMR 524:524:GRACMNT3 345 3 | 29WP | T0 | P42:345:OKGE:SB_GRNT7381:::EHV: | B | 478 | 15.5132 | 108.2719 |  |  |  | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2
00ALL | ERIS | Thermal | 515802 GRACMNT4 138 3WXFMR 524:524:GRACMNT3 345 3 | 29SP | T0 | P42:345:OKGE:SB_GRNT7381:::EHV: | B | 478 | 32.7476 | 111.1711 |  |  |  | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2
00ALL | ERIS | Thermal | 520560 HUGOITC4 138 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | 29WP | T0 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | B | 478 | -20.359 | 107.8834 |  |  |  | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
00ALL | ERIS | Thermal | 520560 HUGOITC4 138 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | 29SP | T0 | P23:345:AEPW:VALLIANT CB 3417A NBTB:::: | B | 478 | -17.0418 | 114.0845 |  |  |  | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
00ALL | ERIS | Thermal | 520560 HUGOITC4 138 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | 26SP | T0 | P23:345:AEPW:VALLIANT CB 3417A NBTB:::: | B | 478 | 18.204 | 104.3989 |  |  |  | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
00ALL | ERIS | Thermal | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | 29WP | T0 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | B | 478 | -19.9482 | 105.5951 |  |  |  | Rebuild line 520560 HUGOITC4 138 520948 HUGO PP4 138 1
00ALL | ERIS | Thermal | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | 29SP | T0 | P23:345:AEPW:VALLIANT CB 3417A NBTB:::: | B | 478 | -16.7048 | 111.649 |  |  |  | Rebuild line 520560 HUGOITC4 138 520948 HUGO PP4 138 1
00ALL | ERIS | Thermal | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | 26SP | T0 | P23:345:AEPW:VALLIANT CB 3417A NBTB:::: | B | 478 | 17.8406 | 102.2084 |  |  |  | Rebuild line 520560 HUGOITC4 138 520948 HUGO PP4 138 1
00ALL | ERIS | Thermal | 521049 SCLMNJC4 138 784980 G24-267-TAP 138 1 | 29SP | T0 | Single 515136 SUNNYSD7 345 560088 BISON7 345 1 | B | 287 | 8.7212 | 100.4042 |  |  |  | Rebuild line 521049 SCLMNJC4 138 784980 G24-267-TAP 138 1
00ALL | ERIS | Thermal | 521157 HUGO 7 345 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | 29WP | T0 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | B | 478 | -20.6998 | 107.9917 |  |  |  | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
00ALL | ERIS | Thermal | 521157 HUGO 7 345 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | 29SP | T0 | P23:345:AEPW:VALLIANT CB 3417A NBTB:::: | B | 478 | -17.2945 | 114.1585 |  |  |  | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
00ALL | ERIS | Thermal | 521157 HUGO 7 345 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | 26SP | T0 | P23:345:AEPW:VALLIANT CB 3417A NBTB:::: | B | 478 | 18.4953 | 104.6701 |  |  |  | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
00ALL | ERIS | Thermal | 521157 HUGO 7 345 560088 BISON 7 345 1 | 29SP | T0 | Single 515136 SUNNYSD7 345 560088 BISON7 345 1 | B | 1195 | 13.2657 | 100.0687 |  |  |  | Rebuild line 521157 HUGO 7 345 560088 BISON 7 345 1
00ALL | ERIS | Thermal | 532765 HOYT 7 345 532766 JEC N 7 345 1 | 29SP | T0 | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | B | 830 | 52.6782 | 117.2246 |  |  |  | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1
00ALL | ERIS | Thermal | 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 | 29SP | T0 | P52:345:WERE:NRSS7:EHV: | B | 952 | 10.3304 | 101.5502 |  |  |  | Rebuild line 532794 ROSEHIL7 345 532800 LATHAMS7 345 1
00ALL | ERIS | Thermal | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | 29WP | T0 | P12:161:INDN:BLUVLY-ECKLES:::HV: | B | 334 | 25.1903 | 177.2062 |  |  |  | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
00ALL | ERIS | Thermal | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | 29SP | T0 | P12:161:INDN:BLUVLY-ECKLES:::HV: | B | 334 | 16.3673 | 165.9585 |  |  |  | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
00ALL | ERIS | Thermal | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | 26SP | T0 | P12:161:INDN:BLUVLY-ECKLES:::HV: | B | 334 | 12.9403 | 144.151 |  |  |  | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
00ALL | ERIS | Thermal | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | 29WP | T0 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 334 | 54.181 | 200.6197 |  |  |  | Rebuild line 543004 BLUMILS5 161 548808 ECKLES-161 161 1
00ALL | ERIS | Thermal | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | 29SP | T0 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 58.7166 | 218.9093 |  |  |  | Rebuild line 543004 BLUMILS5 161 548808 ECKLES-161 161 1
00ALL | ERIS | Thermal | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | 26SP | T0 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 58.7256 | 196.2064 |  |  |  | Rebuild line 543004 BLUMILS5 161 548808 ECKLES-161 161 1
00ALL | ERIS | Thermal | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | 29WP | T0 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 334 | -0.4558 | 204.675 |  |  |  | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
00ALL | ERIS | Thermal | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | 29SP | T0 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | -0.48927 | 223.315 |  |  |  | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
00ALL | ERIS | Thermal | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | 26SP | T0 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | -0.48983 | 200.5394 |  |  |  | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
00ALL | ERIS | Thermal | 548802 SUB H 69 548806 BLUVLY 69 1 | 29WP | T0 | P12:161:INDN:BLUVLY-SUB M:::HV: | B | 72 | 18.8827 | 107.387 |  |  |  | Rebuild line 548802 SUB H 69 548806 BLUVLY 69 1
00ALL | ERIS | Thermal | 548802 SUB H 69 548806 BLUVLY 69 1 | 29SP | T0 | P12:161:INDN:BLUVLY-SUB M:::HV: | B | 58 | 27.3781 | 138.2277 |  |  |  | Rebuild line 548802 SUB H 69 548806 BLUVLY 69 1
00ALL | ERIS | Thermal | 548802 SUB H 69 548806 BLUVLY 69 1 | 26SP | T0 | P12:161:INDN:BLUVLY-SUB M:::HV: | B | 58 | 26.2787 | 125.0711 |  |  |  | Rebuild line 548802 SUB H 69 548806 BLUVLY 69 1
00ALL | ERIS | Thermal | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | 29WP | T0 | P12:161:INDN:BLUVLY-SUB M:::HV: | B | 112 | 54.8829 | 141.1515 |  |  |  | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
00ALL | ERIS | Thermal | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | 29SP | T0 | P12:161:INDN:BLUVLY-SUB M:::HV: | B | 112 | 73.3036 | 160.3715 |  |  |  | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
00ALL | ERIS | Thermal | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | 26SP | T0 | P12:161:INDN:BLUVLY-SUB M:::HV: | B | 112 | 70.7269 | 147.319 |  |  |  | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
00ALL | ERIS | Thermal | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | 29SP | T0 | P12:161:INDN:BLUVLY-SUB M:::HV: | B | 112 | 75.3104 | 164.762 |  |  |  | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
00ALL | ERIS | Thermal | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | 29WP | T0 | P12:161:INDN:BLUVLY-SUB M:::HV: | B | 112 | 56.3854 | 145.0158 |  |  |  | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
00ALL | ERIS | Thermal | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | 26SP | T0 | P12:161:INDN:BLUVLY-SUB M:::HV: | B | 112 | 72.6632 | 151.3522 |  |  |  | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
00ALL | ERIS | Thermal | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | 29WP | T0 | P12:161:INDN:BLUVLY-ECKLES:::HV: | B | 335 | -2.4593 | 196.0328 |  |  |  | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
00ALL | ERIS | Thermal | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | 29SP | T0 | P12:161:INDN:BLUVLY-ECKLES:::HV: | B | 335 | -14.5542 | 190.3166 |  |  |  | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
00ALL | ERIS | Thermal | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | 26SP | T0 | P12:161:INDN:BLUVLY-ECKLES:::HV: | B | 335 | -11.8974 | 167.5741 |  |  |  | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
00ALL | ERIS | Thermal | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | 29WP | T0 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 334 | -0.25935 | 204.3549 |  |  |  | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
00ALL | ERIS | Thermal | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | 29SP | T0 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 309 | -0.27528 | 223.7808 |  |  |  | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
00ALL | ERIS | Thermal | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | 26SP | T0 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 309 | -0.27655 | 200.8079 |  |  |  | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
00ALL | ERIS | Thermal | 548815 SUB M 69 548814 SUB M-161 161 1 | 29WP | T0 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | B | 112 | 71.1248 | 108.0961 |  |  |  | Rebuild 2-winding transformer 548814 SUB M-161 161 548815 SUB M 69 1
00ALL | ERIS | Thermal | 548815 SUB M 69 548814 SUB M-161 161 1 | 29SP | T0 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | B | 112 | 84.9315 | 123.7024 |  |  |  | Rebuild 2-winding transformer 548814 SUB M-161 161 548815 SUB M 69 1
00ALL | ERIS | Thermal | 548815 SUB M 69 548814 SUB M-161 161 1 | 26SP | T0 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | B | 112 | 84.0108 | 115.7018 |  |  |  | Rebuild 2-winding transformer 548814 SUB M-161 161 548815 SUB M 69 1
00ALL | ERIS | Thermal | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | 29WP | T0 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | B | 956 | 81.2313 | 160.3375 |  |  |  | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
00ALL | ERIS | Thermal | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | 29SP | T0 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | B | 956 | 101.6347 | 190.8152 |  |  |  | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
00ALL | ERIS | Thermal | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | 26SP | T0 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | B | 956 | 85.0379 | 151.5669 |  |  |  | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
00ALL | ERIS | Thermal | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | 29SP | T0 | P42:345:NPPD:BKR-MOR-3306:::: | B | 956 | 62.3453 | 103.187 |  |  |  | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
00ALL | ERIS | Thermal | 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | 29SP | T0 | P42:345:NPPD:BKR-MOR-3310:::: | B | 956 | 56.347 | 100.6163 |  |  |  | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1
00ALL | ERIS | Thermal | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | 29SP | T0 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | B | 417 | 64.8969 | 101.9454 |  |  |  | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
00ALL | ERIS | Thermal | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | 29SP | T0 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | B | 417 | 64.8969 | 101.9454 |  |  |  | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
00ALL | ERIS | Thermal | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | 29SP | T0 | P42:345:NPPD:BKR-MOR-3308:::: | B | 240 | 55.9744 | 102.2438 |  |  |  | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
00ALL | ERIS | Thermal | 645455 S3455 3 345 645740 S3740 3 345 1 | 29SP | T0 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | B | 1195 | 110.2486 | 115.6339 |  |  |  | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
00ALL | ERIS | Thermal | 652391 WILLISTON27 115 652421 WILISTN7 115 Z1 | 26SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 201 | -44.6872 | 100.4946 |  |  |  | Rebuild line 652391 WILLISTON27 115 652421 WILISTN7 115 Z1
00ALL | ERIS | Thermal | 655942 N.TWELVE-MW7 115 655959 EPPING -MW7 115 1 | 26SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 203 | -9.933 | 110.3779 |  |  |  | Rebuild line 655942 N.TWELVE-MW7 115 655959 EPPING -MW7 115 1
00ALL | ERIS | Thermal | 655943 W.BANK.S-MW7 115 655945 WHEELS_T-MW7 115 1 | 26SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 189 | 2.0107 | 192.0906 |  |  |  | Rebuild line 655943 W.BANK.S-MW7 115 655945 WHEELS_T-MW7 115 1
00ALL | ERIS | Thermal | 655943 W.BANK.S-MW7 115 655945 WHEELS_T-MW7 115 1 | 29SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 189 | 5.5288 | 154.4497 |  |  |  | Rebuild line 655943 W.BANK.S-MW7 115 655945 WHEELS_T-MW7 115 1
00ALL | ERIS | Thermal | 655943 W.BANK.S-MW7 115 655945 WHEELS_T-MW7 115 1 | 29WP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 239 | 9.7869 | 125.0229 |  |  |  | Rebuild line 655943 W.BANK.S-MW7 115 655945 WHEELS_T-MW7 115 1
00ALL | ERIS | Thermal | 655945 WHEELS_T-MW7 115 655959 EPPING -MW7 115 1 | 26SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 203 | -9.0686 | 111.1475 |  |  |  | Rebuild line 655945 WHEELS_T-MW7 115 655959 EPPING -MW7 115 1
00ALL | ERIS | Thermal | 659070 W.BANK.S-BE3 345 655943 W.BANK.S-MW7 115 1 | 26SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 435 | 26.85 | 134.9735 |  |  |  | Add 2-winding transformer 655943 W.BANK.S-MW7 115 659070 W.BANK.S-BE3 345 M2
00ALL | ERIS | Thermal | 659070 W.BANK.S-BE3 345 655943 W.BANK.S-MW7 115 1 | 29SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 435 | 30.7064 | 120.368 |  |  |  | Add 2-winding transformer 655943 W.BANK.S-MW7 115 659070 W.BANK.S-BE3 345 M2
00ALL | ERIS | Thermal | 659070 W.BANK.S-BE3 345 655943 W.BANK.S-MW7 115 1 | 29WP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 435 | 40.0095 | 127.9484 |  |  |  | Add 2-winding transformer 655943 W.BANK.S-MW7 115 659070 W.BANK.S-BE3 345 M2
00ALL | ERIS | Thermal | 659070 W.BANK.S-BE3 345 779400 G24-081-TAP 345 1 | 26SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | -1.1955 | 112.072 |  |  |  | Rebuild line 659070 W.BANK.S-BE3 345 779400 G24-081-TAP 345 1
00ALL | ERIS | Thermal | 659070 W.BANK.S-BE3 345 779400 G24-081-TAP 345 1 | 29SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | -1.1855 | 124.1936 |  |  |  | Rebuild line 659070 W.BANK.S-BE3 345 779400 G24-081-TAP 345 1
00ALL | ERIS | Thermal | 659070 W.BANK.S-BE3 345 779400 G24-081-TAP 345 1 | 29WP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1195 | -1.076 | 112.0967 |  |  |  | Rebuild line 659070 W.BANK.S-BE3 345 779400 G24-081-TAP 345 1
00ALL | ERIS | Thermal | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | 26SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 506 | 8.9943 | 124.2197 |  |  |  | Rebuild line 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1
00ALL | ERIS | Thermal | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | 26SP | T0 | Single 659070 W.BANK.S-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | -0.60125 | 110.6391 |  |  |  | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
00ALL | ERIS | Thermal | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | 29SP | T0 | Single 659070 W.BANK.S-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | -0.59749 | 122.8967 |  |  |  | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
00ALL | ERIS | Thermal | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | 29WP | T0 | Single 659070 W.BANK.S-BE3 345 779400 G24-081-TAP 345 1 | B | 1195 | -0.53992 | 111.1995 |  |  |  | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
00ALL | ERIS | Thermal | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | 26SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 637 | 7.369 | 100.0222 |  |  |  | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2
00ALL | ERIS | Thermal | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | 29SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 637 | 43.2024 | 103.7431 |  |  |  | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2
00ALL | ERIS | Thermal | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | 29WP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 637 | 47.1363 | 106.3669 |  |  |  | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2
00ALL | ERIS | Thermal | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | 26SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 637 | 7.3686 | 100.0222 |  |  |  | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2
00ALL | ERIS | Thermal | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | 29SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 637 | 43.1351 | 103.7431 |  |  |  | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2
00ALL | ERIS | Thermal | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | 29WP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 637 | 46.9989 | 106.3669 |  |  |  | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2
00ALL | ERIS | Thermal | 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1 | 29WP | T0 | Single 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1143 | -0.52153 | 109.7481 |  |  |  | Rebuild line 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1
00ALL | ERIS | Thermal | 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1 | 29SP | T0 | Single 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1055 | 0.56323 | 119.6839 |  |  |  | Rebuild line 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1
00ALL | ERIS | Thermal | 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1 | 26SP | T0 | Single 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1055 | 0.56471 | 108.039 |  |  |  | Rebuild line 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1
00NR | NRIS | Thermal | 505488 CARTHAG5 161 3WXFMR 300:CRG X1 161 1 | 29SP | T0 | Single 505490 CARTHG2 69 505488 CARTHAG5 161 505489 'CRG X2 1 ' 13 1 | B | 84 | 103.7531 | 102.2131 |  |  |  | Add 3-winding transformer 505487 CRG X1 1 13 505488 CARTHAG5 161 505490 CARTHG 2 69 M2
00NR | NRIS | Thermal | 505488 CARTHAG5 161 3WXFMR 537:CRG X2 161 1 | 29SP | T0 | Single 505490 CARTHG2 69 505488 CARTHAG5 161 505487 'CRG X1 1 ' 13 1 | B | 84 | 103.1366 | 101.605 |  |  |  | Add 3-winding transformer 505488 CARTHAG5 161 505489 CRG X2 1 13 505490 CARTHG 2 69 M2
00NR | NRIS | Thermal | 509817 T.NO.--4 138 509900 46ST-TP-4 138 1 | 26SP | T0 | Single 509784 A.A.---4 138 786510 G24-318-TAP 138 1 | B | 151 | 84.6213 | 103.867 |  |  |  | Rebuild line 509817 T.NO.--4 138 509900 46ST-TP-4 138 1
00NR | NRIS | Thermal | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | 26SP | T0 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | B | 493 | 75.3605 | 131.2898 |  |  |  | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
00NR | NRIS | Thermal | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | 29WP | T0 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | B | 493 | 53.883 | 108.6283 |  |  |  | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
00NR | NRIS | Thermal | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | 29SP | T0 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | B | 493 | 58.0505 | 123.0977 |  |  |  | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
00NR | NRIS | Thermal | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 26SP | T0 | Single 514894 CZECHAL4 138 514898 CIMARON4 138 1 | B | 308 | 82.4127 | 107.2622 |  |  |  | Rebuild line 514863 HAYMAKR4 138 514898 CIMARON4 138 1
00NR | NRIS | Thermal | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 29SP | T0 | Single 514894 CZECHAL4 138 514898 CIMARON4 138 1 | B | 308 | 83.0929 | 107.9927 |  |  |  | Rebuild line 514863 HAYMAKR4 138 514898 CIMARON4 138 1
00NR | NRIS | Thermal | 514889 WRAIRPT4 138 514925 PENN 4 138 1 | 29SP | T0 | Single 514894 CZECHAL4 138 514898 CIMARON4 138 1 | B | 267 | 63.0519 | 100.1547 |  |  |  | Rebuild line 514889 WRAIRPT4 138 514925 PENN 4 138 1
00NR | NRIS | Thermal | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 26SP | T0 | Single 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | B | 382 | 73.14 | 104.9767 |  |  |  | Rebuild line 514893 XEROX 4 138 514894 CZECHAL4 138 1
00NR | NRIS | Thermal | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 29SP | T0 | Single 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | B | 382 | 71.4053 | 103.9974 |  |  |  | Rebuild line 514893 XEROX 4 138 514894 CZECHAL4 138 1
00NR | NRIS | Thermal | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 26SP | T0 | Single 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | B | 444 | 73.1314 | 100.5563 |  |  |  | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1
00NR | NRIS | Thermal | 514898 CIMARON4 138 3WXFMR 524:524:CIMARON2 345 2 | 26SP | T0 | P13:138:OKGE:BKRBKR_3W020:::HV: | B | 478 | 83.464 | 104.2229 |  |  |  | Add 3-winding transformer 514898 CIMARON4 138 514901 CIMARON7 345 515715 CIMARO21 13 M2
00NR | NRIS | Thermal | 514898 CIMARON4 138 3WXFMR 524:524:CIMARON2 345 2 | 29SP | T0 | P13:138:OKGE:BKRBKR_3W020:::HV: | B | 478 | 78.4928 | 101.6081 |  |  |  | Add 3-winding transformer 514898 CIMARON4 138 514901 CIMARON7 345 515715 CIMARO21 13 M2
00NR | NRIS | Thermal | 514901 CIMARON7 345 3WXFMR 524:524:CIMARON2 345 2 | 26SP | T0 | P13:138:OKGE:BKRBKR_3W020:::HV: | B | 478 | 87.1736 | 108.2023 |  |  |  | Add 3-winding transformer 514898 CIMARON4 138 514901 CIMARON7 345 515715 CIMARO21 13 M2
00NR | NRIS | Thermal | 514901 CIMARON7 345 3WXFMR 524:524:CIMARON2 345 2 | 29SP | T0 | P13:138:OKGE:BKRBKR_3W020:::HV: | B | 478 | 81.6977 | 105.4238 |  |  |  | Add 3-winding transformer 514898 CIMARON4 138 514901 CIMARON7 345 515715 CIMARO21 13 M2
00NR | NRIS | Thermal | 514925 PENN 4 138 514926 SANTAFE4 138 1 | 26SP | T0 | Single 514876 SW134TP4 138 514887 WESTMOR4 138 1 | B | 191 | 68.254 | 116.1264 |  |  |  | Rebuild line 514925 PENN 4 138 514926 SANTAFE4 138 1
00NR | NRIS | Thermal | 514925 PENN 4 138 514926 SANTAFE4 138 1 | 29SP | T0 | 272053 | B | 191 | 60.4773 | 110.2494 |  |  |  | Rebuild line 514925 PENN 4 138 514926 SANTAFE4 138 1
00NR | NRIS | Thermal | 514959 FOSTER 4 138 515387 NEWDOMI4 138 1 | 29SP | T0 | Single 514933 DRAPER4 138 515003 BARNES4 138 1 | B | 267 | 52.8123 | 103.8943 |  |  |  | Rebuild line 514959 FOSTER 4 138 515387 NEWDOMI4 138 1
00NR | NRIS | Thermal | 514959 FOSTER 4 138 515387 NEWDOMI4 138 1 | 26SP | T0 | Single 514933 DRAPER4 138 515003 BARNES4 138 1 | B | 267 | 52.783 | 100.3872 |  |  |  | Rebuild line 514959 FOSTER 4 138 515387 NEWDOMI4 138 1
00NR | NRIS | Thermal | 514992 TURNER 4 138 516097 NORMHLL4 138 1 | 29SP | T0 | P12:138:OKGE:BKRBKR1481:::HV: | B | 308 | 50.3008 | 100.3791 |  |  |  | Rebuild line 514992 TURNER 4 138 516097 NORMHLL4 138 1
00NR | NRIS | Thermal | 515055 MAUD 4 138 787770 G24-360-TAP 138 1 | 26SP | T0 | P12:138:OKGE:BKRBKR2170:::HV: | B | 287 | 50.8321 | 103.9043 |  |  |  | Rebuild line 515055 MAUD 4 138 787770 G24-360-TAP 138 1
00NR | NRIS | Thermal | 515055 MAUD 4 138 787770 G24-360-TAP 138 1 | 29SP | T0 | P12:138:OKGE:BKRBKR2170:::HV: | B | 287 | 49.0395 | 107.671 |  |  |  | Rebuild line 515055 MAUD 4 138 787770 G24-360-TAP 138 1
00NR | NRIS | Thermal | 528618 LE-LOVINTON2 69 528334 LE-NRTH_INT3 115 1 | 26SP | T0 | Single 527864 CUNNINHAM3 115 528348 BUCKEYE_TP3 115 1 | B | 100 | 69.4998 | 123.5295 |  |  |  | Rebuild 2-winding transformer 528334 LE-NRTH_INT3 115 528618 LE-LOVINTON2 69 1
00NR | NRIS | Thermal | 528618 LE-LOVINTON2 69 528334 LE-NRTH_INT3 115 1 | 29WP | T0 | Single 528626 LE-PLNSINT2 69 528709 LE-PLNSGOAB2 69 1 | B | 100 | 92.1349 | 122.2188 |  |  |  | Rebuild 2-winding transformer 528334 LE-NRTH_INT3 115 528618 LE-LOVINTON2 69 1
00NR | NRIS | Thermal | 528618 LE-LOVINTON2 69 528334 LE-NRTH_INT3 115 1 | 29SP | T0 | P12:115:SPS:V98.1.CUNN.LE-SNANDR:::HV: | B | 100 | 61.0476 | 113.9441 |  |  |  | Rebuild 2-winding transformer 528334 LE-NRTH_INT3 115 528618 LE-LOVINTON2 69 1
00NR | NRIS | Thermal | 533044 GILL E 4 138 533051 INTERST4 138 1 | 29SP | T0 | Single 533041 EVANSS4 138 533053 LAKERDG4 138 1 | B | 182 | 81.6327 | 101.7057 |  |  |  | Rebuild line 533044 GILL E 4 138 533051 INTERST4 138 1
00NR | NRIS | Thermal | 640066 AXTELL 7 115 640275 MINDEN 7 115 1 | 29SP | T0 | Single 640066 AXTELL7 115 640250 KEARNEY7 115 1 | B | 160 | 94.7369 | 119.1806 |  |  |  | Rebuild line 640066 AXTELL 7 115 640275 MINDEN 7 115 1
00NR | NRIS | Thermal | 640080 BELDEN 7 115 640212 HARTGTN7 115 1 | 29SP | T0 | Single 640149 CREITON7 115 640521 ANTELOPE7 115 1 | B | 123 | 41.2472 | 102.1689 |  |  |  | Rebuild line 640080 BELDEN 7 115 640212 HARTGTN7 115 1
00NR | NRIS | Thermal | 640082 BEVERLY7 115 640326 REDWILO7 115 1 | 29SP | T0 | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | B | 160 | 33.7274 | 102.7006 |  |  |  | Rebuild line 640082 BEVERLY7 115 640326 REDWILO7 115 1
00NR | NRIS | Thermal | 640100 CAMBRIG7 115 640194 GOSPER 7 115 1 | 29SP | T0 | P42:345:NPPD:BKR-GGS-3322:::: | B | 120 | 18.9314 | 109.9704 |  |  |  | Rebuild line 640100 CAMBRIG7 115 640194 GOSPER 7 115 1
00NR | NRIS | Thermal | 640100 CAMBRIG7 115 640269 MCCOOK 7 115 1 | 29SP | T0 | P42:345:NPPD:BKR-GGS-3322:::: | B | 120 | 31.3612 | 122.0051 |  |  |  | Rebuild line 640100 CAMBRIG7 115 640269 MCCOOK 7 115 1
00NR | NRIS | Thermal | 640125 COLMB.E3 345 3WXFMR 640:COL.EAST T4 345 1 | 29SP | T0 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | B | 336 | 30.2226 | 102.7455 |  |  |  | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
00NR | NRIS | Thermal | 640127 COLMB.E7 115 3WXFMR 640:COL.EAST T4 345 1 | 29SP | T0 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | B | 336 | 30.0205 | 102.7455 |  |  |  | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
00NR | NRIS | Thermal | 640194 GOSPER 7 115 640242 JOHN.2 7 115 1 | 29SP | T0 | P42:345:NPPD:BKR-GGS-3322:::: | B | 120 | 15.9771 | 107.0786 |  |  |  | Rebuild line 640194 GOSPER 7 115 640242 JOHN.2 7 115 1
00NR | NRIS | Thermal | 640234 HUMBOLT5 161 3WXFMR 645:S975 T4 69 1 | 26SP | T0 | P12:161:OPPD:S1263-S1280:::HV: | B | 67.2 | 60.4737 | 127.5765 |  |  |  | Rebuild 3-winding transformer 640234 HUMBOLT5 161 647975 S975 8 69 648275 S975T4 9 13 1
00NR | NRIS | Thermal | 640234 HUMBOLT5 161 3WXFMR 645:S975 T4 69 1 | 29WP | T0 | P12:161:OPPD:S1263-S1280:::HV: | B | 67.2 | 69.4759 | 127.4335 |  |  |  | Rebuild 3-winding transformer 640234 HUMBOLT5 161 647975 S975 8 69 648275 S975T4 9 13 1
00NR | NRIS | Thermal | 640234 HUMBOLT5 161 3WXFMR 645:S975 T4 69 1 | 29SP | T0 | P12:161:OPPD:S1263-S1280:::HV: | B | 67.2 | 77.5921 | 151.2446 |  |  |  | Rebuild 3-winding transformer 640234 HUMBOLT5 161 647975 S975 8 69 648275 S975T4 9 13 1
00NR | NRIS | Thermal | 640250 KEARNEY7 115 640383 TOWER 7 115 1 | 29SP | T0 | P12:115:NPPD:1094:RIVERDL7:KEARNEY7 BTB | B | 160 | 83.9319 | 104.9238 |  |  |  | Rebuild line 640250 KEARNEY7 115 640383 TOWER 7 115 1
00NR | NRIS | Thermal | 640261 LOWELL 7 115 640275 MINDEN 7 115 1 | 26SP | T0 | Single 640066 AXTELL7 115 640250 KEARNEY7 115 1 | B | 128 | 82.0408 | 108.2004 |  |  |  | Rebuild line 640261 LOWELL 7 115 640275 MINDEN 7 115 1
00NR | NRIS | Thermal | 640261 LOWELL 7 115 640275 MINDEN 7 115 1 | 29SP | T0 | Single 640066 AXTELL7 115 640250 KEARNEY7 115 1 | B | 128 | 88.4296 | 119.0155 |  |  |  | Rebuild line 640261 LOWELL 7 115 640275 MINDEN 7 115 1
00NR | NRIS | Thermal | 640326 REDWILO7 115 640365 STOCKVL7 115 1 | 29SP | T0 | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | B | 140 | 20.4588 | 106.9426 |  |  |  | Rebuild line 640326 REDWILO7 115 640365 STOCKVL7 115 1
00NR | NRIS | Thermal | 645456 S3456 3 345 645458 S3458 3 345 1 | 29SP | T0 | P55:345:OPPD:S3740 3::FN13:EHV: | B | 982 | 73.9456 | 100.8193 |  |  |  | Rebuild line 645456 S3456 3 345 645458 S3458 3 345 1
00NR | NRIS | Thermal | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | 29SP | T0 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | B | 116 | 77.4703 | 109.2696 |  |  |  | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
00NR | NRIS | Thermal | 647101 AUBRNT 8 69 647975 S975 8 69 1 | 29SP | T0 | P12:161:OPPD:S1263-S1280:::HV: | B | 72 | 42.3428 | 104.2456 |  |  |  | Rebuild line 647101 AUBRNT 8 69 647975 S975 8 69 1
00NR | NRIS | Thermal | 647111 W BROCK8 69 647963 S963 8 69 1 | 29SP | T0 | P13:069-161:OPPD:S975 T4:::HV: | B | 96 | 76.3953 | 105.3743 |  |  |  | Rebuild line 647111 W BROCK8 69 647963 S963 8 69 1
00NR | NRIS | Thermal | 647975 S975 8 69 3WXFMR 645:S975 T4 69 1 | 26SP | T0 | P12:161:OPPD:S1263-S1280:::HV: | B | 67.2 | 60.2291 | 126.9703 |  |  |  | Rebuild 3-winding transformer 640234 HUMBOLT5 161 647975 S975 8 69 648275 S975T4 9 13 1
00NR | NRIS | Thermal | 647975 S975 8 69 3WXFMR 645:S975 T4 69 1 | 29WP | T0 | P12:161:OPPD:S1263-S1280:::HV: | B | 67.2 | 69.2271 | 126.8053 |  |  |  | Rebuild 3-winding transformer 640234 HUMBOLT5 161 647975 S975 8 69 648275 S975T4 9 13 1
00NR | NRIS | Thermal | 647975 S975 8 69 3WXFMR 645:S975 T4 69 1 | 29SP | T0 | P12:161:OPPD:S1263-S1280:::HV: | B | 67.2 | 77.234 | 149.8427 |  |  |  | Rebuild 3-winding transformer 640234 HUMBOLT5 161 647975 S975 8 69 648275 S975T4 9 13 1
00NR | NRIS | Thermal | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | 29SP | T0 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | B | 120 | 76.5691 | 107.5367 |  |  |  | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
00NR | NRIS | Thermal | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | 29SP | T0 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | B | 120 | 76.5691 | 107.5367 |  |  |  | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
00NR | NRIS | Thermal | 652216 WATFORD4 230 659302 CHARL_CK-BE4 230 1 | 29WP | T0 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | B | 538 | 70.0302 | 100.5661 |  |  |  | Rebuild line 652216 WATFORD4 230 659302 CHARL_CK-BE4 230 1
00NR | NRIS | Thermal | 652216 WATFORD4 230 659302 CHARL_CK-BE4 230 1 | 29SP | T0 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | B | 400 | 47.6335 | 104.7031 |  |  |  | Rebuild line 652216 WATFORD4 230 659302 CHARL_CK-BE4 230 1
00NR | NRIS | Thermal | 652296 WARD 4 230 652426 BISMARK4 230 1 | 29SP | T0 | Single 608607 NELSNLK4 230 615901 GRE-STANTON4 230 1 | B | 331 | 73.5809 | 111.5472 |  |  |  | Rebuild line 652296 WARD 4 230 652426 BISMARK4 230 1
00NR | NRIS | Thermal | 652424 BELFELD3 345 659183 CHARL_CK-BE3 345 1 | 29WP | T0 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | B | 531 | 121.6361 | 104.94 |  |  |  | Rebuild line 652424 BELFELD3 345 659183 CHARL_CK-BE3 345 1
00NR | NRIS | Thermal | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 | 26SP | T0 | P12:345:OTP:CENTER3:COYOTE3:1 RAS OFF:EHV: | B | 119 | 124.0329 | 147.0496 |  |  |  | Rebuild line 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1
00NR | NRIS | Thermal | 652497 MAURINE4 230 785430 G24-282-TAP 230 1 | 29SP | T0 | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | B | 305 | 43.2596 | 138.2724 |  |  |  | Rebuild line 652497 MAURINE4 230 785430 G24-282-TAP 230 1
00NR | NRIS | Thermal | 652497 MAURINE4 230 785430 G24-282-TAP 230 1 | 29WP | T0 | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | B | 398 | 70.8098 | 134.2172 |  |  |  | Rebuild line 652497 MAURINE4 230 785430 G24-282-TAP 230 1
00NR | NRIS | Thermal | 652515 HURON 7 115 660009 HUR B TAP 115 1 | 29WP | T0 | P12:230:MDU:ELLENDALE:ELLENDALE345:Z: | B | 120 | 90.4821 | 100.6173 |  |  |  | Rebuild line 652515 HURON 7 115 660009 HUR B TAP 115 1
00NR | NRIS | Thermal | 652552 SIOUXCY2 230 3WXFMR 652:652: SC2 KU1B 230 1 | 26SP | T0 | System Intact | A | 600 | 59.3539 | 104.6808 |  |  |  | Add 3-winding transformer 652305 SIOUXC29 13 652552 SIOUXCY2 230 652564 SIOUXCY3 345 M2
00NR | NRIS | Thermal | 652552 SIOUXCY2 230 3WXFMR 652:652: SC2 KU1B 230 1 | 29SP | T0 | System Intact | A | 600 | 53.2383 | 101.4088 |  |  |  | Add 3-winding transformer 652305 SIOUXC29 13 652552 SIOUXCY2 230 652564 SIOUXCY3 345 M2
00NR | NRIS | Thermal | 652564 SIOUXCY3 345 3WXFMR 652:652: SC2 KU1B 230 1 | 26SP | T0 | System Intact | A | 600 | 59.3539 | 104.6217 |  |  |  | Add 3-winding transformer 652305 SIOUXC29 13 652552 SIOUXCY2 230 652564 SIOUXCY3 345 M2
00NR | NRIS | Thermal | 652564 SIOUXCY3 345 3WXFMR 652:652: SC2 KU1B 230 1 | 29SP | T0 | System Intact | A | 600 | 53.2383 | 101.3435 |  |  |  | Add 3-winding transformer 652305 SIOUXC29 13 652552 SIOUXCY2 230 652564 SIOUXCY3 345 M2
00NR | NRIS | Thermal | 659105 LELAND_O-BE3 345 3WXFMR 659:LOS KU1A 230 1 | 29WP | T0 | P13:345-230.0:UMZ:# N-1 #:: 3WND LELAND_O-BE3-LELAND_O-BE4-LO.KVA2_-BE9-1 LOS KV2A:EHV: | B | 637.4 | 100.1737 | 104.1439 |  |  |  | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659201 LO.KU1A_-BE9 13 M2
00NR | NRIS | Thermal | 659105 LELAND_O-BE3 345 3WXFMR 659:LOS KV2A 230 1 | 29WP | T0 | P13:345-230.0:UMZ:# N-1 #:: 3WND LELAND_O-BE3-LELAND_O-BE4-LO.KU1A_-BE9-1 LOS KU1A:EHV: | B | 617 | 101.5575 | 105.761 |  |  |  | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659202 LO.KVA2_-BE9 13 M2
00NR | NRIS | Thermal | 659106 LELAND_O-BE4 230 3WXFMR 659:LOS KU1A 230 1 | 29WP | T0 | P13:345-230.0:UMZ:# N-1 #:: 3WND LELAND_O-BE3-LELAND_O-BE4-LO.KVA2_-BE9-1 LOS KV2A:EHV: | B | 637 | 101.4257 | 105.0302 |  |  |  | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659201 LO.KU1A_-BE9 13 M2
00NR | NRIS | Thermal | 659106 LELAND_O-BE4 230 3WXFMR 659:LOS KV2A 230 1 | 29WP | T0 | P13:345-230.0:UMZ:# N-1 #:: 3WND LELAND_O-BE3-LELAND_O-BE4-LO.KU1A_-BE9-1 LOS KU1A:EHV: | B | 617 | 102.281 | 106.1455 |  |  |  | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659202 LO.KVA2_-BE9 13 M2
00NR | NRIS | Thermal | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 | 26SP | T0 | P12:345:OTP:CENTER3:COYOTE3:1 RAS OFF:EHV: | B | 119 | 124.9784 | 148.3193 |  |  |  | Rebuild line 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1
00NR | NRIS | Thermal | 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 | 26SP | T0 | P12:345:OTP:CENTER3:COYOTE3:1 RAS OFF:EHV: | B | 120 | 124.2949 | 147.864 |  |  |  | Rebuild line 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1
01ALL | ERIS | Thermal | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 29SP | T0 | P12:345:OTP:JAMESTN3:CENTER3:1 | B | 341 | 79.9953 | 106.6856 |  |  |  | Rebuild line 602006 SHEYNNE4 230 652435 FARGO 4 230 1
01ALL | ERIS | Thermal | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 26SP | T0 | P12:345:OTP:BUFFALO3:JAMESTN3:1 | B | 341 | 100.3381 | 130.388 |  |  |  | Rebuild line 602006 SHEYNNE4 230 652435 FARGO 4 230 1
01ALL | ERIS | Thermal | 620263 FORMN 7 115 652438 FORMAN 7 115 1 | 26SP | T0 | P12:230:MDU:NAPOLEON SW:WISHEK:1: | B | 126 | 8.0397 | 121.4081 |  |  |  | Rebuild line 620263 FORMN 7 115 652438 FORMAN 7 115 1
01ALL | ERIS | Thermal | 620263 FORMN 7 115 652438 FORMAN 7 115 1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | B | 126 | -13.5539 | 110.458 |  |  |  | Rebuild line 620263 FORMN 7 115 652438 FORMAN 7 115 1
01ALL | ERIS | Thermal | 640404 WAYSIDE 4 230 652484 NUNDRWD4 230 1 | 26SP | T0 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | B | 341 | 70.1322 | 115.3235 |  |  |  | Rebuild line 640404 WAYSIDE 4 230 652484 NUNDRWD4 230 1
01ALL | ERIS | Thermal | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 26SP | T0 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | B | 842 | 84.3968 | 104.9348 |  |  |  | Rebuild line 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
01ALL | ERIS | Thermal | 652200 GLENDIVE7 115 652404 DAWSONC7 115 1 | 26SP | T0 | P21:230:MDU:LITTLE MISSOURI:RHAME:1: | B | 132 | 30.7579 | 101.5056 |  |  |  | Rebuild line 652200 GLENDIVE7 115 652404 DAWSONC7 115 1
01ALL | ERIS | Thermal | 652200 GLENDIVE7 115 661032 GLENDCT7 115 1 | 26SP | T0 | P21:230:MDU:LITTLE MISSOURI:RHAME:1: | B | 111 | 37.1766 | 121.385 |  |  |  | Rebuild line 652200 GLENDIVE7 115 661032 GLENDCT7 115 1
01ALL | ERIS | Thermal | 652403 DAWSONC4 230 652411 MI CTYE4 230 1 | 26SP | T0 | P21:230:MDU:LITTLE MISSOURI:RHAME:1: | B | 315 | 11.5664 | 106.7801 |  |  |  | Rebuild line 652403 DAWSONC4 230 652411 MI CTYE4 230 1
01ALL | ERIS | Thermal | 652403 DAWSONC4 230 652616 MINGUSVILLE4 230 1 | 26SP | T0 | P21:230:MDU:LITTLE MISSOURI:RHAME:1: | B | 315 | 23.2462 | 110.0138 |  |  |  | Rebuild line 652403 DAWSONC4 230 652616 MINGUSVILLE4 230 1
01ALL | ERIS | Thermal | 652404 DAWSONC7 115 661056 LEWIS 7 115 1 | 26SP | T0 | P21:230:MDU:LITTLE MISSOURI:RHAME:1: | B | 107 | 47.6721 | 135.54 |  |  |  | Rebuild line 652404 DAWSONC7 115 661056 LEWIS 7 115 1
01ALL | ERIS | Thermal | 652424 BELFELD3 345 3WXFMR 652:652: BEF KU1A 230 1 | 26SP | T0 | P13:345-230.0:UMZ:# N-1 #:: 3WND BELFELD3-BELFELD4-BELFELD29-1 652_ BEF KU2A_:EHV: | B | 390 | 66.4331 | 124.4221 |  |  |  | Add 3-winding transformer 652221 BELFELD9 13 652424 BELFELD3 345 652425 BELFELD4 230 M2
01ALL | ERIS | Thermal | 652424 BELFELD3 345 3WXFMR 659:652: BEF KU2A 230 1 | 26SP | T0 | P13:345-230.0:UMZ:# N-1 #:: 3WND BELFELD3-BELFELD4-BELFELD9-1 652_ BEF KU1A_:EHV: | B | 312 | 85.8894 | 162.4558 |  |  |  | Add 3-winding transformer 652220 BELFELD29 13 652424 BELFELD3 345 652425 BELFELD4 230 M2
01ALL | ERIS | Thermal | 652424 BELFELD3 345 3WXFMR 659:652: BEF KU2A 230 1 | 29SP | T0 | P13:345-230.0:UMZ:# N-1 #:: 3WND BELFELD3-BELFELD4-BELFELD9-1 652_ BEF KU1A_:EHV: | B | 312 | 44.8669 | 100.228 |  |  |  | Add 3-winding transformer 652220 BELFELD29 13 652424 BELFELD3 345 652425 BELFELD4 230 M2
01ALL | ERIS | Thermal | 652424 BELFELD3 345 3WXFMR 659:652: BEF KU2A 230 1 | 29WP | T0 | P13:345-230.0:UMZ:# N-1 #:: 3WND BELFELD3-BELFELD4-BELFELD9-1 652_ BEF KU1A_:EHV: | B | 312 | 60.4414 | 122.3521 |  |  |  | Add 3-winding transformer 652220 BELFELD29 13 652424 BELFELD3 345 652425 BELFELD4 230 M2
01ALL | ERIS | Thermal | 652425 BELFELD4 230 3WXFMR 652:652: BEF KU1A 230 1 | 26SP | T0 | P13:345-230.0:UMZ:# N-1 #:: 3WND BELFELD3-BELFELD4-BELFELD29-1 652_ BEF KU2A_:EHV: | B | 390 | 62.9553 | 120.4414 |  |  |  | Add 3-winding transformer 652221 BELFELD9 13 652424 BELFELD3 345 652425 BELFELD4 230 M2
01ALL | ERIS | Thermal | 652425 BELFELD4 230 3WXFMR 659:652: BEF KU2A 230 1 | 26SP | T0 | P13:345-230.0:UMZ:# N-1 #:: 3WND BELFELD3-BELFELD4-BELFELD9-1 652_ BEF KU1A_:EHV: | B | 312 | 85.7467 | 161.9731 |  |  |  | Add 3-winding transformer 652220 BELFELD29 13 652424 BELFELD3 345 652425 BELFELD4 230 M2
01ALL | ERIS | Thermal | 652425 BELFELD4 230 3WXFMR 659:652: BEF KU2A 230 1 | 29SP | T0 | P13:345-230.0:UMZ:# N-1 #:: 3WND BELFELD3-BELFELD4-BELFELD9-1 652_ BEF KU1A_:EHV: | B | 312 | 44.8181 | 100.0345 |  |  |  | Add 3-winding transformer 652220 BELFELD29 13 652424 BELFELD3 345 652425 BELFELD4 230 M2
01ALL | ERIS | Thermal | 652425 BELFELD4 230 3WXFMR 659:652: BEF KU2A 230 1 | 29WP | T0 | P13:345-230.0:UMZ:# N-1 #:: 3WND BELFELD3-BELFELD4-BELFELD9-1 652_ BEF KU1A_:EHV: | B | 312 | 60.3668 | 122.0819 |  |  |  | Add 3-winding transformer 652220 BELFELD29 13 652424 BELFELD3 345 652425 BELFELD4 230 M2
01ALL | ERIS | Thermal | 652425 BELFELD4 230 659247 MEDORA__-UM4 230 1 | 26SP | T0 | P21:230:MDU:LITTLE MISSOURI:RHAME:1: | B | 319 | 43.9477 | 130.5464 |  |  |  | Rebuild line 652425 BELFELD4 230 659247 MEDORA__-UM4 230 1
01ALL | ERIS | Thermal | 652484 NUNDRWD4 230 652884 NUNDRWD-LNX3 230 Z | 26SP | T0 | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | B | 305 | 40.2939 | 160.3158 |  |  |  | Rebuild line 652484 NUNDRWD4 230 652884 NUNDRWD-LNX3 230 Z
01ALL | ERIS | Thermal | 652484 NUNDRWD4 230 652884 NUNDRWD-LNX3 230 Z | 29SP | T0 | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | B | 305 | 12.2307 | 127.5703 |  |  |  | Rebuild line 652484 NUNDRWD4 230 652884 NUNDRWD-LNX3 230 Z
01ALL | ERIS | Thermal | 652497 MAURINE4 230 659351 BISON___-GE4 230 1 | 26SP | T0 | P12:230.0:UMZ:# N-1 #:: LINE BELFELD4-DAGLUM__-BE4-1 :HV: | B | 305 | 60.2503 | 105.042 |  |  |  | Rebuild line 652497 MAURINE4 230 659351 BISON___-GE4 230 1
01ALL | ERIS | Thermal | 652512 GROTON 7 115 652568 GROTONSOUTH7 115 Z | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | B | 399 | 65.4342 | 111.2209 |  |  |  | Rebuild line 652512 GROTON 7 115 652568 GROTONSOUTH7 115 Z
01ALL | ERIS | Thermal | 652512 GROTON 7 115 652568 GROTONSOUTH7 115 Z | 26SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | B | 399 | 71.3191 | 116.6347 |  |  |  | Rebuild line 652512 GROTON 7 115 652568 GROTONSOUTH7 115 Z
01ALL | ERIS | Thermal | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 29L | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | B | 119 | 78.0588 | 100.3794 |  |  |  | Rebuild line 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1
01ALL | ERIS | Thermal | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | B | 119 | 88.041 | 153.9189 |  |  |  | Rebuild line 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1
01ALL | ERIS | Thermal | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 29WP | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | B | 159 | 48.526 | 103.7534 |  |  |  | Rebuild line 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1
01ALL | ERIS | Thermal | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 26SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | B | 119 | 95.1123 | 161.6909 |  |  |  | Rebuild line 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1
01ALL | ERIS | Thermal | 652512 GROTON 7 115 660001 ABR SIEBRCHT 115 1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | B | 180.3 | 66.6376 | 123.4253 |  |  |  | Rebuild line 652512 GROTON 7 115 660001 ABR SIEBRCHT 115 1
01ALL | ERIS | Thermal | 652512 GROTON 7 115 660001 ABR SIEBRCHT 115 1 | 29WP | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | B | 180.3 | 42.7352 | 102.1338 |  |  |  | Rebuild line 652512 GROTON 7 115 660001 ABR SIEBRCHT 115 1
01ALL | ERIS | Thermal | 652512 GROTON 7 115 660001 ABR SIEBRCHT 115 1 | 26SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | B | 180.3 | 75.2516 | 132.6157 |  |  |  | Rebuild line 652512 GROTON 7 115 660001 ABR SIEBRCHT 115 1
01ALL | ERIS | Thermal | 652515 HURON 7 115 655481 REDFELD-ER7 115 1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | B | 121 | 45.6046 | 104.8409 |  |  |  | Rebuild line 652515 HURON 7 115 655481 REDFELD-ER7 115 1
01ALL | ERIS | Thermal | 652515 HURON 7 115 655481 REDFELD-ER7 115 1 | 26SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | B | 121 | 52.4824 | 110.5965 |  |  |  | Rebuild line 652515 HURON 7 115 655481 REDFELD-ER7 115 1
01ALL | ERIS | Thermal | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | B | 130 | 49.5964 | 108.8234 |  |  |  | Rebuild line 652522 SUMMIT-7 115 652531 WATERTN7 115 1
01ALL | ERIS | Thermal | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 | 26SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | B | 130 | 52.1132 | 111.5678 |  |  |  | Rebuild line 652522 SUMMIT-7 115 652531 WATERTN7 115 1
01ALL | ERIS | Thermal | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | B | 119 | 81.1523 | 146.8444 |  |  |  | Rebuild line 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1
01ALL | ERIS | Thermal | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | 26SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | B | 119 | 88.2809 | 154.6716 |  |  |  | Rebuild line 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1
01ALL | ERIS | Thermal | 652529 WATERTN3 345 3WXFMR 652:652: WT2 KU1A 230 1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-WATERTN-LNX3-Z :EHV: | B | 478 | 66.5466 | 135.3227 |  |  |  | Add 3-winding transformer 652237 WATERT19 13 652529 WATERTN3 345 652530 WATERTN4 230 M2
01ALL | ERIS | Thermal | 652529 WATERTN3 345 3WXFMR 652:652: WT2 KU1A 230 1 | 29WP | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-WATERTN-LNX3-Z :EHV: | B | 478 | 44.52 | 120.9803 |  |  |  | Add 3-winding transformer 652237 WATERT19 13 652529 WATERTN3 345 652530 WATERTN4 230 M2
01ALL | ERIS | Thermal | 652529 WATERTN3 345 3WXFMR 652:652: WT2 KU1A 230 1 | 26SP | T0 | P23:345:UMZW:# 823 #:: WH IN SD. :EHV: | B | 478 | 72.8228 | 139.9279 |  |  |  | Add 3-winding transformer 652237 WATERT19 13 652529 WATERTN3 345 652530 WATERTN4 230 M2
01ALL | ERIS | Thermal | 652529 WATERTN3 345 659165 CROCKER_-BE3 345 1 | 29SP | T0 | P12:115.0:UMZ:# N-1 #:: LINE GROTONSOUTH7-GROTON__-BE7-1 :HV: | B | 717 | 51.6107 | 122.8213 |  |  |  | Rebuild line 652529 WATERTN3 345 659165 CROCKER_-BE3 345 1
01ALL | ERIS | Thermal | 652529 WATERTN3 345 659165 CROCKER_-BE3 345 1 | 26SP | T0 | P12:115.0:UMZ:# N-1 #:: LINE GROTONSOUTH7-GROTON__-BE7-1 :HV: | B | 717 | 57.7684 | 128.6156 |  |  |  | Rebuild line 652529 WATERTN3 345 659165 CROCKER_-BE3 345 1
01ALL | ERIS | Thermal | 652529 WATERTN3 345 659165 CROCKER_-BE3 345 1 | 29WP | T0 | P12:115.0:UMZ:# N-1 #:: LINE GROTON 7-GROTONSOUTH7-Z :HV: | B | 717 | 38.0969 | 104.477 |  |  |  | Rebuild line 652529 WATERTN3 345 659165 CROCKER_-BE3 345 1
01ALL | ERIS | Thermal | 652530 WATERTN4 230 3WXFMR 652:652: WT2 KU1A 230 1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-WATERTN-LNX3-Z :EHV: | B | 478 | 66.9294 | 137.5282 |  |  |  | Add 3-winding transformer 652237 WATERT19 13 652529 WATERTN3 345 652530 WATERTN4 230 M2
01ALL | ERIS | Thermal | 652530 WATERTN4 230 3WXFMR 652:652: WT2 KU1A 230 1 | 29WP | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-WATERTN-LNX3-Z :EHV: | B | 478 | 44.6381 | 122.7057 |  |  |  | Add 3-winding transformer 652237 WATERT19 13 652529 WATERTN3 345 652530 WATERTN4 230 M2
01ALL | ERIS | Thermal | 652530 WATERTN4 230 3WXFMR 652:652: WT2 KU1A 230 1 | 26SP | T0 | P23:345:UMZW:# 823 #:: WH IN SD. :EHV: | B | 478 | 73.3612 | 142.3054 |  |  |  | Add 3-winding transformer 652237 WATERT19 13 652529 WATERTN3 345 652530 WATERTN4 230 M2
01ALL | ERIS | Thermal | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 26SP | T0 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | B | 842 | 84.0149 | 104.273 |  |  |  | Rebuild line 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
01ALL | ERIS | Thermal | 652568 GROTONSOUTH7 115 655481 REDFELD-ER7 115 1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | B | 121 | 53.1702 | 114.5123 |  |  |  | Rebuild line 652568 GROTONSOUTH7 115 655481 REDFELD-ER7 115 1
01ALL | ERIS | Thermal | 652568 GROTONSOUTH7 115 655481 REDFELD-ER7 115 1 | 26SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | B | 121 | 59.8971 | 120.2611 |  |  |  | Rebuild line 652568 GROTONSOUTH7 115 655481 REDFELD-ER7 115 1
01ALL | ERIS | Thermal | 652568 GROTONSOUTH7 115 659187 GROTON__-BE7 115 1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | B | 407 | 49.7916 | 136.9816 |  |  |  | Add line and rebuild line 652568 GROTONSOUTH7 115 659187 GROTON__-BE7 115 M2
01ALL | ERIS | Thermal | 652568 GROTONSOUTH7 115 659187 GROTON__-BE7 115 1 | 29WP | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | B | 438 | 26.8757 | 110.6611 |  |  |  | Add line and rebuild line 652568 GROTONSOUTH7 115 659187 GROTON__-BE7 115 M2
01ALL | ERIS | Thermal | 652568 GROTONSOUTH7 115 659187 GROTON__-BE7 115 1 | 26SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | B | 407 | 58.9858 | 146.8862 |  |  |  | Add line and rebuild line 652568 GROTONSOUTH7 115 659187 GROTON__-BE7 115 M2
01ALL | ERIS | Thermal | 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1 | 26SP | T0 | P21:230:MDU:LITTLE MISSOURI:RHAME:1: | B | 319 | 48.0686 | 134.4452 |  |  |  | Rebuild line 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1
01ALL | ERIS | Thermal | 652884 NUNDRWD-LNX3 230 785430 G24-282-TAP 230 1 | 26SP | T0 | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | B | 305 | 39.2153 | 158.6462 |  |  |  | Rebuild line 652884 NUNDRWD-LNX3 230 785430 G24-282-TAP 230 1
01ALL | ERIS | Thermal | 652884 NUNDRWD-LNX3 230 785430 G24-282-TAP 230 1 | 29SP | T0 | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | B | 305 | 11.7109 | 126.0562 |  |  |  | Rebuild line 652884 NUNDRWD-LNX3 230 785430 G24-282-TAP 230 1
01ALL | ERIS | Thermal | 659106 LELAND_O-BE4 230 659199 BASIN___-BE4 230 1 | 29L | T0 | P13:230-115.0:UMZ:# N-1 #:: 3WND BASIN___-BE4-BASIN___-BE7-BAL.KY1A-BE9-1 KY1A _1:HV: | B | 425 | 44.8439 | 141.6469 |  |  |  | Rebuild line 659106 LELAND_O-BE4 230 659199 BASIN___-BE4 230 1
01ALL | ERIS | Thermal | 659106 LELAND_O-BE4 230 659199 BASIN___-BE4 230 1 | 29SP | T0 | P13:230-115.0:UMZ:# N-1 #:: 3WND BASIN___-BE4-BASIN___-BE7-BAL.KY1A-BE9-1 KY1A _1:HV: | B | 425 | 44.9764 | 142.0204 |  |  |  | Rebuild line 659106 LELAND_O-BE4 230 659199 BASIN___-BE4 230 1
01ALL | ERIS | Thermal | 659106 LELAND_O-BE4 230 659199 BASIN___-BE4 230 1 | 29WP | T0 | P13:230-115.0:UMZ:# N-1 #:: 3WND BASIN___-BE4-BASIN___-BE7-BAL.KY1A-BE9-1 KY1A _1:HV: | B | 478 | 40.1907 | 126.2938 |  |  |  | Rebuild line 659106 LELAND_O-BE4 230 659199 BASIN___-BE4 230 1
01ALL | ERIS | Thermal | 659106 LELAND_O-BE4 230 659199 BASIN___-BE4 230 1 | 26SP | T0 | P13:230-115.0:UMZ:# N-1 #:: 3WND BASIN___-BE4-BASIN___-BE7-BAL.KY1A-BE9-1 KY1A _1:HV: | B | 425 | 45.0898 | 142.3874 |  |  |  | Rebuild line 659106 LELAND_O-BE4 230 659199 BASIN___-BE4 230 1
01ALL | ERIS | Thermal | 659120 BROADLND-BE3 345 3WXFMR 659:BD KU2A 230 1 | 26SP | T0 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV: | B | 478 | 53.7623 | 111.6654 |  |  |  | Add 3-winding transformer 659120 BROADLND-BE3 345 659204 BD.KU2A_-BE9 13 659205 BROADLND-BE4 230 M2
01ALL | ERIS | Thermal | 659120 BROADLND-BE3 345 3WXFMR 659:BD KU2A 230 1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM1-LNX3-Z :EHV: | B | 478 | 42.5441 | 101.8019 |  |  |  | Add 3-winding transformer 659120 BROADLND-BE3 345 659204 BD.KU2A_-BE9 13 659205 BROADLND-BE4 230 M2
01ALL | ERIS | Thermal | 659160 GROTON__-BE3 345 3WXFMR 659:GROTON KU2A 115 1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | B | 400 | 51.3019 | 137.0995 |  |  |  | Add 3-winding transformer 659160 GROTON__-BE3 345 659161 GRT.KU2A-BE9 13 659187 GROTON__-BE7 115 M2
01ALL | ERIS | Thermal | 659160 GROTON__-BE3 345 3WXFMR 659:GROTON KU2A 115 1 | 29WP | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | B | 400 | 29.8735 | 119.9097 |  |  |  | Add 3-winding transformer 659160 GROTON__-BE3 345 659161 GRT.KU2A-BE9 13 659187 GROTON__-BE7 115 M2
01ALL | ERIS | Thermal | 659160 GROTON__-BE3 345 3WXFMR 659:GROTON KU2A 115 1 | 26SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | B | 400 | 60.5874 | 146.7481 |  |  |  | Add 3-winding transformer 659160 GROTON__-BE3 345 659161 GRT.KU2A-BE9 13 659187 GROTON__-BE7 115 M2
01ALL | ERIS | Thermal | 659187 GROTON__-BE7 115 3WXFMR 659:GROTON KU2A 115 1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | B | 400 | 51.336 | 136.9338 |  |  |  | Add 3-winding transformer 659160 GROTON__-BE3 345 659161 GRT.KU2A-BE9 13 659187 GROTON__-BE7 115 M2
01ALL | ERIS | Thermal | 659187 GROTON__-BE7 115 3WXFMR 659:GROTON KU2A 115 1 | 29WP | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | B | 400 | 29.9054 | 119.9938 |  |  |  | Add 3-winding transformer 659160 GROTON__-BE3 345 659161 GRT.KU2A-BE9 13 659187 GROTON__-BE7 115 M2
01ALL | ERIS | Thermal | 659187 GROTON__-BE7 115 3WXFMR 659:GROTON KU2A 115 1 | 26SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | B | 400 | 60.6351 | 146.6298 |  |  |  | Add 3-winding transformer 659160 GROTON__-BE3 345 659161 GRT.KU2A-BE9 13 659187 GROTON__-BE7 115 M2
01ALL | ERIS | Thermal | 659205 BROADLND-BE4 230 3WXFMR 659:BD KU2A 230 1 | 26SP | T0 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV: | B | 478 | 53.7623 | 111.6654 |  |  |  | Add 3-winding transformer 659120 BROADLND-BE3 345 659204 BD.KU2A_-BE9 13 659205 BROADLND-BE4 230 M2
01ALL | ERIS | Thermal | 659205 BROADLND-BE4 230 3WXFMR 659:BD KU2A 230 1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM1-LNX3-Z :EHV: | B | 478 | 42.5441 | 101.8019 |  |  |  | Add 3-winding transformer 659120 BROADLND-BE3 345 659204 BD.KU2A_-BE9 13 659205 BROADLND-BE4 230 M2
01ALL | ERIS | Thermal | 659265 LITTL_MS-BE4 230 659266 RHAME___-BE4 230 1 | 26SP | T0 | Single 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1 | B | 383 | 28.0077 | 112.1119 |  |  |  | Rebuild line 659265 LITTL_MS-BE4 230 659266 RHAME___-BE4 230 1
02ALL | ERIS | Thermal | 532913 KELLY 5 161 3WXFMR 536:KELLY TX-1 115 1 | 26SP | T0 | Single 640140 COOPER5 161 778110 G24-038-TAP 161 1 | B | 122 | 48.2001 | 159.6532 |  |  |  | Add 3-winding transformer 532913 KELLY 5 161 532942 KELLY 1 13 533217 KELLY 3 115 M2
02ALL | ERIS | Thermal | 532913 KELLY 5 161 3WXFMR 536:KELLY TX-1 115 1 | 29SP | T0 | Single 640140 COOPER5 161 778110 G24-038-TAP 161 1 | B | 122 | 34.239 | 144.6839 |  |  |  | Add 3-winding transformer 532913 KELLY 5 161 532942 KELLY 1 13 533217 KELLY 3 115 M2
02ALL | ERIS | Thermal | 532913 KELLY 5 161 3WXFMR 536:KELLY TX-1 115 1 | 29WP | T0 | Single 532920 TECHILL5 161 533181 TECHILW3 115 533885 'TECHIL4X ' 12 1 | B | 122 | 50.2563 | 135.5586 |  |  |  | Add 3-winding transformer 532913 KELLY 5 161 532942 KELLY 1 13 533217 KELLY 3 115 M2
02ALL | ERIS | Thermal | 532913 KELLY 5 161 532920 TECHILL5 161 1 | 29WP | T0 | Single 532913 KELLY5 161 533217 KELLY3 115 532942 'KELLY 1 ' 13 1 | B | 121 | 51.0502 | 123.2348 |  |  |  | Rebuild line 532913 KELLY 5 161 532920 TECHILL5 161 1
02ALL | ERIS | Thermal | 532913 KELLY 5 161 532920 TECHILL5 161 1 | 26SP | T0 | Single 532913 KELLY5 161 533217 KELLY3 115 532942 'KELLY 1 ' 13 1 | B | 121 | 61.1095 | 127.4786 |  |  |  | Rebuild line 532913 KELLY 5 161 532920 TECHILL5 161 1
02ALL | ERIS | Thermal | 532913 KELLY 5 161 532920 TECHILL5 161 1 | 29SP | T0 | Single 532913 KELLY5 161 533217 KELLY3 115 532942 'KELLY 1 ' 13 1 | B | 121 | 37.7494 | 102.0467 |  |  |  | Rebuild line 532913 KELLY 5 161 532920 TECHILL5 161 1
02ALL | ERIS | Thermal | 533210 ENEMEHA3 115 533217 KELLY 3 115 1 | 26SP | T0 | Single 640140 COOPER5 161 778110 G24-038-TAP 161 1 | B | 90 | 59.0998 | 111.0051 |  |  |  | Rebuild line 533210 ENEMEHA3 115 533217 KELLY 3 115 1
02ALL | ERIS | Thermal | 533217 KELLY 3 115 3WXFMR 536:KELLY TX-1 115 1 | 26SP | T0 | Single 640140 COOPER5 161 778110 G24-038-TAP 161 1 | B | 183 | 31.9108 | 106.4355 |  |  |  | Add 3-winding transformer 532913 KELLY 5 161 532942 KELLY 1 13 533217 KELLY 3 115 M2
02ALL | ERIS | Thermal | 640140 COOPER 5 161 778110 G24-038-TAP 161 1 | 26SP | T0 | P12:161:WERE-OPPD:S1399-KELLY:::HV: | B | 295 | -4.6946 | 134.7489 |  |  |  | Rebuild line 640140 COOPER 5 161 778110 G24-038-TAP 161 1
02ALL | ERIS | Thermal | 640140 COOPER 5 161 778110 G24-038-TAP 161 1 | 29SP | T0 | P12:161:WERE-OPPD:S1399-KELLY:::HV: | B | 295 | -12.5956 | 125.2361 |  |  |  | Rebuild line 640140 COOPER 5 161 778110 G24-038-TAP 161 1
02ALL | ERIS | Thermal | 640140 COOPER 5 161 778110 G24-038-TAP 161 1 | 29WP | T0 | P12:161:WERE-OPPD:S1399-KELLY:::HV: | B | 295 | -12.2747 | 126.7648 |  |  |  | Rebuild line 640140 COOPER 5 161 778110 G24-038-TAP 161 1
02ALL | ERIS | Thermal | 640173 FREMONT7 115 3WXFMR 640:FREMONT T1 115 1 | 26SP | T0 | P13:069-115:NPPD:FREMONT T4:::HV: | B | 63 | 32.6278 | 124.1428 |  |  |  | Add 3-winding transformer 640173 FREMONT7 115 643058 FREMONT T1 9 13 647976 S976 8 69 M2
02ALL | ERIS | Thermal | 640173 FREMONT7 115 3WXFMR 640:FREMONT T1 115 1 | 29SP | T0 | P13:069-115:NPPD:FREMONT T4:::HV: | B | 63 | 33.172 | 126.7414 |  |  |  | Add 3-winding transformer 640173 FREMONT7 115 643058 FREMONT T1 9 13 647976 S976 8 69 M2
02ALL | ERIS | Thermal | 640173 FREMONT7 115 3WXFMR 640:FREMONT T1 115 1 | 29WP | T0 | P13:069-115:NPPD:FREMONT T4:::HV: | B | 63 | 37.244 | 125.8835 |  |  |  | Add 3-winding transformer 640173 FREMONT7 115 643058 FREMONT T1 9 13 647976 S976 8 69 M2
02ALL | ERIS | Thermal | 640173 FREMONT7 115 3WXFMR 640:FREMONT T4 115 1 | 26SP | T0 | Single 647976 S9768 69 640173 FREMONT7 115 643058 'FREMONT T1 9' 13 1 | B | 56 | 30.8212 | 131.3105 |  |  |  | Add 3-winding transformer 640173 FREMONT7 115 643059 FREMONT T4 9 13 647976 S976 8 69 M2
02ALL | ERIS | Thermal | 640173 FREMONT7 115 3WXFMR 640:FREMONT T4 115 1 | 29SP | T0 | Single 647976 S9768 69 640173 FREMONT7 115 643058 'FREMONT T1 9' 13 1 | B | 56 | 31.1668 | 134.031 |  |  |  | Add 3-winding transformer 640173 FREMONT7 115 643059 FREMONT T4 9 13 647976 S976 8 69 M2
02ALL | ERIS | Thermal | 640173 FREMONT7 115 3WXFMR 640:FREMONT T4 115 1 | 29WP | T0 | Single 647976 S9768 69 640173 FREMONT7 115 643058 'FREMONT T1 9' 13 1 | B | 56 | 37.5044 | 133.5794 |  |  |  | Add 3-winding transformer 640173 FREMONT7 115 643059 FREMONT T4 9 13 647976 S976 8 69 M2
02ALL | ERIS | Thermal | 640316 PAWNEEL7 115 640340 SEWARD 7 115 1 | 26SP | T0 | P12:115:NPPD:L1156B::NW68&HOLDREGE.PAWNEELAKE.CKT1:: | B | 140 | -8.8097 | 130.9896 |  |  |  | Rebuild line 640316 PAWNEEL7 115 640340 SEWARD 7 115 1
02ALL | ERIS | Thermal | 640316 PAWNEEL7 115 640340 SEWARD 7 115 1 | 29SP | T0 | P12:115:NPPD:L1156B::NW68&HOLDREGE.PAWNEELAKE.CKT1:: | B | 140 | -9.2984 | 130.7248 |  |  |  | Rebuild line 640316 PAWNEEL7 115 640340 SEWARD 7 115 1
02ALL | ERIS | Thermal | 640316 PAWNEEL7 115 640340 SEWARD 7 115 1 | 29WP | T0 | P12:115:NPPD:L1156B::NW68&HOLDREGE.PAWNEELAKE.CKT1:: | B | 140 | -12.8513 | 127.5847 |  |  |  | Rebuild line 640316 PAWNEEL7 115 640340 SEWARD 7 115 1
02ALL | ERIS | Thermal | 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1 | 26SP | T0 | Single 640316 PAWNEEL7 115 640340 SEWARD7 115 1 | B | 154 | -7.9343 | 119.0876 |  |  |  | Rebuild line 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1
02ALL | ERIS | Thermal | 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1 | 29SP | T0 | Single 640316 PAWNEEL7 115 640340 SEWARD7 115 1 | B | 154 | -8.3329 | 118.769 |  |  |  | Rebuild line 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1
02ALL | ERIS | Thermal | 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1 | 29WP | T0 | Single 640316 PAWNEEL7 115 640340 SEWARD7 115 1 | B | 174 | -10.0543 | 102.4752 |  |  |  | Rebuild line 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1
02ALL | ERIS | Thermal | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 26SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE RAUN 3-SIOUXCY3-1 :EHV: | B | 320 | 70.9299 | 103.6656 |  |  |  | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
02ALL | ERIS | Thermal | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE RAUN 3-SIOUXCY3-1 :EHV: | B | 320 | 75.198 | 109.278 |  |  |  | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
02ALL | ERIS | Thermal | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 29WP | T0 | Single 635200 RAUN3 345 640226 HOSKINS3 345 1 | B | 320 | 83.4337 | 119.2256 |  |  |  | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
02ALL | ERIS | Thermal | 646263 S1263 5 161 3WXFMR 645:S1263 T1 69 1 | 29SP | T0 | Single 640234 HUMBOLT5 161 778140 G24-039-TAP 161 1 | B | 107 | 64.7884 | 109.4988 |  |  |  | Rebuild 3-winding transformer 646263 S1263 5 161 647111 W BROCK8 69 648263 S1263T19 13 1
02ALL | ERIS | Thermal | 646263 S1263 5 161 3WXFMR 645:S1263 T1 69 1 | 26SP | T0 | Single 640234 HUMBOLT5 161 778140 G24-039-TAP 161 1 | B | 107 | 67.6004 | 111.9896 |  |  |  | Rebuild 3-winding transformer 646263 S1263 5 161 647111 W BROCK8 69 648263 S1263T19 13 1
02ALL | ERIS | Thermal | 646263 S1263 5 161 3WXFMR 645:S1263 T1 69 1 | 29WP | T0 | Single 640234 HUMBOLT5 161 778140 G24-039-TAP 161 1 | B | 107 | 61.4747 | 108.6709 |  |  |  | Rebuild 3-winding transformer 646263 S1263 5 161 647111 W BROCK8 69 648263 S1263T19 13 1
02ALL | ERIS | Thermal | 646263 S1263 5 161 646280 S1280 5 161 1 | 26SP | T0 | Single 640140 COOPER5 161 778110 G24-038-TAP 161 1 | B | 223 | -15.5029 | 105.0146 |  |  |  | Rebuild line 646263 S1263 5 161 646280 S1280 5 161 1
02ALL | ERIS | Thermal | 646263 S1263 5 161 646280 S1280 5 161 1 | 29SP | T0 | Single 640140 COOPER5 161 778110 G24-038-TAP 161 1 | B | 223 | 2.6119 | 120.8193 |  |  |  | Rebuild line 646263 S1263 5 161 646280 S1280 5 161 1
02ALL | ERIS | Thermal | 646263 S1263 5 161 646280 S1280 5 161 1 | 29WP | T0 | Single 640140 COOPER5 161 778110 G24-038-TAP 161 1 | B | 223 | 2.8632 | 116.291 |  |  |  | Rebuild line 646263 S1263 5 161 646280 S1280 5 161 1
02ALL | ERIS | Thermal | 646280 S1280 5 161 778110 G24-038-TAP 161 1 | 26SP | T0 | Single 640140 COOPER5 161 778110 G24-038-TAP 161 1 | B | 295 | -2.0225 | 100.0967 |  |  |  | Rebuild line 646280 S1280 5 161 778110 G24-038-TAP 161 1
02ALL | ERIS | Thermal | 646280 S1280 5 161 778110 G24-038-TAP 161 1 | 29SP | T0 | Single 640140 COOPER5 161 778110 G24-038-TAP 161 1 | B | 295 | -2.022 | 100.2471 |  |  |  | Rebuild line 646280 S1280 5 161 778110 G24-038-TAP 161 1
02ALL | ERIS | Thermal | 646280 S1280 5 161 778110 G24-038-TAP 161 1 | 29WP | T0 | Single 640140 COOPER5 161 778110 G24-038-TAP 161 1 | B | 295 | -2.0266 | 100.201 |  |  |  | Rebuild line 646280 S1280 5 161 778110 G24-038-TAP 161 1
02ALL | ERIS | Thermal | 647111 W BROCK8 69 3WXFMR 645:S1263 T1 69 1 | 29SP | T0 | Single 640234 HUMBOLT5 161 778140 G24-039-TAP 161 1 | B | 107 | 64.7884 | 109.4988 |  |  |  | Rebuild 3-winding transformer 646263 S1263 5 161 647111 W BROCK8 69 648263 S1263T19 13 1
02ALL | ERIS | Thermal | 647111 W BROCK8 69 3WXFMR 645:S1263 T1 69 1 | 26SP | T0 | Single 640234 HUMBOLT5 161 778140 G24-039-TAP 161 1 | B | 107 | 67.6004 | 111.9896 |  |  |  | Rebuild 3-winding transformer 646263 S1263 5 161 647111 W BROCK8 69 648263 S1263T19 13 1
02ALL | ERIS | Thermal | 647111 W BROCK8 69 3WXFMR 645:S1263 T1 69 1 | 29WP | T0 | Single 640234 HUMBOLT5 161 778140 G24-039-TAP 161 1 | B | 107 | 61.4747 | 108.6709 |  |  |  | Rebuild 3-winding transformer 646263 S1263 5 161 647111 W BROCK8 69 648263 S1263T19 13 1
02ALL | ERIS | Thermal | 647401 NCU903 8 69 647977 S977 8 69 1 | 29SP | T0 | Single 640140 COOPER5 161 778110 G24-038-TAP 161 1 | B | 72 | 43.6985 | 105.9292 |  |  |  | Rebuild line 647401 NCU903 8 69 647977 S977 8 69 1
02ALL | ERIS | Thermal | 647424 FREM D 8 69 647976 S976 8 69 1 | 29SP | T0 | GEN647418 8 | B | 96 | 45.7228 | 111.5714 |  |  |  | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
02ALL | ERIS | Thermal | 647424 FREM D 8 69 647976 S976 8 69 1 | 26SP | T0 | GEN647418 8 | B | 96 | 45.8605 | 109.8902 |  |  |  | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
02ALL | ERIS | Thermal | 647424 FREM D 8 69 647976 S976 8 69 1 | 29WP | T0 | GEN647418 8 | B | 96 | 53.5678 | 115.0969 |  |  |  | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
02ALL | ERIS | Thermal | 647963 S963 8 69 647977 S977 8 69 1 | 29SP | T0 | Single 640140 COOPER5 161 778110 G24-038-TAP 161 1 | B | 72 | 45.8856 | 108.1759 |  |  |  | Rebuild line 647963 S963 8 69 647977 S977 8 69 1
02ALL | ERIS | Thermal | 647976 S976 8 69 3WXFMR 640:FREMONT T1 115 1 | 26SP | T0 | P13:069-115:NPPD:FREMONT T4:::HV: | B | 63 | 32.0961 | 120.9293 |  |  |  | Add 3-winding transformer 640173 FREMONT7 115 643058 FREMONT T1 9 13 647976 S976 8 69 M2
02ALL | ERIS | Thermal | 647976 S976 8 69 3WXFMR 640:FREMONT T1 115 1 | 29SP | T0 | P13:069-115:NPPD:FREMONT T4:::HV: | B | 63 | 32.5921 | 123.2954 |  |  |  | Add 3-winding transformer 640173 FREMONT7 115 643058 FREMONT T1 9 13 647976 S976 8 69 M2
02ALL | ERIS | Thermal | 647976 S976 8 69 3WXFMR 640:FREMONT T1 115 1 | 29WP | T0 | P13:069-115:NPPD:FREMONT T4:::HV: | B | 63 | 36.7738 | 122.7724 |  |  |  | Add 3-winding transformer 640173 FREMONT7 115 643058 FREMONT T1 9 13 647976 S976 8 69 M2
02ALL | ERIS | Thermal | 647976 S976 8 69 3WXFMR 640:FREMONT T4 115 1 | 26SP | T0 | Single 647976 S9768 69 640173 FREMONT7 115 643058 'FREMONT T1 9' 13 1 | B | 56 | 30.45 | 129.0669 |  |  |  | Add 3-winding transformer 640173 FREMONT7 115 643059 FREMONT T4 9 13 647976 S976 8 69 M2
02ALL | ERIS | Thermal | 647976 S976 8 69 3WXFMR 640:FREMONT T4 115 1 | 29SP | T0 | Single 647976 S9768 69 640173 FREMONT7 115 643058 'FREMONT T1 9' 13 1 | B | 56 | 30.7516 | 131.5643 |  |  |  | Add 3-winding transformer 640173 FREMONT7 115 643059 FREMONT T4 9 13 647976 S976 8 69 M2
02ALL | ERIS | Thermal | 647976 S976 8 69 3WXFMR 640:FREMONT T4 115 1 | 29WP | T0 | Single 647976 S9768 69 640173 FREMONT7 115 643058 'FREMONT T1 9' 13 1 | B | 56 | 37.1982 | 131.3757 |  |  |  | Add 3-winding transformer 640173 FREMONT7 115 643059 FREMONT T4 9 13 647976 S976 8 69 M2
03ALL | ERIS | Thermal | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 26SP | T0 | Single 541207 ARCHIE5 161 785640 G24-289-TAP 161 1 | B | 334 | 42.4062 | 124.5613 |  |  |  | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1
03ALL | ERIS | Thermal | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 29WP | T0 | Single 345419 7CLINTON 345 542968 STILWEL7 345 1 | B | 334 | 46.8684 | 112.5496 |  |  |  | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1
03ALL | ERIS | Thermal | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 29SP | T0 | Single 541207 ARCHIE5 161 785640 G24-289-TAP 161 1 | B | 334 | 40.5141 | 121.1523 |  |  |  | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1
03ALL | ERIS | Thermal | 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 | 29SP | T0 | P12:161:AECI:CHOTEAU-MAID:::HV: | B | 1195 | 79.8008 | 103.2914 |  |  |  | Rebuild line 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1
03ALL | ERIS | Thermal | 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 | 26SP | T0 | P12:161:AECI:CHOTEAU-MAID:::HV: | B | 1195 | 81.5602 | 106.2262 |  |  |  | Rebuild line 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1
03ALL | ERIS | Thermal | 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 | 29WP | T0 | P12:161:AECI:CHOTEAU-MAID:::HV: | B | 1195 | 73.8343 | 102.1716 |  |  |  | Rebuild line 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1
03ALL | ERIS | Thermal | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | 29SP | T0 | P12:345:AECI-KCPL:FRPRT:STJ:CPR:: | B | 227 | 69.5858 | 106.443 |  |  |  | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
03ALL | ERIS | Thermal | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | 26SP | T0 | P12:345:AECI-KCPL:FRPRT:STJ:CPR:: | B | 227 | 69.0686 | 103.2081 |  |  |  | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
03ALL | ERIS | Thermal | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | 26SP | T0 | Single 547476 ASB3495 161 547477 CJ3665 161 1 | B | 215 | 68.5797 | 181.9093 |  |  |  | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1
03ALL | ERIS | Thermal | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | 29SP | T0 | Single 547476 ASB3495 161 547477 CJ3665 161 1 | B | 215 | 63.3173 | 172.3281 |  |  |  | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1
03ALL | ERIS | Thermal | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | 29WP | T0 | Single 547476 ASB3495 161 547477 CJ3665 161 1 | B | 293 | 69.4161 | 153.1047 |  |  |  | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1
03ALL | ERIS | Thermal | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | 29SP | T0 | P23:345:AECI:7BLACKBERRY:653::: | B | 829 | 65.7758 | 112.9125 |  |  |  | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
03ALL | ERIS | Thermal | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | 26SP | T0 | P23:345:AECI:7BLACKBERRY:653::: | B | 829 | 74.732 | 124.802 |  |  |  | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
03ALL | ERIS | Thermal | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | 29WP | T0 | P23:345:AECI:7BLACKBERRY:653::: | B | 956 | 55.0232 | 102.1952 |  |  |  | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
03ALL | ERIS | Thermal | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | 29SP | T0 | P42:345:OKGE:SB_REOW7319:::EHV: | B | 222 | 40.2525 | 123.0061 |  |  |  | Rebuild line 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1
03ALL | ERIS | Thermal | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | 26SP | T0 | P42:345:OKGE:SB_REOW7319:::EHV: | B | 222 | 49.6935 | 136.4922 |  |  |  | Rebuild line 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1
03ALL | ERIS | Thermal | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | 29WP | T0 | P42:345:OKGE:SB_REOW7319:::EHV: | B | 270 | 31.2118 | 105.9209 |  |  |  | Rebuild line 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1
03ALL | ERIS | Thermal | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | 29SP | T0 | P42:345:OKGE:SB_REOW7319:::EHV: | B | 222 | 42.5694 | 125.3974 |  |  |  | Rebuild line 514759 NEWKIRK4 138 515381 PECKHMT4 138 1
03ALL | ERIS | Thermal | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | 26SP | T0 | P42:345:OKGE:SB_REOW7319:::EHV: | B | 222 | 52.0743 | 138.9742 |  |  |  | Rebuild line 514759 NEWKIRK4 138 515381 PECKHMT4 138 1
03ALL | ERIS | Thermal | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | 29WP | T0 | P42:345:OKGE:SB_REOW7319:::EHV: | B | 270 | 32.4368 | 107.1925 |  |  |  | Rebuild line 514759 NEWKIRK4 138 515381 PECKHMT4 138 1
03ALL | ERIS | Thermal | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | 29SP | T0 | P42:345:OKGE:SB_REOW7319:::EHV: | B | 222 | 37.0038 | 119.6592 |  |  |  | Rebuild line 514760 KILDARE4 138 514764 NWKRKAT4 138 1
03ALL | ERIS | Thermal | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | 26SP | T0 | P42:345:OKGE:SB_REOW7319:::EHV: | B | 222 | 46.6022 | 133.2823 |  |  |  | Rebuild line 514760 KILDARE4 138 514764 NWKRKAT4 138 1
03ALL | ERIS | Thermal | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | 29WP | T0 | P42:345:OKGE:SB_REOW7319:::EHV: | B | 270 | 28.1991 | 102.8283 |  |  |  | Rebuild line 514760 KILDARE4 138 514764 NWKRKAT4 138 1
03ALL | ERIS | Thermal | 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 | 29SP | T0 | P42:345:OKGE:SB_REOW7319:::EHV: | B | 222 | 44.4297 | 127.2945 |  |  |  | Rebuild line 514804 MIDLTNT4 138 515381 PECKHMT4 138 1
03ALL | ERIS | Thermal | 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 | 26SP | T0 | P42:345:OKGE:SB_REOW7319:::EHV: | B | 222 | 53.8633 | 140.8105 |  |  |  | Rebuild line 514804 MIDLTNT4 138 515381 PECKHMT4 138 1
03ALL | ERIS | Thermal | 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 | 29WP | T0 | P42:345:OKGE:SB_REOW7319:::EHV: | B | 270 | 33.4725 | 108.2316 |  |  |  | Rebuild line 514804 MIDLTNT4 138 515381 PECKHMT4 138 1
03ALL | ERIS | Thermal | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 | 29SP | T0 | P42:345:OKGE:SB_REOW7319:::EHV: | B | 222 | 46.1635 | 129.0435 |  |  |  | Rebuild line 514804 MIDLTNT4 138 532981 CRESWLN4 138 1
03ALL | ERIS | Thermal | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 | 26SP | T0 | P42:345:OKGE:SB_REOW7319:::EHV: | B | 222 | 55.5335 | 142.5026 |  |  |  | Rebuild line 514804 MIDLTNT4 138 532981 CRESWLN4 138 1
03ALL | ERIS | Thermal | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 | 29WP | T0 | P42:345:OKGE:SB_REOW7319:::EHV: | B | 270 | 34.7207 | 109.457 |  |  |  | Rebuild line 514804 MIDLTNT4 138 532981 CRESWLN4 138 1
03ALL | ERIS | Thermal | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 29SP | T0 | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | B | 830 | 53.7055 | 107.359 |  |  |  | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
03ALL | ERIS | Thermal | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 26SP | T0 | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | B | 830 | 64.4 | 118.501 |  |  |  | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
03ALL | ERIS | Thermal | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 29WP | T0 | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | B | 830 | 53.8419 | 116.6365 |  |  |  | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
03ALL | ERIS | Thermal | 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | 29WP | T0 | System Intact | A | 773 | 58.7279 | 101.8225 |  |  |  | Rebuild line 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1
03ALL | ERIS | Thermal | 523106 TXPHSF 3 115 523084 SOONER 3 115 1 | 29SP | T0 | P42:345:SPS:CARPENTER-OR335:::EHV: | B | 120 | 3.7825 | 127.1622 |  |  |  | Add phase shifting xfmr 523084 SOONER 3 115 523106 TXPHSF 3 115 M2
03ALL | ERIS | Thermal | 523106 TXPHSF 3 115 523084 SOONER 3 115 1 | 26SP | T0 | P42:345:SPS:CARPENTER-OR335:::EHV: | B | 120 | 5.6899 | 124.595 |  |  |  | Add phase shifting xfmr 523084 SOONER 3 115 523106 TXPHSF 3 115 M2
03ALL | ERIS | Thermal | 523106 TXPHSF 3 115 523084 SOONER 3 115 1 | 29WP | T0 | P42:345:SPS:CARPENTER-OR335:::EHV: | B | 120 | 7.9126 | 148.8841 |  |  |  | Add phase shifting xfmr 523084 SOONER 3 115 523106 TXPHSF 3 115 M2
03ALL | ERIS | Thermal | 523106 TXPHSF 3 115 539672 E-LIBER3 115 1 | 29SP | T0 | P42:345:SPS:CARPENTER-OR335:::EHV: | B | 80 | 8.5976 | 188.412 |  |  |  | Rebuild line 523106 TXPHSF 3 115 539672 E-LIBER3 115 1
03ALL | ERIS | Thermal | 523106 TXPHSF 3 115 539672 E-LIBER3 115 1 | 26SP | T0 | P42:345:SPS:CARPENTER-OR335:::EHV: | B | 80 | 11.1214 | 184.7205 |  |  |  | Rebuild line 523106 TXPHSF 3 115 539672 E-LIBER3 115 1
03ALL | ERIS | Thermal | 523106 TXPHSF 3 115 539672 E-LIBER3 115 1 | 29WP | T0 | P42:345:SPS:CARPENTER-OR335:::EHV: | B | 80 | 13.552 | 223.4314 |  |  |  | Rebuild line 523106 TXPHSF 3 115 539672 E-LIBER3 115 1
03ALL | ERIS | Thermal | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 29WP | T0 | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | B | 956 | 69.2976 | 138.4923 |  |  |  | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1
03ALL | ERIS | Thermal | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 26SP | T0 | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | B | 956 | 59.6277 | 107.5259 |  |  |  | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1
03ALL | ERIS | Thermal | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 29SP | T0 | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | B | 956 | 44.5091 | 101.5636 |  |  |  | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1
03ALL | ERIS | Thermal | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 29WP | T0 | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | B | 956 | 78.471 | 142.1108 |  |  |  | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1
03ALL | ERIS | Thermal | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 29SP | T0 | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | B | 956 | 60.533 | 113.1642 |  |  |  | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1
03ALL | ERIS | Thermal | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 26SP | T0 | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | B | 956 | 75.6153 | 119.957 |  |  |  | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1
03ALL | ERIS | Thermal | 523961 POTTER_CO 7 345 784950 G24-266_TAP 345 1 | 26SP | T0 | System Intact | A | 773 | 52.5312 | 105.201 |  |  |  | Rebuild line 523961 POTTER_CO 7 345 784950 G24-266_TAP 345 1
03ALL | ERIS | Thermal | 523961 POTTER_CO 7 345 784950 G24-266_TAP 345 1 | 29WP | T0 | System Intact | A | 773 | 55.4666 | 103.2292 |  |  |  | Rebuild line 523961 POTTER_CO 7 345 784950 G24-266_TAP 345 1
03ALL | ERIS | Thermal | 530565 SEWARD 2 69 3WXFMR 531:SEWARD T1 69 1 | 29SP | T0 | Single 530679 SEWRDMW3 115 539692 SEWARD3 115 1 | B | 44.8 | -1.5969 | 186.437 |  |  |  | Rebuild 3-winding transformer 530565 SEWARD 2 69 530631 SWRD1 1 12 530679 SEWRDMW3 115 1
03ALL | ERIS | Thermal | 530565 SEWARD 2 69 3WXFMR 531:SEWARD T1 69 1 | 26SP | T0 | Single 530679 SEWRDMW3 115 539692 SEWARD3 115 1 | B | 44.8 | -1.59 | 185.5567 |  |  |  | Rebuild 3-winding transformer 530565 SEWARD 2 69 530631 SWRD1 1 12 530679 SEWRDMW3 115 1
03ALL | ERIS | Thermal | 530565 SEWARD 2 69 3WXFMR 531:SEWARD T1 69 1 | 29WP | T0 | Single 530679 SEWRDMW3 115 539692 SEWARD3 115 1 | B | 44.8 | -2.4878 | 192.4204 |  |  |  | Rebuild 3-winding transformer 530565 SEWARD 2 69 530631 SWRD1 1 12 530679 SEWRDMW3 115 1
03ALL | ERIS | Thermal | 530565 SEWARD 2 69 530569 GB STH 2 69 1 | 29WP | T0 | Single 530679 SEWRDMW3 115 539692 SEWARD3 115 1 | B | 35 | -5.2632 | 125.0294 |  |  |  | Rebuild line 530565 SEWARD 2 69 530569 GB STH 2 69 1
03ALL | ERIS | Thermal | 530569 GB STH 2 69 530596 WPRTTS 2 69 1 | 29WP | T0 | Single 530679 SEWRDMW3 115 539692 SEWARD3 115 1 | B | 35 | -10.6807 | 120.4443 |  |  |  | Rebuild line 530569 GB STH 2 69 530596 WPRTTS 2 69 1
03ALL | ERIS | Thermal | 530570 GT BND 2 69 530596 WPRTTS 2 69 1 | 29WP | T0 | Single 530679 SEWRDMW3 115 539692 SEWARD3 115 1 | B | 35 | -12.685 | 119.3275 |  |  |  | Rebuild line 530570 GT BND 2 69 530596 WPRTTS 2 69 1
03ALL | ERIS | Thermal | 530582 S HAYS6 230 539679 GRTBEND6 230 1 | 29SP | T0 | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | B | 297 | 56.2558 | 112.2001 |  |  |  | Rebuild line 530582 S HAYS6 230 539679 GRTBEND6 230 1
03ALL | ERIS | Thermal | 530582 S HAYS6 230 539679 GRTBEND6 230 1 | 26SP | T0 | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | B | 297 | 40.2859 | 102.2028 |  |  |  | Rebuild line 530582 S HAYS6 230 539679 GRTBEND6 230 1
03ALL | ERIS | Thermal | 530605 REDLIN 3 115 786630 G24-322-TAP 115 1 | 26SP | T0 | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | B | 99 | -6.6381 | 104.3564 |  |  |  | Rebuild line 530605 REDLIN 3 115 786630 G24-322-TAP 115 1
03ALL | ERIS | Thermal | 530605 REDLIN 3 115 786630 G24-322-TAP 115 1 | 29SP | T0 | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | B | 99 | -7.8409 | 104.4809 |  |  |  | Rebuild line 530605 REDLIN 3 115 786630 G24-322-TAP 115 1
03ALL | ERIS | Thermal | 530618 HUNTSVL3 115 530624 ST JOHN3 115 1 | 29SP | T0 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 99 | -23.808 | 227.1107 |  |  |  | Rebuild line 530618 HUNTSVL3 115 530624 ST JOHN3 115 1
03ALL | ERIS | Thermal | 530618 HUNTSVL3 115 530624 ST JOHN3 115 1 | 26SP | T0 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 99 | -15.7746 | 236.6017 |  |  |  | Rebuild line 530618 HUNTSVL3 115 530624 ST JOHN3 115 1
03ALL | ERIS | Thermal | 530618 HUNTSVL3 115 530624 ST JOHN3 115 1 | 29WP | T0 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 118 | -4.1152 | 212.5689 |  |  |  | Rebuild line 530618 HUNTSVL3 115 530624 ST JOHN3 115 1
03ALL | ERIS | Thermal | 530618 HUNTSVL3 115 530724 CENTENNIAL3 115 1 | 29SP | T0 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 99 | -26.5413 | 223.6214 |  |  |  | Rebuild line 530618 HUNTSVL3 115 530724 CENTENNIAL3 115 1
03ALL | ERIS | Thermal | 530618 HUNTSVL3 115 530724 CENTENNIAL3 115 1 | 26SP | T0 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 99 | -18.3328 | 233.08 |  |  |  | Rebuild line 530618 HUNTSVL3 115 530724 CENTENNIAL3 115 1
03ALL | ERIS | Thermal | 530618 HUNTSVL3 115 530724 CENTENNIAL3 115 1 | 29WP | T0 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 118 | -4.2151 | 210.2877 |  |  |  | Rebuild line 530618 HUNTSVL3 115 530724 CENTENNIAL3 115 1
03ALL | ERIS | Thermal | 530624 ST JOHN3 115 539696 ST-JOHN3 115 Z1 | 29SP | T0 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 179 | 25.8259 | 165.6666 |  |  |  | Rebuild line 530624 ST JOHN3 115 539696 ST-JOHN3 115 Z1
03ALL | ERIS | Thermal | 530624 ST JOHN3 115 539696 ST-JOHN3 115 Z1 | 26SP | T0 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 179 | 25.0571 | 165.7277 |  |  |  | Rebuild line 530624 ST JOHN3 115 539696 ST-JOHN3 115 Z1
03ALL | ERIS | Thermal | 530624 ST JOHN3 115 539696 ST-JOHN3 115 Z1 | 29WP | T0 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 179 | 21.9429 | 165.2081 |  |  |  | Rebuild line 530624 ST JOHN3 115 539696 ST-JOHN3 115 Z1
03ALL | ERIS | Thermal | 530679 SEWRDMW3 115 3WXFMR 531:SEWARD T1 69 1 | 29SP | T0 | Single 530679 SEWRDMW3 115 539692 SEWARD3 115 1 | B | 44.8 | -1.6667 | 186.437 |  |  |  | Rebuild 3-winding transformer 530565 SEWARD 2 69 530631 SWRD1 1 12 530679 SEWRDMW3 115 1
03ALL | ERIS | Thermal | 530679 SEWRDMW3 115 3WXFMR 531:SEWARD T1 69 1 | 26SP | T0 | Single 530679 SEWRDMW3 115 539692 SEWARD3 115 1 | B | 44.8 | -1.6595 | 185.5567 |  |  |  | Rebuild 3-winding transformer 530565 SEWARD 2 69 530631 SWRD1 1 12 530679 SEWRDMW3 115 1
03ALL | ERIS | Thermal | 530679 SEWRDMW3 115 3WXFMR 531:SEWARD T1 69 1 | 29WP | T0 | Single 530679 SEWRDMW3 115 539692 SEWARD3 115 1 | B | 44.8 | -2.5965 | 192.4204 |  |  |  | Rebuild 3-winding transformer 530565 SEWARD 2 69 530631 SWRD1 1 12 530679 SEWRDMW3 115 1
03ALL | ERIS | Thermal | 530679 SEWRDMW3 115 539692 SEWARD 3 115 1 | 29SP | T0 | Single 530679 SEWRDMW3 115 530565 SEWARD2 69 530631 'SWRD1 1 ' 12 1 | B | 40 | -2.8814 | 197.5188 |  |  |  | Rebuild line 530679 SEWRDMW3 115 539692 SEWARD 3 115 1
03ALL | ERIS | Thermal | 530679 SEWRDMW3 115 539692 SEWARD 3 115 1 | 26SP | T0 | Single 530679 SEWRDMW3 115 530565 SEWARD2 69 530631 'SWRD1 1 ' 12 1 | B | 40 | -2.8863 | 197.5931 |  |  |  | Rebuild line 530679 SEWRDMW3 115 539692 SEWARD 3 115 1
03ALL | ERIS | Thermal | 530679 SEWRDMW3 115 539692 SEWARD 3 115 1 | 29WP | T0 | Single 530679 SEWRDMW3 115 530565 SEWARD2 69 530631 'SWRD1 1 ' 12 1 | B | 40 | -2.8921 | 197.5091 |  |  |  | Rebuild line 530679 SEWRDMW3 115 539692 SEWARD 3 115 1
03ALL | ERIS | Thermal | 530724 CENTENNIAL3 115 533412 ARKVALJ3 115 1 | 29SP | T0 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 99 | -35.9115 | 216.4641 |  |  |  | Rebuild line 530724 CENTENNIAL3 115 533412 ARKVALJ3 115 1
03ALL | ERIS | Thermal | 530724 CENTENNIAL3 115 533412 ARKVALJ3 115 1 | 26SP | T0 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 99 | -27.5791 | 225.9944 |  |  |  | Rebuild line 530724 CENTENNIAL3 115 533412 ARKVALJ3 115 1
03ALL | ERIS | Thermal | 530724 CENTENNIAL3 115 533412 ARKVALJ3 115 1 | 29WP | T0 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 118 | -10.3112 | 205.5315 |  |  |  | Rebuild line 530724 CENTENNIAL3 115 533412 ARKVALJ3 115 1
03ALL | ERIS | Thermal | 531357 RULETON3 115 531368 LAWNRID3 115 1 | 29SP | T0 | Single 531365 BIRDCTY3 115 531370 STFRAN3 115 1 | B | 106 | -6.6663 | 133.6268 |  |  |  | Rebuild line 531357 RULETON3 115 531368 LAWNRID3 115 1
03ALL | ERIS | Thermal | 531357 RULETON3 115 531368 LAWNRID3 115 1 | 26SP | T0 | Single 531365 BIRDCTY3 115 531370 STFRAN3 115 1 | B | 106 | -6.7 | 132.845 |  |  |  | Rebuild line 531357 RULETON3 115 531368 LAWNRID3 115 1
03ALL | ERIS | Thermal | 531357 RULETON3 115 531368 LAWNRID3 115 1 | 29WP | T0 | Single 531365 BIRDCTY3 115 531370 STFRAN3 115 1 | B | 129.3 | -3.9614 | 110.6451 |  |  |  | Rebuild line 531357 RULETON3 115 531368 LAWNRID3 115 1
03ALL | ERIS | Thermal | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | 29SP | T0 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | B | 228.7 | -19.4712 | 128.0603 |  |  |  | Rebuild line 531391 PIONEER3 115 531483 GRANTTP3 115 1
03ALL | ERIS | Thermal | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | 26SP | T0 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | B | 228.7 | -19.4973 | 128.2545 |  |  |  | Rebuild line 531391 PIONEER3 115 531483 GRANTTP3 115 1
03ALL | ERIS | Thermal | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | 29WP | T0 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | B | 249 | -13.9444 | 123.4048 |  |  |  | Rebuild line 531391 PIONEER3 115 531483 GRANTTP3 115 1
03ALL | ERIS | Thermal | 531405 WALKMYR3 115 531481 HUGOTON3 115 1 | 29SP | T0 | P23:345:SUNC:HLC_BRK188:::EHV: | B | 230.3 | 1.9239 | 156.0118 |  |  |  | Rebuild line 531405 WALKMYR3 115 531481 HUGOTON3 115 1
03ALL | ERIS | Thermal | 531405 WALKMYR3 115 531481 HUGOTON3 115 1 | 26SP | T0 | P23:345:SUNC:HLC_BRK188:::EHV: | B | 230.3 | 11.3983 | 165.6931 |  |  |  | Rebuild line 531405 WALKMYR3 115 531481 HUGOTON3 115 1
03ALL | ERIS | Thermal | 531405 WALKMYR3 115 531481 HUGOTON3 115 1 | 29WP | T0 | P23:345:SUNC:HLC_BRK188:::EHV: | B | 239 | 19.3141 | 181.9709 |  |  |  | Rebuild line 531405 WALKMYR3 115 531481 HUGOTON3 115 1
03ALL | ERIS | Thermal | 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | 29SP | T0 | P23:345:SUNC:HLC_BRK188:::EHV: | B | 331.4 | 13.1755 | 153.6513 |  |  |  | Add line and rebuild line 531405 WALKMYR3 115 531510 HARBNGR3 115 M2
03ALL | ERIS | Thermal | 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | 26SP | T0 | P23:345:SUNC:HLC_BRK188:::EHV: | B | 331.4 | 22.3626 | 163.2808 |  |  |  | Add line and rebuild line 531405 WALKMYR3 115 531510 HARBNGR3 115 M2
03ALL | ERIS | Thermal | 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | 29WP | T0 | P23:345:SUNC:HLC_BRK188:::EHV: | B | 398.2 | 31.4266 | 162.1801 |  |  |  | Add line and rebuild line 531405 WALKMYR3 115 531510 HARBNGR3 115 M2
03ALL | ERIS | Thermal | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | 29WP | T0 | P23:345:SUNC:HLC_BRK188:::EHV: | B | 197.4 | 44.5077 | 110.1916 |  |  |  | Rebuild line 531405 WALKMYR3 115 539654 CIM-PLT3 115 1
03ALL | ERIS | Thermal | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | 26SP | T0 | P23:345:SUNC:HLC_BRK188:::EHV: | B | 165.1 | 36.5929 | 104.0779 |  |  |  | Rebuild line 531405 WALKMYR3 115 539654 CIM-PLT3 115 1
03ALL | ERIS | Thermal | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | 29SP | T0 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | B | 165.1 | 43.0621 | 100.4985 |  |  |  | Rebuild line 531405 WALKMYR3 115 539654 CIM-PLT3 115 1
03ALL | ERIS | Thermal | 531433 SCOTCTY3 115 531464 SETAB 3 115 1 | 29L | T0 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | B | 248.8 | 32.4786 | 112.691 |  |  |  | Rebuild line 531433 SCOTCTY3 115 531464 SETAB 3 115 1
03ALL | ERIS | Thermal | 531433 SCOTCTY3 115 531464 SETAB 3 115 1 | 29SP | T0 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | B | 230.3 | 10.6866 | 128.1663 |  |  |  | Rebuild line 531433 SCOTCTY3 115 531464 SETAB 3 115 1
03ALL | ERIS | Thermal | 531433 SCOTCTY3 115 531464 SETAB 3 115 1 | 26SP | T0 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | B | 230.3 | 24.691 | 136.259 |  |  |  | Rebuild line 531433 SCOTCTY3 115 531464 SETAB 3 115 1
03ALL | ERIS | Thermal | 531433 SCOTCTY3 115 531464 SETAB 3 115 1 | 29WP | T0 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | B | 275.7 | 19.4444 | 111.6117 |  |  |  | Rebuild line 531433 SCOTCTY3 115 531464 SETAB 3 115 1
03ALL | ERIS | Thermal | 531448 HOLCOMB3 115 3WXFMR 534:HOLCOMB 345 1 | 29WP | T0 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | B | 358.5 | 54.7251 | 130.8737 |  |  |  | Add 3-winding transformer 531448 HOLCOMB3 115 531449 HOLCOMB7 345 531450 HOLCTER1 13 M2
03ALL | ERIS | Thermal | 531449 HOLCOMB7 345 3WXFMR 534:HOLCOMB 345 1 | 29WP | T0 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | B | 358.5 | 54.7251 | 130.8737 |  |  |  | Add 3-winding transformer 531448 HOLCOMB3 115 531449 HOLCOMB7 345 531450 HOLCTER1 13 M2
03ALL | ERIS | Thermal | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 29SP | T0 | P23:345:SUNC:HLC_BRK282:::EHV: | B | 966 | 35.9901 | 134.7629 |  |  |  | Rebuild line 531451 MINGO 7 345 767280 G22-015-TAP 345 1
03ALL | ERIS | Thermal | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 26SP | T0 | P23:345:SUNC:HLC_BRK282:::EHV: | B | 966 | 27.9962 | 127.259 |  |  |  | Rebuild line 531451 MINGO 7 345 767280 G22-015-TAP 345 1
03ALL | ERIS | Thermal | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 29WP | T0 | P23:345:SUNC:HLC_BRK282:::EHV: | B | 966 | 35.1442 | 139.9749 |  |  |  | Rebuild line 531451 MINGO 7 345 767280 G22-015-TAP 345 1
03ALL | ERIS | Thermal | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 29L | T0 | P23:345:SUNC:HLC_BRK282:::EHV: | B | 966 | 53.8245 | 117.4451 |  |  |  | Rebuild line 531451 MINGO 7 345 767280 G22-015-TAP 345 1
03ALL | ERIS | Thermal | 531464 SETAB 3 115 3WXFMR 534:SETAB 345 1 | 29SP | T0 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | B | 308 | 7.7478 | 120.8114 |  |  |  | Add 3-winding transformer 531259 SETAB 1 13 531464 SETAB 3 115 531465 SETAB 7 345 M2
03ALL | ERIS | Thermal | 531464 SETAB 3 115 3WXFMR 534:SETAB 345 1 | 26SP | T0 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | B | 308 | 23.238 | 126.2026 |  |  |  | Add 3-winding transformer 531259 SETAB 1 13 531464 SETAB 3 115 531465 SETAB 7 345 M2
03ALL | ERIS | Thermal | 531464 SETAB 3 115 3WXFMR 534:SETAB 345 1 | 29WP | T0 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | B | 308 | 21.7722 | 120.3092 |  |  |  | Add 3-winding transformer 531259 SETAB 1 13 531464 SETAB 3 115 531465 SETAB 7 345 M2
03ALL | ERIS | Thermal | 531465 SETAB 7 345 3WXFMR 534:SETAB 345 1 | 29SP | T0 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | B | 308 | 7.7803 | 120.8224 |  |  |  | Add 3-winding transformer 531259 SETAB 1 13 531464 SETAB 3 115 531465 SETAB 7 345 M2
03ALL | ERIS | Thermal | 531465 SETAB 7 345 3WXFMR 534:SETAB 345 1 | 26SP | T0 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | B | 308 | 23.3195 | 126.2133 |  |  |  | Add 3-winding transformer 531259 SETAB 1 13 531464 SETAB 3 115 531465 SETAB 7 345 M2
03ALL | ERIS | Thermal | 531465 SETAB 7 345 3WXFMR 534:SETAB 345 1 | 29WP | T0 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | B | 308 | 21.8398 | 120.3116 |  |  |  | Add 3-winding transformer 531259 SETAB 1 13 531464 SETAB 3 115 531465 SETAB 7 345 M2
03ALL | ERIS | Thermal | 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | 26SP | T0 | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | B | 1793 | 63.1231 | 107.735 |  |  |  | Rebuild line 531469 SPERVIL7 345 763677 G19-030-TAP 345 1
03ALL | ERIS | Thermal | 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | 29SP | T0 | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | B | 1793 | 55.0054 | 103.1691 |  |  |  | Rebuild line 531469 SPERVIL7 345 763677 G19-030-TAP 345 1
03ALL | ERIS | Thermal | 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | 29WP | T0 | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | B | 1793 | 60.8233 | 111.3133 |  |  |  | Rebuild line 531469 SPERVIL7 345 763677 G19-030-TAP 345 1
03ALL | ERIS | Thermal | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | 26SP | T0 | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 2 | B | 1526.2 | 52.6395 | 100.135 |  |  |  | Rebuild line 531469 SPERVIL7 345 765911 G21-068-TAP 345 1
03ALL | ERIS | Thermal | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | 29SP | T0 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | B | 230.3 | -17.4637 | 129.2041 |  |  |  | Rebuild line 531481 HUGOTON3 115 531483 GRANTTP3 115 1
03ALL | ERIS | Thermal | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | 26SP | T0 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | B | 230.3 | -17.475 | 129.4247 |  |  |  | Rebuild line 531481 HUGOTON3 115 531483 GRANTTP3 115 1
03ALL | ERIS | Thermal | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | 29WP | T0 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | B | 275.7 | -11.579 | 112.5932 |  |  |  | Rebuild line 531481 HUGOTON3 115 531483 GRANTTP3 115 1
03ALL | ERIS | Thermal | 531510 HARBNGR3 115 3WXFMR 534:HARBGR345 345 1 | 29WP | T0 | P23:345:SUNC:HLC_BRK188:::EHV: | B | 385 | 32.7697 | 155.1155 |  |  |  | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2
03ALL | ERIS | Thermal | 531510 HARBNGR3 115 3WXFMR 534:HARBGR345 345 1 | 29SP | T0 | P23:345:SUNC:HLC_BRK188:::EHV: | B | 385 | 11.4337 | 125.4621 |  |  |  | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2
03ALL | ERIS | Thermal | 531510 HARBNGR3 115 3WXFMR 534:HARBGR345 345 1 | 26SP | T0 | P23:345:SUNC:HLC_BRK188:::EHV: | B | 385 | 19.5816 | 133.2735 |  |  |  | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2
03ALL | ERIS | Thermal | 531512 HARBNGR7 345 3WXFMR 534:HARBGR345 345 1 | 29WP | T0 | P23:345:SUNC:HLC_BRK188:::EHV: | B | 385 | 33.1499 | 154.9674 |  |  |  | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2
03ALL | ERIS | Thermal | 531512 HARBNGR7 345 3WXFMR 534:HARBGR345 345 1 | 29SP | T0 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | B | 385 | 25.0747 | 129.3632 |  |  |  | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2
03ALL | ERIS | Thermal | 531512 HARBNGR7 345 3WXFMR 534:HARBGR345 345 1 | 26SP | T0 | P23:345:SUNC:HLC_BRK188:::EHV: | B | 385 | 19.718 | 141.1173 |  |  |  | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2
03ALL | ERIS | Thermal | 532765 HOYT 7 345 532766 JEC N 7 345 1 | 29SP | T0 | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | B | 830 | 154.3841 | 169.1147 |  |  |  | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1
03ALL | ERIS | Thermal | 532765 HOYT 7 345 532766 JEC N 7 345 1 | 26SP | T0 | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | B | 830 | 134.9694 | 157.0734 |  |  |  | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1
03ALL | ERIS | Thermal | 532765 HOYT 7 345 532766 JEC N 7 345 1 | 29WP | T0 | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | B | 830 | 137.9782 | 154.0697 |  |  |  | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1
03ALL | ERIS | Thermal | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | 29SP | T0 | P23:345:AECI:7BLACKBERRY:653::: | B | 829 | 66.5904 | 107.2399 |  |  |  | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
03ALL | ERIS | Thermal | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | 26SP | T0 | P23:345:AECI:7BLACKBERRY:653::: | B | 829 | 75.7225 | 119.9498 |  |  |  | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
03ALL | ERIS | Thermal | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 26SP | T0 | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | B | 830 | 55.4669 | 109.2178 |  |  |  | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
03ALL | ERIS | Thermal | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 29WP | T0 | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | B | 830 | 43.6535 | 106.0868 |  |  |  | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
03ALL | ERIS | Thermal | 532856 SWISVAL6 230 785250 G24-276-TAP 230 1 | 26SP | T0 | Single 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 278 | -6.1411 | 105.4501 |  |  |  | Rebuild line 532856 SWISVAL6 230 785250 G24-276-TAP 230 1
03ALL | ERIS | Thermal | 532856 SWISVAL6 230 785250 G24-276-TAP 230 1 | 29SP | T0 | Single 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 278 | -6.1418 | 105.435 |  |  |  | Rebuild line 532856 SWISVAL6 230 785250 G24-276-TAP 230 1
03ALL | ERIS | Thermal | 532856 SWISVAL6 230 785250 G24-276-TAP 230 1 | 29WP | T0 | Single 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 278 | -6.1194 | 105.6449 |  |  |  | Rebuild line 532856 SWISVAL6 230 785250 G24-276-TAP 230 1
03ALL | ERIS | Thermal | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | 29SP | T0 | P12:345:WERE:HOYT-JEC-345:EHV: | B | 278 | 91.653 | 137.7779 |  |  |  | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
03ALL | ERIS | Thermal | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | 26SP | T0 | Single 532851 AUBURN6 230 533151 AUBURN3 115 532880 'AUBURN 1 ' 14 1 | B | 278 | 85.0949 | 130.7599 |  |  |  | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
03ALL | ERIS | Thermal | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | 29WP | T0 | Single 532856 SWISVAL6 230 785250 G24-276-TAP 230 1 | B | 278 | -4.6425 | 105.5374 |  |  |  | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
03ALL | ERIS | Thermal | 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 | 26SP | T0 | Single 532871 CIRCLE6 230 533413 CIRCLE3 115 532892 'CIRCLE 1 ' 13 1 | B | 278 | 53.1014 | 133.4363 |  |  |  | Rebuild line 532871 CIRCLE 6 230 532872 EMCPHER6 230 1
03ALL | ERIS | Thermal | 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 | 29SP | T0 | Single 532871 CIRCLE6 230 533413 CIRCLE3 115 532892 'CIRCLE 1 ' 13 1 | B | 278 | 49.6674 | 130.8894 |  |  |  | Rebuild line 532871 CIRCLE 6 230 532872 EMCPHER6 230 1
03ALL | ERIS | Thermal | 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 | 29WP | T0 | Single 532871 CIRCLE6 230 533413 CIRCLE3 115 532892 'CIRCLE 1 ' 13 1 | B | 365 | 40.7965 | 101.0484 |  |  |  | Rebuild line 532871 CIRCLE 6 230 532872 EMCPHER6 230 1
03ALL | ERIS | Thermal | 533075 VIOLA 4 138 539009 CONWAY 4 138 1 | 29SP | T0 | P12:138:ITCGP:FLATRIDGE-THISTLE:::HV: | B | 136.7 | 2.5919 | 151.4104 |  |  |  | Rebuild line 533075 VIOLA 4 138 539009 CONWAY 4 138 1
03ALL | ERIS | Thermal | 533075 VIOLA 4 138 539009 CONWAY 4 138 1 | 26SP | T0 | P12:138:ITCGP:FLATRIDGE-THISTLE:::HV: | B | 136.7 | 4.5911 | 156.3188 |  |  |  | Rebuild line 533075 VIOLA 4 138 539009 CONWAY 4 138 1
03ALL | ERIS | Thermal | 533075 VIOLA 4 138 539009 CONWAY 4 138 1 | 29WP | T0 | P12:138:ITCGP:FLATRIDGE-THISTLE:::HV: | B | 162.5 | 15.2901 | 147.7165 |  |  |  | Rebuild line 533075 VIOLA 4 138 539009 CONWAY 4 138 1
03ALL | ERIS | Thermal | 533413 CIRCLE 3 115 533416 RENO 3 115 2 | 29WP | T0 | P12:115:WERE:CIRC-RENO-115-1:HV: | B | 194 | 16.0983 | 107.3261 |  |  |  | Rebuild line 533413 CIRCLE 3 115 533416 RENO 3 115 2
03ALL | ERIS | Thermal | 533763 HUDSON-2 69 533770 PITTSBG2 69 1 | 29SP | T0 | P12:69:WERE:LITC-SPIT-69:HV:FUTURE | B | 30 | 56.1493 | 104.9381 |  |  |  | Rebuild line 533763 HUDSON-2 69 533770 PITTSBG2 69 1
03ALL | ERIS | Thermal | 539009 CONWAY 4 138 539881 SPRVLSTR 138 1 | 29SP | T0 | P12:138:ITCGP:FLATRIDGE-THISTLE:::HV: | B | 136.7 | 4.6061 | 153.7113 |  |  |  | Rebuild line 539009 CONWAY 4 138 539881 SPRVLSTR 138 1
03ALL | ERIS | Thermal | 539009 CONWAY 4 138 539881 SPRVLSTR 138 1 | 26SP | T0 | P12:138:ITCGP:FLATRIDGE-THISTLE:::HV: | B | 136.7 | 7.4813 | 158.5675 |  |  |  | Rebuild line 539009 CONWAY 4 138 539881 SPRVLSTR 138 1
03ALL | ERIS | Thermal | 539009 CONWAY 4 138 539881 SPRVLSTR 138 1 | 29WP | T0 | P12:138:ITCGP:FLATRIDGE-THISTLE:::HV: | B | 162.5 | 16.8409 | 149.053 |  |  |  | Rebuild line 539009 CONWAY 4 138 539881 SPRVLSTR 138 1
03ALL | ERIS | Thermal | 539010 SADLHRN3 115 539648 PRICHRD3 115 1 | 26SP | T0 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 298.8 | -9.5724 | 131.1173 |  |  |  | Rebuild line 539010 SADLHRN3 115 539648 PRICHRD3 115 1
03ALL | ERIS | Thermal | 539010 SADLHRN3 115 539648 PRICHRD3 115 1 | 29SP | T0 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 298.8 | -9.5815 | 127.4968 |  |  |  | Rebuild line 539010 SADLHRN3 115 539648 PRICHRD3 115 1
03ALL | ERIS | Thermal | 539010 SADLHRN3 115 539648 PRICHRD3 115 1 | 29WP | T0 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 298.8 | -7.3943 | 139.624 |  |  |  | Rebuild line 539010 SADLHRN3 115 539648 PRICHRD3 115 1
03ALL | ERIS | Thermal | 539010 SADLHRN3 115 539696 ST-JOHN3 115 1 | 26SP | T0 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 303.8 | -9.5141 | 128.8973 |  |  |  | Rebuild line 539010 SADLHRN3 115 539696 ST-JOHN3 115 1
03ALL | ERIS | Thermal | 539010 SADLHRN3 115 539696 ST-JOHN3 115 1 | 29SP | T0 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 303.8 | -9.5167 | 125.3354 |  |  |  | Rebuild line 539010 SADLHRN3 115 539696 ST-JOHN3 115 1
03ALL | ERIS | Thermal | 539010 SADLHRN3 115 539696 ST-JOHN3 115 1 | 29WP | T0 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 364.3 | -6.1745 | 114.4852 |  |  |  | Rebuild line 539010 SADLHRN3 115 539696 ST-JOHN3 115 1
03ALL | ERIS | Thermal | 539638 FLATRDG4 138 539674 BARBER 4 138 1 | 26SP | T0 | Single 539010 SADLHRN3 115 539648 PRICHRD3 115 1 | B | 364.5 | 5.0301 | 113.1342 |  |  |  | Rebuild line 539638 FLATRDG4 138 539674 BARBER 4 138 1
03ALL | ERIS | Thermal | 539638 FLATRDG4 138 539674 BARBER 4 138 1 | 29SP | T0 | Single 539010 SADLHRN3 115 539648 PRICHRD3 115 1 | B | 364.5 | 4.0779 | 109.6693 |  |  |  | Rebuild line 539638 FLATRDG4 138 539674 BARBER 4 138 1
03ALL | ERIS | Thermal | 539638 FLATRDG4 138 539674 BARBER 4 138 1 | 29WP | T0 | Single 539010 SADLHRN3 115 539648 PRICHRD3 115 1 | B | 437.2 | 8.1295 | 104.0709 |  |  |  | Rebuild line 539638 FLATRDG4 138 539674 BARBER 4 138 1
03ALL | ERIS | Thermal | 539642 ELLSWTP3 115 539678 GRTBEND3 115 1 | 26SP | T0 | Single 532871 CIRCLE6 230 763862 G19-054-TAP 230 1 | B | 89.8 | 59.5318 | 113.8333 |  |  |  | Rebuild line 539642 ELLSWTP3 115 539678 GRTBEND3 115 1
03ALL | ERIS | Thermal | 539648 PRICHRD3 115 539753 PRATTENERGY3 115 1 | 29SP | T0 | Single 539754 SEMCRDE3 115 539756 SKLYVL_GOAB3 115 1 | B | 79.7 | -1.6535 | 272.0573 |  |  |  | Rebuild line 539648 PRICHRD3 115 539753 PRATTENERGY3 115 1
03ALL | ERIS | Thermal | 539648 PRICHRD3 115 539753 PRATTENERGY3 115 1 | 26SP | T0 | Single 539754 SEMCRDE3 115 539756 SKLYVL_GOAB3 115 1 | B | 79.7 | -1.6553 | 272.4581 |  |  |  | Rebuild line 539648 PRICHRD3 115 539753 PRATTENERGY3 115 1
03ALL | ERIS | Thermal | 539648 PRICHRD3 115 539753 PRATTENERGY3 115 1 | 29WP | T0 | Single 539754 SEMCRDE3 115 539756 SKLYVL_GOAB3 115 1 | B | 79.7 | -1.6514 | 273.1722 |  |  |  | Rebuild line 539648 PRICHRD3 115 539753 PRATTENERGY3 115 1
03ALL | ERIS | Thermal | 539649 SAWYER 3 115 539760 BARBER 3 115 1 | 29SP | T0 | Single 539010 SADLHRN3 115 539648 PRICHRD3 115 1 | B | 296.4 | -9.1821 | 128.9175 |  |  |  | Rebuild line 539649 SAWYER 3 115 539760 BARBER 3 115 1
03ALL | ERIS | Thermal | 539649 SAWYER 3 115 539760 BARBER 3 115 1 | 26SP | T0 | Single 539010 SADLHRN3 115 539648 PRICHRD3 115 1 | B | 296.4 | -9.2319 | 133.0215 |  |  |  | Rebuild line 539649 SAWYER 3 115 539760 BARBER 3 115 1
03ALL | ERIS | Thermal | 539649 SAWYER 3 115 539760 BARBER 3 115 1 | 29WP | T0 | Single 539010 SADLHRN3 115 539648 PRICHRD3 115 1 | B | 296.4 | -7.5408 | 143.5862 |  |  |  | Rebuild line 539649 SAWYER 3 115 539760 BARBER 3 115 1
03ALL | ERIS | Thermal | 539650 BELOIT 3 115 539657 CONCORD3 115 1 | 29SP | T0 | P12:115:SUNC:SMITHCENTER-BELOIT:::HV: | B | 113.9 | -5.7943 | 127.1517 |  |  |  | Rebuild line 539650 BELOIT 3 115 539657 CONCORD3 115 1
03ALL | ERIS | Thermal | 539650 BELOIT 3 115 539657 CONCORD3 115 1 | 26SP | T0 | P12:115:SUNC:SMITHCENTER-BELOIT:::HV: | B | 113.9 | -5.7993 | 129.8033 |  |  |  | Rebuild line 539650 BELOIT 3 115 539657 CONCORD3 115 1
03ALL | ERIS | Thermal | 539650 BELOIT 3 115 539657 CONCORD3 115 1 | 29WP | T0 | P12:115:SUNC:SMITHCENTER-BELOIT:::HV: | B | 135.4 | 2.9691 | 114.6212 |  |  |  | Rebuild line 539650 BELOIT 3 115 539657 CONCORD3 115 1
03ALL | ERIS | Thermal | 539650 BELOIT 3 115 539663 GLENELD3 115 1 | 29SP | T0 | P12:115:SUNC:BELOIT-CONCORDIA(SOUTH):::HV: | B | 113.9 | -5.9911 | 129.2061 |  |  |  | Rebuild line 539650 BELOIT 3 115 539663 GLENELD3 115 1
03ALL | ERIS | Thermal | 539650 BELOIT 3 115 539663 GLENELD3 115 1 | 26SP | T0 | P12:115:SUNC:BELOIT-CONCORDIA(SOUTH):::HV: | B | 113.9 | -6.0297 | 131.9222 |  |  |  | Rebuild line 539650 BELOIT 3 115 539663 GLENELD3 115 1
03ALL | ERIS | Thermal | 539650 BELOIT 3 115 539663 GLENELD3 115 1 | 29WP | T0 | P12:115:SUNC:BELOIT-CONCORDIA(SOUTH):::HV: | B | 135.4 | 2.9829 | 116.5343 |  |  |  | Rebuild line 539650 BELOIT 3 115 539663 GLENELD3 115 1
03ALL | ERIS | Thermal | 539652 CMRIVTP3 115 539654 CIM-PLT3 115 1 | 29SP | T0 | Single 539652 CMRIVTP3 115 539672 E-LIBER3 115 1 | B | 113.9 | 26.0018 | 132.8591 |  |  |  | Rebuild line 539652 CMRIVTP3 115 539654 CIM-PLT3 115 1
03ALL | ERIS | Thermal | 539652 CMRIVTP3 115 539654 CIM-PLT3 115 1 | 26SP | T0 | Single 539652 CMRIVTP3 115 539672 E-LIBER3 115 1 | B | 113.9 | 27.8018 | 132.5804 |  |  |  | Rebuild line 539652 CMRIVTP3 115 539654 CIM-PLT3 115 1
03ALL | ERIS | Thermal | 539652 CMRIVTP3 115 539654 CIM-PLT3 115 1 | 29WP | T0 | Single 539652 CMRIVTP3 115 539672 E-LIBER3 115 1 | B | 135.4 | 27.7623 | 121.6814 |  |  |  | Rebuild line 539652 CMRIVTP3 115 539654 CIM-PLT3 115 1
03ALL | ERIS | Thermal | 539656 CLIFTON3 115 539657 CONCORD3 115 1 | 29SP | T0 | Single 539805 ELMCREEK7 345 539639 ELMCREK6 230 539806 'ELMCREEK1 ' 13 1 | B | 113.9 | 47.9192 | 102.3499 |  |  |  | Rebuild line 539656 CLIFTON3 115 539657 CONCORD3 115 1
03ALL | ERIS | Thermal | 539663 GLENELD3 115 539693 SMITH-C3 115 1 | 29SP | T0 | P12:115:SUNC:BELOIT-CONCORDIA(SOUTH):::HV: | B | 120.1 | -8.4485 | 114.6947 |  |  |  | Rebuild line 539663 GLENELD3 115 539693 SMITH-C3 115 1
03ALL | ERIS | Thermal | 539663 GLENELD3 115 539693 SMITH-C3 115 1 | 26SP | T0 | P12:115:SUNC:BELOIT-CONCORDIA(SOUTH):::HV: | B | 120.1 | -8.8673 | 117.1674 |  |  |  | Rebuild line 539663 GLENELD3 115 539693 SMITH-C3 115 1
03ALL | ERIS | Thermal | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 29SP | T0 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 120 | -61.1948 | 180.9418 |  |  |  | Rebuild line 539666 GBENDTP3 115 539692 SEWARD 3 115 1
03ALL | ERIS | Thermal | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 26SP | T0 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 120 | -59.8264 | 187.1943 |  |  |  | Rebuild line 539666 GBENDTP3 115 539692 SEWARD 3 115 1
03ALL | ERIS | Thermal | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 29WP | T0 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 120 | -44.5044 | 206.3134 |  |  |  | Rebuild line 539666 GBENDTP3 115 539692 SEWARD 3 115 1
03ALL | ERIS | Thermal | 539668 HARPER 4 138 539881 SPRVLSTR 138 1 | 29SP | T0 | P12:138:ITCGP:FLATRIDGE-THISTLE:::HV: | B | 136.7 | 10.1769 | 158.748 |  |  |  | Rebuild line 539668 HARPER 4 138 539881 SPRVLSTR 138 1
03ALL | ERIS | Thermal | 539668 HARPER 4 138 539881 SPRVLSTR 138 1 | 26SP | T0 | P12:138:ITCGP:FLATRIDGE-THISTLE:::HV: | B | 136.7 | 13.34 | 163.7039 |  |  |  | Rebuild line 539668 HARPER 4 138 539881 SPRVLSTR 138 1
03ALL | ERIS | Thermal | 539668 HARPER 4 138 539881 SPRVLSTR 138 1 | 29WP | T0 | P12:138:ITCGP:FLATRIDGE-THISTLE:::HV: | B | 162.5 | 20.1125 | 151.9467 |  |  |  | Rebuild line 539668 HARPER 4 138 539881 SPRVLSTR 138 1
03ALL | ERIS | Thermal | 539674 BARBER 4 138 3WXFMR 534:BARBER 4 138 1 | 29SP | T0 | Single 539010 SADLHRN3 115 539648 PRICHRD3 115 1 | B | 275 | 5.5019 | 134.1751 |  |  |  | Add 3-winding transformer 539674 BARBER 4 138 539760 BARBER 3 115 539917 BARBER-1 13 M2
03ALL | ERIS | Thermal | 539674 BARBER 4 138 3WXFMR 534:BARBER 4 138 1 | 26SP | T0 | Single 539010 SADLHRN3 115 539648 PRICHRD3 115 1 | B | 275 | 6.7945 | 137.1687 |  |  |  | Add 3-winding transformer 539674 BARBER 4 138 539760 BARBER 3 115 539917 BARBER-1 13 M2
03ALL | ERIS | Thermal | 539674 BARBER 4 138 3WXFMR 534:BARBER 4 138 1 | 29WP | T0 | Single 539010 SADLHRN3 115 539648 PRICHRD3 115 1 | B | 275 | 13.0618 | 147.021 |  |  |  | Add 3-winding transformer 539674 BARBER 4 138 539760 BARBER 3 115 539917 BARBER-1 13 M2
03ALL | ERIS | Thermal | 539678 GRTBEND3 115 539684 OTISSUB3 115 1 | 29SP | T0 | P11:345:AMMO::CALLAWAY:1 | B | 37.6 | -13.6249 | 405.433 |  |  |  | Rebuild line 539678 GRTBEND3 115 539684 OTISSUB3 115 1
03ALL | ERIS | Thermal | 539678 GRTBEND3 115 539684 OTISSUB3 115 1 | 26SP | T0 | P11:345:AMMO::CALLAWAY:1 | B | 37.6 | -13.6212 | 405.0072 |  |  |  | Rebuild line 539678 GRTBEND3 115 539684 OTISSUB3 115 1
03ALL | ERIS | Thermal | 539678 GRTBEND3 115 539684 OTISSUB3 115 1 | 29WP | T0 | System Intact | A | 119.5 | -2.7784 | 128.368 |  |  |  | Rebuild line 539678 GRTBEND3 115 539684 OTISSUB3 115 1
03ALL | ERIS | Thermal | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 29SP | T0 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 101 | -74.9795 | 231.6239 |  |  |  | Rebuild line 539692 SEWARD 3 115 539696 ST-JOHN3 115 1
03ALL | ERIS | Thermal | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 26SP | T0 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 101 | -73.8726 | 241.8637 |  |  |  | Rebuild line 539692 SEWARD 3 115 539696 ST-JOHN3 115 1
03ALL | ERIS | Thermal | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 29WP | T0 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 125.5 | -48.898 | 214.6381 |  |  |  | Rebuild line 539692 SEWARD 3 115 539696 ST-JOHN3 115 1
03ALL | ERIS | Thermal | 539753 PRATTENERGY3 115 539756 SKLYVL_GOAB3 115 1 | 29SP | T0 | System Intact | A | 153.4 | -9.5513 | 133.7801 |  |  |  | Rebuild line 539753 PRATTENERGY3 115 539756 SKLYVL_GOAB3 115 1
03ALL | ERIS | Thermal | 539753 PRATTENERGY3 115 539756 SKLYVL_GOAB3 115 1 | 26SP | T0 | System Intact | A | 153.4 | -9.3977 | 134.0359 |  |  |  | Rebuild line 539753 PRATTENERGY3 115 539756 SKLYVL_GOAB3 115 1
03ALL | ERIS | Thermal | 539753 PRATTENERGY3 115 539756 SKLYVL_GOAB3 115 1 | 29WP | T0 | System Intact | A | 188.2 | -4.8845 | 111.4362 |  |  |  | Rebuild line 539753 PRATTENERGY3 115 539756 SKLYVL_GOAB3 115 1
03ALL | ERIS | Thermal | 539760 BARBER 3 115 3WXFMR 534:BARBER 4 138 1 | 29SP | T0 | Single 539010 SADLHRN3 115 539648 PRICHRD3 115 1 | B | 275 | 5.489 | 130.9254 |  |  |  | Add 3-winding transformer 539674 BARBER 4 138 539760 BARBER 3 115 539917 BARBER-1 13 M2
03ALL | ERIS | Thermal | 539760 BARBER 3 115 3WXFMR 534:BARBER 4 138 1 | 26SP | T0 | Single 539010 SADLHRN3 115 539648 PRICHRD3 115 1 | B | 275 | 6.7772 | 133.6808 |  |  |  | Add 3-winding transformer 539674 BARBER 4 138 539760 BARBER 3 115 539917 BARBER-1 13 M2
03ALL | ERIS | Thermal | 539760 BARBER 3 115 3WXFMR 534:BARBER 4 138 1 | 29WP | T0 | Single 539010 SADLHRN3 115 539648 PRICHRD3 115 1 | B | 275 | 13.0306 | 142.5713 |  |  |  | Add 3-winding transformer 539674 BARBER 4 138 539760 BARBER 3 115 539917 BARBER-1 13 M2
03ALL | ERIS | Thermal | 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | 26SP | T0 | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | B | 1793 | 70.9891 | 116.7635 |  |  |  | Rebuild line 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1
03ALL | ERIS | Thermal | 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | 29SP | T0 | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | B | 1793 | 62.842 | 112.1793 |  |  |  | Rebuild line 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1
03ALL | ERIS | Thermal | 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | 29WP | T0 | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | B | 1793 | 69.3906 | 120.9981 |  |  |  | Rebuild line 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1
03ALL | ERIS | Thermal | 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | 29SP | T0 | P42:345:SPS:CARPENTER-OR335:::EHV: | B | 1123 | 87.6298 | 164.255 |  |  |  | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1
03ALL | ERIS | Thermal | 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | 26SP | T0 | P42:345:SPS:CARPENTER-OR335:::EHV: | B | 1123 | 101.1055 | 170.5318 |  |  |  | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1
03ALL | ERIS | Thermal | 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | 29WP | T0 | P42:345:SPS:CARPENTER-OR335:::EHV: | B | 1123 | 90.4744 | 170.3227 |  |  |  | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1
03ALL | ERIS | Thermal | 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | 26SP | T0 | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | B | 1793 | 68.5785 | 113.6438 |  |  |  | Rebuild line 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1
03ALL | ERIS | Thermal | 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | 29SP | T0 | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | B | 1793 | 60.4332 | 109.0246 |  |  |  | Rebuild line 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1
03ALL | ERIS | Thermal | 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | 29WP | T0 | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | B | 1793 | 67.0356 | 118.0764 |  |  |  | Rebuild line 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1
03ALL | ERIS | Thermal | 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | 29SP | T0 | P42:345:SPS:CARPENTER-OR335:::EHV: | B | 1140 | 100.055 | 175.6474 |  |  |  | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1
03ALL | ERIS | Thermal | 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | 26SP | T0 | P42:345:SPS:CARPENTER-OR335:::EHV: | B | 1140 | 113.2804 | 181.9081 |  |  |  | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1
03ALL | ERIS | Thermal | 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | 29WP | T0 | P42:345:SPS:CARPENTER-OR335:::EHV: | B | 1140 | 104.5891 | 184.0034 |  |  |  | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1
03ALL | ERIS | Thermal | 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | 29L | T0 | P42:345:SPS:CARPENTER-OR335:::EHV: | B | 1140 | 91.7068 | 117.12 |  |  |  | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1
03ALL | ERIS | Thermal | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | 29SP | T0 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | B | 261 | 52.9793 | 155.8553 |  |  |  | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
03ALL | ERIS | Thermal | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | 26SP | T0 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | B | 261 | 47.5399 | 150.8348 |  |  |  | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
03ALL | ERIS | Thermal | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | 29WP | T0 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | B | 297 | 53.2803 | 140.7678 |  |  |  | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
03ALL | ERIS | Thermal | 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 | 26SP | T0 | Single 541203 NASHUA5 161 541204 SMTHVL5 161 1 | B | 261 | -8.0093 | 122.1601 |  |  |  | Rebuild line 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1
03ALL | ERIS | Thermal | 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 | 29SP | T0 | Single 541203 NASHUA5 161 541204 SMTHVL5 161 1 | B | 261 | -8.0994 | 122.152 |  |  |  | Rebuild line 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1
03ALL | ERIS | Thermal | 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 | 29WP | T0 | Single 541203 NASHUA5 161 541204 SMTHVL5 161 1 | B | 297 | -5.6615 | 108.0166 |  |  |  | Rebuild line 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1
03ALL | ERIS | Thermal | 541207 ARCHIE 5 161 785640 G24-289-TAP 161 1 | 26SP | T0 | Single 761278 G17-108-TAP 161 785640 G24-289-TAP 161 1 | B | 280 | -4.107 | 123.2775 |  |  |  | Rebuild line 541207 ARCHIE 5 161 785640 G24-289-TAP 161 1
03ALL | ERIS | Thermal | 541207 ARCHIE 5 161 785640 G24-289-TAP 161 1 | 29SP | T0 | Single 761278 G17-108-TAP 161 785640 G24-289-TAP 161 1 | B | 280 | -4.1023 | 123.3198 |  |  |  | Rebuild line 541207 ARCHIE 5 161 785640 G24-289-TAP 161 1
03ALL | ERIS | Thermal | 541207 ARCHIE 5 161 785640 G24-289-TAP 161 1 | 29WP | T0 | Single 761278 G17-108-TAP 161 785640 G24-289-TAP 161 1 | B | 280 | -4.1087 | 123.2615 |  |  |  | Rebuild line 541207 ARCHIE 5 161 785640 G24-289-TAP 161 1
03ALL | ERIS | Thermal | 543094 SWAVRLY2 69 543063 SWAVRLY5 161 1 | 26SP | T0 | Single 543064 NORTON5 161 788220 G24-375-TAP 161 1 | B | 61 | -27.7101 | 139.2708 |  |  |  | Rebuild 2-winding transformer 543063 SWAVRLY5 161 543094 SWAVRLY2 69 1
03ALL | ERIS | Thermal | 543094 SWAVRLY2 69 543063 SWAVRLY5 161 1 | 29SP | T0 | Single 543064 NORTON5 161 788220 G24-375-TAP 161 1 | B | 61 | -27.3796 | 139.9402 |  |  |  | Rebuild 2-winding transformer 543063 SWAVRLY5 161 543094 SWAVRLY2 69 1
03ALL | ERIS | Thermal | 543094 SWAVRLY2 69 543063 SWAVRLY5 161 1 | 29WP | T0 | Single 543064 NORTON5 161 788220 G24-375-TAP 161 1 | B | 61 | -31.0096 | 142.1711 |  |  |  | Rebuild 2-winding transformer 543063 SWAVRLY5 161 543094 SWAVRLY2 69 1
03ALL | ERIS | Thermal | 543094 SWAVRLY2 69 543658 DOVER_TAP2 69 1 | 26SP | T0 | Single 543064 NORTON5 161 788220 G24-375-TAP 161 1 | B | 73 | 27.0561 | 160.513 |  |  |  | Rebuild line 543094 SWAVRLY2 69 543658 DOVER_TAP2 69 1
03ALL | ERIS | Thermal | 543094 SWAVRLY2 69 543658 DOVER_TAP2 69 1 | 29SP | T0 | Single 543064 NORTON5 161 788220 G24-375-TAP 161 1 | B | 73 | 27.4401 | 160.6795 |  |  |  | Rebuild line 543094 SWAVRLY2 69 543658 DOVER_TAP2 69 1
03ALL | ERIS | Thermal | 543094 SWAVRLY2 69 543658 DOVER_TAP2 69 1 | 29WP | T0 | Single 543064 NORTON5 161 788220 G24-375-TAP 161 1 | B | 97 | 22.1788 | 124.174 |  |  |  | Rebuild line 543094 SWAVRLY2 69 543658 DOVER_TAP2 69 1
03ALL | ERIS | Thermal | 543096 MAYVWTP2 69 543100 AMOCOPL2 69 1 | 26SP | T0 | Single 543064 NORTON5 161 788220 G24-375-TAP 161 1 | B | 48 | -17.0402 | 207.3514 |  |  |  | Rebuild line 543096 MAYVWTP2 69 543100 AMOCOPL2 69 1
03ALL | ERIS | Thermal | 543096 MAYVWTP2 69 543100 AMOCOPL2 69 1 | 29SP | T0 | Single 543064 NORTON5 161 788220 G24-375-TAP 161 1 | B | 48 | -17.4878 | 207.0386 |  |  |  | Rebuild line 543096 MAYVWTP2 69 543100 AMOCOPL2 69 1
03ALL | ERIS | Thermal | 543096 MAYVWTP2 69 543100 AMOCOPL2 69 1 | 29WP | T0 | Single 543064 NORTON5 161 788220 G24-375-TAP 161 1 | B | 52 | 11.3342 | 202.899 |  |  |  | Rebuild line 543096 MAYVWTP2 69 543100 AMOCOPL2 69 1
03ALL | ERIS | Thermal | 543098 CTY HIG2 69 543099 HIGNSVL2 69 1 | 26SP | T0 | Single 543064 NORTON5 161 788220 G24-375-TAP 161 1 | B | 73 | 10.9075 | 140.9245 |  |  |  | Rebuild line 543098 CTY HIG2 69 543099 HIGNSVL2 69 1
03ALL | ERIS | Thermal | 543098 CTY HIG2 69 543099 HIGNSVL2 69 1 | 29SP | T0 | Single 543064 NORTON5 161 788220 G24-375-TAP 161 1 | B | 73 | 11.13 | 140.7376 |  |  |  | Rebuild line 543098 CTY HIG2 69 543099 HIGNSVL2 69 1
03ALL | ERIS | Thermal | 543098 CTY HIG2 69 543099 HIGNSVL2 69 1 | 29WP | T0 | Single 543064 NORTON5 161 788220 G24-375-TAP 161 1 | B | 97 | 9.6768 | 112.1858 |  |  |  | Rebuild line 543098 CTY HIG2 69 543099 HIGNSVL2 69 1
03ALL | ERIS | Thermal | 543098 CTY HIG2 69 543657 CORDERTP2 69 1 | 26SP | T0 | Single 543064 NORTON5 161 788220 G24-375-TAP 161 1 | B | 73 | 24.156 | 157.7774 |  |  |  | Rebuild line 543098 CTY HIG2 69 543657 CORDERTP2 69 1
03ALL | ERIS | Thermal | 543098 CTY HIG2 69 543657 CORDERTP2 69 1 | 29SP | T0 | Single 543064 NORTON5 161 788220 G24-375-TAP 161 1 | B | 73 | 24.5943 | 157.9932 |  |  |  | Rebuild line 543098 CTY HIG2 69 543657 CORDERTP2 69 1
03ALL | ERIS | Thermal | 543098 CTY HIG2 69 543657 CORDERTP2 69 1 | 29WP | T0 | Single 543064 NORTON5 161 788220 G24-375-TAP 161 1 | B | 97 | 20.4829 | 122.4473 |  |  |  | Rebuild line 543098 CTY HIG2 69 543657 CORDERTP2 69 1
03ALL | ERIS | Thermal | 543099 HIGNSVL2 69 543102 WHGNSVL2 69 1 | 26SP | T0 | Single 543064 NORTON5 161 788220 G24-375-TAP 161 1 | B | 73 | 10.9136 | 140.3853 |  |  |  | Rebuild line 543099 HIGNSVL2 69 543102 WHGNSVL2 69 1
03ALL | ERIS | Thermal | 543099 HIGNSVL2 69 543102 WHGNSVL2 69 1 | 29SP | T0 | Single 543064 NORTON5 161 788220 G24-375-TAP 161 1 | B | 73 | 11.1521 | 140.1646 |  |  |  | Rebuild line 543099 HIGNSVL2 69 543102 WHGNSVL2 69 1
03ALL | ERIS | Thermal | 543099 HIGNSVL2 69 543102 WHGNSVL2 69 1 | 29WP | T0 | Single 543064 NORTON5 161 788220 G24-375-TAP 161 1 | B | 97 | 9.2833 | 111.8019 |  |  |  | Rebuild line 543099 HIGNSVL2 69 543102 WHGNSVL2 69 1
03ALL | ERIS | Thermal | 543100 AMOCOPL2 69 543102 WHGNSVL2 69 1 | 26SP | T0 | Single 543064 NORTON5 161 788220 G24-375-TAP 161 1 | B | 73 | 10.959 | 139.5843 |  |  |  | Rebuild line 543100 AMOCOPL2 69 543102 WHGNSVL2 69 1
03ALL | ERIS | Thermal | 543100 AMOCOPL2 69 543102 WHGNSVL2 69 1 | 29SP | T0 | Single 543064 NORTON5 161 788220 G24-375-TAP 161 1 | B | 73 | 11.2148 | 139.377 |  |  |  | Rebuild line 543100 AMOCOPL2 69 543102 WHGNSVL2 69 1
03ALL | ERIS | Thermal | 543100 AMOCOPL2 69 543102 WHGNSVL2 69 1 | 29WP | T0 | Single 543064 NORTON5 161 788220 G24-375-TAP 161 1 | B | 97 | 8.7292 | 111.2709 |  |  |  | Rebuild line 543100 AMOCOPL2 69 543102 WHGNSVL2 69 1
03ALL | ERIS | Thermal | 543657 CORDERTP2 69 543658 DOVER_TAP2 69 1 | 26SP | T0 | Single 543064 NORTON5 161 788220 G24-375-TAP 161 1 | B | 73 | 27.0775 | 160.49 |  |  |  | Rebuild line 543657 CORDERTP2 69 543658 DOVER_TAP2 69 1
03ALL | ERIS | Thermal | 543657 CORDERTP2 69 543658 DOVER_TAP2 69 1 | 29SP | T0 | Single 543064 NORTON5 161 788220 G24-375-TAP 161 1 | B | 73 | 27.4621 | 160.6571 |  |  |  | Rebuild line 543657 CORDERTP2 69 543658 DOVER_TAP2 69 1
03ALL | ERIS | Thermal | 543657 CORDERTP2 69 543658 DOVER_TAP2 69 1 | 29WP | T0 | Single 543064 NORTON5 161 788220 G24-375-TAP 161 1 | B | 73 | 29.4805 | 164.9669 |  |  |  | Rebuild line 543657 CORDERTP2 69 543658 DOVER_TAP2 69 1
03ALL | ERIS | Thermal | 547467 ORO110 5 161 547490 FIR417 5 161 1 | 26SP | T0 | Single 547476 ASB3495 161 547491 PUR4215 161 1 | B | 290 | 46.643 | 140.2763 |  |  |  | Rebuild line 547467 ORO110 5 161 547490 FIR417 5 161 1
03ALL | ERIS | Thermal | 547467 ORO110 5 161 547490 FIR417 5 161 1 | 29SP | T0 | Single 547476 ASB3495 161 547491 PUR4215 161 1 | B | 290 | 42.1939 | 132.222 |  |  |  | Rebuild line 547467 ORO110 5 161 547490 FIR417 5 161 1
03ALL | ERIS | Thermal | 547467 ORO110 5 161 547490 FIR417 5 161 1 | 29WP | T0 | Single 547476 ASB3495 161 547491 PUR4215 161 1 | B | 335 | 58.0599 | 139.6985 |  |  |  | Rebuild line 547467 ORO110 5 161 547490 FIR417 5 161 1
03ALL | ERIS | Thermal | 547468 AUR124 5 161 779490 G24-084-TAP 161 1 | 26SP | T0 | Single 547473 RDS2955 161 779490 G24-084-TAP 161 1 | B | 163 | -0.86691 | 101.3692 |  |  |  | Rebuild line 547468 AUR124 5 161 779490 G24-084-TAP 161 1
03ALL | ERIS | Thermal | 547468 AUR124 5 161 779490 G24-084-TAP 161 1 | 29SP | T0 | Single 547473 RDS2955 161 779490 G24-084-TAP 161 1 | B | 163 | -0.87199 | 100.9075 |  |  |  | Rebuild line 547468 AUR124 5 161 779490 G24-084-TAP 161 1
03ALL | ERIS | Thermal | 547468 AUR124 5 161 779490 G24-084-TAP 161 1 | 29WP | T0 | Single 547473 RDS2955 161 779490 G24-084-TAP 161 1 | B | 163 | -0.86652 | 101.7775 |  |  |  | Rebuild line 547468 AUR124 5 161 779490 G24-084-TAP 161 1
03ALL | ERIS | Thermal | 547473 RDS295 5 161 779490 G24-084-TAP 161 1 | 26SP | T0 | P12:161:EES:TABLE R5!:RVS438 5!:1:HV: | B | 163 | 59.4082 | 101.4313 |  |  |  | Rebuild line 547473 RDS295 5 161 779490 G24-084-TAP 161 1
03ALL | ERIS | Thermal | 547476 ASB349 5 161 547477 CJ 366 5 161 1 | 29WP | T0 | Single 547476 ASB3495 161 547491 PUR4215 161 1 | B | 322 | 69.5289 | 154.6192 |  |  |  | Rebuild line 547476 ASB349 5 161 547477 CJ 366 5 161 1
03ALL | ERIS | Thermal | 547476 ASB349 5 161 547477 CJ 366 5 161 1 | 26SP | T0 | Single 547476 ASB3495 161 547491 PUR4215 161 1 | B | 290 | 56.2857 | 150.0778 |  |  |  | Rebuild line 547476 ASB349 5 161 547477 CJ 366 5 161 1
03ALL | ERIS | Thermal | 547476 ASB349 5 161 547477 CJ 366 5 161 1 | 29SP | T0 | Single 547476 ASB3495 161 547491 PUR4215 161 1 | B | 290 | 51.9859 | 142.178 |  |  |  | Rebuild line 547476 ASB349 5 161 547477 CJ 366 5 161 1
03ALL | ERIS | Thermal | 547476 ASB349 5 161 547491 PUR421 5 161 1 | 26SP | T0 | Single 547476 ASB3495 161 547477 CJ3665 161 1 | B | 290 | 57.9324 | 142.0532 |  |  |  | Rebuild line 547476 ASB349 5 161 547491 PUR421 5 161 1
03ALL | ERIS | Thermal | 547476 ASB349 5 161 547491 PUR421 5 161 1 | 29SP | T0 | Single 547476 ASB3495 161 547477 CJ3665 161 1 | B | 290 | 54.1521 | 135.0594 |  |  |  | Rebuild line 547476 ASB349 5 161 547491 PUR421 5 161 1
03ALL | ERIS | Thermal | 547476 ASB349 5 161 547491 PUR421 5 161 1 | 29WP | T0 | Single 547476 ASB3495 161 547477 CJ3665 161 1 | B | 322 | 69.8414 | 146.1118 |  |  |  | Rebuild line 547476 ASB349 5 161 547491 PUR421 5 161 1
03ALL | ERIS | Thermal | 547477 CJ 366 5 161 547490 FIR417 5 161 1 | 26SP | T0 | Single 547476 ASB3495 161 547491 PUR4215 161 1 | B | 290 | 52.3912 | 146.1174 |  |  |  | Rebuild line 547477 CJ 366 5 161 547490 FIR417 5 161 1
03ALL | ERIS | Thermal | 547477 CJ 366 5 161 547490 FIR417 5 161 1 | 29SP | T0 | Single 547476 ASB3495 161 547491 PUR4215 161 1 | B | 290 | 48.0301 | 138.1563 |  |  |  | Rebuild line 547477 CJ 366 5 161 547490 FIR417 5 161 1
03ALL | ERIS | Thermal | 547477 CJ 366 5 161 547490 FIR417 5 161 1 | 29WP | T0 | Single 547476 ASB3495 161 547491 PUR4215 161 1 | B | 335 | 63.2895 | 145.0107 |  |  |  | Rebuild line 547477 CJ 366 5 161 547490 FIR417 5 161 1
03ALL | ERIS | Thermal | 547485 CAR395 5 161 547491 PUR421 5 161 1 | 26SP | T0 | Single 547476 ASB3495 161 547477 CJ3665 161 1 | B | 290 | 55.6683 | 139.7451 |  |  |  | Rebuild line 547485 CAR395 5 161 547491 PUR421 5 161 1
03ALL | ERIS | Thermal | 547485 CAR395 5 161 547491 PUR421 5 161 1 | 29SP | T0 | Single 547476 ASB3495 161 547477 CJ3665 161 1 | B | 290 | 51.8511 | 132.7182 |  |  |  | Rebuild line 547485 CAR395 5 161 547491 PUR421 5 161 1
03ALL | ERIS | Thermal | 547485 CAR395 5 161 547491 PUR421 5 161 1 | 29WP | T0 | Single 547476 ASB3495 161 547477 CJ3665 161 1 | B | 335 | 65.0806 | 138.3414 |  |  |  | Rebuild line 547485 CAR395 5 161 547491 PUR421 5 161 1
03ALL | ERIS | Thermal | 547554 BAX492 2 69 547601 HOC404 2 69 1 | 26SP | T0 | Single 547469 RIV4525 161 547729 BAX4885 161 1 | B | 66 | 66.8443 | 110.8216 |  |  |  | Rebuild line 547554 BAX492 2 69 547601 HOC404 2 69 1
03ALL | ERIS | Thermal | 547554 BAX492 2 69 547601 HOC404 2 69 1 | 29SP | T0 | Single 547469 RIV4525 161 547729 BAX4885 161 1 | B | 66 | 58.5785 | 105.1788 |  |  |  | Rebuild line 547554 BAX492 2 69 547601 HOC404 2 69 1
03ALL | ERIS | Thermal | 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | 29SP | T0 | P55:345:OPPD:S3458 3::FN13:EHV: | B | 956 | 67.8421 | 102.8881 |  |  |  | Rebuild line 635017 ATCHISON 3 345 640139 COOPER 3 345 1
03ALL | ERIS | Thermal | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | 29L | T0 | P42:345:NPPD:BKR-AXT-3308:::: | B | 254 | 63.3332 | 107.1888 |  |  |  | Rebuild line 640066 AXTELL 7 115 640250 KEARNEY7 115 1
03ALL | ERIS | Thermal | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | 29SP | T0 | P42:345:NPPD:BKR-AXT-3308:::: | B | 254 | 83.7101 | 144.4949 |  |  |  | Rebuild line 640066 AXTELL 7 115 640250 KEARNEY7 115 1
03ALL | ERIS | Thermal | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | 26SP | T0 | P42:345:NPPD:BKR-AXT-3308:::: | B | 254 | 63.9233 | 133.8298 |  |  |  | Rebuild line 640066 AXTELL 7 115 640250 KEARNEY7 115 1
03ALL | ERIS | Thermal | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | 29WP | T0 | P42:345:NPPD:BKR-AXT-3308:::: | B | 254 | 63.9352 | 133.9614 |  |  |  | Rebuild line 640066 AXTELL 7 115 640250 KEARNEY7 115 1
03ALL | ERIS | Thermal | 640139 COOPER 3 345 778170 G24-040-TAP 345 1 | 29SP | T0 | P12:345:MEC:ORIENT:NORTHBORO:1 | B | 1195 | 64.5829 | 109.0573 |  |  |  | Rebuild line 640139 COOPER 3 345 778170 G24-040-TAP 345 1
03ALL | ERIS | Thermal | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | 29WP | T0 | P23:345:SUNC:HLC_BRK282:::EHV: | B | 956 | 19.292 | 101.7852 |  |  |  | Rebuild line 640183 GENTLMN3 345 640325 REDWILO3 345 1
03ALL | ERIS | Thermal | 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | 29SP | T0 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | B | 956 | 68.6808 | 142.9808 |  |  |  | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1
03ALL | ERIS | Thermal | 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | 26SP | T0 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | B | 956 | 56.791 | 135.5824 |  |  |  | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1
03ALL | ERIS | Thermal | 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | 29WP | T0 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | B | 956 | 51.9182 | 125.7392 |  |  |  | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1
03ALL | ERIS | Thermal | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | 29SP | T0 | P42:345:NPPD:BKR-TOB-3304:::: | B | 956 | 82.9703 | 135.8717 |  |  |  | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
03ALL | ERIS | Thermal | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | 26SP | T0 | P42:345:NPPD:BKR-TOB-3304:::: | B | 956 | 56.7286 | 128.4402 |  |  |  | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
03ALL | ERIS | Thermal | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | 29WP | T0 | P42:345:NPPD:BKR-TOB-3304:::: | B | 956 | 57.1084 | 120.6146 |  |  |  | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
03ALL | ERIS | Thermal | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | 29SP | T0 | P42:345:NPPD:BKR-MOR-3306:::: | B | 956 | 59.8683 | 102.1623 |  |  |  | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
03ALL | ERIS | Thermal | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | 26SP | T0 | P42:345:NPPD:BKR-MOR-3306:::: | B | 956 | 45.6533 | 101.0414 |  |  |  | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
03ALL | ERIS | Thermal | 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | 29SP | T0 | P42:345:NPPD:BKR-MOR-3310:::: | B | 956 | 54.9714 | 104.9699 |  |  |  | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1
03ALL | ERIS | Thermal | 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | 26SP | T0 | P42:345:NPPD:BKR-MOR-3310:::: | B | 956 | 39.5694 | 101.4804 |  |  |  | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1
03ALL | ERIS | Thermal | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | 29SP | T0 | P23:345:SUNC:HLC_BRK282:::EHV: | B | 966 | 45.6263 | 146.6299 |  |  |  | Rebuild line 640325 REDWILO3 345 767280 G22-015-TAP 345 1
03ALL | ERIS | Thermal | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | 26SP | T0 | P23:345:SUNC:HLC_BRK282:::EHV: | B | 966 | 37.2967 | 138.7556 |  |  |  | Rebuild line 640325 REDWILO3 345 767280 G22-015-TAP 345 1
03ALL | ERIS | Thermal | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | 29WP | T0 | P23:345:SUNC:HLC_BRK282:::EHV: | B | 966 | 36.8017 | 142.8935 |  |  |  | Rebuild line 640325 REDWILO3 345 767280 G22-015-TAP 345 1
03ALL | ERIS | Thermal | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | 29L | T0 | P23:345:SUNC:HLC_BRK282:::EHV: | B | 966 | 53.5741 | 117.4451 |  |  |  | Rebuild line 640325 REDWILO3 345 767280 G22-015-TAP 345 1
03ALL | ERIS | Thermal | 645458 S3458 3 345 778170 G24-040-TAP 345 1 | 29SP | T0 | P12:345:MEC:ORIENT:NORTHBORO:1 | B | 1195 | 64.4778 | 114.664 |  |  |  | Rebuild line 645458 S3458 3 345 778170 G24-040-TAP 345 1
03ALL | ERIS | Thermal | 645458 S3458 3 345 778170 G24-040-TAP 345 1 | 26SP | T0 | P12:345:MEC:ORIENT:NORTHBORO:1 | B | 1195 | 43.1101 | 104.5707 |  |  |  | Rebuild line 645458 S3458 3 345 778170 G24-040-TAP 345 1
03ALL | ERIS | Thermal | 761278 G17-108-TAP 161 785640 G24-289-TAP 161 1 | 29WP | T0 | Single 541207 ARCHIE5 161 785640 G24-289-TAP 161 1 | B | 280 | -2.601 | 121.963 |  |  |  | Rebuild line 761278 G17-108-TAP 161 785640 G24-289-TAP 161 1
03ALL | ERIS | Thermal | 761278 G17-108-TAP 161 785640 G24-289-TAP 161 1 | 26SP | T0 | Single 541207 ARCHIE5 161 785640 G24-289-TAP 161 1 | B | 280 | -2.5899 | 122.0815 |  |  |  | Rebuild line 761278 G17-108-TAP 161 785640 G24-289-TAP 161 1
03ALL | ERIS | Thermal | 761278 G17-108-TAP 161 785640 G24-289-TAP 161 1 | 29SP | T0 | Single 541207 ARCHIE5 161 785640 G24-289-TAP 161 1 | B | 280 | -2.5887 | 122.0731 |  |  |  | Rebuild line 761278 G17-108-TAP 161 785640 G24-289-TAP 161 1
04ALL | ERIS | Thermal | 337505 3EMMET 115 507448 NHOPE 3 115 1 | 29SP | T0 | Single 338875 3PATMOS.W# 115 503912 FULTON3 115 1 | B | 155 | 72.2066 | 179.9213 |  |  |  | Rebuild line 337505 3EMMET 115 507448 NHOPE 3 115 1
04ALL | ERIS | Thermal | 337505 3EMMET 115 507448 NHOPE 3 115 1 | 29WP | T0 | Single 338875 3PATMOS.W# 115 503912 FULTON3 115 1 | B | 155 | 73.5773 | 192.6057 |  |  |  | Rebuild line 337505 3EMMET 115 507448 NHOPE 3 115 1
04ALL | ERIS | Thermal | 337505 3EMMET 115 507448 NHOPE 3 115 1 | 26SP | T0 | Single 338875 3PATMOS.W# 115 503912 FULTON3 115 1 | B | 155 | 64.8563 | 182.3785 |  |  |  | Rebuild line 337505 3EMMET 115 507448 NHOPE 3 115 1
04ALL | ERIS | Thermal | 338110 5HILLTOP% 161 505507 SWPINEY5 161 1 | 26SP | T0 | System Intact | A | 189 | 73.993 | 102.9098 |  |  |  | Rebuild line 338110 5HILLTOP% 161 505507 SWPINEY5 161 1
04ALL | ERIS | Thermal | 338758 5HEBER.N# 161 505422 GREERSF5 161 1 | 26SP | T0 | Single 774620 G23-132-TAP 161 780390 G24-114-TAP 161 1 | B | 228 | 37.4438 | 115.4535 |  |  |  | Rebuild line 338758 5HEBER.N# 161 505422 GREERSF5 161 1
04ALL | ERIS | Thermal | 338758 5HEBER.N# 161 505422 GREERSF5 161 1 | 29SP | T0 | Single 774620 G23-132-TAP 161 780390 G24-114-TAP 161 1 | B | 228 | 37.7426 | 120.8102 |  |  |  | Rebuild line 338758 5HEBER.N# 161 505422 GREERSF5 161 1
04ALL | ERIS | Thermal | 338758 5HEBER.N# 161 505422 GREERSF5 161 1 | 29WP | T0 | Single 774620 G23-132-TAP 161 780390 G24-114-TAP 161 1 | B | 228 | 31.7942 | 118.6549 |  |  |  | Rebuild line 338758 5HEBER.N# 161 505422 GREERSF5 161 1
04ALL | ERIS | Thermal | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | 29SP | T0 | Single 507449 NWHOPE3 115 507452 HOPESWI3 115 1 | B | 157 | 81.5466 | 177.1568 |  |  |  | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
04ALL | ERIS | Thermal | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | 29WP | T0 | Single 507449 NWHOPE3 115 507452 HOPESWI3 115 1 | B | 159 | 81.4834 | 186.254 |  |  |  | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
04ALL | ERIS | Thermal | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | 26SP | T0 | Single 507449 NWHOPE3 115 507452 HOPESWI3 115 1 | B | 157 | 73.846 | 178.7966 |  |  |  | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
04ALL | ERIS | Thermal | 504122 MCNAB 3 115 507453 HOPE 3 115 1 | 29SP | T0 | P12:345:AEPW:TURK7:NWTXARK7::: | B | 288 | 46.7153 | 105.9293 |  |  |  | Rebuild line 504122 MCNAB 3 115 507453 HOPE 3 115 1
04ALL | ERIS | Thermal | 504122 MCNAB 3 115 507453 HOPE 3 115 1 | 26SP | T0 | P12:345:AEPW:TURK7:NWTXARK7::: | B | 288 | 42.4282 | 107.115 |  |  |  | Rebuild line 504122 MCNAB 3 115 507453 HOPE 3 115 1
04ALL | ERIS | Thermal | 504122 MCNAB 3 115 507456 TURK 3 115 1 | 26SP | T0 | P12:345:AEPW:TURK7:NWTXARK7::: | B | 275 | 47.3052 | 115.1657 |  |  |  | Rebuild line 504122 MCNAB 3 115 507456 TURK 3 115 1
04ALL | ERIS | Thermal | 504122 MCNAB 3 115 507456 TURK 3 115 1 | 29SP | T0 | P12:345:AEPW:TURK7:NWTXARK7::: | B | 275 | 51.9167 | 114.0267 |  |  |  | Rebuild line 504122 MCNAB 3 115 507456 TURK 3 115 1
04ALL | ERIS | Thermal | 504122 MCNAB 3 115 507456 TURK 3 115 1 | 29WP | T0 | P12:345:AEPW:TURK7:NWTXARK7::: | B | 311 | 44.3385 | 106.1841 |  |  |  | Rebuild line 504122 MCNAB 3 115 507456 TURK 3 115 1
04ALL | ERIS | Thermal | 505507 SWPINEY5 161 505508 DARDANE5 161 1 | 26SP | T0 | System Intact | A | 189 | 79.8213 | 108.8527 |  |  |  | Rebuild line 505507 SWPINEY5 161 505508 DARDANE5 161 1
04ALL | ERIS | Thermal | 505592 WELEETK4 138 505595 GREASYC4 138 1 | 29SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 147 | 21.5127 | 103.4868 |  |  |  | Rebuild line 505592 WELEETK4 138 505595 GREASYC4 138 1
04ALL | ERIS | Thermal | 505592 WELEETK4 138 505595 GREASYC4 138 1 | 26SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 147 | 17.1651 | 102.4715 |  |  |  | Rebuild line 505592 WELEETK4 138 505595 GREASYC4 138 1
04ALL | ERIS | Thermal | 505595 GREASYC4 138 505596 EXPLOR 4 138 1 | 29SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 147 | 26.9015 | 109.0026 |  |  |  | Rebuild line 505595 GREASYC4 138 505596 EXPLOR 4 138 1
04ALL | ERIS | Thermal | 505595 GREASYC4 138 505596 EXPLOR 4 138 1 | 26SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 147 | 22.3075 | 108.8971 |  |  |  | Rebuild line 505595 GREASYC4 138 505596 EXPLOR 4 138 1
04ALL | ERIS | Thermal | 505596 EXPLOR 4 138 505598 ALLEN 4 138 1 | 29SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 147 | 33.6356 | 115.6924 |  |  |  | Rebuild line 505596 EXPLOR 4 138 505598 ALLEN 4 138 1
04ALL | ERIS | Thermal | 505596 EXPLOR 4 138 505598 ALLEN 4 138 1 | 26SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 147 | 29.0062 | 115.6976 |  |  |  | Rebuild line 505596 EXPLOR 4 138 505598 ALLEN 4 138 1
04ALL | ERIS | Thermal | 505598 ALLEN 4 138 505600 TUPELO 4 138 1 | 29SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 147 | 45.424 | 128.7878 |  |  |  | Rebuild line 505598 ALLEN 4 138 505600 TUPELO 4 138 1
04ALL | ERIS | Thermal | 505598 ALLEN 4 138 505600 TUPELO 4 138 1 | 26SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 147 | 40.7946 | 131.8164 |  |  |  | Rebuild line 505598 ALLEN 4 138 505600 TUPELO 4 138 1
04ALL | ERIS | Thermal | 505600 TUPELO 4 138 505602 S BROWN4 138 1 | 29SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 147 | 74.696 | 169.0637 |  |  |  | Rebuild line 505600 TUPELO 4 138 505602 S BROWN4 138 1
04ALL | ERIS | Thermal | 505600 TUPELO 4 138 505602 S BROWN4 138 1 | 29WP | T0 | Single 520918 FROGVIL4 138 773820 G23-092-TAP 138 1 | B | 159 | 60.2847 | 162.415 |  |  |  | Rebuild line 505600 TUPELO 4 138 505602 S BROWN4 138 1
04ALL | ERIS | Thermal | 505600 TUPELO 4 138 505602 S BROWN4 138 1 | 26SP | T0 | Single 520918 FROGVIL4 138 773820 G23-092-TAP 138 1 | B | 147 | 55.4193 | 172.4551 |  |  |  | Rebuild line 505600 TUPELO 4 138 505602 S BROWN4 138 1
04ALL | ERIS | Thermal | 505600 TUPELO 4 138 510881 ALLENGT4 138 1 | 26SP | T0 | Single 510887 ATOKA--4 138 782490 G24-184-TAP 138 1 | B | 152 | -17.1809 | 111.9511 |  |  |  | Rebuild line 505600 TUPELO 4 138 510881 ALLENGT4 138 1
04ALL | ERIS | Thermal | 505600 TUPELO 4 138 510881 ALLENGT4 138 1 | 29SP | T0 | Single 510887 ATOKA--4 138 782490 G24-184-TAP 138 1 | B | 152 | -16.9218 | 112.1374 |  |  |  | Rebuild line 505600 TUPELO 4 138 510881 ALLENGT4 138 1
04ALL | ERIS | Thermal | 505602 S BROWN4 138 769060 G22-104-TAP 138 1 | 29SP | T0 | Single 520918 FROGVIL4 138 773820 G23-092-TAP 138 1 | B | 287 | 65.2966 | 189.927 |  |  |  | Rebuild line 505602 S BROWN4 138 769060 G22-104-TAP 138 1
04ALL | ERIS | Thermal | 505602 S BROWN4 138 769060 G22-104-TAP 138 1 | 29WP | T0 | Single 520918 FROGVIL4 138 773820 G23-092-TAP 138 1 | B | 287 | 63.9703 | 190.0274 |  |  |  | Rebuild line 505602 S BROWN4 138 769060 G22-104-TAP 138 1
04ALL | ERIS | Thermal | 505602 S BROWN4 138 769060 G22-104-TAP 138 1 | 26SP | T0 | Single 520918 FROGVIL4 138 773820 G23-092-TAP 138 1 | B | 287 | 65.1759 | 189.5377 |  |  |  | Rebuild line 505602 S BROWN4 138 769060 G22-104-TAP 138 1
04ALL | ERIS | Thermal | 507448 NHOPE 3 115 507449 NWHOPE 3 115 1 | 29SP | T0 | Single 338875 3PATMOS.W# 115 503912 FULTON3 115 1 | B | 142 | 84.2224 | 202.4055 |  |  |  | Rebuild line 507448 NHOPE 3 115 507449 NWHOPE 3 115 1
04ALL | ERIS | Thermal | 507448 NHOPE 3 115 507449 NWHOPE 3 115 1 | 29WP | T0 | Single 338875 3PATMOS.W# 115 503912 FULTON3 115 1 | B | 160 | 75.4889 | 191.2626 |  |  |  | Rebuild line 507448 NHOPE 3 115 507449 NWHOPE 3 115 1
04ALL | ERIS | Thermal | 507448 NHOPE 3 115 507449 NWHOPE 3 115 1 | 26SP | T0 | Single 338875 3PATMOS.W# 115 503912 FULTON3 115 1 | B | 142 | 75.7703 | 204.4096 |  |  |  | Rebuild line 507448 NHOPE 3 115 507449 NWHOPE 3 115 1
04ALL | ERIS | Thermal | 507449 NWHOPE 3 115 507452 HOPESWI3 115 1 | 29SP | T0 | Single 338875 3PATMOS.W# 115 503912 FULTON3 115 1 | B | 142 | 95.3741 | 212.008 |  |  |  | Rebuild line 507449 NWHOPE 3 115 507452 HOPESWI3 115 1
04ALL | ERIS | Thermal | 507449 NWHOPE 3 115 507452 HOPESWI3 115 1 | 29WP | T0 | Single 338875 3PATMOS.W# 115 503912 FULTON3 115 1 | B | 160 | 84.0982 | 198.3733 |  |  |  | Rebuild line 507449 NWHOPE 3 115 507452 HOPESWI3 115 1
04ALL | ERIS | Thermal | 507449 NWHOPE 3 115 507452 HOPESWI3 115 1 | 26SP | T0 | Single 338875 3PATMOS.W# 115 503912 FULTON3 115 1 | B | 142 | 87.6493 | 214.6163 |  |  |  | Rebuild line 507449 NWHOPE 3 115 507452 HOPESWI3 115 1
04ALL | ERIS | Thermal | 507452 HOPESWI3 115 507453 HOPE 3 115 1 | 29SP | T0 | ASGI-2024-023_POI_783390_Generator_outage | B | 142 | 88.6763 | 156.3171 |  |  |  | Rebuild line 507452 HOPESWI3 115 507453 HOPE 3 115 1
04ALL | ERIS | Thermal | 507452 HOPESWI3 115 507453 HOPE 3 115 1 | 29WP | T0 | Single 338875 3PATMOS.W# 115 503912 FULTON3 115 1 | B | 160 | 96.0288 | 137.0033 |  |  |  | Rebuild line 507452 HOPESWI3 115 507453 HOPE 3 115 1
04ALL | ERIS | Thermal | 507452 HOPESWI3 115 507453 HOPE 3 115 1 | 26SP | T0 | Single 338875 3PATMOS.W# 115 503912 FULTON3 115 1 | B | 142 | 104.1939 | 149.737 |  |  |  | Rebuild line 507452 HOPESWI3 115 507453 HOPE 3 115 1
04ALL | ERIS | Thermal | 507454 TURK 4 138 3WXFMR 520:TURK 2 138 1 | 29WP | T0 | P12:345:AEPW:TURK7:NWTXARK7::: | B | 250 | 55.7086 | 131.2848 |  |  |  | Add 3-winding transformer 507454 TURK 4 138 507456 TURK 3 115 507458 TURK1 1 13 M2
04ALL | ERIS | Thermal | 507454 TURK 4 138 3WXFMR 520:TURK 2 138 1 | 26SP | T0 | P12:345:AEPW:TURK7:NWTXARK7::: | B | 177 | 74.2317 | 178.4258 |  |  |  | Add 3-winding transformer 507454 TURK 4 138 507456 TURK 3 115 507458 TURK1 1 13 M2
04ALL | ERIS | Thermal | 507454 TURK 4 138 3WXFMR 520:TURK 2 138 1 | 29SP | T0 | P12:345:AEPW:TURK7:NWTXARK7::: | B | 250 | 57.6794 | 125.2699 |  |  |  | Add 3-winding transformer 507454 TURK 4 138 507456 TURK 3 115 507458 TURK1 1 13 M2
04ALL | ERIS | Thermal | 507456 TURK 3 115 3WXFMR 520:TURK 2 138 1 | 29WP | T0 | P12:345:AEPW:TURK7:NWTXARK7::: | B | 250 | 55.8016 | 131.0228 |  |  |  | Add 3-winding transformer 507454 TURK 4 138 507456 TURK 3 115 507458 TURK1 1 13 M2
04ALL | ERIS | Thermal | 507456 TURK 3 115 3WXFMR 520:TURK 2 138 1 | 26SP | T0 | P12:345:AEPW:TURK7:NWTXARK7::: | B | 177 | 74.505 | 178.1308 |  |  |  | Add 3-winding transformer 507454 TURK 4 138 507456 TURK 3 115 507458 TURK1 1 13 M2
04ALL | ERIS | Thermal | 507456 TURK 3 115 3WXFMR 520:TURK 2 138 1 | 29SP | T0 | P12:345:AEPW:TURK7:NWTXARK7::: | B | 250 | 57.7893 | 124.9782 |  |  |  | Add 3-winding transformer 507454 TURK 4 138 507456 TURK 3 115 507458 TURK1 1 13 M2
04ALL | ERIS | Thermal | 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | 26SP | T0 | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | B | 188 | 80.9132 | 111.5021 |  |  |  | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1
04ALL | ERIS | Thermal | 508055 BLOOMBG2 69 783570 G24-220-TAP 69 1 | 29SP | T0 | Single 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | -1.188 | 101.6948 |  |  |  | Rebuild line 508055 BLOOMBG2 69 783570 G24-220-TAP 69 1
04ALL | ERIS | Thermal | 508055 BLOOMBG2 69 783570 G24-220-TAP 69 1 | 26SP | T0 | Single 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | -1.1782 | 101.4884 |  |  |  | Rebuild line 508055 BLOOMBG2 69 783570 G24-220-TAP 69 1
04ALL | ERIS | Thermal | 508072 NWTXARK7 345 508359 WELSH 7 345 1 | 26SP | T0 | Single 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | B | 927 | 25.3588 | 100.5821 |  |  |  | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1
04ALL | ERIS | Thermal | 508072 NWTXARK7 345 508359 WELSH 7 345 1 | 29SP | T0 | Single 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | B | 927 | 16.6772 | 100.9725 |  |  |  | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1
04ALL | ERIS | Thermal | 508089 WATLANT2 69 779100 G24-071-TAP 69 1 | 29SP | T0 | Single 508054 BANN4 138 508075 REDSPRG4 138 1 | B | 76 | -14.5133 | 112.6004 |  |  |  | Rebuild line 508089 WATLANT2 69 779100 G24-071-TAP 69 1
04ALL | ERIS | Thermal | 508089 WATLANT2 69 779100 G24-071-TAP 69 1 | 26SP | T0 | Single 508054 BANN4 138 508075 REDSPRG4 138 1 | B | 76 | -12.297 | 111.6206 |  |  |  | Rebuild line 508089 WATLANT2 69 779100 G24-071-TAP 69 1
04ALL | ERIS | Thermal | 508089 WATLANT2 69 779100 G24-071-TAP 69 1 | 29WP | T0 | Single 508054 BANN4 138 508075 REDSPRG4 138 1 | B | 85 | -7.5926 | 104.5347 |  |  |  | Rebuild line 508089 WATLANT2 69 779100 G24-071-TAP 69 1
04ALL | ERIS | Thermal | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | 29SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 1059 | 33.995 | 101.0357 |  |  |  | Rebuild line 508298 LYDIA 7 345 779010 G24-068-TAP 345 1
04ALL | ERIS | Thermal | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | 26SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 1059 | 37.112 | 101.1849 |  |  |  | Rebuild line 508298 LYDIA 7 345 779010 G24-068-TAP 345 1
04ALL | ERIS | Thermal | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 29SP | T0 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | B | 1000 | 68.2051 | 130.5437 |  |  |  | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1
04ALL | ERIS | Thermal | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 29WP | T0 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | B | 1220 | 61.1991 | 111.4934 |  |  |  | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1
04ALL | ERIS | Thermal | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 26SP | T0 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | B | 1000 | 70.1587 | 130.5327 |  |  |  | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1
04ALL | ERIS | Thermal | 508359 WELSH 7 345 776060 G23-204-TAP 345 1 | 29SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 1059 | 33.6252 | 128.8688 |  |  |  | Rebuild line 508359 WELSH 7 345 776060 G23-204-TAP 345 1
04ALL | ERIS | Thermal | 508359 WELSH 7 345 776060 G23-204-TAP 345 1 | 29WP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 1186 | 34.043 | 118.9915 |  |  |  | Rebuild line 508359 WELSH 7 345 776060 G23-204-TAP 345 1
04ALL | ERIS | Thermal | 508359 WELSH 7 345 776060 G23-204-TAP 345 1 | 26SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 1059 | 36.8527 | 129.0174 |  |  |  | Rebuild line 508359 WELSH 7 345 776060 G23-204-TAP 345 1
04ALL | ERIS | Thermal | 508803 GILLIAM2 69 508815 SUPEROR2 69 1 | 29SP | T0 | Single 508804 HOSSTON2 69 508817 VIVIAN2 69 1 | B | 39 | 36.9147 | 100.2968 |  |  |  | Rebuild line 508803 GILLIAM2 69 508815 SUPEROR2 69 1
04ALL | ERIS | Thermal | 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | 29SP | T0 | P12:69:AEPW:WATLANT2:LINDEN 2::: | B | 53 | -6.2384 | 100.7104 |  |  |  | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1
04ALL | ERIS | Thermal | 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | 29WP | T0 | P12:69:AEPW:WATLANT2:LINDEN 2::: | B | 53 | 5.3195 | 108.1009 |  |  |  | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1
04ALL | ERIS | Thermal | 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | 26SP | T0 | P12:69:AEPW:WATLANT2:LINDEN 2::: | B | 53 | -9.0699 | 100.2559 |  |  |  | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1
04ALL | ERIS | Thermal | 508805 LIEBERM2 69 508812 OILCITY2 69 1 | 29SP | T0 | Single 508834 JEFFRSN2 69 786120 G24-305-TAP 69 1 | B | 53 | 14.3183 | 130.2631 |  |  |  | Rebuild line 508805 LIEBERM2 69 508812 OILCITY2 69 1
04ALL | ERIS | Thermal | 508805 LIEBERM2 69 508812 OILCITY2 69 1 | 26SP | T0 | Single 508813 PLAINDL2 69 778290 G24-044-TAP 69 1 | B | 53 | -13.6989 | 120.1914 |  |  |  | Rebuild line 508805 LIEBERM2 69 508812 OILCITY2 69 1
04ALL | ERIS | Thermal | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | 29SP | T0 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | B | 162 | 63.0491 | 127.1816 |  |  |  | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
04ALL | ERIS | Thermal | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | 26SP | T0 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | B | 162 | 31.4454 | 120.4257 |  |  |  | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
04ALL | ERIS | Thermal | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | 29WP | T0 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | B | 183 | 39.3204 | 111.5985 |  |  |  | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
04ALL | ERIS | Thermal | 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | 26SP | T0 | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | B | 188 | 82.8004 | 113.4126 |  |  |  | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1
04ALL | ERIS | Thermal | 508812 OILCITY2 69 508815 SUPEROR2 69 1 | 29SP | T0 | Single 508834 JEFFRSN2 69 786120 G24-305-TAP 69 1 | B | 53 | 16.1029 | 135.6499 |  |  |  | Rebuild line 508812 OILCITY2 69 508815 SUPEROR2 69 1
04ALL | ERIS | Thermal | 508812 OILCITY2 69 508815 SUPEROR2 69 1 | 26SP | T0 | Single 508813 PLAINDL2 69 778290 G24-044-TAP 69 1 | B | 53 | 12.0374 | 127.5962 |  |  |  | Rebuild line 508812 OILCITY2 69 508815 SUPEROR2 69 1
04ALL | ERIS | Thermal | 508813 PLAINDL2 69 778290 G24-044-TAP 69 1 | 29SP | T0 | Single 508812 OILCITY2 69 508815 SUPEROR2 69 1 | B | 39 | 34.4938 | 132.5463 |  |  |  | Rebuild line 508813 PLAINDL2 69 778290 G24-044-TAP 69 1
04ALL | ERIS | Thermal | 508813 PLAINDL2 69 778290 G24-044-TAP 69 1 | 26SP | T0 | Single 508812 OILCITY2 69 508815 SUPEROR2 69 1 | B | 39 | 20.3136 | 129.2905 |  |  |  | Rebuild line 508813 PLAINDL2 69 778290 G24-044-TAP 69 1
04ALL | ERIS | Thermal | 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1 | 29SP | T0 | P12:69:AEPW:WATLANT2:LINDEN 2::: | B | 53 | -2.1551 | 103.4106 |  |  |  | Rebuild line 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1
04ALL | ERIS | Thermal | 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1 | 26SP | T0 | P12:69:AEPW:WATLANT2:LINDEN 2::: | B | 53 | -5.4472 | 102.8502 |  |  |  | Rebuild line 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1
04ALL | ERIS | Thermal | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | 29SP | T0 | P12:69:AEPW:WATLANT2:LINDEN 2::: | B | 53 | 9.4063 | 113.5197 |  |  |  | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
04ALL | ERIS | Thermal | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | 26SP | T0 | P12:69:AEPW:WATLANT2:LINDEN 2::: | B | 53 | 10.0564 | 113.4974 |  |  |  | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
04ALL | ERIS | Thermal | 508830 BALDWIN2 69 508842 WOODLWN2 69 1 | 29SP | T0 | Single 508812 OILCITY2 69 508815 SUPEROR2 69 1 | B | 27 | 81.6641 | 111.9112 |  |  |  | Rebuild line 508830 BALDWIN2 69 508842 WOODLWN2 69 1
04ALL | ERIS | Thermal | 508830 BALDWIN2 69 508842 WOODLWN2 69 1 | 26SP | T0 | Single 508815 SUPEROR2 69 786120 G24-305-TAP 69 1 | B | 27 | 58.8897 | 106.8046 |  |  |  | Rebuild line 508830 BALDWIN2 69 508842 WOODLWN2 69 1
04ALL | ERIS | Thermal | 509106 HEMPHIL4 138 509107 SIXMILE4 138 1 | 29SP | T0 | P23:345:EES::7ROCKYCRK%:1:EHV: | B | 135 | 32.4429 | 107.9031 |  |  |  | Rebuild line 509106 HEMPHIL4 138 509107 SIXMILE4 138 1
04ALL | ERIS | Thermal | 509106 HEMPHIL4 138 509107 SIXMILE4 138 1 | 26SP | T0 | P23:345:EES::7ROCKYCRK%:1:EHV: | B | 135 | 13.0977 | 100.0485 |  |  |  | Rebuild line 509106 HEMPHIL4 138 509107 SIXMILE4 138 1
04ALL | ERIS | Thermal | 509752 INOLATP4 138 509790 CATOOSA4 138 1 | 29SP | T0 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | B | 212 | 70.4908 | 149.0116 |  |  |  | Rebuild line 509752 INOLATP4 138 509790 CATOOSA4 138 1
04ALL | ERIS | Thermal | 509752 INOLATP4 138 509790 CATOOSA4 138 1 | 26SP | T0 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | B | 212 | 59.4755 | 126.8359 |  |  |  | Rebuild line 509752 INOLATP4 138 509790 CATOOSA4 138 1
04ALL | ERIS | Thermal | 509752 INOLATP4 138 510442 GUAVA 4 138 1 | 29SP | T0 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | B | 212 | 76.1519 | 154.9696 |  |  |  | Rebuild line 509752 INOLATP4 138 510442 GUAVA 4 138 1
04ALL | ERIS | Thermal | 509752 INOLATP4 138 510442 GUAVA 4 138 1 | 26SP | T0 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | B | 212 | 63.5541 | 132.7111 |  |  |  | Rebuild line 509752 INOLATP4 138 510442 GUAVA 4 138 1
04ALL | ERIS | Thermal | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | 29SP | T0 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | B | 235 | 59.7559 | 113.8093 |  |  |  | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
04ALL | ERIS | Thermal | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | 29WP | T0 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | B | 293 | 49.1084 | 104.6698 |  |  |  | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
04ALL | ERIS | Thermal | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | 26SP | T0 | Single 509915 ANTHEM7 345 510442 GUAVA4 138 1 | B | 235 | 48.8787 | 102.1916 |  |  |  | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
04ALL | ERIS | Thermal | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | 29SP | T0 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | B | 188 | 99.6515 | 192.0351 |  |  |  | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
04ALL | ERIS | Thermal | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | 29WP | T0 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | B | 188 | 119.7031 | 225.4842 |  |  |  | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
04ALL | ERIS | Thermal | 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | 29SP | T0 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 60.131 | 110.8553 |  |  |  | Rebuild line 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1
04ALL | ERIS | Thermal | 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | 29WP | T0 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 83.0315 | 146.0565 |  |  |  | Rebuild line 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1
04ALL | ERIS | Thermal | 510379 DELWARE4 138 763113 G18-079-TAP 138 1 | 29SP | T0 | Single 512734 FARML4 138 778710 G24-058-TAP 138 1 | B | 287 | 50.6058 | 123.4285 |  |  |  | Rebuild line 510379 DELWARE4 138 763113 G18-079-TAP 138 1
04ALL | ERIS | Thermal | 510379 DELWARE4 138 763113 G18-079-TAP 138 1 | 29WP | T0 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | B | 287 | 32.9382 | 126.284 |  |  |  | Rebuild line 510379 DELWARE4 138 763113 G18-079-TAP 138 1
04ALL | ERIS | Thermal | 510379 DELWARE4 138 763113 G18-079-TAP 138 1 | 26SP | T0 | Single 512734 FARML4 138 778710 G24-058-TAP 138 1 | B | 287 | 50.4807 | 123.4994 |  |  |  | Rebuild line 510379 DELWARE4 138 763113 G18-079-TAP 138 1
04ALL | ERIS | Thermal | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | 29SP | T0 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | B | 1176 | 105.5012 | 106.1419 |  |  |  | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
04ALL | ERIS | Thermal | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | 26SP | T0 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | B | 1176 | 95.2733 | 103.3876 |  |  |  | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
04ALL | ERIS | Thermal | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | 29SP | T0 | Single 510380 DELWARE7 345 580555 MONETT345 345 1 | B | 829 | 83.8815 | 133.279 |  |  |  | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
04ALL | ERIS | Thermal | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | 26SP | T0 | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | B | 829 | 81.7802 | 140.0909 |  |  |  | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
04ALL | ERIS | Thermal | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | 29WP | T0 | Single 510380 DELWARE7 345 580555 MONETT345 345 1 | B | 956 | 63.3718 | 125.6761 |  |  |  | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
04ALL | ERIS | Thermal | 510422 COFFEYT4 138 533002 DEARING4 138 1 | 29SP | T0 | P23:345:WERE:N345-345-20:EHV: | B | 478 | 66.8776 | 134.3436 |  |  |  | Rebuild line 510422 COFFEYT4 138 533002 DEARING4 138 1
04ALL | ERIS | Thermal | 510422 COFFEYT4 138 533002 DEARING4 138 1 | 29WP | T0 | P23:345:WERE:N345-345-20:EHV: | B | 478 | 53.6511 | 138.321 |  |  |  | Rebuild line 510422 COFFEYT4 138 533002 DEARING4 138 1
04ALL | ERIS | Thermal | 510422 COFFEYT4 138 533002 DEARING4 138 1 | 26SP | T0 | P23:345:WERE:N345-345-20:EHV: | B | 478 | 59.0986 | 136.0962 |  |  |  | Rebuild line 510422 COFFEYT4 138 533002 DEARING4 138 1
04ALL | ERIS | Thermal | 510422 COFFEYT4 138 787350 G24-346-TAP 138 1 | 29SP | T0 | System Intact | A | 371 | 46.7304 | 101.9666 |  |  |  | Rebuild line 510422 COFFEYT4 138 787350 G24-346-TAP 138 1
04ALL | ERIS | Thermal | 510422 COFFEYT4 138 787350 G24-346-TAP 138 1 | 26SP | T0 | System Intact | A | 371 | 43.1548 | 102.1647 |  |  |  | Rebuild line 510422 COFFEYT4 138 787350 G24-346-TAP 138 1
04ALL | ERIS | Thermal | 510880 COALGTP4 138 510881 ALLENGT4 138 1 | 26SP | T0 | Single 510887 ATOKA--4 138 782490 G24-184-TAP 138 1 | B | 152 | -8.5006 | 120.5255 |  |  |  | Rebuild line 510880 COALGTP4 138 510881 ALLENGT4 138 1
04ALL | ERIS | Thermal | 510880 COALGTP4 138 510881 ALLENGT4 138 1 | 29SP | T0 | Single 510887 ATOKA--4 138 782490 G24-184-TAP 138 1 | B | 152 | -8.3493 | 120.5706 |  |  |  | Rebuild line 510880 COALGTP4 138 510881 ALLENGT4 138 1
04ALL | ERIS | Thermal | 510880 COALGTP4 138 510895 LEHIGH-4 138 1 | 26SP | T0 | Single 510887 ATOKA--4 138 782490 G24-184-TAP 138 1 | B | 152 | -5.732 | 123.2794 |  |  |  | Rebuild line 510880 COALGTP4 138 510895 LEHIGH-4 138 1
04ALL | ERIS | Thermal | 510880 COALGTP4 138 510895 LEHIGH-4 138 1 | 29SP | T0 | Single 510887 ATOKA--4 138 782490 G24-184-TAP 138 1 | B | 152 | -5.666 | 123.226 |  |  |  | Rebuild line 510880 COALGTP4 138 510895 LEHIGH-4 138 1
04ALL | ERIS | Thermal | 510880 COALGTP4 138 510895 LEHIGH-4 138 1 | 29WP | T0 | Single 510887 ATOKA--4 138 782490 G24-184-TAP 138 1 | B | 189 | -2.9851 | 101.2851 |  |  |  | Rebuild line 510880 COALGTP4 138 510895 LEHIGH-4 138 1
04ALL | ERIS | Thermal | 510887 ATOKA--4 138 782490 G24-184-TAP 138 1 | 29SP | T0 | Single 510895 LEHIGH-4 138 782490 G24-184-TAP 138 1 | B | 152 | -0.30269 | 128.6306 |  |  |  | Rebuild line 510887 ATOKA--4 138 782490 G24-184-TAP 138 1
04ALL | ERIS | Thermal | 510887 ATOKA--4 138 782490 G24-184-TAP 138 1 | 29WP | T0 | Single 510895 LEHIGH-4 138 782490 G24-184-TAP 138 1 | B | 189 | -0.24251 | 104.1118 |  |  |  | Rebuild line 510887 ATOKA--4 138 782490 G24-184-TAP 138 1
04ALL | ERIS | Thermal | 510887 ATOKA--4 138 782490 G24-184-TAP 138 1 | 26SP | T0 | Single 510895 LEHIGH-4 138 782490 G24-184-TAP 138 1 | B | 152 | -0.30171 | 129.1798 |  |  |  | Rebuild line 510887 ATOKA--4 138 782490 G24-184-TAP 138 1
04ALL | ERIS | Thermal | 510895 LEHIGH-4 138 782490 G24-184-TAP 138 1 | 26SP | T0 | Single 510887 ATOKA--4 138 782490 G24-184-TAP 138 1 | B | 152 | -0.83861 | 129.0383 |  |  |  | Rebuild line 510895 LEHIGH-4 138 782490 G24-184-TAP 138 1
04ALL | ERIS | Thermal | 510895 LEHIGH-4 138 782490 G24-184-TAP 138 1 | 29SP | T0 | Single 510887 ATOKA--4 138 782490 G24-184-TAP 138 1 | B | 152 | -0.83737 | 128.8995 |  |  |  | Rebuild line 510895 LEHIGH-4 138 782490 G24-184-TAP 138 1
04ALL | ERIS | Thermal | 510895 LEHIGH-4 138 782490 G24-184-TAP 138 1 | 29WP | T0 | Single 510887 ATOKA--4 138 782490 G24-184-TAP 138 1 | B | 189 | -0.67105 | 104.2249 |  |  |  | Rebuild line 510895 LEHIGH-4 138 782490 G24-184-TAP 138 1
04ALL | ERIS | Thermal | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 29SP | T0 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | B | 956 | 76.1342 | 172.43 |  |  |  | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
04ALL | ERIS | Thermal | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 29WP | T0 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | B | 956 | 43.0364 | 160.044 |  |  |  | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
04ALL | ERIS | Thermal | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 26SP | T0 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | B | 956 | 51.7235 | 171.4793 |  |  |  | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
04ALL | ERIS | Thermal | 511409 TREASILD7 345 764550 G20-087-TAP 345 1 | 29SP | T0 | P52:138:AEPW:NR5O.K.U:::: | B | 1176 | 50.173 | 115.2559 |  |  |  | Rebuild line 511409 TREASILD7 345 764550 G20-087-TAP 345 1
04ALL | ERIS | Thermal | 511409 TREASILD7 345 764550 G20-087-TAP 345 1 | 29WP | T0 | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | B | 1324 | 36.1278 | 101.439 |  |  |  | Rebuild line 511409 TREASILD7 345 764550 G20-087-TAP 345 1
04ALL | ERIS | Thermal | 511409 TREASILD7 345 764550 G20-087-TAP 345 1 | 26SP | T0 | P52:138:AEPW:NR5O.K.U:::: | B | 1176 | 44.713 | 113.4052 |  |  |  | Rebuild line 511409 TREASILD7 345 764550 G20-087-TAP 345 1
04ALL | ERIS | Thermal | 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | 29SP | T0 | System Intact | A | 1196 | 73.8943 | 124.603 |  |  |  | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1
04ALL | ERIS | Thermal | 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | 29WP | T0 | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | B | 1775 | 54.7147 | 103.7176 |  |  |  | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1
04ALL | ERIS | Thermal | 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | 26SP | T0 | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | B | 1541 | 66.0994 | 118.6945 |  |  |  | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1
04ALL | ERIS | Thermal | 511423 FLE TAP4 138 511467 L.E.S.-4 138 1 | 29SP | T0 | Single 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | B | 173 | 39.4754 | 113.72 |  |  |  | Rebuild line 511423 FLE TAP4 138 511467 L.E.S.-4 138 1
04ALL | ERIS | Thermal | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 29SP | T0 | P42:345:OKGE:SB_GRNT7381:::EHV: | B | 212 | 73.5462 | 173.9574 |  |  |  | Rebuild line 511425 TUTCONT4 138 511501 TUTTLE4 138 1
04ALL | ERIS | Thermal | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 26SP | T0 | P42:345:OKGE:SB_GRNT7381:::EHV: | B | 212 | 61.569 | 161.9945 |  |  |  | Rebuild line 511425 TUTCONT4 138 511501 TUTTLE4 138 1
04ALL | ERIS | Thermal | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 29WP | T0 | P42:345:OKGE:SB_GRNT7381:::EHV: | B | 263 | 48.1339 | 132.3205 |  |  |  | Rebuild line 511425 TUTCONT4 138 511501 TUTTLE4 138 1
04ALL | ERIS | Thermal | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 29SP | T0 | P42:345:OKGE:SB_GRNT7381:::EHV: | B | 191 | 81.5055 | 193.0036 |  |  |  | Rebuild line 511425 TUTCONT4 138 514898 CIMARON4 138 1
04ALL | ERIS | Thermal | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 29WP | T0 | P42:345:OKGE:SB_GRNT7381:::EHV: | B | 191 | 66.1539 | 182.1298 |  |  |  | Rebuild line 511425 TUTCONT4 138 514898 CIMARON4 138 1
04ALL | ERIS | Thermal | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 26SP | T0 | P42:345:OKGE:SB_GRNT7381:::EHV: | B | 191 | 68.1933 | 179.7216 |  |  |  | Rebuild line 511425 TUTCONT4 138 514898 CIMARON4 138 1
04ALL | ERIS | Thermal | 511435 SNYDER-4 138 3WXFMR 520:SNYDER 138 1 | 26SP | T0 | Single 511440 ALTUSJT4 138 781710 G24-158-TAP 138 1 | B | 75 | 107.7661 | 116.3239 |  |  |  | Add 3-winding transformer 511419 SNYDRTER 13 511435 SNYDER-4 138 511475 SNYDER-2 69 M2
04ALL | ERIS | Thermal | 511435 SNYDER-4 138 3WXFMR 520:SNYDER 138 1 | 29SP | T0 | Single 511440 ALTUSJT4 138 781710 G24-158-TAP 138 1 | B | 75 | 118.0251 | 127.7544 |  |  |  | Add 3-winding transformer 511419 SNYDRTER 13 511435 SNYDER-4 138 511475 SNYDER-2 69 M2
04ALL | ERIS | Thermal | 511435 SNYDER-4 138 3WXFMR 520:SNYDER 138 1 | 29WP | T0 | Single 511440 ALTUSJT4 138 781710 G24-158-TAP 138 1 | B | 75 | 77.2895 | 102.5076 |  |  |  | Add 3-winding transformer 511419 SNYDRTER 13 511435 SNYDER-4 138 511475 SNYDER-2 69 M2
04ALL | ERIS | Thermal | 511435 SNYDER-4 138 765230 G20-012-TAP 138 1 | 26SP | T0 | Single 511440 ALTUSJT4 138 781710 G24-158-TAP 138 1 | B | 238 | 46.5295 | 124.7816 |  |  |  | Rebuild line 511435 SNYDER-4 138 765230 G20-012-TAP 138 1
04ALL | ERIS | Thermal | 511435 SNYDER-4 138 765230 G20-012-TAP 138 1 | 29SP | T0 | Single 511440 ALTUSJT4 138 781710 G24-158-TAP 138 1 | B | 238 | 46.6231 | 124.8953 |  |  |  | Rebuild line 511435 SNYDER-4 138 765230 G20-012-TAP 138 1
04ALL | ERIS | Thermal | 511435 SNYDER-4 138 765230 G20-012-TAP 138 1 | 29WP | T0 | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | B | 238 | 9.758 | 130.3691 |  |  |  | Rebuild line 511435 SNYDER-4 138 765230 G20-012-TAP 138 1
04ALL | ERIS | Thermal | 511440 ALTUSJT4 138 521043 RUSSELL4 138 1 | 29SP | T0 | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | B | 152 | 51.3603 | 130.3632 |  |  |  | Rebuild line 511440 ALTUSJT4 138 521043 RUSSELL4 138 1
04ALL | ERIS | Thermal | 511440 ALTUSJT4 138 521043 RUSSELL4 138 1 | 26SP | T0 | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | B | 152 | 43.9262 | 123.6328 |  |  |  | Rebuild line 511440 ALTUSJT4 138 521043 RUSSELL4 138 1
04ALL | ERIS | Thermal | 511440 ALTUSJT4 138 521043 RUSSELL4 138 1 | 29WP | T0 | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | B | 189 | 32.8026 | 104.069 |  |  |  | Rebuild line 511440 ALTUSJT4 138 521043 RUSSELL4 138 1
04ALL | ERIS | Thermal | 511440 ALTUSJT4 138 529345 OMPARK-4 138 1 | 26SP | T0 | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | B | 215 | -28.1509 | 113.8434 |  |  |  | Rebuild line 511440 ALTUSJT4 138 529345 OMPARK-4 138 1
04ALL | ERIS | Thermal | 511440 ALTUSJT4 138 529345 OMPARK-4 138 1 | 29SP | T0 | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | B | 215 | -28.7974 | 113.4433 |  |  |  | Rebuild line 511440 ALTUSJT4 138 529345 OMPARK-4 138 1
04ALL | ERIS | Thermal | 511440 ALTUSJT4 138 529345 OMPARK-4 138 1 | 29WP | T0 | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | B | 215 | -14.0969 | 127.2423 |  |  |  | Rebuild line 511440 ALTUSJT4 138 529345 OMPARK-4 138 1
04ALL | ERIS | Thermal | 511440 ALTUSJT4 138 781710 G24-158-TAP 138 1 | 26SP | T0 | Single 511435 SNYDER-4 138 765230 G20-012-TAP 138 1 | B | 238 | 46.7093 | 125.7396 |  |  |  | Rebuild line 511440 ALTUSJT4 138 781710 G24-158-TAP 138 1
04ALL | ERIS | Thermal | 511440 ALTUSJT4 138 781710 G24-158-TAP 138 1 | 29SP | T0 | Single 511435 SNYDER-4 138 765230 G20-012-TAP 138 1 | B | 238 | 46.7828 | 125.7605 |  |  |  | Rebuild line 511440 ALTUSJT4 138 781710 G24-158-TAP 138 1
04ALL | ERIS | Thermal | 511440 ALTUSJT4 138 781710 G24-158-TAP 138 1 | 29WP | T0 | Single 511435 SNYDER-4 138 765230 G20-012-TAP 138 1 | B | 238 | 46.6352 | 125.6232 |  |  |  | Rebuild line 511440 ALTUSJT4 138 781710 G24-158-TAP 138 1
04ALL | ERIS | Thermal | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 29SP | T0 | Single 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | B | 171 | 90.1395 | 122.8078 |  |  |  | Rebuild line 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1
04ALL | ERIS | Thermal | 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | 29SP | T0 | Single 511435 SNYDER-4 138 765230 G20-012-TAP 138 1 | B | 170 | -11.8736 | 189.4734 |  |  |  | Rebuild line 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1
04ALL | ERIS | Thermal | 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | 29WP | T0 | Single 511435 SNYDER-4 138 765230 G20-012-TAP 138 1 | B | 202 | 2.8341 | 169.0054 |  |  |  | Rebuild line 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1
04ALL | ERIS | Thermal | 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | 26SP | T0 | Single 511435 SNYDER-4 138 765230 G20-012-TAP 138 1 | B | 170 | -10.7162 | 190.9508 |  |  |  | Rebuild line 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1
04ALL | ERIS | Thermal | 511467 L.E.S.-4 138 3WXFMR 520:LES 5 345 2 | 29SP | T0 | Single 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | B | 515 | 72.2441 | 113.6999 |  |  |  | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
04ALL | ERIS | Thermal | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 29SP | T0 | Single 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | B | 173 | 71.3918 | 103.7559 |  |  |  | Rebuild line 511467 L.E.S.-4 138 511494 COMMTAP4 138 1
04ALL | ERIS | Thermal | 511468 L.E.S.-7 345 3WXFMR 520:LES 5 345 2 | 29SP | T0 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | B | 515 | 71.496 | 113.1714 |  |  |  | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
04ALL | ERIS | Thermal | 511475 SNYDER-2 69 3WXFMR 520:SNYDER 138 1 | 26SP | T0 | Single 511440 ALTUSJT4 138 781710 G24-158-TAP 138 1 | B | 75 | 107.3786 | 115.7101 |  |  |  | Add 3-winding transformer 511419 SNYDRTER 13 511435 SNYDER-4 138 511475 SNYDER-2 69 M2
04ALL | ERIS | Thermal | 511475 SNYDER-2 69 3WXFMR 520:SNYDER 138 1 | 29SP | T0 | Single 511440 ALTUSJT4 138 781710 G24-158-TAP 138 1 | B | 75 | 117.1809 | 127.3569 |  |  |  | Add 3-winding transformer 511419 SNYDRTER 13 511435 SNYDER-4 138 511475 SNYDER-2 69 M2
04ALL | ERIS | Thermal | 511475 SNYDER-2 69 3WXFMR 520:SNYDER 138 1 | 29WP | T0 | Single 511440 ALTUSJT4 138 781710 G24-158-TAP 138 1 | B | 75 | 77.1489 | 102.2217 |  |  |  | Add 3-winding transformer 511419 SNYDRTER 13 511435 SNYDER-4 138 511475 SNYDER-2 69 M2
04ALL | ERIS | Thermal | 511477 S.W.S.-4 138 511586 TONKAWA4 138 1 | 29SP | T0 | Single 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | B | 212 | 49.9636 | 109.4971 |  |  |  | Rebuild line 511477 S.W.S.-4 138 511586 TONKAWA4 138 1
04ALL | ERIS | Thermal | 511477 S.W.S.-4 138 511586 TONKAWA4 138 1 | 29WP | T0 | Single 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | B | 229 | 48.2263 | 102.5765 |  |  |  | Rebuild line 511477 S.W.S.-4 138 511586 TONKAWA4 138 1
04ALL | ERIS | Thermal | 511477 S.W.S.-4 138 520814 ANADARK4 138 1 | 29SP | T0 | P12:138:AEPW-WFEC:S.W.S.-4:WASHITA4::: | B | 212 | 95.9233 | 143.1476 |  |  |  | Rebuild line 511477 S.W.S.-4 138 520814 ANADARK4 138 1
04ALL | ERIS | Thermal | 511477 S.W.S.-4 138 520814 ANADARK4 138 1 | 26SP | T0 | P12:138:AEPW-WFEC:S.W.S.-4:WASHITA4::: | B | 212 | 84.0113 | 135.7527 |  |  |  | Rebuild line 511477 S.W.S.-4 138 520814 ANADARK4 138 1
04ALL | ERIS | Thermal | 511477 S.W.S.-4 138 521089 WASHITA4 138 1 | 29SP | T0 | Single 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | B | 353 | 89.0259 | 130.5477 |  |  |  | Rebuild line 511477 S.W.S.-4 138 521089 WASHITA4 138 1
04ALL | ERIS | Thermal | 511477 S.W.S.-4 138 521089 WASHITA4 138 1 | 26SP | T0 | Single 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | B | 353 | 78.0048 | 117.7111 |  |  |  | Rebuild line 511477 S.W.S.-4 138 521089 WASHITA4 138 1
04ALL | ERIS | Thermal | 511477 S.W.S.-4 138 521089 WASHITA4 138 1 | 29WP | T0 | Single 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | B | 382 | 54.0795 | 103.7807 |  |  |  | Rebuild line 511477 S.W.S.-4 138 521089 WASHITA4 138 1
04ALL | ERIS | Thermal | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | 29WP | T0 | P42:345:OKGE:SB_GRNT7381:::EHV: | B | 373 | 52.722 | 100.8024 |  |  |  | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
04ALL | ERIS | Thermal | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 29SP | T0 | Single 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | B | 171 | 90.3188 | 122.9752 |  |  |  | Rebuild line 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
04ALL | ERIS | Thermal | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 29SP | T0 | P42:345:OKGE:SB_GRNT7381:::EHV: | B | 212 | 76.2764 | 176.8103 |  |  |  | Rebuild line 511501 TUTTLE4 138 511575 LEONARD4 138 1
04ALL | ERIS | Thermal | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 26SP | T0 | P42:345:OKGE:SB_GRNT7381:::EHV: | B | 212 | 64.2738 | 164.8664 |  |  |  | Rebuild line 511501 TUTTLE4 138 511575 LEONARD4 138 1
04ALL | ERIS | Thermal | 511564 MARTHA 4 138 529302 OMALTUS4 138 1 | 26SP | T0 | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | B | 170 | -3.0334 | 176.3067 |  |  |  | Rebuild line 511564 MARTHA 4 138 529302 OMALTUS4 138 1
04ALL | ERIS | Thermal | 511564 MARTHA 4 138 529302 OMALTUS4 138 1 | 29SP | T0 | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | B | 170 | -3.0171 | 176.6239 |  |  |  | Rebuild line 511564 MARTHA 4 138 529302 OMALTUS4 138 1
04ALL | ERIS | Thermal | 511564 MARTHA 4 138 529302 OMALTUS4 138 1 | 29WP | T0 | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | B | 202 | -2.3571 | 149.4331 |  |  |  | Rebuild line 511564 MARTHA 4 138 529302 OMALTUS4 138 1
04ALL | ERIS | Thermal | 511564 MARTHA 4 138 781800 G24-161-TAP 138 1 | 26SP | T0 | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | B | 170 | -2.3115 | 178.2113 |  |  |  | Rebuild line 511564 MARTHA 4 138 781800 G24-161-TAP 138 1
04ALL | ERIS | Thermal | 511564 MARTHA 4 138 781800 G24-161-TAP 138 1 | 29SP | T0 | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | B | 170 | -2.3036 | 178.5045 |  |  |  | Rebuild line 511564 MARTHA 4 138 781800 G24-161-TAP 138 1
04ALL | ERIS | Thermal | 511564 MARTHA 4 138 781800 G24-161-TAP 138 1 | 29WP | T0 | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | B | 202 | -1.9591 | 150.4609 |  |  |  | Rebuild line 511564 MARTHA 4 138 781800 G24-161-TAP 138 1
04ALL | ERIS | Thermal | 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | 26SP | T0 | P42:345:OKGE:SB_GRNT7313:::EHV: | B | 1176 | 56.5173 | 106.9812 |  |  |  | Rebuild line 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1
04ALL | ERIS | Thermal | 512101 CHILD4WT 138 512110 LAKEP4WT 138 1 | 26SP | T0 | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | B | 107 | 51.0073 | 104.0858 |  |  |  | Rebuild line 512101 CHILD4WT 138 512110 LAKEP4WT 138 1
04ALL | ERIS | Thermal | 512101 CHILD4WT 138 512110 LAKEP4WT 138 1 | 29SP | T0 | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | B | 107 | 60.3981 | 114.4697 |  |  |  | Rebuild line 512101 CHILD4WT 138 512110 LAKEP4WT 138 1
04ALL | ERIS | Thermal | 512101 CHILD4WT 138 512110 LAKEP4WT 138 1 | 29WP | T0 | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | B | 107 | 49.9863 | 115.7771 |  |  |  | Rebuild line 512101 CHILD4WT 138 512110 LAKEP4WT 138 1
04ALL | ERIS | Thermal | 512110 LAKEP4WT 138 521043 RUSSELL4 138 1 | 26SP | T0 | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | B | 107 | 49.7402 | 103.9347 |  |  |  | Rebuild line 512110 LAKEP4WT 138 521043 RUSSELL4 138 1
04ALL | ERIS | Thermal | 512110 LAKEP4WT 138 521043 RUSSELL4 138 1 | 29WP | T0 | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | B | 107 | 47.9733 | 113.0365 |  |  |  | Rebuild line 512110 LAKEP4WT 138 521043 RUSSELL4 138 1
04ALL | ERIS | Thermal | 512110 LAKEP4WT 138 521043 RUSSELL4 138 1 | 29SP | T0 | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | B | 107 | 60.5093 | 112.9146 |  |  |  | Rebuild line 512110 LAKEP4WT 138 521043 RUSSELL4 138 1
04ALL | ERIS | Thermal | 512623 CATSAGD4 138 3WXFMR 523:CATAUTO1 138 1 | 26SP | T0 | P13:138-161:GRDA:CATAUTO2:::HV: | B | 188 | 48.967 | 100.7112 |  |  |  | Add 3-winding transformer 512623 CATSAGD4 138 512638 CATSAGR5 161 512833 CATTER1 1 13 M2
04ALL | ERIS | Thermal | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 29SP | T0 | System Intact | A | 194 | 83.561 | 133.6704 |  |  |  | Rebuild line 512631 MIAMI 5 161 512632 AFTON 5 161 1
04ALL | ERIS | Thermal | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 29WP | T0 | System Intact | A | 248 | 59.3207 | 108.8809 |  |  |  | Rebuild line 512631 MIAMI 5 161 512632 AFTON 5 161 1
04ALL | ERIS | Thermal | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 26SP | T0 | System Intact | A | 194 | 81.7276 | 142.3117 |  |  |  | Rebuild line 512631 MIAMI 5 161 512632 AFTON 5 161 1
04ALL | ERIS | Thermal | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 29SP | T0 | System Intact | A | 194 | 50.0544 | 103.9836 |  |  |  | Rebuild line 512631 MIAMI 5 161 547487 HOC404 5 161 1
04ALL | ERIS | Thermal | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 26SP | T0 | System Intact | A | 194 | 48.1081 | 112.7124 |  |  |  | Rebuild line 512631 MIAMI 5 161 547487 HOC404 5 161 1
04ALL | ERIS | Thermal | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 29SP | T0 | System Intact | A | 194 | 94.7414 | 145.4599 |  |  |  | Rebuild line 512632 AFTON 5 161 512669 KETCHUM5 161 1
04ALL | ERIS | Thermal | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 29WP | T0 | System Intact | A | 248 | 67.1407 | 117.4869 |  |  |  | Rebuild line 512632 AFTON 5 161 512669 KETCHUM5 161 1
04ALL | ERIS | Thermal | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 26SP | T0 | System Intact | A | 194 | 92.9955 | 154.3764 |  |  |  | Rebuild line 512632 AFTON 5 161 512669 KETCHUM5 161 1
04ALL | ERIS | Thermal | 512636 CATSAGR4 138 3WXFMR 523:CATAUTO2 138 2 | 26SP | T0 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 49.1179 | 101.0201 |  |  |  | Add 3-winding transformer 512636 CATSAGR4 138 512638 CATSAGR5 161 512834 CATTER2 1 13 M2
04ALL | ERIS | Thermal | 512636 CATSAGR4 138 3WXFMR 523:CATAUTO2 138 2 | 29SP | T0 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 60.9866 | 111.9148 |  |  |  | Add 3-winding transformer 512636 CATSAGR4 138 512638 CATSAGR5 161 512834 CATTER2 1 13 M2
04ALL | ERIS | Thermal | 512636 CATSAGR4 138 3WXFMR 523:CATAUTO2 138 2 | 29WP | T0 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 84.5023 | 147.1297 |  |  |  | Add 3-winding transformer 512636 CATSAGR4 138 512638 CATSAGR5 161 512834 CATTER2 1 13 M2
04ALL | ERIS | Thermal | 512638 CATSAGR5 161 3WXFMR 523:CATAUTO1 138 1 | 26SP | T0 | P13:138-161:GRDA:CATAUTO2:::HV: | B | 188 | 48.9527 | 100.6522 |  |  |  | Add 3-winding transformer 512623 CATSAGD4 138 512638 CATSAGR5 161 512833 CATTER1 1 13 M2
04ALL | ERIS | Thermal | 512638 CATSAGR5 161 3WXFMR 523:CATAUTO2 138 2 | 26SP | T0 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 49.0975 | 100.9359 |  |  |  | Add 3-winding transformer 512636 CATSAGR4 138 512638 CATSAGR5 161 512834 CATTER2 1 13 M2
04ALL | ERIS | Thermal | 512638 CATSAGR5 161 3WXFMR 523:CATAUTO2 138 2 | 29SP | T0 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 60.9474 | 111.8194 |  |  |  | Add 3-winding transformer 512636 CATSAGR4 138 512638 CATSAGR5 161 512834 CATTER2 1 13 M2
04ALL | ERIS | Thermal | 512638 CATSAGR5 161 3WXFMR 523:CATAUTO2 138 2 | 29WP | T0 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 84.4672 | 146.9449 |  |  |  | Add 3-winding transformer 512636 CATSAGR4 138 512638 CATSAGR5 161 512834 CATTER2 1 13 M2
04ALL | ERIS | Thermal | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | 29SP | T0 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | B | 1195 | 68.8272 | 123.0653 |  |  |  | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
04ALL | ERIS | Thermal | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | 29WP | T0 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | B | 1195 | 69.6782 | 130.517 |  |  |  | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
04ALL | ERIS | Thermal | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | 26SP | T0 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | B | 1195 | 75.0866 | 133.2333 |  |  |  | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
04ALL | ERIS | Thermal | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 29SP | T0 | System Intact | A | 194 | 99.3057 | 150.1707 |  |  |  | Rebuild line 512654 PENSA 5 161 512669 KETCHUM5 161 1
04ALL | ERIS | Thermal | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 29WP | T0 | System Intact | A | 248 | 72.3625 | 122.984 |  |  |  | Rebuild line 512654 PENSA 5 161 512669 KETCHUM5 161 1
04ALL | ERIS | Thermal | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 26SP | T0 | System Intact | A | 194 | 97.557 | 159.1079 |  |  |  | Rebuild line 512654 PENSA 5 161 512669 KETCHUM5 161 1
04ALL | ERIS | Thermal | 512734 FARML 4 138 778710 G24-058-TAP 138 1 | 29SP | T0 | Single 510422 COFFEYT4 138 787350 G24-346-TAP 138 1 | B | 287 | 73.1081 | 130.4835 |  |  |  | Rebuild line 512734 FARML 4 138 778710 G24-058-TAP 138 1
04ALL | ERIS | Thermal | 512734 FARML 4 138 778710 G24-058-TAP 138 1 | 29WP | T0 | Single 510422 COFFEYT4 138 787350 G24-346-TAP 138 1 | B | 287 | 70.7171 | 126.6369 |  |  |  | Rebuild line 512734 FARML 4 138 778710 G24-058-TAP 138 1
04ALL | ERIS | Thermal | 512734 FARML 4 138 778710 G24-058-TAP 138 1 | 26SP | T0 | Single 510422 COFFEYT4 138 787350 G24-346-TAP 138 1 | B | 287 | 81.6694 | 132.8558 |  |  |  | Rebuild line 512734 FARML 4 138 778710 G24-058-TAP 138 1
04ALL | ERIS | Thermal | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | 29SP | T0 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | B | 1055 | 66.8747 | 130.7663 |  |  |  | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
04ALL | ERIS | Thermal | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | 29WP | T0 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | B | 1182 | 61.4901 | 121.285 |  |  |  | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
04ALL | ERIS | Thermal | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | 26SP | T0 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | B | 1055 | 65.9321 | 132.2268 |  |  |  | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
04ALL | ERIS | Thermal | 514710 WAUKOMI4 138 514711 WAUKOTP4 138 1 | 29SP | T0 | Single 514827 CTNWOOD4 138 515377 CRESENT4 138 1 | B | 287 | 60.2356 | 123.2854 |  |  |  | Rebuild line 514710 WAUKOMI4 138 514711 WAUKOTP4 138 1
04ALL | ERIS | Thermal | 514710 WAUKOMI4 138 514711 WAUKOTP4 138 1 | 29WP | T0 | Single 514827 CTNWOOD4 138 515377 CRESENT4 138 1 | B | 287 | 57.3157 | 121.5988 |  |  |  | Rebuild line 514710 WAUKOMI4 138 514711 WAUKOTP4 138 1
04ALL | ERIS | Thermal | 514710 WAUKOMI4 138 514711 WAUKOTP4 138 1 | 26SP | T0 | Single 514827 CTNWOOD4 138 515377 CRESENT4 138 1 | B | 287 | 59.5096 | 124.6717 |  |  |  | Rebuild line 514710 WAUKOMI4 138 514711 WAUKOTP4 138 1
04ALL | ERIS | Thermal | 514710 WAUKOMI4 138 514774 HENESEY4 138 1 | 29SP | T0 | Single 514827 CTNWOOD4 138 515377 CRESENT4 138 1 | B | 287 | 62.0392 | 125.1889 |  |  |  | Rebuild line 514710 WAUKOMI4 138 514774 HENESEY4 138 1
04ALL | ERIS | Thermal | 514710 WAUKOMI4 138 514774 HENESEY4 138 1 | 29WP | T0 | Single 514827 CTNWOOD4 138 515377 CRESENT4 138 1 | B | 287 | 58.9189 | 123.2725 |  |  |  | Rebuild line 514710 WAUKOMI4 138 514774 HENESEY4 138 1
04ALL | ERIS | Thermal | 514710 WAUKOMI4 138 514774 HENESEY4 138 1 | 26SP | T0 | Single 514827 CTNWOOD4 138 515377 CRESENT4 138 1 | B | 287 | 61.2817 | 126.5523 |  |  |  | Rebuild line 514710 WAUKOMI4 138 514774 HENESEY4 138 1
04ALL | ERIS | Thermal | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | 26SP | T0 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | B | 1195 | 74.0482 | 101.4435 |  |  |  | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1
04ALL | ERIS | Thermal | 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | 29SP | T0 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | B | 1195 | 82.1949 | 104.263 |  |  |  | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1
04ALL | ERIS | Thermal | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | 29SP | T0 | System Intact | A | 194 | 73.5146 | 109.2805 |  |  |  | Rebuild line 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1
04ALL | ERIS | Thermal | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | 26SP | T0 | System Intact | A | 194 | 65.203 | 102.4712 |  |  |  | Rebuild line 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1
04ALL | ERIS | Thermal | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | 29SP | T0 | System Intact | A | 194 | 70.7582 | 106.5943 |  |  |  | Rebuild line 514759 NEWKIRK4 138 515381 PECKHMT4 138 1
04ALL | ERIS | Thermal | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | 29SP | T0 | System Intact | A | 194 | 77.4314 | 113.1041 |  |  |  | Rebuild line 514760 KILDARE4 138 514764 NWKRKAT4 138 1
04ALL | ERIS | Thermal | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | 26SP | T0 | System Intact | A | 194 | 68.9901 | 106.1965 |  |  |  | Rebuild line 514760 KILDARE4 138 514764 NWKRKAT4 138 1
04ALL | ERIS | Thermal | 514774 HENESEY4 138 520535 BULFTTP4 138 1 | 29SP | T0 | Single 514827 CTNWOOD4 138 515377 CRESENT4 138 1 | B | 287 | 66.334 | 129.9386 |  |  |  | Rebuild line 514774 HENESEY4 138 520535 BULFTTP4 138 1
04ALL | ERIS | Thermal | 514774 HENESEY4 138 520535 BULFTTP4 138 1 | 29WP | T0 | Single 514827 CTNWOOD4 138 515377 CRESENT4 138 1 | B | 287 | 62.6642 | 127.3841 |  |  |  | Rebuild line 514774 HENESEY4 138 520535 BULFTTP4 138 1
04ALL | ERIS | Thermal | 514774 HENESEY4 138 520535 BULFTTP4 138 1 | 26SP | T0 | Single 514827 CTNWOOD4 138 515377 CRESENT4 138 1 | B | 287 | 65.431 | 131.1816 |  |  |  | Rebuild line 514774 HENESEY4 138 520535 BULFTTP4 138 1
04ALL | ERIS | Thermal | 514782 WODWRD 2 69 521096 WOODWRD2 69 1 | 29L | T0 | P12:138:OKGE:BKRBKR0830:::HV: | B | 110 | 101.0566 | 105.2776 |  |  |  | Rebuild line 514782 WODWRD 2 69 521096 WOODWRD2 69 1
04ALL | ERIS | Thermal | 514782 WODWRD 2 69 521096 WOODWRD2 69 1 | 29WP | T0 | P12:138:OKGE:BKRBKR0830:::HV: | B | 110 | 85.7222 | 108.4985 |  |  |  | Rebuild line 514782 WODWRD 2 69 521096 WOODWRD2 69 1
04ALL | ERIS | Thermal | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 29L | T0 | 272357 | B | 200 | 148.7818 | 161.6792 |  |  |  | Rebuild line 514785 WOODWRD4 138 515785 WINDFRM4 138 1
04ALL | ERIS | Thermal | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 29WP | T0 | 272357 | B | 200 | 135.3154 | 174.312 |  |  |  | Rebuild line 514785 WOODWRD4 138 515785 WINDFRM4 138 1
04ALL | ERIS | Thermal | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 26SP | T0 | Single 520430 NOELSW4 138 774060 G23-104-TAP 138 1 | B | 200 | 106.4249 | 120.2716 |  |  |  | Rebuild line 514785 WOODWRD4 138 515785 WINDFRM4 138 1
04ALL | ERIS | Thermal | 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | 29SP | T0 | 272357 | B | 200 | 104.0517 | 109.7011 |  |  |  | Rebuild line 514785 WOODWRD4 138 515785 WINDFRM4 138 1
04ALL | ERIS | Thermal | 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 | 29SP | T0 | System Intact | A | 194 | 68.6286 | 104.5121 |  |  |  | Rebuild line 514804 MIDLTNT4 138 515381 PECKHMT4 138 1
04ALL | ERIS | Thermal | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 | 29SP | T0 | System Intact | A | 194 | 99.7761 | 134.677 |  |  |  | Rebuild line 514804 MIDLTNT4 138 532981 CRESWLN4 138 1
04ALL | ERIS | Thermal | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 | 29WP | T0 | System Intact | A | 249 | 60.6049 | 105.7062 |  |  |  | Rebuild line 514804 MIDLTNT4 138 532981 CRESWLN4 138 1
04ALL | ERIS | Thermal | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 | 26SP | T0 | System Intact | A | 194 | 91.7794 | 127.9 |  |  |  | Rebuild line 514804 MIDLTNT4 138 532981 CRESWLN4 138 1
04ALL | ERIS | Thermal | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 | 29SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 222 | 68.4268 | 118.7348 |  |  |  | Rebuild line 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1
04ALL | ERIS | Thermal | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 | 26SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 222 | 49.5361 | 113.5857 |  |  |  | Rebuild line 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1
04ALL | ERIS | Thermal | 514827 CTNWOOD4 138 515377 CRESENT4 138 1 | 29SP | T0 | Single 520535 BULFTTP4 138 520882 DOVERSW4 138 1 | B | 287 | 80.05 | 144.0335 |  |  |  | Rebuild line 514827 CTNWOOD4 138 515377 CRESENT4 138 1
04ALL | ERIS | Thermal | 514827 CTNWOOD4 138 515377 CRESENT4 138 1 | 29WP | T0 | Single 520535 BULFTTP4 138 520882 DOVERSW4 138 1 | B | 287 | 80.6015 | 141.6708 |  |  |  | Rebuild line 514827 CTNWOOD4 138 515377 CRESENT4 138 1
04ALL | ERIS | Thermal | 514827 CTNWOOD4 138 515377 CRESENT4 138 1 | 26SP | T0 | Single 520535 BULFTTP4 138 520882 DOVERSW4 138 1 | B | 287 | 81.1693 | 146.4912 |  |  |  | Rebuild line 514827 CTNWOOD4 138 515377 CRESENT4 138 1
04ALL | ERIS | Thermal | 514947 CANADN-4 138 766111 G21-088-TAP 138 1 | 29SP | T0 | P42:345:OKGE:SB_GRNT7381:::EHV: | B | 287 | 44.3602 | 129.6463 |  |  |  | Rebuild line 514947 CANADN-4 138 766111 G21-088-TAP 138 1
04ALL | ERIS | Thermal | 514947 CANADN-4 138 766111 G21-088-TAP 138 1 | 26SP | T0 | P42:345:OKGE:SB_GRNT7381:::EHV: | B | 287 | 36.5035 | 122.9695 |  |  |  | Rebuild line 514947 CANADN-4 138 766111 G21-088-TAP 138 1
04ALL | ERIS | Thermal | 514947 CANADN-4 138 766111 G21-088-TAP 138 1 | 29WP | T0 | P42:345:OKGE:SB_GRNT7381:::EHV: | B | 287 | 24.5207 | 110.6277 |  |  |  | Rebuild line 514947 CANADN-4 138 766111 G21-088-TAP 138 1
04ALL | ERIS | Thermal | 514948 CEDARLN4 138 766111 G21-088-TAP 138 1 | 29SP | T0 | P42:345:OKGE:SB_GRNT7381:::EHV: | B | 287 | 44.354 | 129.6425 |  |  |  | Rebuild line 514948 CEDARLN4 138 766111 G21-088-TAP 138 1
04ALL | ERIS | Thermal | 514948 CEDARLN4 138 766111 G21-088-TAP 138 1 | 26SP | T0 | P42:345:OKGE:SB_GRNT7381:::EHV: | B | 287 | 36.4966 | 122.9655 |  |  |  | Rebuild line 514948 CEDARLN4 138 766111 G21-088-TAP 138 1
04ALL | ERIS | Thermal | 514948 CEDARLN4 138 766111 G21-088-TAP 138 1 | 29WP | T0 | P42:345:OKGE:SB_GRNT7381:::EHV: | B | 287 | 24.513 | 110.6241 |  |  |  | Rebuild line 514948 CEDARLN4 138 766111 G21-088-TAP 138 1
04ALL | ERIS | Thermal | 514959 FOSTER 4 138 514962 DISCVRY4 138 1 | 29SP | T0 | MULTIGEN514941 | B | 267 | 72.8249 | 100.8839 |  |  |  | Rebuild line 514959 FOSTER 4 138 514962 DISCVRY4 138 1
04ALL | ERIS | Thermal | 515044 SEMINOL4 138 515531 VANOSTP4 138 1 | 29SP | T0 | Single 515178 PARKLN4 138 515977 LKKONWA4 138 1 | B | 287 | 21.2257 | 116.173 |  |  |  | Rebuild line 515044 SEMINOL4 138 515531 VANOSTP4 138 1
04ALL | ERIS | Thermal | 515044 SEMINOL4 138 515531 VANOSTP4 138 1 | 29WP | T0 | Single 515178 PARKLN4 138 515977 LKKONWA4 138 1 | B | 287 | 21.3941 | 110.7099 |  |  |  | Rebuild line 515044 SEMINOL4 138 515531 VANOSTP4 138 1
04ALL | ERIS | Thermal | 515044 SEMINOL4 138 515531 VANOSTP4 138 1 | 26SP | T0 | Single 515178 PARKLN4 138 515977 LKKONWA4 138 1 | B | 287 | 18.5867 | 113.1965 |  |  |  | Rebuild line 515044 SEMINOL4 138 515531 VANOSTP4 138 1
04ALL | ERIS | Thermal | 515049 SEMINOLE9 765 515045 SEMINOL7 345 1 | 29WP | T0 | Single 515049 SEMINOLE9 765 515045 SEMINOL7 345 2 | B | 1650 | 83.6841 | 113.1913 |  |  |  | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 1
04ALL | ERIS | Thermal | 515049 SEMINOLE9 765 515045 SEMINOL7 345 2 | 29WP | T0 | Single 515049 SEMINOLE9 765 515045 SEMINOL7 345 1 | B | 1650 | 83.6841 | 113.1913 |  |  |  | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 2
04ALL | ERIS | Thermal | 515097 WLNUTCK4 138 515100 PAOLI- 4 138 1 | 29SP | T0 | Single 515044 SEMINOL4 138 775520 G23-177-TAP 138 1 | B | 191 | 51.7168 | 123.413 |  |  |  | Rebuild line 515097 WLNUTCK4 138 515100 PAOLI- 4 138 1
04ALL | ERIS | Thermal | 515097 WLNUTCK4 138 515100 PAOLI- 4 138 1 | 29WP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 191 | 40.4596 | 108.3481 |  |  |  | Rebuild line 515097 WLNUTCK4 138 515100 PAOLI- 4 138 1
04ALL | ERIS | Thermal | 515097 WLNUTCK4 138 515100 PAOLI- 4 138 1 | 26SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 191 | 52.5898 | 120.8428 |  |  |  | Rebuild line 515097 WLNUTCK4 138 515100 PAOLI- 4 138 1
04ALL | ERIS | Thermal | 515100 PAOLI- 4 138 515124 MAYSVIL4 138 1 | 29SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 177 | 38.7436 | 107.6053 |  |  |  | Rebuild line 515100 PAOLI- 4 138 515124 MAYSVIL4 138 1
04ALL | ERIS | Thermal | 515100 PAOLI- 4 138 515124 MAYSVIL4 138 1 | 26SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 177 | 28.1586 | 104.0577 |  |  |  | Rebuild line 515100 PAOLI- 4 138 515124 MAYSVIL4 138 1
04ALL | ERIS | Thermal | 515105 WYNWOD 2 69 515113 CHIGLEY2 69 1 | 29SP | T0 | P12:138:OKGE:BKRBKR3460:::HV: | B | 60 | 47.7361 | 115.967 |  |  |  | Rebuild line 515105 WYNWOD 2 69 515113 CHIGLEY2 69 1
04ALL | ERIS | Thermal | 515105 WYNWOD 2 69 515113 CHIGLEY2 69 1 | 29WP | T0 | P12:138:OKGE:BKRBKR3460:::HV: | B | 60 | 40.2112 | 110.0229 |  |  |  | Rebuild line 515105 WYNWOD 2 69 515113 CHIGLEY2 69 1
04ALL | ERIS | Thermal | 515105 WYNWOD 2 69 515113 CHIGLEY2 69 1 | 26SP | T0 | P12:138:OKGE:BKRBKR3460:::HV: | B | 60 | 42.8714 | 113.2608 |  |  |  | Rebuild line 515105 WYNWOD 2 69 515113 CHIGLEY2 69 1
04ALL | ERIS | Thermal | 515113 CHIGLEY2 69 3WXFMR 524:524:CHIGLEY3 138 3 | 29SP | T0 | P12:138:OKGE:BKRBKR3460:::HV: | B | 67 | 54.8791 | 105.0538 |  |  |  | Rebuild 3-winding transformer 515113 CHIGLEY2 69 515114 CHIGLEY4 138 515712 CHIGLEY1 13 3
04ALL | ERIS | Thermal | 515113 CHIGLEY2 69 3WXFMR 524:524:CHIGLEY3 138 3 | 26SP | T0 | P12:138:OKGE:BKRBKR3460:::HV: | B | 67 | 51.9858 | 103.6495 |  |  |  | Rebuild 3-winding transformer 515113 CHIGLEY2 69 515114 CHIGLEY4 138 515712 CHIGLEY1 13 3
04ALL | ERIS | Thermal | 515114 CHIGLEY4 138 3WXFMR 524:524:CHIGLEY3 138 3 | 29SP | T0 | P12:138:OKGE:BKRBKR3460:::HV: | B | 67 | 54.8791 | 105.0538 |  |  |  | Rebuild 3-winding transformer 515113 CHIGLEY2 69 515114 CHIGLEY4 138 515712 CHIGLEY1 13 3
04ALL | ERIS | Thermal | 515114 CHIGLEY4 138 3WXFMR 524:524:CHIGLEY3 138 3 | 26SP | T0 | P12:138:OKGE:BKRBKR3460:::HV: | B | 67 | 51.9858 | 103.6495 |  |  |  | Rebuild 3-winding transformer 515113 CHIGLEY2 69 515114 CHIGLEY4 138 515712 CHIGLEY1 13 3
04ALL | ERIS | Thermal | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | 29SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 191 | 74.2318 | 132.4142 |  |  |  | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1
04ALL | ERIS | Thermal | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | 29WP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 191 | 45.0074 | 117.074 |  |  |  | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1
04ALL | ERIS | Thermal | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | 26SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 191 | 52.2878 | 126.423 |  |  |  | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1
04ALL | ERIS | Thermal | 515117 ARBUCKL4 138 515133 BLUERIV4 138 1 | 26SP | T0 | Single 515117 ARBUCKL4 138 515531 VANOSTP4 138 1 | B | 191 | 25.1246 | 153.1153 |  |  |  | Rebuild line 515117 ARBUCKL4 138 515133 BLUERIV4 138 1
04ALL | ERIS | Thermal | 515117 ARBUCKL4 138 515133 BLUERIV4 138 1 | 29SP | T0 | Single 515117 ARBUCKL4 138 515531 VANOSTP4 138 1 | B | 191 | 32.4629 | 155.6929 |  |  |  | Rebuild line 515117 ARBUCKL4 138 515133 BLUERIV4 138 1
04ALL | ERIS | Thermal | 515117 ARBUCKL4 138 515133 BLUERIV4 138 1 | 29WP | T0 | Single 515117 ARBUCKL4 138 515531 VANOSTP4 138 1 | B | 191 | 30.5887 | 149.9135 |  |  |  | Rebuild line 515117 ARBUCKL4 138 515133 BLUERIV4 138 1
04ALL | ERIS | Thermal | 515117 ARBUCKL4 138 515531 VANOSTP4 138 1 | 29SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 287 | 49.2384 | 146.6326 |  |  |  | Rebuild line 515117 ARBUCKL4 138 515531 VANOSTP4 138 1
04ALL | ERIS | Thermal | 515117 ARBUCKL4 138 515531 VANOSTP4 138 1 | 29WP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 287 | 38.8005 | 140.7781 |  |  |  | Rebuild line 515117 ARBUCKL4 138 515531 VANOSTP4 138 1
04ALL | ERIS | Thermal | 515117 ARBUCKL4 138 515531 VANOSTP4 138 1 | 26SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 287 | 37.4307 | 142.0204 |  |  |  | Rebuild line 515117 ARBUCKL4 138 515531 VANOSTP4 138 1
04ALL | ERIS | Thermal | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 | 29SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 222 | 67.5796 | 117.8594 |  |  |  | Rebuild line 515121 MILLCKT4 138 515122 SXMLCKT4 138 1
04ALL | ERIS | Thermal | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 | 26SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 222 | 48.6934 | 112.7118 |  |  |  | Rebuild line 515121 MILLCKT4 138 515122 SXMLCKT4 138 1
04ALL | ERIS | Thermal | 515124 MAYSVIL4 138 515570 MAYSVLT4 138 1 | 29SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 177 | 40.4092 | 109.3217 |  |  |  | Rebuild line 515124 MAYSVIL4 138 515570 MAYSVLT4 138 1
04ALL | ERIS | Thermal | 515124 MAYSVIL4 138 515570 MAYSVLT4 138 1 | 26SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 177 | 29.9201 | 105.7505 |  |  |  | Rebuild line 515124 MAYSVIL4 138 515570 MAYSVLT4 138 1
04ALL | ERIS | Thermal | 515129 RATLIFF4 138 515134 PRARPNT4 138 1 | 29SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 177 | 55.8854 | 125.7363 |  |  |  | Rebuild line 515129 RATLIFF4 138 515134 PRARPNT4 138 1
04ALL | ERIS | Thermal | 515129 RATLIFF4 138 515134 PRARPNT4 138 1 | 26SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 177 | 45.6953 | 121.9969 |  |  |  | Rebuild line 515129 RATLIFF4 138 515134 PRARPNT4 138 1
04ALL | ERIS | Thermal | 515129 RATLIFF4 138 515561 CARTRCO4 138 1 | 29SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 177 | 74.5173 | 142.2565 |  |  |  | Rebuild line 515129 RATLIFF4 138 515561 CARTRCO4 138 1
04ALL | ERIS | Thermal | 515129 RATLIFF4 138 515561 CARTRCO4 138 1 | 26SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 177 | 64.4762 | 138.9759 |  |  |  | Rebuild line 515129 RATLIFF4 138 515561 CARTRCO4 138 1
04ALL | ERIS | Thermal | 515129 RATLIFF4 138 515561 CARTRCO4 138 1 | 29WP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 215 | 53.0892 | 112.7504 |  |  |  | Rebuild line 515129 RATLIFF4 138 515561 CARTRCO4 138 1
04ALL | ERIS | Thermal | 515133 BLUERIV4 138 515178 PARKLN 4 138 1 | 29SP | T0 | Single 515117 ARBUCKL4 138 515531 VANOSTP4 138 1 | B | 191 | 57.6801 | 182.7248 |  |  |  | Rebuild line 515133 BLUERIV4 138 515178 PARKLN 4 138 1
04ALL | ERIS | Thermal | 515133 BLUERIV4 138 515178 PARKLN 4 138 1 | 29WP | T0 | Single 515117 ARBUCKL4 138 515531 VANOSTP4 138 1 | B | 191 | 56.2982 | 181.3367 |  |  |  | Rebuild line 515133 BLUERIV4 138 515178 PARKLN 4 138 1
04ALL | ERIS | Thermal | 515133 BLUERIV4 138 515178 PARKLN 4 138 1 | 26SP | T0 | Single 515117 ARBUCKL4 138 515531 VANOSTP4 138 1 | B | 191 | 51.5592 | 180.2147 |  |  |  | Rebuild line 515133 BLUERIV4 138 515178 PARKLN 4 138 1
04ALL | ERIS | Thermal | 515134 PRARPNT4 138 515570 MAYSVLT4 138 1 | 29SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 177 | 42.6196 | 111.6224 |  |  |  | Rebuild line 515134 PRARPNT4 138 515570 MAYSVLT4 138 1
04ALL | ERIS | Thermal | 515134 PRARPNT4 138 515570 MAYSVLT4 138 1 | 26SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 177 | 32.106 | 108.0121 |  |  |  | Rebuild line 515134 PRARPNT4 138 515570 MAYSVLT4 138 1
04ALL | ERIS | Thermal | 515150 CANEYCK4 138 515151 LTLCITY4 138 1 | 26SP | T0 | Single 520918 FROGVIL4 138 773820 G23-092-TAP 138 1 | B | 222 | 39.4392 | 100.2832 |  |  |  | Rebuild line 515150 CANEYCK4 138 515151 LTLCITY4 138 1
04ALL | ERIS | Thermal | 515151 LTLCITY4 138 515157 BROWN 4 138 1 | 26SP | T0 | Single 520918 FROGVIL4 138 773820 G23-092-TAP 138 1 | B | 222 | 40.238 | 101.4172 |  |  |  | Rebuild line 515151 LTLCITY4 138 515157 BROWN 4 138 1
04ALL | ERIS | Thermal | 515178 PARKLN 4 138 515977 LKKONWA4 138 1 | 29SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 382 | 27.8877 | 110.2908 |  |  |  | Rebuild line 515178 PARKLN 4 138 515977 LKKONWA4 138 1
04ALL | ERIS | Thermal | 515178 PARKLN 4 138 515977 LKKONWA4 138 1 | 29WP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 382 | 20.8944 | 103.5123 |  |  |  | Rebuild line 515178 PARKLN 4 138 515977 LKKONWA4 138 1
04ALL | ERIS | Thermal | 515178 PARKLN 4 138 515977 LKKONWA4 138 1 | 26SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 382 | 20.1222 | 105.0141 |  |  |  | Rebuild line 515178 PARKLN 4 138 515977 LKKONWA4 138 1
04ALL | ERIS | Thermal | 515235 PECANCK7 345 516374 KEEFTON7 345 1 | 29SP | T0 | P22:345:EES:MUSKOGE7!:::EHV: | B | 1195 | 50.2738 | 106.5125 |  |  |  | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1
04ALL | ERIS | Thermal | 515336 VBI 2 69 3WXFMR 524:524:VBI2 161 2 | 29SP | T0 | System Intact | A | 76 | 98.3627 | 108.2886 |  |  |  | Rebuild 3-winding transformer 515336 VBI 2 69 515339 VBI 5 161 515769 VBI 1 13 2
04ALL | ERIS | Thermal | 515339 VBI 5 161 3WXFMR 524:524:VBI2 161 2 | 29SP | T0 | System Intact | A | 76 | 98.3627 | 108.2886 |  |  |  | Rebuild 3-winding transformer 515336 VBI 2 69 515339 VBI 5 161 515769 VBI 1 13 2
04ALL | ERIS | Thermal | 515375 WWRDEHV7 345 3WXFMR 524:WOODWRT2 345 2 | 29L | T0 | P13:138:OKGE:BKRBKR_3W077:::HV: | B | 478 | 123.7808 | 112.1147 |  |  |  | Add 3-winding transformer 515375 WWRDEHV7 345 515376 WWRDEHV4 138 515795 WWDEHV21 13 M2
04ALL | ERIS | Thermal | 515375 WWRDEHV7 345 3WXFMR 524:WOODWRT3 345 3 | 29L | T0 | P13:138:OKGE:BKRBKR_3W076:::HV: | B | 478 | 124.3574 | 112.6276 |  |  |  | Add 3-winding transformer 515375 WWRDEHV7 345 515376 WWRDEHV4 138 515799 WWDEHV31 13 M2
04ALL | ERIS | Thermal | 515376 WWRDEHV4 138 3WXFMR 524:WOODWRT2 345 2 | 29L | T0 | P13:138:OKGE:BKRBKR_3W077:::HV: | B | 478 | 119.4597 | 108.5436 |  |  |  | Add 3-winding transformer 515375 WWRDEHV7 345 515376 WWRDEHV4 138 515795 WWDEHV21 13 M2
04ALL | ERIS | Thermal | 515376 WWRDEHV4 138 3WXFMR 524:WOODWRT3 345 3 | 29L | T0 | P13:138:OKGE:BKRBKR_3W076:::HV: | B | 478 | 120.4273 | 109.414 |  |  |  | Add 3-winding transformer 515375 WWRDEHV7 345 515376 WWRDEHV4 138 515799 WWDEHV31 13 M2
04ALL | ERIS | Thermal | 515376 WWRDEHV4 138 515425 WWDPST 4 138 1 | 29L | T0 | 272357 | B | 287 | 149.5823 | 146.9799 |  |  |  | Rebuild line 515376 WWRDEHV4 138 515425 WWDPST 4 138 1
04ALL | ERIS | Thermal | 515376 WWRDEHV4 138 515425 WWDPST 4 138 1 | 29WP | T0 | 272357 | B | 287 | 104.6716 | 129.9725 |  |  |  | Rebuild line 515376 WWRDEHV4 138 515425 WWDPST 4 138 1
04ALL | ERIS | Thermal | 515377 CRESENT4 138 521073 TWNLKSW4 138 1 | 26SP | T0 | Single 514827 CTNWOOD4 138 515377 CRESENT4 138 1 | B | 234 | 93.7695 | 138.9848 |  |  |  | Rebuild line 515377 CRESENT4 138 521073 TWNLKSW4 138 1
04ALL | ERIS | Thermal | 515377 CRESENT4 138 521073 TWNLKSW4 138 1 | 29SP | T0 | Single 514827 CTNWOOD4 138 515377 CRESENT4 138 1 | B | 234 | 93.6338 | 138.8622 |  |  |  | Rebuild line 515377 CRESENT4 138 521073 TWNLKSW4 138 1
04ALL | ERIS | Thermal | 515377 CRESENT4 138 521073 TWNLKSW4 138 1 | 29WP | T0 | Single 514827 CTNWOOD4 138 515377 CRESENT4 138 1 | B | 279 | 79.5843 | 115.8626 |  |  |  | Rebuild line 515377 CRESENT4 138 521073 TWNLKSW4 138 1
04ALL | ERIS | Thermal | 515425 WWDPST 4 138 514785 WOODWRD4 138 8 | 29L | T0 | 272357 | B | 286 | 150.729 | 148.2522 |  |  |  | Add phase shifting xfmr 514785 WOODWRD4 138 515425 WWDPST 4 138 M2
04ALL | ERIS | Thermal | 515425 WWDPST 4 138 514785 WOODWRD4 138 8 | 29WP | T0 | 272357 | B | 286 | 106.2109 | 130.3914 |  |  |  | Add phase shifting xfmr 514785 WOODWRD4 138 515425 WWDPST 4 138 M2
04ALL | ERIS | Thermal | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 29SP | T0 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | B | 830 | 132.5953 | 158.3252 |  |  |  | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
04ALL | ERIS | Thermal | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 29WP | T0 | System Intact | A | 830 | 81.7429 | 134.4233 |  |  |  | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
04ALL | ERIS | Thermal | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 26SP | T0 | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | B | 830 | 100.62 | 153.3456 |  |  |  | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
04ALL | ERIS | Thermal | 515785 WINDFRM4 138 520999 MOORLND4 138 1 | 29WP | T0 | 272357 | B | 287 | 86.2657 | 116.158 |  |  |  | Rebuild line 515785 WINDFRM4 138 520999 MOORLND4 138 1
04ALL | ERIS | Thermal | 515800 GRACMNT7 345 3WXFMR 524:524:GRACMNT3 345 3 | 29SP | T0 | P42:345:OKGE:SB_GRNT7381:::EHV: | B | 478 | 60.0207 | 119.3844 |  |  |  | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2
04ALL | ERIS | Thermal | 515800 GRACMNT7 345 3WXFMR 524:524:GRACMNT3 345 3 | 29WP | T0 | Single 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | B | 478 | 73.2475 | 112.5649 |  |  |  | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2
04ALL | ERIS | Thermal | 515800 GRACMNT7 345 3WXFMR 524:524:GRACMNT3 345 3 | 26SP | T0 | P42:345:OKGE:SB_GRNT7381:::EHV: | B | 478 | 48.2915 | 103.4577 |  |  |  | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2
04ALL | ERIS | Thermal | 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | 29SP | T0 | System Intact | A | 1196 | 72.9707 | 123.942 |  |  |  | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1
04ALL | ERIS | Thermal | 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | 29WP | T0 | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | B | 1775 | 54.1368 | 103.347 |  |  |  | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1
04ALL | ERIS | Thermal | 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | 26SP | T0 | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | B | 1541 | 65.3163 | 118.1606 |  |  |  | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1
04ALL | ERIS | Thermal | 515802 GRACMNT4 138 3WXFMR 524:524:GRACMNT3 345 3 | 29SP | T0 | P42:345:OKGE:SB_GRNT7381:::EHV: | B | 478 | 60.0207 | 119.3844 |  |  |  | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2
04ALL | ERIS | Thermal | 515802 GRACMNT4 138 3WXFMR 524:524:GRACMNT3 345 3 | 29WP | T0 | P42:345:OKGE:SB_GRNT7381:::EHV: | B | 478 | 55.9615 | 112.3921 |  |  |  | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2
04ALL | ERIS | Thermal | 515802 GRACMNT4 138 3WXFMR 524:524:GRACMNT3 345 3 | 26SP | T0 | P42:345:OKGE:SB_GRNT7381:::EHV: | B | 478 | 48.2915 | 103.4577 |  |  |  | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2
04ALL | ERIS | Thermal | 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | 29SP | T0 | P41:345:OKGE:SB_MUGE7384:::EHV: | B | 1540 | 40.0904 | 100.3632 |  |  |  | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1
04ALL | ERIS | Thermal | 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | 29WP | T0 | P41:345:OKGE:SB_MUGE7384:::EHV: | B | 1195 | 40.6791 | 114.7908 |  |  |  | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1
04ALL | ERIS | Thermal | 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | 29SP | T0 | P41:345:OKGE:SB_MUGE7384:::EHV: | B | 1195 | 42.8017 | 118.099 |  |  |  | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1
04ALL | ERIS | Thermal | 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | 26SP | T0 | 272286 | B | 1195 | 25.4455 | 112.9155 |  |  |  | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1
04ALL | ERIS | Thermal | 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | 29SP | T0 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | B | 1195 | 37.5274 | 129.5412 |  |  |  | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1
04ALL | ERIS | Thermal | 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | 29WP | T0 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | B | 1195 | 20.5344 | 120.564 |  |  |  | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1
04ALL | ERIS | Thermal | 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | 26SP | T0 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | B | 1195 | 21.3113 | 127.3119 |  |  |  | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1
04ALL | ERIS | Thermal | 520400 NOBLE4 138 520842 CANADNS4 138 1 | 26SP | T0 | Single 514947 CANADN-4 138 766111 G21-088-TAP 138 1 | B | 234 | 22.6943 | 108.4344 |  |  |  | Rebuild line 520400 NOBLE4 138 520842 CANADNS4 138 1
04ALL | ERIS | Thermal | 520400 NOBLE4 138 520842 CANADNS4 138 1 | 29SP | T0 | Single 514947 CANADN-4 138 766111 G21-088-TAP 138 1 | B | 234 | 27.0675 | 110.0553 |  |  |  | Rebuild line 520400 NOBLE4 138 520842 CANADNS4 138 1
04ALL | ERIS | Thermal | 520400 NOBLE4 138 520975 LIDDELL4 138 1 | 29SP | T0 | Single 514947 CANADN-4 138 766111 G21-088-TAP 138 1 | B | 234 | 20.3927 | 100.1276 |  |  |  | Rebuild line 520400 NOBLE4 138 520975 LIDDELL4 138 1
04ALL | ERIS | Thermal | 520405 KGFSJCT4 138 520600 EKFSHTP4 138 1 | 29SP | T0 | P12:138:OKGE-WFEC:BKRBKR0770:::HV: | B | 187 | 66.5197 | 105.176 |  |  |  | Rebuild line 520405 KGFSJCT4 138 520600 EKFSHTP4 138 1
04ALL | ERIS | Thermal | 520405 KGFSJCT4 138 520600 EKFSHTP4 138 1 | 26SP | T0 | P12:138:OKGE-WFEC:BKRBKR0770:::HV: | B | 136 | 91.7135 | 146.5259 |  |  |  | Rebuild line 520405 KGFSJCT4 138 520600 EKFSHTP4 138 1
04ALL | ERIS | Thermal | 520405 KGFSJCT4 138 520603 NKNGFSH4 138 1 | 29SP | T0 | P12:138:OKGE-WFEC:BKRBKR0770:::HV: | B | 187 | 66.5262 | 105.1842 |  |  |  | Rebuild line 520405 KGFSJCT4 138 520603 NKNGFSH4 138 1
04ALL | ERIS | Thermal | 520405 KGFSJCT4 138 520603 NKNGFSH4 138 1 | 26SP | T0 | P12:138:OKGE-WFEC:BKRBKR0770:::HV: | B | 187 | 66.7129 | 106.5755 |  |  |  | Rebuild line 520405 KGFSJCT4 138 520603 NKNGFSH4 138 1
04ALL | ERIS | Thermal | 520425 PIC4 138 520848 CDRDLTP4 138 1 | 26SP | T0 | Single 520999 MOORLND4 138 786210 G24-308-TAP 138 1 | B | 187 | -1.7055 | 104.8218 |  |  |  | Rebuild line 520425 PIC4 138 520848 CDRDLTP4 138 1
04ALL | ERIS | Thermal | 520425 PIC4 138 520848 CDRDLTP4 138 1 | 29L | T0 | Single 520999 MOORLND4 138 786210 G24-308-TAP 138 1 | B | 187 | -1.7004 | 105.3019 |  |  |  | Rebuild line 520425 PIC4 138 520848 CDRDLTP4 138 1
04ALL | ERIS | Thermal | 520425 PIC4 138 520848 CDRDLTP4 138 1 | 29SP | T0 | Single 520999 MOORLND4 138 786210 G24-308-TAP 138 1 | B | 187 | -1.7032 | 104.9062 |  |  |  | Rebuild line 520425 PIC4 138 520848 CDRDLTP4 138 1
04ALL | ERIS | Thermal | 520425 PIC4 138 786210 G24-308-TAP 138 1 | 26SP | T0 | Single 520999 MOORLND4 138 786210 G24-308-TAP 138 1 | B | 187 | -1.1685 | 105.5926 |  |  |  | Rebuild line 520425 PIC4 138 786210 G24-308-TAP 138 1
04ALL | ERIS | Thermal | 520425 PIC4 138 786210 G24-308-TAP 138 1 | 29L | T0 | Single 520999 MOORLND4 138 786210 G24-308-TAP 138 1 | B | 187 | -1.1881 | 105.6397 |  |  |  | Rebuild line 520425 PIC4 138 786210 G24-308-TAP 138 1
04ALL | ERIS | Thermal | 520425 PIC4 138 786210 G24-308-TAP 138 1 | 29SP | T0 | Single 520999 MOORLND4 138 786210 G24-308-TAP 138 1 | B | 187 | -1.1647 | 105.6839 |  |  |  | Rebuild line 520425 PIC4 138 786210 G24-308-TAP 138 1
04ALL | ERIS | Thermal | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 29SP | T0 | P42:345:OKGE:SB_GRNT7381:::EHV: | B | 283 | 82.8926 | 108.7624 |  |  |  | Rebuild line 520508 CLVLDSW4 138 520814 ANADARK4 138 1
04ALL | ERIS | Thermal | 520533 KGFSHSW4 138 520600 EKFSHTP4 138 1 | 29SP | T0 | P12:138:OKGE-WFEC:BKRBKR0770:::HV: | B | 187 | 62.9072 | 101.5153 |  |  |  | Rebuild line 520533 KGFSHSW4 138 520600 EKFSHTP4 138 1
04ALL | ERIS | Thermal | 520533 KGFSHSW4 138 520600 EKFSHTP4 138 1 | 26SP | T0 | P12:138:OKGE-WFEC:BKRBKR0770:::HV: | B | 187 | 63.185 | 102.9923 |  |  |  | Rebuild line 520533 KGFSHSW4 138 520600 EKFSHTP4 138 1
04ALL | ERIS | Thermal | 520535 BULFTTP4 138 520882 DOVERSW4 138 1 | 29SP | T0 | Single 514827 CTNWOOD4 138 515377 CRESENT4 138 1 | B | 234 | 84.5753 | 163.1884 |  |  |  | Rebuild line 520535 BULFTTP4 138 520882 DOVERSW4 138 1
04ALL | ERIS | Thermal | 520535 BULFTTP4 138 520882 DOVERSW4 138 1 | 29WP | T0 | Single 514827 CTNWOOD4 138 515377 CRESENT4 138 1 | B | 279 | 67.1754 | 134.2417 |  |  |  | Rebuild line 520535 BULFTTP4 138 520882 DOVERSW4 138 1
04ALL | ERIS | Thermal | 520535 BULFTTP4 138 520882 DOVERSW4 138 1 | 26SP | T0 | Single 514827 CTNWOOD4 138 515377 CRESENT4 138 1 | B | 234 | 83.417 | 164.7079 |  |  |  | Rebuild line 520535 BULFTTP4 138 520882 DOVERSW4 138 1
04ALL | ERIS | Thermal | 520603 NKNGFSH4 138 520882 DOVERSW4 138 1 | 29SP | T0 | P12:138:OKGE-WFEC:BKRBKR0770:::HV: | B | 187 | 69.0192 | 107.7088 |  |  |  | Rebuild line 520603 NKNGFSH4 138 520882 DOVERSW4 138 1
04ALL | ERIS | Thermal | 520603 NKNGFSH4 138 520882 DOVERSW4 138 1 | 26SP | T0 | P12:138:OKGE-WFEC:BKRBKR0770:::HV: | B | 187 | 69.1408 | 109.0316 |  |  |  | Rebuild line 520603 NKNGFSH4 138 520882 DOVERSW4 138 1
04ALL | ERIS | Thermal | 520826 BENNGTN4 138 520884 DURANTP4 138 1 | 26SP | T0 | Single 505602 SBROWN4 138 769060 G22-104-TAP 138 1 | B | 287 | 34.3797 | 107.361 |  |  |  | Rebuild line 520826 BENNGTN4 138 520884 DURANTP4 138 1
04ALL | ERIS | Thermal | 520826 BENNGTN4 138 520884 DURANTP4 138 1 | 29SP | T0 | Single 505602 SBROWN4 138 769060 G22-104-TAP 138 1 | B | 287 | 34.3534 | 107.3269 |  |  |  | Rebuild line 520826 BENNGTN4 138 520884 DURANTP4 138 1
04ALL | ERIS | Thermal | 520826 BENNGTN4 138 520884 DURANTP4 138 1 | 29WP | T0 | Single 505602 SBROWN4 138 769060 G22-104-TAP 138 1 | B | 287 | 32.6396 | 105.1757 |  |  |  | Rebuild line 520826 BENNGTN4 138 520884 DURANTP4 138 1
04ALL | ERIS | Thermal | 520842 CANADNS4 138 520976 LIL AXE4 138 1 | 29SP | T0 | P12:138:WFEC:PAOLI_PAYNE:::: | B | 234 | -12.0822 | 101.7571 |  |  |  | Rebuild line 520842 CANADNS4 138 520976 LIL AXE4 138 1
04ALL | ERIS | Thermal | 520847 TWNLKJT4 138 521073 TWNLKSW4 138 1 | 26SP | T0 | Single 514827 CTNWOOD4 138 515377 CRESENT4 138 1 | B | 187 | 68.0499 | 105.783 |  |  |  | Rebuild line 520847 TWNLKJT4 138 521073 TWNLKSW4 138 1
04ALL | ERIS | Thermal | 520847 TWNLKJT4 138 521073 TWNLKSW4 138 1 | 29SP | T0 | Single 514827 CTNWOOD4 138 515377 CRESENT4 138 1 | B | 187 | 67.4836 | 105.1079 |  |  |  | Rebuild line 520847 TWNLKJT4 138 521073 TWNLKSW4 138 1
04ALL | ERIS | Thermal | 520848 CDRDLTP4 138 521016 OKEENE 4 138 1 | 26SP | T0 | Single 520999 MOORLND4 138 786210 G24-308-TAP 138 1 | B | 187 | -3.8386 | 104.0243 |  |  |  | Rebuild line 520848 CDRDLTP4 138 521016 OKEENE 4 138 1
04ALL | ERIS | Thermal | 520848 CDRDLTP4 138 521016 OKEENE 4 138 1 | 29L | T0 | Single 520999 MOORLND4 138 786210 G24-308-TAP 138 1 | B | 187 | -3.8596 | 104.937 |  |  |  | Rebuild line 520848 CDRDLTP4 138 521016 OKEENE 4 138 1
04ALL | ERIS | Thermal | 520848 CDRDLTP4 138 521016 OKEENE 4 138 1 | 29SP | T0 | Single 520999 MOORLND4 138 786210 G24-308-TAP 138 1 | B | 187 | -3.8322 | 104.1046 |  |  |  | Rebuild line 520848 CDRDLTP4 138 521016 OKEENE 4 138 1
04ALL | ERIS | Thermal | 520854 CIVIT 4 138 521023 PAOLI 4 138 1 | 29SP | T0 | System Intact | A | 145 | 19.6969 | 124.2737 |  |  |  | Rebuild line 520854 CIVIT 4 138 521023 PAOLI 4 138 1
04ALL | ERIS | Thermal | 520854 CIVIT 4 138 521023 PAOLI 4 138 1 | 26SP | T0 | System Intact | A | 145 | 15.8127 | 120.1977 |  |  |  | Rebuild line 520854 CIVIT 4 138 521023 PAOLI 4 138 1
04ALL | ERIS | Thermal | 520854 CIVIT 4 138 782580 G24-187-TAP 138 1 | 29SP | T0 | System Intact | A | 145 | 22.2717 | 127.2011 |  |  |  | Rebuild line 520854 CIVIT 4 138 782580 G24-187-TAP 138 1
04ALL | ERIS | Thermal | 520854 CIVIT 4 138 782580 G24-187-TAP 138 1 | 26SP | T0 | System Intact | A | 145 | 17.9433 | 123.0652 |  |  |  | Rebuild line 520854 CIVIT 4 138 782580 G24-187-TAP 138 1
04ALL | ERIS | Thermal | 520861 COLE 4 138 520868 CRINER 4 138 1 | 26SP | T0 | Single 520973 LEXNGTN4 138 520976 LILAXE4 138 1 | B | 187 | 12.8574 | 100.6897 |  |  |  | Rebuild line 520861 COLE 4 138 520868 CRINER 4 138 1
04ALL | ERIS | Thermal | 520861 COLE 4 138 520868 CRINER 4 138 1 | 29SP | T0 | Single 520973 LEXNGTN4 138 520976 LILAXE4 138 1 | B | 187 | 16.4705 | 102.9948 |  |  |  | Rebuild line 520861 COLE 4 138 520868 CRINER 4 138 1
04ALL | ERIS | Thermal | 520868 CRINER 4 138 520888 PAYNESW4 138 1 | 26SP | T0 | Single 520973 LEXNGTN4 138 520976 LILAXE4 138 1 | B | 187 | 14.8626 | 103.7286 |  |  |  | Rebuild line 520868 CRINER 4 138 520888 PAYNESW4 138 1
04ALL | ERIS | Thermal | 520868 CRINER 4 138 520888 PAYNESW4 138 1 | 29SP | T0 | Single 520973 LEXNGTN4 138 520976 LILAXE4 138 1 | B | 187 | 18.7066 | 106.0984 |  |  |  | Rebuild line 520868 CRINER 4 138 520888 PAYNESW4 138 1
04ALL | ERIS | Thermal | 520882 DOVERSW4 138 521016 OKEENE 4 138 1 | 29SP | T0 | Single 520535 BULFTTP4 138 520882 DOVERSW4 138 1 | B | 136 | 70.0864 | 125.0167 |  |  |  | Rebuild line 520882 DOVERSW4 138 521016 OKEENE 4 138 1
04ALL | ERIS | Thermal | 520882 DOVERSW4 138 521016 OKEENE 4 138 1 | 29WP | T0 | Single 520535 BULFTTP4 138 520882 DOVERSW4 138 1 | B | 161 | 60.1918 | 114.5371 |  |  |  | Rebuild line 520882 DOVERSW4 138 521016 OKEENE 4 138 1
04ALL | ERIS | Thermal | 520882 DOVERSW4 138 521016 OKEENE 4 138 1 | 26SP | T0 | Single 520535 BULFTTP4 138 520882 DOVERSW4 138 1 | B | 136 | 66.3593 | 122.8912 |  |  |  | Rebuild line 520882 DOVERSW4 138 521016 OKEENE 4 138 1
04ALL | ERIS | Thermal | 520884 DURANTP4 138 784980 G24-267-TAP 138 1 | 26SP | T0 | Single 505602 SBROWN4 138 769060 G22-104-TAP 138 1 | B | 287 | 36.9034 | 110.0534 |  |  |  | Rebuild line 520884 DURANTP4 138 784980 G24-267-TAP 138 1
04ALL | ERIS | Thermal | 520884 DURANTP4 138 784980 G24-267-TAP 138 1 | 29SP | T0 | Single 505602 SBROWN4 138 769060 G22-104-TAP 138 1 | B | 287 | 36.8898 | 110.0342 |  |  |  | Rebuild line 520884 DURANTP4 138 784980 G24-267-TAP 138 1
04ALL | ERIS | Thermal | 520884 DURANTP4 138 784980 G24-267-TAP 138 1 | 29WP | T0 | Single 505602 SBROWN4 138 769060 G22-104-TAP 138 1 | B | 287 | 35.7566 | 108.383 |  |  |  | Rebuild line 520884 DURANTP4 138 784980 G24-267-TAP 138 1
04ALL | ERIS | Thermal | 520888 PAYNESW4 138 521023 PAOLI 4 138 1 | 26SP | T0 | Single 520973 LEXNGTN4 138 520976 LILAXE4 138 1 | B | 169 | -21.0007 | 122.3938 |  |  |  | Rebuild line 520888 PAYNESW4 138 521023 PAOLI 4 138 1
04ALL | ERIS | Thermal | 520888 PAYNESW4 138 521023 PAOLI 4 138 1 | 29SP | T0 | Single 520973 LEXNGTN4 138 520976 LILAXE4 138 1 | B | 169 | -17.5 | 126.0382 |  |  |  | Rebuild line 520888 PAYNESW4 138 521023 PAOLI 4 138 1
04ALL | ERIS | Thermal | 520888 PAYNESW4 138 521023 PAOLI 4 138 1 | 29WP | T0 | Single 520973 LEXNGTN4 138 520976 LILAXE4 138 1 | B | 201 | -23.8662 | 100.8989 |  |  |  | Rebuild line 520888 PAYNESW4 138 521023 PAOLI 4 138 1
04ALL | ERIS | Thermal | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 | 29SP | T0 | Single 514827 CTNWOOD4 138 515377 CRESENT4 138 1 | B | 136 | 103.3491 | 158.353 |  |  |  | Rebuild line 520893 EL RENO4 138 520899 SCOTTSW4 138 1
04ALL | ERIS | Thermal | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 | 26SP | T0 | Single 514827 CTNWOOD4 138 515377 CRESENT4 138 1 | B | 136 | 103.9178 | 160.5304 |  |  |  | Rebuild line 520893 EL RENO4 138 520899 SCOTTSW4 138 1
04ALL | ERIS | Thermal | 520893 EL RENO4 138 520899 SCOTTSW4 138 1 | 29WP | T0 | Single 514827 CTNWOOD4 138 515377 CRESENT4 138 1 | B | 161 | 82.0591 | 125.3712 |  |  |  | Rebuild line 520893 EL RENO4 138 520899 SCOTTSW4 138 1
04ALL | ERIS | Thermal | 520918 FROGVIL4 138 520948 HUGO PP4 138 1 | 29WP | T0 | Single 505602 SBROWN4 138 769060 G22-104-TAP 138 1 | B | 287 | 61.5145 | 192.0577 |  |  |  | Rebuild line 520918 FROGVIL4 138 520948 HUGO PP4 138 1
04ALL | ERIS | Thermal | 520918 FROGVIL4 138 520948 HUGO PP4 138 1 | 26SP | T0 | Single 505602 SBROWN4 138 769060 G22-104-TAP 138 1 | B | 287 | 63.6965 | 194.1951 |  |  |  | Rebuild line 520918 FROGVIL4 138 520948 HUGO PP4 138 1
04ALL | ERIS | Thermal | 520918 FROGVIL4 138 520948 HUGO PP4 138 1 | 29SP | T0 | Single 505602 SBROWN4 138 769060 G22-104-TAP 138 1 | B | 287 | 63.5093 | 194.0265 |  |  |  | Rebuild line 520918 FROGVIL4 138 520948 HUGO PP4 138 1
04ALL | ERIS | Thermal | 520918 FROGVIL4 138 773820 G23-092-TAP 138 1 | 29WP | T0 | Single 505602 SBROWN4 138 769060 G22-104-TAP 138 1 | B | 287 | 63.1032 | 193.7203 |  |  |  | Rebuild line 520918 FROGVIL4 138 773820 G23-092-TAP 138 1
04ALL | ERIS | Thermal | 520918 FROGVIL4 138 773820 G23-092-TAP 138 1 | 26SP | T0 | Single 505602 SBROWN4 138 769060 G22-104-TAP 138 1 | B | 287 | 65.0704 | 195.6044 |  |  |  | Rebuild line 520918 FROGVIL4 138 773820 G23-092-TAP 138 1
04ALL | ERIS | Thermal | 520918 FROGVIL4 138 773820 G23-092-TAP 138 1 | 29SP | T0 | Single 505602 SBROWN4 138 769060 G22-104-TAP 138 1 | B | 287 | 64.963 | 195.5171 |  |  |  | Rebuild line 520918 FROGVIL4 138 773820 G23-092-TAP 138 1
04ALL | ERIS | Thermal | 520939 HLDTNTP4 138 520981 LOCO 4 138 1 | 29SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 136 | 49.4504 | 106.5312 |  |  |  | Rebuild line 520939 HLDTNTP4 138 520981 LOCO 4 138 1
04ALL | ERIS | Thermal | 520939 HLDTNTP4 138 520981 LOCO 4 138 1 | 26SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 136 | 39.0928 | 105.6705 |  |  |  | Rebuild line 520939 HLDTNTP4 138 520981 LOCO 4 138 1
04ALL | ERIS | Thermal | 520969 LASALLE4 138 520971 LATTAJT4 138 1 | 26SP | T0 | Single 520854 CIVIT4 138 782580 G24-187-TAP 138 1 | B | 169 | -16.1706 | 100.3964 |  |  |  | Rebuild line 520969 LASALLE4 138 520971 LATTAJT4 138 1
04ALL | ERIS | Thermal | 520969 LASALLE4 138 520971 LATTAJT4 138 1 | 29SP | T0 | Single 520854 CIVIT4 138 782580 G24-187-TAP 138 1 | B | 169 | -16.1796 | 100.3378 |  |  |  | Rebuild line 520969 LASALLE4 138 520971 LATTAJT4 138 1
04ALL | ERIS | Thermal | 520971 LATTAJT4 138 521014 OILCRTP4 138 1 | 26SP | T0 | Single 520854 CIVIT4 138 782580 G24-187-TAP 138 1 | B | 169 | -6.7718 | 109.2285 |  |  |  | Rebuild line 520971 LATTAJT4 138 521014 OILCRTP4 138 1
04ALL | ERIS | Thermal | 520971 LATTAJT4 138 521014 OILCRTP4 138 1 | 29SP | T0 | Single 520854 CIVIT4 138 782580 G24-187-TAP 138 1 | B | 169 | -6.7754 | 109.1181 |  |  |  | Rebuild line 520971 LATTAJT4 138 521014 OILCRTP4 138 1
04ALL | ERIS | Thermal | 520973 LEXNGTN4 138 520976 LIL AXE4 138 1 | 29SP | T0 | P42:345:OKGE:SB_GRNT7381:::EHV: | B | 234 | 17.3303 | 107.6197 |  |  |  | Rebuild line 520973 LEXNGTN4 138 520976 LIL AXE4 138 1
04ALL | ERIS | Thermal | 520973 LEXNGTN4 138 520976 LIL AXE4 138 1 | 26SP | T0 | P12:138:WFEC:PAOLI_PAYNE:::: | B | 234 | -6.6096 | 105.3919 |  |  |  | Rebuild line 520973 LEXNGTN4 138 520976 LIL AXE4 138 1
04ALL | ERIS | Thermal | 520995 MOORLND2 69 3WXFMR 525:525:MOORELAND AUTO 69 1 | 29L | T0 | P12:138:OKGE:BKRBKR0830:::HV: | B | 72 | 87.9146 | 100.7837 |  |  |  | Rebuild 3-winding transformer 520995 MOORLND2 69 520999 MOORLND4 138 521180 MLNDTERT 2 1
04ALL | ERIS | Thermal | 520995 MOORLND2 69 3WXFMR 525:525:MOORELAND AUTO 69 1 | 29WP | T0 | P12:138:OKGE:BKRBKR0830:::HV: | B | 72 | 97.9664 | 117.1011 |  |  |  | Rebuild 3-winding transformer 520995 MOORLND2 69 520999 MOORLND4 138 521180 MLNDTERT 2 1
04ALL | ERIS | Thermal | 520995 MOORLND2 69 521197 CRTSJCT2 69 1 | 29L | T0 | P12:138:OKGE:BKRBKR0830:::HV: | B | 68 | 92.7988 | 106.3553 |  |  |  | Rebuild line 520995 MOORLND2 69 521197 CRTSJCT2 69 1
04ALL | ERIS | Thermal | 520995 MOORLND2 69 521197 CRTSJCT2 69 1 | 29WP | T0 | P12:138:OKGE:BKRBKR0830:::HV: | B | 72 | 97.2211 | 117.0651 |  |  |  | Rebuild line 520995 MOORLND2 69 521197 CRTSJCT2 69 1
04ALL | ERIS | Thermal | 520999 MOORLND4 138 3WXFMR 525:525:MOORELAND AUTO 69 1 | 29L | T0 | P12:138:OKGE:BKRBKR0830:::HV: | B | 72 | 89.3894 | 102.4499 |  |  |  | Rebuild 3-winding transformer 520995 MOORLND2 69 520999 MOORLND4 138 521180 MLNDTERT 2 1
04ALL | ERIS | Thermal | 520999 MOORLND4 138 3WXFMR 525:525:MOORELAND AUTO 69 1 | 29WP | T0 | P12:138:OKGE:BKRBKR0830:::HV: | B | 72 | 99.1631 | 119.402 |  |  |  | Rebuild 3-winding transformer 520995 MOORLND2 69 520999 MOORLND4 138 521180 MLNDTERT 2 1
04ALL | ERIS | Thermal | 520999 MOORLND4 138 786210 G24-308-TAP 138 1 | 29L | T0 | System Intact | A | 160 | 6.3724 | 115.5143 |  |  |  | Rebuild line 520999 MOORLND4 138 786210 G24-308-TAP 138 1
04ALL | ERIS | Thermal | 520999 MOORLND4 138 786210 G24-308-TAP 138 1 | 29SP | T0 | System Intact | A | 160 | 10.5469 | 150.6039 |  |  |  | Rebuild line 520999 MOORLND4 138 786210 G24-308-TAP 138 1
04ALL | ERIS | Thermal | 520999 MOORLND4 138 786210 G24-308-TAP 138 1 | 29WP | T0 | Single 520535 BULFTTP4 138 520882 DOVERSW4 138 1 | B | 223 | 15.5103 | 130.9427 |  |  |  | Rebuild line 520999 MOORLND4 138 786210 G24-308-TAP 138 1
04ALL | ERIS | Thermal | 520999 MOORLND4 138 786210 G24-308-TAP 138 1 | 26SP | T0 | System Intact | A | 160 | 5.3849 | 145.5474 |  |  |  | Rebuild line 520999 MOORLND4 138 786210 G24-308-TAP 138 1
04ALL | ERIS | Thermal | 521014 OILCRTP4 138 521056 STRATFD4 138 1 | 26SP | T0 | Single 520854 CIVIT4 138 782580 G24-187-TAP 138 1 | B | 169 | -2.7083 | 113.3633 |  |  |  | Rebuild line 521014 OILCRTP4 138 521056 STRATFD4 138 1
04ALL | ERIS | Thermal | 521014 OILCRTP4 138 521056 STRATFD4 138 1 | 29SP | T0 | Single 520854 CIVIT4 138 782580 G24-187-TAP 138 1 | B | 169 | -2.7094 | 113.237 |  |  |  | Rebuild line 521014 OILCRTP4 138 521056 STRATFD4 138 1
04ALL | ERIS | Thermal | 521015 OKEENE 2 69 3WXFMR 525:525:OKEENE AUTO 69 1 | 29WP | T0 | Single 520999 MOORLND4 138 786210 G24-308-TAP 138 1 | B | 70 | 37.5815 | 146.7107 |  |  |  | Rebuild 3-winding transformer 521015 OKEENE 2 69 521016 OKEENE 4 138 521173 OKENTERT 13 1
04ALL | ERIS | Thermal | 521015 OKEENE 2 69 3WXFMR 525:525:OKEENE AUTO 69 1 | 29SP | T0 | Single 520999 MOORLND4 138 786210 G24-308-TAP 138 1 | B | 70 | 43.9822 | 137.3256 |  |  |  | Rebuild 3-winding transformer 521015 OKEENE 2 69 521016 OKEENE 4 138 521173 OKENTERT 13 1
04ALL | ERIS | Thermal | 521015 OKEENE 2 69 3WXFMR 525:525:OKEENE AUTO 69 1 | 26SP | T0 | Single 520999 MOORLND4 138 786210 G24-308-TAP 138 1 | B | 70 | 37.6741 | 132.8141 |  |  |  | Rebuild 3-winding transformer 521015 OKEENE 2 69 521016 OKEENE 4 138 521173 OKENTERT 13 1
04ALL | ERIS | Thermal | 521016 OKEENE 4 138 3WXFMR 525:525:OKEENE AUTO 69 1 | 29WP | T0 | Single 520999 MOORLND4 138 786210 G24-308-TAP 138 1 | B | 70 | 37.5815 | 146.7107 |  |  |  | Rebuild 3-winding transformer 521015 OKEENE 2 69 521016 OKEENE 4 138 521173 OKENTERT 13 1
04ALL | ERIS | Thermal | 521016 OKEENE 4 138 3WXFMR 525:525:OKEENE AUTO 69 1 | 29SP | T0 | Single 520999 MOORLND4 138 786210 G24-308-TAP 138 1 | B | 70 | 43.9822 | 137.3256 |  |  |  | Rebuild 3-winding transformer 521015 OKEENE 2 69 521016 OKEENE 4 138 521173 OKENTERT 13 1
04ALL | ERIS | Thermal | 521016 OKEENE 4 138 3WXFMR 525:525:OKEENE AUTO 69 1 | 26SP | T0 | Single 520999 MOORLND4 138 786210 G24-308-TAP 138 1 | B | 70 | 37.6741 | 132.8141 |  |  |  | Rebuild 3-winding transformer 521015 OKEENE 2 69 521016 OKEENE 4 138 521173 OKENTERT 13 1
04ALL | ERIS | Thermal | 521042 RUSSELL2 69 3WXFMR 525:525:RUSSELL AUTO 69 1 | 29SP | T0 | P12:138:AEPW-WFEC:LAKEP4WT:RUSSELL4::: | B | 46.6 | 91.1256 | 172.6237 |  |  |  | Rebuild 3-winding transformer 521042 RUSSELL2 69 521043 RUSSELL4 138 521175 RSLTERT 13 1
04ALL | ERIS | Thermal | 521042 RUSSELL2 69 3WXFMR 525:525:RUSSELL AUTO 69 1 | 29WP | T0 | P12:138:AEPW-WFEC:LAKEP4WT:RUSSELL4::: | B | 46.6 | 72.3663 | 164.5039 |  |  |  | Rebuild 3-winding transformer 521042 RUSSELL2 69 521043 RUSSELL4 138 521175 RSLTERT 13 1
04ALL | ERIS | Thermal | 521042 RUSSELL2 69 3WXFMR 525:525:RUSSELL AUTO 69 1 | 26SP | T0 | P12:138:AEPW-WFEC:LAKEP4WT:RUSSELL4::: | B | 46.6 | 84.3968 | 165.0298 |  |  |  | Rebuild 3-winding transformer 521042 RUSSELL2 69 521043 RUSSELL4 138 521175 RSLTERT 13 1
04ALL | ERIS | Thermal | 521042 RUSSELL2 69 529342 OMMANGM2 69 1 | 29SP | T0 | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | B | 42 | 16.0497 | 123.1871 |  |  |  | Rebuild line 521042 RUSSELL2 69 529342 OMMANGM2 69 1
04ALL | ERIS | Thermal | 521042 RUSSELL2 69 529342 OMMANGM2 69 1 | 26SP | T0 | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | B | 42 | 12.0207 | 117.2646 |  |  |  | Rebuild line 521042 RUSSELL2 69 529342 OMMANGM2 69 1
04ALL | ERIS | Thermal | 521042 RUSSELL2 69 529342 OMMANGM2 69 1 | 29WP | T0 | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | B | 49 | 6.047 | 105.4978 |  |  |  | Rebuild line 521042 RUSSELL2 69 529342 OMMANGM2 69 1
04ALL | ERIS | Thermal | 521043 RUSSELL4 138 3WXFMR 525:525:RUSSELL AUTO 69 1 | 29SP | T0 | P12:138:AEPW-WFEC:LAKEP4WT:RUSSELL4::: | B | 46.6 | 91.1256 | 172.6237 |  |  |  | Rebuild 3-winding transformer 521042 RUSSELL2 69 521043 RUSSELL4 138 521175 RSLTERT 13 1
04ALL | ERIS | Thermal | 521043 RUSSELL4 138 3WXFMR 525:525:RUSSELL AUTO 69 1 | 29WP | T0 | P12:138:AEPW-WFEC:LAKEP4WT:RUSSELL4::: | B | 46.6 | 72.3663 | 164.5039 |  |  |  | Rebuild 3-winding transformer 521042 RUSSELL2 69 521043 RUSSELL4 138 521175 RSLTERT 13 1
04ALL | ERIS | Thermal | 521043 RUSSELL4 138 3WXFMR 525:525:RUSSELL AUTO 69 1 | 26SP | T0 | P12:138:AEPW-WFEC:LAKEP4WT:RUSSELL4::: | B | 46.6 | 84.3968 | 165.0298 |  |  |  | Rebuild 3-winding transformer 521042 RUSSELL2 69 521043 RUSSELL4 138 521175 RSLTERT 13 1
04ALL | ERIS | Thermal | 521049 SCLMNJC4 138 769060 G22-104-TAP 138 1 | 26SP | T0 | Single 520918 FROGVIL4 138 773820 G23-092-TAP 138 1 | B | 287 | 26.8228 | 150.9264 |  |  |  | Rebuild line 521049 SCLMNJC4 138 769060 G22-104-TAP 138 1
04ALL | ERIS | Thermal | 521049 SCLMNJC4 138 769060 G22-104-TAP 138 1 | 29SP | T0 | Single 520918 FROGVIL4 138 773820 G23-092-TAP 138 1 | B | 287 | 26.7783 | 151.1654 |  |  |  | Rebuild line 521049 SCLMNJC4 138 769060 G22-104-TAP 138 1
04ALL | ERIS | Thermal | 521049 SCLMNJC4 138 769060 G22-104-TAP 138 1 | 29WP | T0 | Single 520918 FROGVIL4 138 773820 G23-092-TAP 138 1 | B | 287 | 25.0315 | 150.4344 |  |  |  | Rebuild line 521049 SCLMNJC4 138 769060 G22-104-TAP 138 1
04ALL | ERIS | Thermal | 521049 SCLMNJC4 138 784980 G24-267-TAP 138 1 | 26SP | T0 | Single 520918 FROGVIL4 138 773820 G23-092-TAP 138 1 | B | 287 | 28.5737 | 152.7319 |  |  |  | Rebuild line 521049 SCLMNJC4 138 784980 G24-267-TAP 138 1
04ALL | ERIS | Thermal | 521049 SCLMNJC4 138 784980 G24-267-TAP 138 1 | 29SP | T0 | Single 520918 FROGVIL4 138 773820 G23-092-TAP 138 1 | B | 287 | 28.5492 | 152.9872 |  |  |  | Rebuild line 521049 SCLMNJC4 138 784980 G24-267-TAP 138 1
04ALL | ERIS | Thermal | 521049 SCLMNJC4 138 784980 G24-267-TAP 138 1 | 29WP | T0 | Single 520918 FROGVIL4 138 773820 G23-092-TAP 138 1 | B | 287 | 27.85 | 153.3509 |  |  |  | Rebuild line 521049 SCLMNJC4 138 784980 G24-267-TAP 138 1
04ALL | ERIS | Thermal | 521056 STRATFD4 138 782580 G24-187-TAP 138 1 | 26SP | T0 | Single 520854 CIVIT4 138 782580 G24-187-TAP 138 1 | B | 169 | -1.0587 | 115.9971 |  |  |  | Rebuild line 521056 STRATFD4 138 782580 G24-187-TAP 138 1
04ALL | ERIS | Thermal | 521056 STRATFD4 138 782580 G24-187-TAP 138 1 | 29SP | T0 | Single 520854 CIVIT4 138 782580 G24-187-TAP 138 1 | B | 169 | -1.0581 | 115.8634 |  |  |  | Rebuild line 521056 STRATFD4 138 782580 G24-187-TAP 138 1
04ALL | ERIS | Thermal | 521096 WOODWRD2 69 521197 CRTSJCT2 69 1 | 29WP | T0 | P12:138:OKGE:BKRBKR0830:::HV: | B | 72 | 93.0525 | 112.8848 |  |  |  | Rebuild line 521096 WOODWRD2 69 521197 CRTSJCT2 69 1
04ALL | ERIS | Thermal | 521098 WSBNKTP4 138 773820 G23-092-TAP 138 1 | 26SP | T0 | Single 505602 SBROWN4 138 769060 G22-104-TAP 138 1 | B | 287 | 22.7517 | 151.4358 |  |  |  | Rebuild line 521098 WSBNKTP4 138 773820 G23-092-TAP 138 1
04ALL | ERIS | Thermal | 521098 WSBNKTP4 138 773820 G23-092-TAP 138 1 | 29SP | T0 | Single 505602 SBROWN4 138 769060 G22-104-TAP 138 1 | B | 287 | 22.6424 | 151.3375 |  |  |  | Rebuild line 521098 WSBNKTP4 138 773820 G23-092-TAP 138 1
04ALL | ERIS | Thermal | 521098 WSBNKTP4 138 773820 G23-092-TAP 138 1 | 29WP | T0 | Single 505602 SBROWN4 138 769060 G22-104-TAP 138 1 | B | 287 | 20.6898 | 149.3614 |  |  |  | Rebuild line 521098 WSBNKTP4 138 773820 G23-092-TAP 138 1
04ALL | ERIS | Thermal | 521098 WSBNKTP4 138 778530 G24-052-TAP 138 1 | 26SP | T0 | Single 505602 SBROWN4 138 769060 G22-104-TAP 138 1 | B | 287 | 24.7501 | 153.5815 |  |  |  | Rebuild line 521098 WSBNKTP4 138 778530 G24-052-TAP 138 1
04ALL | ERIS | Thermal | 521098 WSBNKTP4 138 778530 G24-052-TAP 138 1 | 29SP | T0 | Single 505602 SBROWN4 138 769060 G22-104-TAP 138 1 | B | 287 | 24.7559 | 153.6102 |  |  |  | Rebuild line 521098 WSBNKTP4 138 778530 G24-052-TAP 138 1
04ALL | ERIS | Thermal | 521098 WSBNKTP4 138 778530 G24-052-TAP 138 1 | 29WP | T0 | Single 505602 SBROWN4 138 769060 G22-104-TAP 138 1 | B | 287 | 23.7033 | 152.6171 |  |  |  | Rebuild line 521098 WSBNKTP4 138 778530 G24-052-TAP 138 1
04ALL | ERIS | Thermal | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 29SP | T0 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | B | 956 | 77.7734 | 129.9933 |  |  |  | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1
04ALL | ERIS | Thermal | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 29SP | T0 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | B | 956 | 63.1608 | 119.111 |  |  |  | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1
04ALL | ERIS | Thermal | 529298 OMPVET-4 138 529302 OMALTUS4 138 1 | 26SP | T0 | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | B | 215 | -12.3859 | 128.5364 |  |  |  | Rebuild line 529298 OMPVET-4 138 529302 OMALTUS4 138 1
04ALL | ERIS | Thermal | 529298 OMPVET-4 138 529302 OMALTUS4 138 1 | 29SP | T0 | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | B | 215 | -12.6406 | 128.5014 |  |  |  | Rebuild line 529298 OMPVET-4 138 529302 OMALTUS4 138 1
04ALL | ERIS | Thermal | 529298 OMPVET-4 138 529302 OMALTUS4 138 1 | 29WP | T0 | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | B | 215 | -7.3005 | 133.9851 |  |  |  | Rebuild line 529298 OMPVET-4 138 529302 OMALTUS4 138 1
04ALL | ERIS | Thermal | 529298 OMPVET-4 138 529345 OMPARK-4 138 1 | 26SP | T0 | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | B | 215 | -19.3205 | 121.8854 |  |  |  | Rebuild line 529298 OMPVET-4 138 529345 OMPARK-4 138 1
04ALL | ERIS | Thermal | 529298 OMPVET-4 138 529345 OMPARK-4 138 1 | 29SP | T0 | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | B | 215 | -19.7448 | 121.6895 |  |  |  | Rebuild line 529298 OMPVET-4 138 529345 OMPARK-4 138 1
04ALL | ERIS | Thermal | 529298 OMPVET-4 138 529345 OMPARK-4 138 1 | 29WP | T0 | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | B | 215 | -9.9797 | 131.257 |  |  |  | Rebuild line 529298 OMPVET-4 138 529345 OMPARK-4 138 1
04ALL | ERIS | Thermal | 532765 HOYT 7 345 532766 JEC N 7 345 1 | 29SP | T0 | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | B | 830 | 154.0081 | 206.3251 |  |  |  | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1
04ALL | ERIS | Thermal | 532768 EMPEC 7 345 532803 BURNS 7 345 1 | 29SP | T0 | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | B | 829 | 60.265 | 125.4999 |  |  |  | Rebuild line 532768 EMPEC 7 345 532803 BURNS 7 345 1
04ALL | ERIS | Thermal | 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | 29SP | T0 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | B | 1180 | 84.3415 | 137.7873 |  |  |  | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1
04ALL | ERIS | Thermal | 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | 29SP | T0 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | B | 1076 | 95.6808 | 144.7116 |  |  |  | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1
04ALL | ERIS | Thermal | 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | 26SP | T0 | System Intact | A | 1076 | 69.852 | 108.1701 |  |  |  | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1
04ALL | ERIS | Thermal | 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | 29SP | T0 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | B | 1076 | 95.6842 | 144.7101 |  |  |  | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1
04ALL | ERIS | Thermal | 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | 26SP | T0 | System Intact | A | 1076 | 69.8521 | 108.1683 |  |  |  | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1
04ALL | ERIS | Thermal | 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | 29SP | T0 | P51:25:WERE:WOLFCRK7:EHV: | B | 911 | 73.4379 | 150.6319 |  |  |  | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1
04ALL | ERIS | Thermal | 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | 29WP | T0 | System Intact | A | 911 | 37.4918 | 109.2705 |  |  |  | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1
04ALL | ERIS | Thermal | 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | 26SP | T0 | P51:25:WERE:WOLFCRK7:EHV: | B | 911 | 63.4471 | 150.5033 |  |  |  | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1
04ALL | ERIS | Thermal | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | 29SP | T0 | Single 510380 DELWARE7 345 580555 MONETT345 345 1 | B | 829 | 83.839 | 171.855 |  |  |  | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
04ALL | ERIS | Thermal | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | 29WP | T0 | Single 510380 DELWARE7 345 580555 MONETT345 345 1 | B | 956 | 63.3765 | 159.7883 |  |  |  | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
04ALL | ERIS | Thermal | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | 26SP | T0 | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | B | 829 | 81.8046 | 179.2219 |  |  |  | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
04ALL | ERIS | Thermal | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 29SP | T0 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | B | 1806 | 89.0194 | 105.6473 |  |  |  | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
04ALL | ERIS | Thermal | 532796 WICHITA7 345 532798 VIOLA 7 345 1 | 29SP | T0 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | B | 830 | 80.977 | 125.8843 |  |  |  | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1
04ALL | ERIS | Thermal | 532796 WICHITA7 345 532798 VIOLA 7 345 1 | 26SP | T0 | System Intact | A | 830 | 56.8909 | 103.1201 |  |  |  | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1
04ALL | ERIS | Thermal | 532796 WICHITA7 345 532803 BURNS 7 345 1 | 29SP | T0 | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | B | 829 | 61.6765 | 126.1072 |  |  |  | Rebuild line 532796 WICHITA7 345 532803 BURNS 7 345 1
04ALL | ERIS | Thermal | 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | 29SP | T0 | P51:13:WERE:EMPEC 7:EHV: | B | 1195 | 89.2006 | 153.2792 |  |  |  | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1
04ALL | ERIS | Thermal | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 29SP | T0 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | B | 830 | 132.3801 | 158.231 |  |  |  | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
04ALL | ERIS | Thermal | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 29WP | T0 | System Intact | A | 830 | 81.3011 | 134.2942 |  |  |  | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
04ALL | ERIS | Thermal | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 26SP | T0 | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | B | 830 | 100.6151 | 153.3367 |  |  |  | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
04ALL | ERIS | Thermal | 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | 29SP | T0 | P51:13:WERE:EMPEC 7:EHV: | B | 1328 | 81.724 | 139.3391 |  |  |  | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1
04ALL | ERIS | Thermal | 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | 26SP | T0 | System Intact | A | 1183 | 60.0816 | 100.6699 |  |  |  | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1
04ALL | ERIS | Thermal | 532996 TIOGA 4 138 533001 ALTOONA4 138 1 | 29SP | T0 | System Intact | A | 121 | 49.4913 | 109.6165 |  |  |  | Rebuild line 532996 TIOGA 4 138 533001 ALTOONA4 138 1
04ALL | ERIS | Thermal | 533001 ALTOONA4 138 533006 TAYLOR 4 138 1 | 29SP | T0 | P23:345:WERE:N345-345-20:EHV: | B | 182 | 44.2552 | 117.2364 |  |  |  | Rebuild line 533001 ALTOONA4 138 533006 TAYLOR 4 138 1
04ALL | ERIS | Thermal | 533001 ALTOONA4 138 533006 TAYLOR 4 138 1 | 26SP | T0 | P23:345:WERE:N345-345-20:EHV: | B | 182 | 35.9113 | 118.897 |  |  |  | Rebuild line 533001 ALTOONA4 138 533006 TAYLOR 4 138 1
04ALL | ERIS | Thermal | 533002 DEARING4 138 533003 LIBERTY4 138 1 | 29SP | T0 | P23:345:WERE:N345-345-20:EHV: | B | 191 | 57.0361 | 134.468 |  |  |  | Rebuild line 533002 DEARING4 138 533003 LIBERTY4 138 1
04ALL | ERIS | Thermal | 533002 DEARING4 138 533003 LIBERTY4 138 1 | 29WP | T0 | P23:345:WERE:N345-345-20:EHV: | B | 191 | 50.0561 | 145.763 |  |  |  | Rebuild line 533002 DEARING4 138 533003 LIBERTY4 138 1
04ALL | ERIS | Thermal | 533002 DEARING4 138 533003 LIBERTY4 138 1 | 26SP | T0 | P23:345:WERE:N345-345-20:EHV: | B | 191 | 48.9221 | 136.7507 |  |  |  | Rebuild line 533002 DEARING4 138 533003 LIBERTY4 138 1
04ALL | ERIS | Thermal | 533002 DEARING4 138 533004 MONTGOM4 138 1 | 29SP | T0 | P12:138:WERE:DEAR-LIBE-138:HV: | B | 191 | 62.0511 | 132.909 |  |  |  | Rebuild line 533002 DEARING4 138 533004 MONTGOM4 138 1
04ALL | ERIS | Thermal | 533002 DEARING4 138 533004 MONTGOM4 138 1 | 29WP | T0 | P12:138:WERE:DEAR-LIBE-138:HV: | B | 191 | 43.7845 | 133.9406 |  |  |  | Rebuild line 533002 DEARING4 138 533004 MONTGOM4 138 1
04ALL | ERIS | Thermal | 533002 DEARING4 138 533004 MONTGOM4 138 1 | 26SP | T0 | P12:138:WERE:DEAR-LIBE-138:HV: | B | 191 | 52.8213 | 133.1955 |  |  |  | Rebuild line 533002 DEARING4 138 533004 MONTGOM4 138 1
04ALL | ERIS | Thermal | 533003 LIBERTY4 138 533008 TV1MNDV4 138 1 | 29WP | T0 | P23:345:WERE:N345-345-20:EHV: | B | 166 | 42.9449 | 153.8747 |  |  |  | Rebuild line 533003 LIBERTY4 138 533008 TV1MNDV4 138 1
04ALL | ERIS | Thermal | 533003 LIBERTY4 138 533008 TV1MNDV4 138 1 | 29SP | T0 | P23:345:WERE:N345-345-20:EHV: | B | 166 | 45.6932 | 135.7949 |  |  |  | Rebuild line 533003 LIBERTY4 138 533008 TV1MNDV4 138 1
04ALL | ERIS | Thermal | 533003 LIBERTY4 138 533008 TV1MNDV4 138 1 | 26SP | T0 | P23:345:WERE:N345-345-20:EHV: | B | 166 | 36.646 | 138.6936 |  |  |  | Rebuild line 533003 LIBERTY4 138 533008 TV1MNDV4 138 1
04ALL | ERIS | Thermal | 533004 MONTGOM4 138 533006 TAYLOR 4 138 1 | 29SP | T0 | P23:345:WERE:N345-345-20:EHV: | B | 182 | 50.1463 | 123.9206 |  |  |  | Rebuild line 533004 MONTGOM4 138 533006 TAYLOR 4 138 1
04ALL | ERIS | Thermal | 533004 MONTGOM4 138 533006 TAYLOR 4 138 1 | 26SP | T0 | P23:345:WERE:N345-345-20:EHV: | B | 182 | 41.075 | 124.9175 |  |  |  | Rebuild line 533004 MONTGOM4 138 533006 TAYLOR 4 138 1
04ALL | ERIS | Thermal | 533008 TV1MNDV4 138 533020 NEOSHOS4 138 1 | 29WP | T0 | P23:345:WERE:N345-345-20:EHV: | B | 166 | 40.9427 | 151.5982 |  |  |  | Rebuild line 533008 TV1MNDV4 138 533020 NEOSHOS4 138 1
04ALL | ERIS | Thermal | 533008 TV1MNDV4 138 533020 NEOSHOS4 138 1 | 26SP | T0 | P23:345:WERE:N345-345-20:EHV: | B | 166 | 34.0816 | 135.6963 |  |  |  | Rebuild line 533008 TV1MNDV4 138 533020 NEOSHOS4 138 1
04ALL | ERIS | Thermal | 533008 TV1MNDV4 138 533020 NEOSHOS4 138 1 | 29SP | T0 | P23:345:WERE:N345-345-20:EHV: | B | 166 | 43.0577 | 132.8381 |  |  |  | Rebuild line 533008 TV1MNDV4 138 533020 NEOSHOS4 138 1
04ALL | ERIS | Thermal | 533680 CHRYJCT2 69 533697 LIBERT-2 69 1 | 29SP | T0 | P12:138:WERE:DEAR-MONT-138:HV: | B | 95 | 57.7152 | 107.4595 |  |  |  | Rebuild line 533680 CHRYJCT2 69 533697 LIBERT-2 69 1
04ALL | ERIS | Thermal | 533680 CHRYJCT2 69 533697 LIBERT-2 69 1 | 26SP | T0 | P12:138:WERE:DEAR-MONT-138:HV: | B | 95 | 51.2704 | 108.2583 |  |  |  | Rebuild line 533680 CHRYJCT2 69 533697 LIBERT-2 69 1
04ALL | ERIS | Thermal | 533683 COFFSUB2 69 533685 CRA S 2 69 1 | 29SP | T0 | P12:138:WERE:DEAR-LIBE-138:HV: | B | 72 | 86.6837 | 146.6844 |  |  |  | Rebuild line 533683 COFFSUB2 69 533685 CRA S 2 69 1
04ALL | ERIS | Thermal | 533683 COFFSUB2 69 533685 CRA S 2 69 1 | 29WP | T0 | P12:138:WERE:DEAR-LIBE-138:HV: | B | 72 | 78.0309 | 153.7576 |  |  |  | Rebuild line 533683 COFFSUB2 69 533685 CRA S 2 69 1
04ALL | ERIS | Thermal | 533683 COFFSUB2 69 533685 CRA S 2 69 1 | 26SP | T0 | P12:138:WERE:DEAR-LIBE-138:HV: | B | 72 | 78.3069 | 147.5343 |  |  |  | Rebuild line 533683 COFFSUB2 69 533685 CRA S 2 69 1
04ALL | ERIS | Thermal | 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | 29SP | T0 | P42:345:OKGE:SB_DGSE7313:::EHV: | B | 1123 | 83.5263 | 137.138 |  |  |  | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1
04ALL | ERIS | Thermal | 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | 29WP | T0 | P42:345:OKGE:SB_DGSE7313:::EHV: | B | 1123 | 50.8905 | 120.2288 |  |  |  | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1
04ALL | ERIS | Thermal | 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | 26SP | T0 | P42:345:OKGE:SB_DGSE7313:::EHV: | B | 1123 | 72.5693 | 134.861 |  |  |  | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1
04ALL | ERIS | Thermal | 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | 29SP | T0 | P42:345:OKGE:SB_DGSE7313:::EHV: | B | 1140 | 82.4247 | 135.3493 |  |  |  | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1
04ALL | ERIS | Thermal | 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | 29WP | T0 | P42:345:OKGE:SB_DGSE7313:::EHV: | B | 1140 | 50.4502 | 118.6738 |  |  |  | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1
04ALL | ERIS | Thermal | 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | 26SP | T0 | P42:345:OKGE:SB_DGSE7313:::EHV: | B | 1140 | 71.642 | 133.1228 |  |  |  | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1
04ALL | ERIS | Thermal | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 29SP | T0 | System Intact | A | 717 | 75.4599 | 112.7617 |  |  |  | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1
04ALL | ERIS | Thermal | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 26SP | T0 | System Intact | A | 717 | 63.4638 | 107.9984 |  |  |  | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1
04ALL | ERIS | Thermal | 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | 29SP | T0 | System Intact | A | 1183 | 77.1401 | 101.3077 |  |  |  | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1
04ALL | ERIS | Thermal | 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | 29SP | T0 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | B | 1792 | 90.5216 | 120.4706 |  |  |  | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1
04ALL | ERIS | Thermal | 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | 29SP | T0 | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | B | 1792 | 115.9923 | 149.2208 |  |  |  | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2
04ALL | ERIS | Thermal | 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | 29WP | T0 | System Intact | A | 1792 | 83.262 | 111.7847 |  |  |  | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2
04ALL | ERIS | Thermal | 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | 26SP | T0 | System Intact | A | 1713 | 86.4464 | 116.1211 |  |  |  | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2
04ALL | ERIS | Thermal | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | 29SP | T0 | P51:13:WERE:EMPEC 7:EHV: | B | 1328 | 81.544 | 139.3391 |  |  |  | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1
04ALL | ERIS | Thermal | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | 26SP | T0 | System Intact | A | 1183 | 59.9791 | 100.5548 |  |  |  | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1
04ALL | ERIS | Thermal | 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | 29SP | T0 | P51:25:WERE:WOLFCRK7:EHV: | B | 911 | 73.038 | 155.208 |  |  |  | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1
04ALL | ERIS | Thermal | 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | 29WP | T0 | System Intact | A | 911 | 36.9262 | 108.6954 |  |  |  | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1
04ALL | ERIS | Thermal | 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | 26SP | T0 | P51:25:WERE:WOLFCRK7:EHV: | B | 911 | 62.9848 | 154.4736 |  |  |  | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1
04ALL | ERIS | Thermal | 547469 RIV4525 161 547729 BAX488 5 161 1 | 29SP | T0 | System Intact | A | 278 | 45.4068 | 103.0986 |  |  |  | Rebuild line 547469 RIV4525 161 547729 BAX488 5 161 1
04ALL | ERIS | Thermal | 547469 RIV4525 161 547729 BAX488 5 161 1 | 26SP | T0 | System Intact | A | 278 | 42.8387 | 111.2704 |  |  |  | Rebuild line 547469 RIV4525 161 547729 BAX488 5 161 1
04ALL | ERIS | Thermal | 547487 HOC404 5 161 547729 BAX488 5 161 1 | 29SP | T0 | System Intact | A | 268 | 47.1629 | 107.0043 |  |  |  | Rebuild line 547487 HOC404 5 161 547729 BAX488 5 161 1
04ALL | ERIS | Thermal | 547487 HOC404 5 161 547729 BAX488 5 161 1 | 26SP | T0 | System Intact | A | 268 | 44.499 | 115.4782 |  |  |  | Rebuild line 547487 HOC404 5 161 547729 BAX488 5 161 1
04ALL | ERIS | Thermal | 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | 29SP | T0 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | B | 1055 | 46.0289 | 107.5556 |  |  |  | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1
04ALL | ERIS | Thermal | 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | 26SP | T0 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | B | 1055 | 47.4775 | 109.3451 |  |  |  | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1
04ALL | ERIS | Thermal | 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | 29SP | T0 | P51:25:WERE:WOLFCRK7:EHV: | B | 911 | 73.0528 | 155.2292 |  |  |  | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1
04ALL | ERIS | Thermal | 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | 29WP | T0 | System Intact | A | 911 | 36.9373 | 108.7186 |  |  |  | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1
04ALL | ERIS | Thermal | 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | 26SP | T0 | P51:25:WERE:WOLFCRK7:EHV: | B | 911 | 62.9996 | 154.497 |  |  |  | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1
04ALL | ERIS | Thermal | 774620 G23-132-TAP 161 780390 G24-114-TAP 161 1 | 29SP | T0 | P23:500:EES-EAI:KEO:B4941::EHV: | B | 237 | 39.8298 | 122.7867 |  |  |  | Rebuild line 774620 G23-132-TAP 161 780390 G24-114-TAP 161 1
04ALL | ERIS | Thermal | 774620 G23-132-TAP 161 780390 G24-114-TAP 161 1 | 29WP | T0 | P23:500:EES-EAI:KEO:B4941::EHV: | B | 277 | 40.4512 | 114.464 |  |  |  | Rebuild line 774620 G23-132-TAP 161 780390 G24-114-TAP 161 1
04ALL | ERIS | Thermal | 774620 G23-132-TAP 161 780390 G24-114-TAP 161 1 | 26SP | T0 | P23:500:EES-EAI:KEO:B4941::EHV: | B | 237 | 42.7527 | 124.5138 |  |  |  | Rebuild line 774620 G23-132-TAP 161 780390 G24-114-TAP 161 1
04ALL | ERIS | Thermal | 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | 29SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 1059 | 33.7285 | 128.9156 |  |  |  | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1
04ALL | ERIS | Thermal | 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | 29WP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 1186 | 34.1358 | 119.0391 |  |  |  | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1
04ALL | ERIS | Thermal | 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | 26SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 1059 | 36.9245 | 129.0645 |  |  |  | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1
04ALL | ERIS | Thermal | 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | 29SP | T0 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | B | 1076 | 95.6842 | 144.7116 |  |  |  | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1
04ALL | ERIS | Thermal | 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | 26SP | T0 | System Intact | A | 1076 | 69.8521 | 108.1701 |  |  |  | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1
04ALL | ERIS | Thermal | 781680 GEN-2024-157 138 781800 G24-161-TAP 138 1 | 29SP | T0 | Single 511435 SNYDER-4 138 765230 G20-012-TAP 138 1 | B | 170 | -11.9346 | 109.6145 |  |  |  | Rebuild line 781680 GEN-2024-157 138 781800 G24-161-TAP 138 1
04ALL | ERIS | Thermal | 781680 GEN-2024-157 138 781800 G24-161-TAP 138 1 | 26SP | T0 | Single 511435 SNYDER-4 138 765230 G20-012-TAP 138 1 | B | 170 | -10.8986 | 110.8588 |  |  |  | Rebuild line 781680 GEN-2024-157 138 781800 G24-161-TAP 138 1
04ALL | ERIS | Thermal | 781680 GEN-2024-157 138 781800 G24-161-TAP 138 1 | 29WP | T0 | Single 511435 SNYDER-4 138 765230 G20-012-TAP 138 1 | B | 202 | 3.2071 | 101.7875 |  |  |  | Rebuild line 781680 GEN-2024-157 138 781800 G24-161-TAP 138 1
05ALL | ERIS | Thermal | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | 26SP | T0 | System Intact | A | 339 | 55.5321 | 107.8234 |  |  |  | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
05ALL | ERIS | Thermal | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | 29SP | T0 | System Intact | A | 339 | 48.3953 | 100.5487 |  |  |  | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
05ALL | ERIS | Thermal | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | 29WP | T0 | System Intact | A | 331 | 35.3826 | 106.405 |  |  |  | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
05ALL | ERIS | Thermal | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | 26SP | T0 | System Intact | A | 339 | 56.3185 | 107.8234 |  |  |  | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
05ALL | ERIS | Thermal | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | 29SP | T0 | System Intact | A | 339 | 48.8796 | 100.5487 |  |  |  | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
05ALL | ERIS | Thermal | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | 29WP | T0 | System Intact | A | 331 | 35.7906 | 106.405 |  |  |  | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
05ALL | ERIS | Thermal | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 26SP | T0 | System Intact | A | 353 | 50.6305 | 103.1009 |  |  |  | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
05ALL | ERIS | Thermal | 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | 26SP | T0 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | B | 353 | 24.1779 | 116.613 |  |  |  | Rebuild line 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1
05ALL | ERIS | Thermal | 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | 29SP | T0 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | B | 353 | 18.3338 | 105.6653 |  |  |  | Rebuild line 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1
05ALL | ERIS | Thermal | 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | 29WP | T0 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | B | 439 | 22.3062 | 104.1363 |  |  |  | Rebuild line 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1
05ALL | ERIS | Thermal | 512106 SHAM 2WT 69 3WXFMR 520:SHAMRCK1 115 1 | 26SP | T0 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | B | 63 | 47.2403 | 107.6567 |  |  |  | Rebuild 3-winding transformer 512106 SHAM 2WT 69 512107 SHAM 3WT 115 512109 SR1TERT 14 1
05ALL | ERIS | Thermal | 512107 SHAM 3WT 115 3WXFMR 520:SHAMRCK1 115 1 | 26SP | T0 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | B | 63 | 47.2403 | 107.6567 |  |  |  | Rebuild 3-winding transformer 512106 SHAM 2WT 69 512107 SHAM 3WT 115 512109 SR1TERT 14 1
05ALL | ERIS | Thermal | 523095 HITCHLAND 6 230 3WXFMR 526:H TB80155502 230 1 | 26SP | T0 | Single 523097 HITCHLAND7 345 523095 HITCHLAND6 230 523094 'HITCHLD_TR21' 13 2 | B | 644 | -19.5059 | 116.4745 |  |  |  | Add 3-winding transformer 523091 HITCHLD_TR01 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2
05ALL | ERIS | Thermal | 523095 HITCHLAND 6 230 3WXFMR 526:H TB80155502 230 1 | 29SP | T0 | Single 523097 HITCHLAND7 345 523095 HITCHLAND6 230 523094 'HITCHLD_TR21' 13 2 | B | 644 | -22.0054 | 112.9265 |  |  |  | Add 3-winding transformer 523091 HITCHLD_TR01 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2
05ALL | ERIS | Thermal | 523095 HITCHLAND 6 230 3WXFMR 526:H TB80155502 230 1 | 29WP | T0 | Single 523097 HITCHLAND7 345 523095 HITCHLAND6 230 523094 'HITCHLD_TR21' 13 2 | B | 700 | -21.4232 | 102.6993 |  |  |  | Add 3-winding transformer 523091 HITCHLD_TR01 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2
05ALL | ERIS | Thermal | 523095 HITCHLAND 6 230 3WXFMR 526:SIEM 8743067 230 2 | 26SP | T0 | Single 523097 HITCHLAND7 345 523095 HITCHLAND6 230 523091 'HITCHLD_TR01' 13 1 | B | 644 | -20.0181 | 120.1733 |  |  |  | Add 3-winding transformer 523094 HITCHLD_TR21 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2
05ALL | ERIS | Thermal | 523095 HITCHLAND 6 230 3WXFMR 526:SIEM 8743067 230 2 | 29SP | T0 | Single 523097 HITCHLAND7 345 523095 HITCHLAND6 230 523091 'HITCHLD_TR01' 13 1 | B | 644 | -22.6852 | 116.5241 |  |  |  | Add 3-winding transformer 523094 HITCHLD_TR21 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2
05ALL | ERIS | Thermal | 523095 HITCHLAND 6 230 3WXFMR 526:SIEM 8743067 230 2 | 29WP | T0 | Single 523097 HITCHLAND7 345 523095 HITCHLAND6 230 523091 'HITCHLD_TR01' 13 1 | B | 700 | -22.0218 | 106.0136 |  |  |  | Add 3-winding transformer 523094 HITCHLD_TR21 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2
05ALL | ERIS | Thermal | 523095 HITCHLAND 6 230 778320 G24-045-TAP 230 1 | 26SP | T0 | Single 523309 MOORE_CNTY6 230 778320 G24-045-TAP 230 1 | B | 548 | -5.1044 | 128.4643 |  |  |  | Rebuild line 523095 HITCHLAND 6 230 778320 G24-045-TAP 230 1
05ALL | ERIS | Thermal | 523095 HITCHLAND 6 230 778320 G24-045-TAP 230 1 | 29SP | T0 | Single 523309 MOORE_CNTY6 230 778320 G24-045-TAP 230 1 | B | 548 | -5.0012 | 128.5647 |  |  |  | Rebuild line 523095 HITCHLAND 6 230 778320 G24-045-TAP 230 1
05ALL | ERIS | Thermal | 523095 HITCHLAND 6 230 778320 G24-045-TAP 230 1 | 29WP | T0 | Single 523309 MOORE_CNTY6 230 778320 G24-045-TAP 230 1 | B | 609 | -4.5355 | 115.6285 |  |  |  | Rebuild line 523095 HITCHLAND 6 230 778320 G24-045-TAP 230 1
05ALL | ERIS | Thermal | 523097 HITCHLAND 7 345 3WXFMR 526:H TB80155502 230 1 | 26SP | T0 | Single 523097 HITCHLAND7 345 523095 HITCHLAND6 230 523094 'HITCHLD_TR21' 13 2 | B | 644 | -19.6485 | 123.7258 |  |  |  | Add 3-winding transformer 523091 HITCHLD_TR01 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2
05ALL | ERIS | Thermal | 523097 HITCHLAND 7 345 3WXFMR 526:H TB80155502 230 1 | 29SP | T0 | Single 523097 HITCHLAND7 345 523095 HITCHLAND6 230 523094 'HITCHLD_TR21' 13 2 | B | 644 | -22.3646 | 119.228 |  |  |  | Add 3-winding transformer 523091 HITCHLD_TR01 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2
05ALL | ERIS | Thermal | 523097 HITCHLAND 7 345 3WXFMR 526:H TB80155502 230 1 | 29WP | T0 | Single 523097 HITCHLAND7 345 523095 HITCHLAND6 230 523094 'HITCHLD_TR21' 13 2 | B | 700 | -21.5798 | 108.2874 |  |  |  | Add 3-winding transformer 523091 HITCHLD_TR01 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2
05ALL | ERIS | Thermal | 523097 HITCHLAND 7 345 3WXFMR 526:SIEM 8743067 230 2 | 26SP | T0 | Single 523097 HITCHLAND7 345 523095 HITCHLAND6 230 523091 'HITCHLD_TR01' 13 1 | B | 644 | -20.1451 | 127.0024 |  |  |  | Add 3-winding transformer 523094 HITCHLD_TR21 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2
05ALL | ERIS | Thermal | 523097 HITCHLAND 7 345 3WXFMR 526:SIEM 8743067 230 2 | 29SP | T0 | Single 523097 HITCHLAND7 345 523095 HITCHLAND6 230 523091 'HITCHLD_TR01' 13 1 | B | 644 | -23.0109 | 122.4663 |  |  |  | Add 3-winding transformer 523094 HITCHLD_TR21 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2
05ALL | ERIS | Thermal | 523097 HITCHLAND 7 345 3WXFMR 526:SIEM 8743067 230 2 | 29WP | T0 | Single 523097 HITCHLAND7 345 523095 HITCHLAND6 230 523091 'HITCHLD_TR01' 13 1 | B | 700 | -22.1631 | 111.2894 |  |  |  | Add 3-winding transformer 523094 HITCHLD_TR21 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2
05ALL | ERIS | Thermal | 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 1 | 26SP | T0 | Single 523267 PRINGLE6 230 523979 HARRNG_EST6 230 1 | B | 159 | 21.717 | 132.6772 |  |  |  | Rebuild line 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 1
05ALL | ERIS | Thermal | 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 1 | 29SP | T0 | Single 523267 PRINGLE6 230 523979 HARRNG_EST6 230 1 | B | 159 | 19.1112 | 130.2361 |  |  |  | Rebuild line 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 1
05ALL | ERIS | Thermal | 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 1 | 29WP | T0 | Single 523267 PRINGLE6 230 523979 HARRNG_EST6 230 1 | B | 167 | -3.6088 | 109.9312 |  |  |  | Rebuild line 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 1
05ALL | ERIS | Thermal | 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 2 | 26SP | T0 | Single 523186 SPEARMAN3 115 523266 PRINGLE3 115 1 | B | 159 | 34.5448 | 114.7405 |  |  |  | Rebuild line 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 2
05ALL | ERIS | Thermal | 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 2 | 29SP | T0 | Single 523186 SPEARMAN3 115 523266 PRINGLE3 115 1 | B | 159 | 34.8682 | 113.9917 |  |  |  | Rebuild line 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 2
05ALL | ERIS | Thermal | 523266 PRINGLE 3 115 3WXFMR 526:ENRCO13617-1 115 1 | 26SP | T0 | Single 523267 PRINGLE6 230 523979 HARRNG_EST6 230 1 | B | 193 | -5.8368 | 328.0363 |  |  |  | Rebuild 3-winding transformer and add 3-winding transformer 523265 PRINGLE_TR 1 13 523266 PRINGLE 3 115 523267 PRINGLE 6 230 1
05ALL | ERIS | Thermal | 523266 PRINGLE 3 115 3WXFMR 526:ENRCO13617-1 115 1 | 29SP | T0 | MULTIGEN523979 | B | 193 | -5.5116 | 324.9423 |  |  |  | Rebuild 3-winding transformer and add 3-winding transformer 523265 PRINGLE_TR 1 13 523266 PRINGLE 3 115 523267 PRINGLE 6 230 1
05ALL | ERIS | Thermal | 523266 PRINGLE 3 115 3WXFMR 526:ENRCO13617-1 115 1 | 29WP | T0 | Single 523267 PRINGLE6 230 523979 HARRNG_EST6 230 1 | B | 210 | -5.7463 | 304.9536 |  |  |  | Rebuild 3-winding transformer and add 3-winding transformer 523265 PRINGLE_TR 1 13 523266 PRINGLE 3 115 523267 PRINGLE 6 230 1
05ALL | ERIS | Thermal | 523266 PRINGLE 3 115 523377 RIVERVIEW 3 115 1 | 26SP | T0 | MULTIGEN523979 | B | 176 | -7.8159 | 123.1653 |  |  |  | Rebuild line 523266 PRINGLE 3 115 523377 RIVERVIEW 3 115 1
05ALL | ERIS | Thermal | 523266 PRINGLE 3 115 523377 RIVERVIEW 3 115 1 | 29SP | T0 | MULTIGEN523979 | B | 176 | -7.8646 | 117.8265 |  |  |  | Rebuild line 523266 PRINGLE 3 115 523377 RIVERVIEW 3 115 1
05ALL | ERIS | Thermal | 523266 PRINGLE 3 115 523377 RIVERVIEW 3 115 1 | 29WP | T0 | MULTIGEN523979 | B | 195 | 13.2165 | 120.8541 |  |  |  | Rebuild line 523266 PRINGLE 3 115 523377 RIVERVIEW 3 115 1
05ALL | ERIS | Thermal | 523267 PRINGLE 6 230 3WXFMR 526:ENRCO13617-1 115 1 | 26SP | T0 | Single 523267 PRINGLE6 230 523979 HARRNG_EST6 230 1 | B | 193 | -5.9313 | 328.0363 |  |  |  | Rebuild 3-winding transformer and add 3-winding transformer 523265 PRINGLE_TR 1 13 523266 PRINGLE 3 115 523267 PRINGLE 6 230 1
05ALL | ERIS | Thermal | 523267 PRINGLE 6 230 3WXFMR 526:ENRCO13617-1 115 1 | 29SP | T0 | MULTIGEN523979 | B | 193 | -5.6007 | 324.9423 |  |  |  | Rebuild 3-winding transformer and add 3-winding transformer 523265 PRINGLE_TR 1 13 523266 PRINGLE 3 115 523267 PRINGLE 6 230 1
05ALL | ERIS | Thermal | 523267 PRINGLE 6 230 3WXFMR 526:ENRCO13617-1 115 1 | 29WP | T0 | Single 523267 PRINGLE6 230 523979 HARRNG_EST6 230 1 | B | 210 | -5.8391 | 304.9536 |  |  |  | Rebuild 3-winding transformer and add 3-winding transformer 523265 PRINGLE_TR 1 13 523266 PRINGLE 3 115 523267 PRINGLE 6 230 1
05ALL | ERIS | Thermal | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1 | 26SP | T0 | Single 523267 PRINGLE6 230 523266 PRINGLE3 115 523265 'PRINGLE_TR 1' 13 1 | B | 357 | -7.5672 | 170.6276 |  |  |  | Rebuild line 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
05ALL | ERIS | Thermal | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1 | 29SP | T0 | Single 523267 PRINGLE6 230 523266 PRINGLE3 115 523265 'PRINGLE_TR 1' 13 1 | B | 357 | -7.4724 | 171.0382 |  |  |  | Rebuild line 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
05ALL | ERIS | Thermal | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1 | 29WP | T0 | Single 523267 PRINGLE6 230 523266 PRINGLE3 115 523265 'PRINGLE_TR 1' 13 1 | B | 438 | -6.1913 | 138.5419 |  |  |  | Rebuild line 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
05ALL | ERIS | Thermal | 523309 MOORE_CNTY 6 230 778320 G24-045-TAP 230 1 | 26SP | T0 | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | B | 548 | -4.1411 | 127.9168 |  |  |  | Rebuild line 523309 MOORE_CNTY 6 230 778320 G24-045-TAP 230 1
05ALL | ERIS | Thermal | 523309 MOORE_CNTY 6 230 778320 G24-045-TAP 230 1 | 29SP | T0 | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | B | 548 | -4.0443 | 127.5644 |  |  |  | Rebuild line 523309 MOORE_CNTY 6 230 778320 G24-045-TAP 230 1
05ALL | ERIS | Thermal | 523309 MOORE_CNTY 6 230 778320 G24-045-TAP 230 1 | 29WP | T0 | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | B | 609 | -3.6991 | 114.1189 |  |  |  | Rebuild line 523309 MOORE_CNTY 6 230 778320 G24-045-TAP 230 1
05ALL | ERIS | Thermal | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 26SP | T0 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | B | 353 | 8.6472 | 109.5429 |  |  |  | Rebuild line 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1
05ALL | ERIS | Thermal | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 26SP | T0 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | B | 956 | 30.1262 | 133.2402 |  |  |  | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1
05ALL | ERIS | Thermal | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 29SP | T0 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | B | 956 | 40.0438 | 141.6763 |  |  |  | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1
05ALL | ERIS | Thermal | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 29WP | T0 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | B | 956 | 22.4354 | 120.7713 |  |  |  | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1
05ALL | ERIS | Thermal | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 29SP | T0 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | B | 956 | 27.1423 | 128.2829 |  |  |  | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1
05ALL | ERIS | Thermal | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 26SP | T0 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | B | 956 | 19.6468 | 118.4192 |  |  |  | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1
05ALL | ERIS | Thermal | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 29WP | T0 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | B | 956 | 20.6164 | 117.691 |  |  |  | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1
05ALL | ERIS | Thermal | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1 | 26SP | T0 | Single 524243 OUTPOST3 115 524266 BUSHLAND3 115 1 | B | 459 | 50.3459 | 186.4318 |  |  |  | Rebuild line 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
05ALL | ERIS | Thermal | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1 | 29SP | T0 | Single 524243 OUTPOST3 115 524266 BUSHLAND3 115 1 | B | 459 | 56.1892 | 191.2045 |  |  |  | Rebuild line 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
05ALL | ERIS | Thermal | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1 | 29WP | T0 | Single 524243 OUTPOST3 115 524266 BUSHLAND3 115 1 | B | 519 | 34.7411 | 168.0069 |  |  |  | Rebuild line 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
05ALL | ERIS | Thermal | 524243 OUTPOST 3 115 524266 BUSHLAND 3 115 1 | 29SP | T0 | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | B | 273 | 73.7381 | 194.6109 |  |  |  | Add line and rebuild line 524243 OUTPOST 3 115 524266 BUSHLAND 3 115 M2
05ALL | ERIS | Thermal | 524243 OUTPOST 3 115 524266 BUSHLAND 3 115 1 | 26SP | T0 | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | B | 273 | 67.0162 | 189.1496 |  |  |  | Add line and rebuild line 524243 OUTPOST 3 115 524266 BUSHLAND 3 115 M2
05ALL | ERIS | Thermal | 524243 OUTPOST 3 115 524266 BUSHLAND 3 115 1 | 29WP | T0 | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | B | 303 | 48.4396 | 169.9089 |  |  |  | Add line and rebuild line 524243 OUTPOST 3 115 524266 BUSHLAND 3 115 M2
05ALL | ERIS | Thermal | 524243 OUTPOST 3 115 524560 ARNOT 3 115 1 | 26SP | T0 | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | B | 273 | 60.1798 | 182.4166 |  |  |  | Rebuild line 524243 OUTPOST 3 115 524560 ARNOT 3 115 1
05ALL | ERIS | Thermal | 524243 OUTPOST 3 115 524560 ARNOT 3 115 1 | 29SP | T0 | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | B | 273 | 65.5228 | 186.4743 |  |  |  | Rebuild line 524243 OUTPOST 3 115 524560 ARNOT 3 115 1
05ALL | ERIS | Thermal | 524243 OUTPOST 3 115 524560 ARNOT 3 115 1 | 29WP | T0 | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | B | 303 | 42.3217 | 163.8702 |  |  |  | Rebuild line 524243 OUTPOST 3 115 524560 ARNOT 3 115 1
05ALL | ERIS | Thermal | 524266 BUSHLAND 3 115 3WXFMR 526:HYUN 201096010 115 1 | 29SP | T0 | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | B | 248 | 81.3638 | 214.6453 |  |  |  | Rebuild 3-winding transformer and add 3-winding transformer 524263 BSHLND_TR1 1 13 524266 BUSHLAND 3 115 524267 BUSHLAND 6 230 1
05ALL | ERIS | Thermal | 524266 BUSHLAND 3 115 3WXFMR 526:HYUN 201096010 115 1 | 26SP | T0 | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | B | 248 | 74.1185 | 208.4729 |  |  |  | Rebuild 3-winding transformer and add 3-winding transformer 524263 BSHLND_TR1 1 13 524266 BUSHLAND 3 115 524267 BUSHLAND 6 230 1
05ALL | ERIS | Thermal | 524266 BUSHLAND 3 115 3WXFMR 526:HYUN 201096010 115 1 | 29WP | T0 | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | B | 273 | 53.8435 | 188.9449 |  |  |  | Rebuild 3-winding transformer and add 3-winding transformer 524263 BSHLND_TR1 1 13 524266 BUSHLAND 3 115 524267 BUSHLAND 6 230 1
05ALL | ERIS | Thermal | 524267 BUSHLAND 6 230 3WXFMR 526:HYUN 201096010 115 1 | 26SP | T0 | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | B | 248 | 75.9091 | 225.0018 |  |  |  | Rebuild 3-winding transformer and add 3-winding transformer 524263 BSHLND_TR1 1 13 524266 BUSHLAND 3 115 524267 BUSHLAND 6 230 1
05ALL | ERIS | Thermal | 524267 BUSHLAND 6 230 3WXFMR 526:HYUN 201096010 115 1 | 29SP | T0 | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | B | 248 | 83.5495 | 234.889 |  |  |  | Rebuild 3-winding transformer and add 3-winding transformer 524263 BSHLND_TR1 1 13 524266 BUSHLAND 3 115 524267 BUSHLAND 6 230 1
05ALL | ERIS | Thermal | 524267 BUSHLAND 6 230 3WXFMR 526:HYUN 201096010 115 1 | 29WP | T0 | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | B | 273 | 54.589 | 201.6416 |  |  |  | Rebuild 3-winding transformer and add 3-winding transformer 524263 BSHLND_TR1 1 13 524266 BUSHLAND 3 115 524267 BUSHLAND 6 230 1
05ALL | ERIS | Thermal | 524300 HILLSIDE 3 115 524306 COULTER 3 115 1 | 26SP | T0 | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | B | 239 | 45.3027 | 186.4201 |  |  |  | Rebuild line 524300 HILLSIDE 3 115 524306 COULTER 3 115 1
05ALL | ERIS | Thermal | 524300 HILLSIDE 3 115 524306 COULTER 3 115 1 | 29SP | T0 | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | B | 239 | 45.0815 | 184.5475 |  |  |  | Rebuild line 524300 HILLSIDE 3 115 524306 COULTER 3 115 1
05ALL | ERIS | Thermal | 524300 HILLSIDE 3 115 524306 COULTER 3 115 1 | 29WP | T0 | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | B | 239 | 33.4337 | 188.5258 |  |  |  | Rebuild line 524300 HILLSIDE 3 115 524306 COULTER 3 115 1
05ALL | ERIS | Thermal | 524300 HILLSIDE 3 115 524560 ARNOT 3 115 1 | 26SP | T0 | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | B | 273 | 51.5565 | 174.149 |  |  |  | Rebuild line 524300 HILLSIDE 3 115 524560 ARNOT 3 115 1
05ALL | ERIS | Thermal | 524300 HILLSIDE 3 115 524560 ARNOT 3 115 1 | 29SP | T0 | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | B | 273 | 52.9644 | 174.2902 |  |  |  | Rebuild line 524300 HILLSIDE 3 115 524560 ARNOT 3 115 1
05ALL | ERIS | Thermal | 524300 HILLSIDE 3 115 524560 ARNOT 3 115 1 | 29WP | T0 | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | B | 303 | 36.0828 | 157.8469 |  |  |  | Rebuild line 524300 HILLSIDE 3 115 524560 ARNOT 3 115 1
05ALL | ERIS | Thermal | 524623 DEAFSMITH 6 230 525520 OLSON 6 230 1 | 29SP | T0 | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | B | 416 | 54.5896 | 110.9842 |  |  |  | Rebuild line 524623 DEAFSMITH 6 230 525520 OLSON 6 230 1
05ALL | ERIS | Thermal | 524623 DEAFSMITH 6 230 525520 OLSON 6 230 1 | 26SP | T0 | Single 525481 PLANT_X6 230 525520 OLSON6 230 1 | B | 416 | 35.4571 | 105.0112 |  |  |  | Rebuild line 524623 DEAFSMITH 6 230 525520 OLSON 6 230 1
05ALL | ERIS | Thermal | 524623 DEAFSMITH 6 230 525520 OLSON 6 230 1 | 29WP | T0 | Single 525481 PLANT_X6 230 525520 OLSON6 230 1 | B | 416 | 35.441 | 105.196 |  |  |  | Rebuild line 524623 DEAFSMITH 6 230 525520 OLSON 6 230 1
05ALL | ERIS | Thermal | 524662 PARMER_CO 3 115 524668 DS-#20 +3 115 1 | 29WP | T0 | P12:230:SPS:K11_K21::1_BUSHL_DFSMTH_PLANTX:HV: | B | 113.3 | 35.2341 | 106.0213 |  |  |  | Rebuild line 524662 PARMER_CO 3 115 524668 DS-#20 +3 115 1
05ALL | ERIS | Thermal | 524764 NORRIS_TP 3 115 524863 FE-CHZPLT 3 115 1 | 26SP | T0 | Single 524875 OASIS6 230 524909 ROOSEVELT6 230 1 | B | 128 | -17.2307 | 102.2247 |  |  |  | Rebuild line 524764 NORRIS_TP 3 115 524863 FE-CHZPLT 3 115 1
05ALL | ERIS | Thermal | 524764 NORRIS_TP 3 115 524863 FE-CHZPLT 3 115 1 | 29SP | T0 | Single 524875 OASIS6 230 524909 ROOSEVELT6 230 1 | B | 128 | -9.8488 | 102.9487 |  |  |  | Rebuild line 524764 NORRIS_TP 3 115 524863 FE-CHZPLT 3 115 1
05ALL | ERIS | Thermal | 524863 FE-CHZPLT 3 115 524874 OASIS 3 115 1 | 26SP | T0 | Single 524875 OASIS6 230 524909 ROOSEVELT6 230 1 | B | 130 | 17.7992 | 112.009 |  |  |  | Rebuild line 524863 FE-CHZPLT 3 115 524874 OASIS 3 115 1
05ALL | ERIS | Thermal | 524863 FE-CHZPLT 3 115 524874 OASIS 3 115 1 | 29SP | T0 | Single 524875 OASIS6 230 524909 ROOSEVELT6 230 1 | B | 130 | 7.5143 | 113.8944 |  |  |  | Rebuild line 524863 FE-CHZPLT 3 115 524874 OASIS 3 115 1
05ALL | ERIS | Thermal | 524874 OASIS 3 115 3WXFMR 526:ABB LLM60041 115 1 | 26SP | T0 | Single 524875 OASIS6 230 524909 ROOSEVELT6 230 1 | B | 239 | 25.1375 | 110.2584 |  |  |  | Add 3-winding transformer 524872 OASIS_TR1 1 13 524874 OASIS 3 115 524875 OASIS 6 230 M2
05ALL | ERIS | Thermal | 524874 OASIS 3 115 3WXFMR 526:ABB LLM60041 115 1 | 29SP | T0 | Single 524875 OASIS6 230 524909 ROOSEVELT6 230 1 | B | 239 | 13.7053 | 112.8837 |  |  |  | Add 3-winding transformer 524872 OASIS_TR1 1 13 524874 OASIS 3 115 524875 OASIS 6 230 M2
05ALL | ERIS | Thermal | 524874 OASIS 3 115 3WXFMR 526:ABB LLM60041 115 1 | 29WP | T0 | Single 524875 OASIS6 230 524909 ROOSEVELT6 230 1 | B | 239 | 15.6529 | 107.8381 |  |  |  | Add 3-winding transformer 524872 OASIS_TR1 1 13 524874 OASIS 3 115 524875 OASIS 6 230 M2
05ALL | ERIS | Thermal | 524875 OASIS 6 230 3WXFMR 526:ABB LLM60041 115 1 | 26SP | T0 | Single 524875 OASIS6 230 524909 ROOSEVELT6 230 1 | B | 239 | 25.6534 | 110.4325 |  |  |  | Add 3-winding transformer 524872 OASIS_TR1 1 13 524874 OASIS 3 115 524875 OASIS 6 230 M2
05ALL | ERIS | Thermal | 524875 OASIS 6 230 3WXFMR 526:ABB LLM60041 115 1 | 29SP | T0 | Single 524875 OASIS6 230 524909 ROOSEVELT6 230 1 | B | 239 | 13.7742 | 112.8837 |  |  |  | Add 3-winding transformer 524872 OASIS_TR1 1 13 524874 OASIS 3 115 524875 OASIS 6 230 M2
05ALL | ERIS | Thermal | 524875 OASIS 6 230 3WXFMR 526:ABB LLM60041 115 1 | 29WP | T0 | Single 524875 OASIS6 230 524909 ROOSEVELT6 230 1 | B | 239 | 15.8696 | 108.881 |  |  |  | Add 3-winding transformer 524872 OASIS_TR1 1 13 524874 OASIS 3 115 524875 OASIS 6 230 M2
05ALL | ERIS | Thermal | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1 | 26SP | T0 | Single 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH6 230 1 | B | 544 | -23.6645 | 149.7395 |  |  |  | Rebuild line 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
05ALL | ERIS | Thermal | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1 | 29SP | T0 | Single 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH6 230 1 | B | 544 | -26.815 | 145.7176 |  |  |  | Rebuild line 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
05ALL | ERIS | Thermal | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1 | 29WP | T0 | Single 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH6 230 1 | B | 604 | -23.4406 | 133.1318 |  |  |  | Rebuild line 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
05ALL | ERIS | Thermal | 524875 OASIS 6 230 787680 G24-357-TAP 230 1 | 26SP | T0 | Single 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH6 230 1 | B | 319 | -26.261 | 254.4424 |  |  |  | Rebuild line 524875 OASIS 6 230 787680 G24-357-TAP 230 1
05ALL | ERIS | Thermal | 524875 OASIS 6 230 787680 G24-357-TAP 230 1 | 29SP | T0 | Single 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH6 230 1 | B | 319 | -25.8156 | 248.3753 |  |  |  | Rebuild line 524875 OASIS 6 230 787680 G24-357-TAP 230 1
05ALL | ERIS | Thermal | 524875 OASIS 6 230 787680 G24-357-TAP 230 1 | 29WP | T0 | Single 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH6 230 1 | B | 319 | -32.6381 | 246.31 |  |  |  | Rebuild line 524875 OASIS 6 230 787680 G24-357-TAP 230 1
05ALL | ERIS | Thermal | 524885 SN_JUAN_SS 6 230 785100 G24-271-TAP 230 1 | 26SP | T0 | Single 524885 SN_JUAN_SS6 230 787680 G24-357-TAP 230 1 | B | 478 | 7.1992 | 114.6954 |  |  |  | Rebuild line 524885 SN_JUAN_SS 6 230 785100 G24-271-TAP 230 1
05ALL | ERIS | Thermal | 524885 SN_JUAN_SS 6 230 785100 G24-271-TAP 230 1 | 29SP | T0 | Single 524885 SN_JUAN_SS6 230 787680 G24-357-TAP 230 1 | B | 478 | 6.9477 | 115.6438 |  |  |  | Rebuild line 524885 SN_JUAN_SS 6 230 785100 G24-271-TAP 230 1
05ALL | ERIS | Thermal | 524885 SN_JUAN_SS 6 230 785100 G24-271-TAP 230 1 | 29WP | T0 | Single 524885 SN_JUAN_SS6 230 787680 G24-357-TAP 230 1 | B | 500 | 6.5247 | 108.7621 |  |  |  | Rebuild line 524885 SN_JUAN_SS 6 230 785100 G24-271-TAP 230 1
05ALL | ERIS | Thermal | 524885 SN_JUAN_SS 6 230 787680 G24-357-TAP 230 1 | 26SP | T0 | Single 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH6 230 1 | B | 319 | -23.2576 | 254.5173 |  |  |  | Rebuild line 524885 SN_JUAN_SS 6 230 787680 G24-357-TAP 230 1
05ALL | ERIS | Thermal | 524885 SN_JUAN_SS 6 230 787680 G24-357-TAP 230 1 | 29SP | T0 | Single 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH6 230 1 | B | 319 | -23.6434 | 248.4623 |  |  |  | Rebuild line 524885 SN_JUAN_SS 6 230 787680 G24-357-TAP 230 1
05ALL | ERIS | Thermal | 524885 SN_JUAN_SS 6 230 787680 G24-357-TAP 230 1 | 29WP | T0 | Single 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH6 230 1 | B | 319 | -31.0472 | 246.4076 |  |  |  | Rebuild line 524885 SN_JUAN_SS 6 230 787680 G24-357-TAP 230 1
05ALL | ERIS | Thermal | 525481 PLANT_X 6 230 525520 OLSON 6 230 1 | 26SP | T0 | Single 524623 DEAFSMITH6 230 525520 OLSON6 230 1 | B | 416 | 35.5536 | 106.3462 |  |  |  | Rebuild line 525481 PLANT_X 6 230 525520 OLSON 6 230 1
05ALL | ERIS | Thermal | 525481 PLANT_X 6 230 525520 OLSON 6 230 1 | 29SP | T0 | P12:230:SPS:K11_K21::1_BUSHL_DFSMTH_PLANTX:HV: | B | 416 | 35.7616 | 106.0723 |  |  |  | Rebuild line 525481 PLANT_X 6 230 525520 OLSON 6 230 1
05ALL | ERIS | Thermal | 525481 PLANT_X 6 230 525520 OLSON 6 230 1 | 29WP | T0 | Single 524623 DEAFSMITH6 230 525520 OLSON6 230 1 | B | 416 | 35.6392 | 105.7227 |  |  |  | Rebuild line 525481 PLANT_X 6 230 525520 OLSON 6 230 1
05ALL | ERIS | Thermal | 525830 TUCO_INT 6 230 3WXFMR 526:SIEM 8743066 230 2 | 29WP | T0 | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | B | 637 | 75.2766 | 162.2676 |  |  |  | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2
05ALL | ERIS | Thermal | 525830 TUCO_INT 6 230 3WXFMR 526:SIEM 8743066 230 2 | 26SP | T0 | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | B | 637 | 73.7353 | 130.6872 |  |  |  | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2
05ALL | ERIS | Thermal | 525830 TUCO_INT 6 230 3WXFMR 526:SIEM 8743066 230 2 | 29SP | T0 | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | B | 637 | 65.9362 | 124.6824 |  |  |  | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2
05ALL | ERIS | Thermal | 525830 TUCO_INT 6 230 3WXFMR 526:UPDATE LATER _11 230 1 | 29WP | T0 | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | B | 699 | 72.4293 | 153.1365 |  |  |  | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2
05ALL | ERIS | Thermal | 525830 TUCO_INT 6 230 3WXFMR 526:UPDATE LATER _11 230 1 | 26SP | T0 | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | B | 699 | 69.7403 | 124.4321 |  |  |  | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2
05ALL | ERIS | Thermal | 525830 TUCO_INT 6 230 3WXFMR 526:UPDATE LATER _11 230 1 | 29SP | T0 | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | B | 699 | 63.1225 | 118.0011 |  |  |  | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2
05ALL | ERIS | Thermal | 525832 TUCO_INT 7 345 3WXFMR 526:SIEM 8743066 230 2 | 29WP | T0 | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | B | 637 | 78.5222 | 162.2676 |  |  |  | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2
05ALL | ERIS | Thermal | 525832 TUCO_INT 7 345 3WXFMR 526:SIEM 8743066 230 2 | 26SP | T0 | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | B | 637 | 78.5062 | 133.226 |  |  |  | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2
05ALL | ERIS | Thermal | 525832 TUCO_INT 7 345 3WXFMR 526:SIEM 8743066 230 2 | 29SP | T0 | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | B | 637 | 68.6934 | 125.1345 |  |  |  | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2
05ALL | ERIS | Thermal | 525832 TUCO_INT 7 345 3WXFMR 526:UPDATE LATER _11 230 1 | 29WP | T0 | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | B | 699 | 76.1099 | 153.0121 |  |  |  | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2
05ALL | ERIS | Thermal | 525832 TUCO_INT 7 345 3WXFMR 526:UPDATE LATER _11 230 1 | 26SP | T0 | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | B | 699 | 78.272 | 126.3567 |  |  |  | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2
05ALL | ERIS | Thermal | 525832 TUCO_INT 7 345 3WXFMR 526:UPDATE LATER _11 230 1 | 29SP | T0 | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | B | 699 | 66.6684 | 118.4972 |  |  |  | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2
05ALL | ERIS | Thermal | 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | 29SP | T0 | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | B | 1792 | 51.6406 | 113.842 |  |  |  | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2
05ALL | ERIS | Thermal | 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | 29WP | T0 | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | B | 1792 | 32.2298 | 104.3709 |  |  |  | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2
05ALL | ERIS | Thermal | 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | 29SP | T0 | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | B | 1792 | 50.7035 | 118.8776 |  |  |  | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1
05ALL | ERIS | Thermal | 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | 29WP | T0 | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | B | 1792 | 30.9487 | 109.4151 |  |  |  | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1
05ALL | ERIS | Thermal | 526460 AMOCO_SS 6 230 777420 G24-015-TAP 230 1 | 26SP | T0 | P42:345:SPS:TUCO-NR50:::EHV: | B | 414 | 24.8586 | 102.0533 |  |  |  | Rebuild line 526460 AMOCO_SS 6 230 777420 G24-015-TAP 230 1
05ALL | ERIS | Thermal | 526460 AMOCO_SS 6 230 777420 G24-015-TAP 230 1 | 29SP | T0 | P42:345:SPS:TUCO-NR50:::EHV: | B | 414 | 27.8555 | 104.8857 |  |  |  | Rebuild line 526460 AMOCO_SS 6 230 777420 G24-015-TAP 230 1
05ALL | ERIS | Thermal | 527482 CHAVES_CNTY3 115 527546 SAMSON 3 115 1 | 26SP | T0 | Single 527564 ROSWLL_INT3 115 527597 TWEEDY3 115 1 | B | 175 | -29.3969 | 101.747 |  |  |  | Rebuild line 527482 CHAVES_CNTY3 115 527546 SAMSON 3 115 1
05ALL | ERIS | Thermal | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1 | 26SP | T0 | Single 524885 SN_JUAN_SS6 230 787680 G24-357-TAP 230 1 | B | 547 | -11.214 | 169.3097 |  |  |  | Rebuild line 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
05ALL | ERIS | Thermal | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1 | 29SP | T0 | Single 524885 SN_JUAN_SS6 230 787680 G24-357-TAP 230 1 | B | 547 | -13.2107 | 169.3895 |  |  |  | Rebuild line 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
05ALL | ERIS | Thermal | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1 | 29WP | T0 | Single 524885 SN_JUAN_SS6 230 787680 G24-357-TAP 230 1 | B | 607 | -17.9052 | 149.7754 |  |  |  | Rebuild line 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
05ALL | ERIS | Thermal | 527522 ROSWELL_CTY3 115 527534 SW4J795_W 3 115 1 | 26SP | T0 | Single 527564 ROSWLL_INT3 115 527597 TWEEDY3 115 1 | B | 159 | -15.8495 | 109.1636 |  |  |  | Rebuild line 527522 ROSWELL_CTY3 115 527534 SW4J795_W 3 115 1
05ALL | ERIS | Thermal | 527522 ROSWELL_CTY3 115 527534 SW4J795_W 3 115 1 | 29SP | T0 | Single 527564 ROSWLL_INT3 115 527597 TWEEDY3 115 1 | B | 159 | -15.6855 | 106.4861 |  |  |  | Rebuild line 527522 ROSWELL_CTY3 115 527534 SW4J795_W 3 115 1
05ALL | ERIS | Thermal | 527522 ROSWELL_CTY3 115 527534 SW4J795_W 3 115 1 | 29WP | T0 | Single 527564 ROSWLL_INT3 115 527597 TWEEDY3 115 1 | B | 167 | -12.2172 | 106.9903 |  |  |  | Rebuild line 527522 ROSWELL_CTY3 115 527534 SW4J795_W 3 115 1
05ALL | ERIS | Thermal | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1 | 26SP | T0 | Single 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH6 230 1 | B | 229 | 8.5247 | 169.8626 |  |  |  | Rebuild line 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
05ALL | ERIS | Thermal | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1 | 29SP | T0 | Single 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH6 230 1 | B | 229 | 4.3299 | 166.3359 |  |  |  | Rebuild line 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
05ALL | ERIS | Thermal | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1 | 29WP | T0 | Single 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH6 230 1 | B | 243 | -11.9008 | 154.0056 |  |  |  | Rebuild line 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
05ALL | ERIS | Thermal | 527597 TWEEDY 3 115 527798 EDDY_NTH 3 115 1 | 26SP | T0 | Single 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH6 230 1 | B | 180 | -12.5985 | 207.0655 |  |  |  | Rebuild line 527597 TWEEDY 3 115 527798 EDDY_NTH 3 115 1
05ALL | ERIS | Thermal | 527597 TWEEDY 3 115 527798 EDDY_NTH 3 115 1 | 29SP | T0 | Single 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH6 230 1 | B | 180 | -4.2278 | 201.9972 |  |  |  | Rebuild line 527597 TWEEDY 3 115 527798 EDDY_NTH 3 115 1
05ALL | ERIS | Thermal | 527597 TWEEDY 3 115 527798 EDDY_NTH 3 115 1 | 29WP | T0 | Single 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH6 230 1 | B | 200 | -21.8614 | 179.2373 |  |  |  | Rebuild line 527597 TWEEDY 3 115 527798 EDDY_NTH 3 115 1
05ALL | ERIS | Thermal | 527799 EDDY_NORTH 6 230 3WXFMR 526:ABB AEM30711 230 1 | 26SP | T0 | Single 524885 SN_JUAN_SS6 230 787680 G24-357-TAP 230 1 | B | 558 | -18.3179 | 108.705 |  |  |  | Add 3-winding transformer 527796 EDDY_TR 1 13 527799 EDDY_NORTH 6 230 527802 EDDY_CNTY 7 345 M2
05ALL | ERIS | Thermal | 527799 EDDY_NORTH 6 230 3WXFMR 526:ABB AEM30711 230 1 | 29SP | T0 | Single 524885 SN_JUAN_SS6 230 787680 G24-357-TAP 230 1 | B | 558 | -17.219 | 106.2964 |  |  |  | Add 3-winding transformer 527796 EDDY_TR 1 13 527799 EDDY_NORTH 6 230 527802 EDDY_CNTY 7 345 M2
05ALL | ERIS | Thermal | 527799 EDDY_NORTH 6 230 3WXFMR 526:ABB AEM30711 230 1 | 29WP | T0 | Single 524885 SN_JUAN_SS6 230 787680 G24-357-TAP 230 1 | B | 558 | -24.4395 | 106.7441 |  |  |  | Add 3-winding transformer 527796 EDDY_TR 1 13 527799 EDDY_NORTH 6 230 527802 EDDY_CNTY 7 345 M2
05ALL | ERIS | Thermal | 527799 EDDY_NORTH 6 230 528095 7-RIVERS 6 230 1 | 29SP | T0 | Single 527802 EDDY_CNTY7 345 527799 EDDY_NORTH6 230 527796 'EDDY_TR 1' 13 1 | B | 319 | 8.1566 | 105.7499 |  |  |  | Rebuild line 527799 EDDY_NORTH 6 230 528095 7-RIVERS 6 230 1
05ALL | ERIS | Thermal | 527799 EDDY_NORTH 6 230 528095 7-RIVERS 6 230 1 | 29WP | T0 | Single 527802 EDDY_CNTY7 345 527799 EDDY_NORTH6 230 527796 'EDDY_TR 1' 13 1 | B | 319 | -8.5289 | 106.8132 |  |  |  | Rebuild line 527799 EDDY_NORTH 6 230 528095 7-RIVERS 6 230 1
05ALL | ERIS | Thermal | 527799 EDDY_NORTH 6 230 528095 7-RIVERS 6 230 1 | 26SP | T0 | Single 527802 EDDY_CNTY7 345 527799 EDDY_NORTH6 230 527796 'EDDY_TR 1' 13 1 | B | 319 | -19.3477 | 102.6474 |  |  |  | Rebuild line 527799 EDDY_NORTH 6 230 528095 7-RIVERS 6 230 1
05ALL | ERIS | Thermal | 527802 EDDY_CNTY 7 345 3WXFMR 526:ABB AEM30711 230 1 | 26SP | T0 | Single 524885 SN_JUAN_SS6 230 787680 G24-357-TAP 230 1 | B | 558 | -19.209 | 114.8734 |  |  |  | Add 3-winding transformer 527796 EDDY_TR 1 13 527799 EDDY_NORTH 6 230 527802 EDDY_CNTY 7 345 M2
05ALL | ERIS | Thermal | 527802 EDDY_CNTY 7 345 3WXFMR 526:ABB AEM30711 230 1 | 29SP | T0 | Single 524885 SN_JUAN_SS6 230 787680 G24-357-TAP 230 1 | B | 558 | -20.3029 | 111.8404 |  |  |  | Add 3-winding transformer 527796 EDDY_TR 1 13 527799 EDDY_NORTH 6 230 527802 EDDY_CNTY 7 345 M2
05ALL | ERIS | Thermal | 527802 EDDY_CNTY 7 345 3WXFMR 526:ABB AEM30711 230 1 | 29WP | T0 | Single 524885 SN_JUAN_SS6 230 787680 G24-357-TAP 230 1 | B | 558 | -28.4531 | 112.0271 |  |  |  | Add 3-winding transformer 527796 EDDY_TR 1 13 527799 EDDY_NORTH 6 230 527802 EDDY_CNTY 7 345 M2
05ALL | ERIS | Thermal | 527891 HOBBS_INT 3 115 784800 G24-261-TAP 115 1 | 26SP | T0 | Single 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1 | B | 199 | 33.2534 | 106.7284 |  |  |  | Rebuild line 527891 HOBBS_INT 3 115 784800 G24-261-TAP 115 1
05ALL | ERIS | Thermal | 527891 HOBBS_INT 3 115 784800 G24-261-TAP 115 1 | 29SP | T0 | Single 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1 | B | 199 | 33.691 | 106.8076 |  |  |  | Rebuild line 527891 HOBBS_INT 3 115 784800 G24-261-TAP 115 1
05ALL | ERIS | Thermal | 527891 HOBBS_INT 3 115 784800 G24-261-TAP 115 1 | 29WP | T0 | Single 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1 | B | 199 | 33.7121 | 107.075 |  |  |  | Rebuild line 527891 HOBBS_INT 3 115 784800 G24-261-TAP 115 1
05ALL | ERIS | Thermal | 527956 SBCRDWRDLEA 115 528505 LEA_ROAD 3 115 1 | 26SP | T0 | Single 528554 COOPER_RNCH3 115 528581 BYRD_TP3 115 1 | B | 154 | -3.9261 | 118.3637 |  |  |  | Rebuild line 527956 SBCRDWRDLEA 115 528505 LEA_ROAD 3 115 1
05ALL | ERIS | Thermal | 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 1 | 26SP | T0 | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | B | 429 | -43.9054 | 187.9533 |  |  |  | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2
05ALL | ERIS | Thermal | 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 1 | 29SP | T0 | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | B | 429 | -43.9768 | 199.902 |  |  |  | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2
05ALL | ERIS | Thermal | 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 1 | 29WP | T0 | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | B | 441 | -46.3787 | 189.4628 |  |  |  | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2
05ALL | ERIS | Thermal | 528015 PHANTOM 7 345 528013 PHANTOM 3 115 4 | 26SP | T0 | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | B | 435 | -215.4863 | 199.9595 |  |  |  | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4
05ALL | ERIS | Thermal | 528015 PHANTOM 7 345 528013 PHANTOM 3 115 4 | 29SP | T0 | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | B | 435 | -271.3781 | 100.3046 |  |  |  | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4
05ALL | ERIS | Thermal | 528016 SAND_DUNES 3 115 528018 RED_BLUFF 3 115 1 | 26SP | T0 | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | B | 239 | 19.0222 | 139.0276 |  |  |  | Rebuild line 528016 SAND_DUNES 3 115 528018 RED_BLUFF 3 115 1
05ALL | ERIS | Thermal | 528016 SAND_DUNES 3 115 528018 RED_BLUFF 3 115 1 | 29SP | T0 | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | B | 239 | 28.1157 | 157.5089 |  |  |  | Rebuild line 528016 SAND_DUNES 3 115 528018 RED_BLUFF 3 115 1
05ALL | ERIS | Thermal | 528016 SAND_DUNES 3 115 528018 RED_BLUFF 3 115 1 | 29WP | T0 | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | B | 239 | 18.8993 | 150.7055 |  |  |  | Rebuild line 528016 SAND_DUNES 3 115 528018 RED_BLUFF 3 115 1
05ALL | ERIS | Thermal | 528018 RED_BLUFF 3 115 528235 WOLFCAMP_TP3 115 1 | 26SP | T0 | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | B | 429 | 17.4375 | 116.6186 |  |  |  | Rebuild line 528018 RED_BLUFF 3 115 528235 WOLFCAMP_TP3 115 1
05ALL | ERIS | Thermal | 528018 RED_BLUFF 3 115 528235 WOLFCAMP_TP3 115 1 | 29SP | T0 | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | B | 429 | 21.8871 | 128.6698 |  |  |  | Rebuild line 528018 RED_BLUFF 3 115 528235 WOLFCAMP_TP3 115 1
05ALL | ERIS | Thermal | 528018 RED_BLUFF 3 115 528235 WOLFCAMP_TP3 115 1 | 29WP | T0 | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | B | 440 | 15.6577 | 123.4508 |  |  |  | Rebuild line 528018 RED_BLUFF 3 115 528235 WOLFCAMP_TP3 115 1
05ALL | ERIS | Thermal | 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 1 | 26SP | T0 | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | B | 429 | -43.9201 | 187.9586 |  |  |  | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2
05ALL | ERIS | Thermal | 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 1 | 29SP | T0 | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | B | 429 | -43.9914 | 199.9087 |  |  |  | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2
05ALL | ERIS | Thermal | 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 1 | 29WP | T0 | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | B | 441 | -46.391 | 189.4692 |  |  |  | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2
05ALL | ERIS | Thermal | 528095 7-RIVERS 6 230 528179 PECOS 6 230 1 | 29WP | T0 | Single 527802 EDDY_CNTY7 345 527799 EDDY_NORTH6 230 527796 'EDDY_TR 1' 13 1 | B | 319 | -19.0869 | 100.5563 |  |  |  | Rebuild line 528095 7-RIVERS 6 230 528179 PECOS 6 230 1
05ALL | ERIS | Thermal | 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1 | 26SP | T0 | Single 528185 N_LOVING7 345 528187 SENDERO_345 345 1 | B | 308 | -65.5445 | 184.7858 |  |  |  | Rebuild line 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1
05ALL | ERIS | Thermal | 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1 | 29SP | T0 | Single 528185 N_LOVING7 345 528187 SENDERO_345 345 1 | B | 308 | 58.9868 | 181.3837 |  |  |  | Rebuild line 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1
05ALL | ERIS | Thermal | 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1 | 29WP | T0 | Single 528185 N_LOVING7 345 528187 SENDERO_345 345 1 | B | 316 | -53.2949 | 174.6551 |  |  |  | Rebuild line 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1
05ALL | ERIS | Thermal | 528184 SENDERO +3 115 528193 BLACKRIVER 3 115 1 | 26SP | T0 | Single 528185 N_LOVING7 345 528187 SENDERO_345 345 1 | B | 308 | -71.1624 | 174.6265 |  |  |  | Rebuild line 528184 SENDERO +3 115 528193 BLACKRIVER 3 115 1
05ALL | ERIS | Thermal | 528184 SENDERO +3 115 528193 BLACKRIVER 3 115 1 | 29SP | T0 | Single 528185 N_LOVING7 345 528187 SENDERO_345 345 1 | B | 308 | -66.7961 | 163.8647 |  |  |  | Rebuild line 528184 SENDERO +3 115 528193 BLACKRIVER 3 115 1
05ALL | ERIS | Thermal | 528184 SENDERO +3 115 528193 BLACKRIVER 3 115 1 | 29WP | T0 | Single 528185 N_LOVING7 345 528187 SENDERO_345 345 1 | B | 316 | -65.22 | 156.2696 |  |  |  | Rebuild line 528184 SENDERO +3 115 528193 BLACKRIVER 3 115 1
05ALL | ERIS | Thermal | 528187 SENDERO_345 345 528184 SENDERO +3 115 1 | 26SP | T0 | Single 528185 N_LOVING7 345 528187 SENDERO_345 345 1 | B | 435 | -67.6568 | 105.4583 |  |  |  | Add 2-winding transformer 528184 SENDERO +3 115 528187 SENDERO_345 345 M2
05ALL | ERIS | Thermal | 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1 | 26SP | T0 | Single 527891 HOBBS_INT3 115 784800 G24-261-TAP 115 1 | B | 199.4 | 38.0785 | 110.5901 |  |  |  | Rebuild line 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1
05ALL | ERIS | Thermal | 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1 | 29SP | T0 | Single 527891 HOBBS_INT3 115 784800 G24-261-TAP 115 1 | B | 199.4 | 35.1413 | 107.8299 |  |  |  | Rebuild line 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1
05ALL | ERIS | Thermal | 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1 | 29WP | T0 | Single 527891 HOBBS_INT3 115 784800 G24-261-TAP 115 1 | B | 199.4 | 36.6963 | 109.5285 |  |  |  | Rebuild line 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1
05ALL | ERIS | Thermal | 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1 | 26SP | T0 | Single 528554 COOPER_RNCH3 115 528581 BYRD_TP3 115 1 | B | 154 | -2.8167 | 120.2313 |  |  |  | Rebuild line 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1
05ALL | ERIS | Thermal | 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1 | 29SP | T0 | System Intact | A | 120 | 51.2006 | 138.4973 |  |  |  | Rebuild line 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1
05ALL | ERIS | Thermal | 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1 | 29WP | T0 | System Intact | A | 143 | 32.6054 | 111.3739 |  |  |  | Rebuild line 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1
05ALL | ERIS | Thermal | 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1 | 26SP | T0 | Single 528547 S_JAL3 115 785400 G24-281-TAP 115 1 | B | 175 | -5.6044 | 134.8379 |  |  |  | Rebuild line 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1
05ALL | ERIS | Thermal | 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1 | 29SP | T0 | Single 528547 S_JAL3 115 785400 G24-281-TAP 115 1 | B | 175 | -5.283 | 135.5248 |  |  |  | Rebuild line 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1
05ALL | ERIS | Thermal | 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1 | 29WP | T0 | Single 528547 S_JAL3 115 785400 G24-281-TAP 115 1 | B | 194 | -4.7399 | 122.2712 |  |  |  | Rebuild line 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1
05ALL | ERIS | Thermal | 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | 26SP | T0 | Single 528547 S_JAL3 115 785400 G24-281-TAP 115 1 | B | 154 | -5.7282 | 157.598 |  |  |  | Rebuild line 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1
05ALL | ERIS | Thermal | 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | 29SP | T0 | Single 528547 S_JAL3 115 785400 G24-281-TAP 115 1 | B | 154 | -5.5133 | 157.8012 |  |  |  | Rebuild line 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1
05ALL | ERIS | Thermal | 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | 29WP | T0 | Single 528547 S_JAL3 115 785400 G24-281-TAP 115 1 | B | 154 | -5.5094 | 157.7413 |  |  |  | Rebuild line 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1
05ALL | ERIS | Thermal | 528547 S_JAL 3 115 785400 G24-281-TAP 115 1 | 26SP | T0 | Single 528526 TEAGUE3 115 785400 G24-281-TAP 115 1 | B | 154 | -6.2604 | 157.2756 |  |  |  | Rebuild line 528547 S_JAL 3 115 785400 G24-281-TAP 115 1
05ALL | ERIS | Thermal | 528547 S_JAL 3 115 785400 G24-281-TAP 115 1 | 29SP | T0 | Single 528526 TEAGUE3 115 785400 G24-281-TAP 115 1 | B | 154 | -5.906 | 157.954 |  |  |  | Rebuild line 528547 S_JAL 3 115 785400 G24-281-TAP 115 1
05ALL | ERIS | Thermal | 528547 S_JAL 3 115 785400 G24-281-TAP 115 1 | 29WP | T0 | Single 528526 TEAGUE3 115 785400 G24-281-TAP 115 1 | B | 154 | -5.9221 | 157.6979 |  |  |  | Rebuild line 528547 S_JAL 3 115 785400 G24-281-TAP 115 1
05ALL | ERIS | Thermal | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1 | 29SP | T0 | Single 528554 COOPER_RNCH3 115 528581 BYRD_TP3 115 1 | B | 158 | -2.3768 | 118.906 |  |  |  | Rebuild line 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
05ALL | ERIS | Thermal | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1 | 29WP | T0 | Single 528554 COOPER_RNCH3 115 528581 BYRD_TP3 115 1 | B | 175 | -2.1487 | 107.2164 |  |  |  | Rebuild line 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
05ALL | ERIS | Thermal | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1 | 26SP | T0 | Single 528554 COOPER_RNCH3 115 528581 BYRD_TP3 115 1 | B | 158 | -2.6087 | 117.2098 |  |  |  | Rebuild line 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
05ALL | ERIS | Thermal | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1 | 26SP | T0 | Single 528552 OIL_CENTER3 115 528554 COOPER_RNCH3 115 1 | B | 157 | -2.6049 | 118.0644 |  |  |  | Rebuild line 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
05ALL | ERIS | Thermal | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1 | 29SP | T0 | Single 528552 OIL_CENTER3 115 528554 COOPER_RNCH3 115 1 | B | 157 | -2.5101 | 118.5068 |  |  |  | Rebuild line 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
05ALL | ERIS | Thermal | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1 | 29WP | T0 | Single 528552 OIL_CENTER3 115 528554 COOPER_RNCH3 115 1 | B | 174 | -2.2621 | 106.9673 |  |  |  | Rebuild line 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
05ALL | ERIS | Thermal | 532791 BENTON 7 345 532796 WICHITA7 345 1 | 26SP | T0 | P23:345:WERE:EMPR-345-300:EHV: | B | 911 | 31.4242 | 100.2783 |  |  |  | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1
05ALL | ERIS | Thermal | 532791 BENTON 7 345 532796 WICHITA7 345 1 | 29WP | T0 | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | B | 911 | 27.9143 | 100.3119 |  |  |  | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1
05ALL | ERIS | Thermal | 532796 WICHITA7 345 532798 VIOLA 7 345 1 | 26SP | T0 | P42:345:OKGE:SB_DGSE7313:::EHV: | B | 830 | 31.9318 | 119.5964 |  |  |  | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1
05ALL | ERIS | Thermal | 532796 WICHITA7 345 532798 VIOLA 7 345 1 | 29SP | T0 | P42:345:OKGE:SB_DGSE7313:::EHV: | B | 830 | 36.4055 | 127.9043 |  |  |  | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1
05ALL | ERIS | Thermal | 532796 WICHITA7 345 532798 VIOLA 7 345 1 | 29WP | T0 | P42:345:OKGE:SB_DGSE7313:::EHV: | B | 830 | 26.1261 | 118.0063 |  |  |  | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1
05ALL | ERIS | Thermal | 532828 VIOLA9 765 532798 VIOLA 7 345 1 | 26SP | T0 | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | B | 1650 | 35.5683 | 151.8279 |  |  |  | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2
05ALL | ERIS | Thermal | 532828 VIOLA9 765 532798 VIOLA 7 345 1 | 29SP | T0 | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | B | 1650 | 37.398 | 152.7466 |  |  |  | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2
05ALL | ERIS | Thermal | 532828 VIOLA9 765 532798 VIOLA 7 345 1 | 29WP | T0 | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | B | 1650 | 16.9783 | 144.1864 |  |  |  | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2
05ALL | ERIS | Thermal | 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | 29SP | T0 | P42:345:SPS:CARPENTER-OR335:::EHV: | B | 1123 | 29.7695 | 117.6525 |  |  |  | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1
05ALL | ERIS | Thermal | 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | 26SP | T0 | P42:345:SPS:CARPENTER-OR335:::EHV: | B | 1123 | 16.9212 | 104.4825 |  |  |  | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1
05ALL | ERIS | Thermal | 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | 29WP | T0 | P42:345:SPS:CARPENTER-OR335:::EHV: | B | 1123 | 8.4572 | 104.941 |  |  |  | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1
05ALL | ERIS | Thermal | 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | 29SP | T0 | P42:345:SPS:CARPENTER-OR335:::EHV: | B | 1140 | 29.8111 | 116.6658 |  |  |  | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1
05ALL | ERIS | Thermal | 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | 26SP | T0 | P42:345:SPS:CARPENTER-OR335:::EHV: | B | 1140 | 16.7883 | 103.6709 |  |  |  | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1
05ALL | ERIS | Thermal | 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | 29WP | T0 | P42:345:SPS:CARPENTER-OR335:::EHV: | B | 1140 | 10.2024 | 104.0997 |  |  |  | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1
00ALL | ERIS | Thermal | 507727 FLOURNY4 138 507732 GENMOTR4 138 1 | 29SP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 265 | 72.4082 | 107.7084 |  |  |  | Rebuild line 507727 FLOURNY4 138 507732 GENMOTR4 138 1
00ALL | ERIS | Thermal | 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | 29WP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 281 | 53.7148 | 101.9475 |  |  |  | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1
00ALL | ERIS | Thermal | 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | 29SP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 281 | 87.9335 | 121.2157 |  |  |  | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1
00ALL | ERIS | Thermal | 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | 26SP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 281 | 79.7263 | 107.7093 |  |  |  | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1
00ALL | ERIS | Thermal | 507732 GENMOTR4 138 507759 SW SHV 4 138 1 | 29SP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 265 | 72.0442 | 107.307 |  |  |  | Rebuild line 507732 GENMOTR4 138 507759 SW SHV 4 138 1
00ALL | ERIS | Thermal | 507774 NORAM 4 138 508808 LONGWD 4 138 1 | 29SP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 265 | 86.1907 | 103.4161 |  |  |  | Rebuild line 507774 NORAM 4 138 508808 LONGWD 4 138 1
00ALL | ERIS | Thermal | 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | 29WP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 281 | 55.5279 | 103.7623 |  |  |  | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1
00ALL | ERIS | Thermal | 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | 29SP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 281 | 89.2217 | 122.5064 |  |  |  | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1
00ALL | ERIS | Thermal | 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | 26SP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 281 | 81.0034 | 108.9872 |  |  |  | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1
00ALL | ERIS | Thermal | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 | 29SP | T1 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 265 | 55.9524 | 112.6415 |  |  |  | Rebuild line 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1
00ALL | ERIS | Thermal | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | 29SP | T1 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 265 | 52.2348 | 108.7075 |  |  |  | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1
00ALL | ERIS | Thermal | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 | 29SP | T1 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 265 | 55.2541 | 111.9188 |  |  |  | Rebuild line 515121 MILLCKT4 138 515122 SXMLCKT4 138 1
00ALL | ERIS | Thermal | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | 29SP | T1 | P42:345:NPPD:BKR-MOR-3308:::: | B | 260 | 58.449 | 105.0104 |  |  |  | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
00ALL | ERIS | Thermal | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | 26SP | T1 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 637 | 6.9802 | 101.5312 |  |  |  | Rebuild line 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1
00NR | NRIS | Thermal | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | 26SP | T1 | Single 514894 CZECHAL4 138 514898 CIMARON4 138 1 | B | 308 | 73.924 | 101.6749 |  |  |  | Rebuild line 514853 DVISION4 138 514863 HAYMAKR4 138 1
00NR | NRIS | Thermal | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | 29SP | T1 | Single 514894 CZECHAL4 138 514898 CIMARON4 138 1 | B | 308 | 72.7089 | 100.6627 |  |  |  | Rebuild line 514853 DVISION4 138 514863 HAYMAKR4 138 1
00NR | NRIS | Thermal | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 26SP | T1 | Single 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | B | 472 | 75.0342 | 102.5277 |  |  |  | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1
00NR | NRIS | Thermal | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 29SP | T1 | Single 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | B | 472 | 73.4268 | 101.6739 |  |  |  | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1
00NR | NRIS | Thermal | 652216 WATFORD4 230 659302 CHARL_CK-BE4 230 1 | 29WP | T1 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | B | 519 | 74.0233 | 106.3396 |  |  |  | Rebuild line 652216 WATFORD4 230 659302 CHARL_CK-BE4 230 1
00NR | NRIS | Thermal | 652296 WARD 4 230 652426 BISMARK4 230 1 | 29WP | T1 | Single 608607 NELSNLK4 230 615901 GRE-STANTON4 230 1 | B | 386 | 97.484 | 125.0409 |  |  |  | Rebuild line 652296 WARD 4 230 652426 BISMARK4 230 1
00NR | NRIS | Thermal | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 | 26SP | T1 | P12:345:OTP:CENTER3:COYOTE3:1 RAS OFF:EHV: | B | 176 | 85.4939 | 101.5224 |  |  |  | Rebuild line 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1
00NR | NRIS | Thermal | 652497 MAURINE4 230 785430 G24-282-TAP 230 1 | 29WP | T1 | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | B | 519 | 55.0234 | 104.2032 |  |  |  | Rebuild line 652497 MAURINE4 230 785430 G24-282-TAP 230 1
01ALL | ERIS | Thermal | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 26SP | T1 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | B | 878 | 80.6242 | 100.2249 |  |  |  | Rebuild line 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
01ALL | ERIS | Thermal | 652568 GROTONSOUTH7 115 659187 GROTON__-BE7 115 1 | 26SP | T1 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | B | 598 | 42.2139 | 104.1254 |  |  |  | Add line and rebuild line 652568 GROTONSOUTH7 115 659187 GROTON__-BE7 115 M2
02ALL | ERIS | Thermal | 533210 ENEMEHA3 115 533212 KINGFISH3 115 1 | 26SP | T1 | Single 640140 COOPER5 161 778110 G24-038-TAP 161 1 | B | 90 | 48.266 | 100.7991 |  |  |  | Rebuild line 533210 ENEMEHA3 115 533212 KINGFISH3 115 1
02ALL | ERIS | Thermal | 646263 S1263 5 161 3WXFMR 645:S1263 T1 69 1 | 26SP | T1 | Single 640234 HUMBOLT5 161 778140 G24-039-TAP 161 1 | B | 120 | 60.2727 | 100.091 |  |  |  | Rebuild 3-winding transformer 646263 S1263 5 161 647111 W BROCK8 69 648263 S1263T19 13 1
02ALL | ERIS | Thermal | 647111 W BROCK8 69 3WXFMR 645:S1263 T1 69 1 | 26SP | T1 | Single 640234 HUMBOLT5 161 778140 G24-039-TAP 161 1 | B | 120 | 60.2727 | 100.091 |  |  |  | Rebuild 3-winding transformer 646263 S1263 5 161 647111 W BROCK8 69 648263 S1263T19 13 1
03ALL | ERIS | Thermal | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | 29WP | T1 | Single 547476 ASB3495 161 547477 CJ3665 161 1 | B | 446 | 46.8432 | 103.404 |  |  |  | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1
03ALL | ERIS | Thermal | 523106 TXPHSF 3 115 539672 E-LIBER3 115 1 | 29WP | T1 | P42:345:SPS:CARPENTER-OR335:::EHV: | B | 217 | 17.0573 | 103.5232 |  |  |  | Rebuild line 523106 TXPHSF 3 115 539672 E-LIBER3 115 1
03ALL | ERIS | Thermal | 530618 HUNTSVL3 115 530624 ST JOHN3 115 1 | 29WP | T1 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 260 | 1.4702 | 105.5851 |  |  |  | Rebuild line 530618 HUNTSVL3 115 530624 ST JOHN3 115 1
03ALL | ERIS | Thermal | 530618 HUNTSVL3 115 530724 CENTENNIAL3 115 1 | 29WP | T1 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 260 | 1.1724 | 104.5481 |  |  |  | Rebuild line 530618 HUNTSVL3 115 530724 CENTENNIAL3 115 1
03ALL | ERIS | Thermal | 530624 ST JOHN3 115 539696 ST-JOHN3 115 Z1 | 26SP | T1 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 297 | 16.1281 | 107.9018 |  |  |  | Rebuild line 530624 ST JOHN3 115 539696 ST-JOHN3 115 Z1
03ALL | ERIS | Thermal | 530624 ST JOHN3 115 539696 ST-JOHN3 115 Z1 | 29SP | T1 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 297 | 16.1988 | 107.6449 |  |  |  | Rebuild line 530624 ST JOHN3 115 539696 ST-JOHN3 115 Z1
03ALL | ERIS | Thermal | 530624 ST JOHN3 115 539696 ST-JOHN3 115 Z1 | 29WP | T1 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 297 | 14.655 | 108.228 |  |  |  | Rebuild line 530624 ST JOHN3 115 539696 ST-JOHN3 115 Z1
03ALL | ERIS | Thermal | 530724 CENTENNIAL3 115 533412 ARKVALJ3 115 1 | 29WP | T1 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 260 | -2.579 | 101.9508 |  |  |  | Rebuild line 530724 CENTENNIAL3 115 533412 ARKVALJ3 115 1
03ALL | ERIS | Thermal | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | 29WP | T1 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | B | 297 | -11.6102 | 103.6787 |  |  |  | Rebuild line 531391 PIONEER3 115 531483 GRANTTP3 115 1
03ALL | ERIS | Thermal | 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | 29WP | T1 | P23:345:SUNC:HLC_BRK188:::EHV: | B | 598 | 22.9923 | 116.0895 |  |  |  | Add line and rebuild line 531405 WALKMYR3 115 531510 HARBNGR3 115 M2
03ALL | ERIS | Thermal | 531419 DOBSON 3 115 531493 GANO 3 115 1 | 26SP | T1 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | B | 228.5 | -1.2596 | 101.0289 |  |  |  | Rebuild line 531419 DOBSON 3 115 531493 GANO 3 115 1
03ALL | ERIS | Thermal | 531432 PILE 3 115 531433 SCOTCTY3 115 1 | 26SP | T1 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | B | 228.5 | 1.1025 | 102.6038 |  |  |  | Rebuild line 531432 PILE 3 115 531433 SCOTCTY3 115 1
03ALL | ERIS | Thermal | 531432 PILE 3 115 531493 GANO 3 115 1 | 26SP | T1 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | B | 228.5 | -0.62659 | 101.5034 |  |  |  | Rebuild line 531432 PILE 3 115 531493 GANO 3 115 1
03ALL | ERIS | Thermal | 531433 SCOTCTY3 115 531464 SETAB 3 115 1 | 26SP | T1 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | B | 329 | 19.3944 | 105.9644 |  |  |  | Rebuild line 531433 SCOTCTY3 115 531464 SETAB 3 115 1
03ALL | ERIS | Thermal | 531433 SCOTCTY3 115 531464 SETAB 3 115 1 | 29SP | T1 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | B | 329 | 8.2859 | 100.0132 |  |  |  | Rebuild line 531433 SCOTCTY3 115 531464 SETAB 3 115 1
03ALL | ERIS | Thermal | 531433 SCOTCTY3 115 531464 SETAB 3 115 1 | 29WP | T1 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | B | 329 | 19.0588 | 105.3674 |  |  |  | Rebuild line 531433 SCOTCTY3 115 531464 SETAB 3 115 1
03ALL | ERIS | Thermal | 533412 ARKVALJ3 115 533413 CIRCLE 3 115 1 | 26SP | T1 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 239 | -10.2155 | 100.4289 |  |  |  | Rebuild line 533412 ARKVALJ3 115 533413 CIRCLE 3 115 1
03ALL | ERIS | Thermal | 533412 ARKVALJ3 115 533413 CIRCLE 3 115 1 | 29WP | T1 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 239 | -3.7033 | 110.0508 |  |  |  | Rebuild line 533412 ARKVALJ3 115 533413 CIRCLE 3 115 1
03ALL | ERIS | Thermal | 539009 CONWAY 4 138 539881 SPRVLSTR 138 1 | 29WP | T1 | P12:138:ITCGP:FLATRIDGE-THISTLE:::HV: | B | 265 | 12.117 | 100.2607 |  |  |  | Rebuild line 539009 CONWAY 4 138 539881 SPRVLSTR 138 1
03ALL | ERIS | Thermal | 539010 SADLHRN3 115 539696 ST-JOHN3 115 1 | 26SP | T1 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 394 | -7.1141 | 103.616 |  |  |  | Rebuild line 539010 SADLHRN3 115 539696 ST-JOHN3 115 1
03ALL | ERIS | Thermal | 539010 SADLHRN3 115 539696 ST-JOHN3 115 1 | 29SP | T1 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 394 | -7.0868 | 100.4123 |  |  |  | Rebuild line 539010 SADLHRN3 115 539696 ST-JOHN3 115 1
03ALL | ERIS | Thermal | 539010 SADLHRN3 115 539696 ST-JOHN3 115 1 | 29WP | T1 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 394 | -5.6988 | 111.6991 |  |  |  | Rebuild line 539010 SADLHRN3 115 539696 ST-JOHN3 115 1
03ALL | ERIS | Thermal | 539652 CMRIVTP3 115 539672 E-LIBER3 115 1 | 29WP | T1 | Single 539652 CMRIVTP3 115 539654 CIM-PLT3 115 1 | B | 148.2 | 24.3203 | 104.054 |  |  |  | Rebuild line 539652 CMRIVTP3 115 539672 E-LIBER3 115 1
03ALL | ERIS | Thermal | 539652 CMRIVTP3 115 539672 E-LIBER3 115 1 | 26SP | T1 | Single 539652 CMRIVTP3 115 539654 CIM-PLT3 115 1 | B | 138 | 23.1873 | 101.0249 |  |  |  | Rebuild line 539652 CMRIVTP3 115 539672 E-LIBER3 115 1
03ALL | ERIS | Thermal | 539652 CMRIVTP3 115 539672 E-LIBER3 115 1 | 29SP | T1 | Single 539652 CMRIVTP3 115 539654 CIM-PLT3 115 1 | B | 138 | 22.2476 | 101.334 |  |  |  | Rebuild line 539652 CMRIVTP3 115 539672 E-LIBER3 115 1
03ALL | ERIS | Thermal | 539666 GBENDTP3 115 539678 GRTBEND3 115 1 | 29WP | T1 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 148.2 | -30.5685 | 107.1608 |  |  |  | Rebuild line 539666 GBENDTP3 115 539678 GRTBEND3 115 1
03ALL | ERIS | Thermal | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 29WP | T1 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 260 | -21.7787 | 102.0667 |  |  |  | Rebuild line 539666 GBENDTP3 115 539692 SEWARD 3 115 1
03ALL | ERIS | Thermal | 539668 HARPER 4 138 539881 SPRVLSTR 138 1 | 29WP | T1 | P12:138:ITCGP:FLATRIDGE-THISTLE:::HV: | B | 265 | 14.1611 | 102.212 |  |  |  | Rebuild line 539668 HARPER 4 138 539881 SPRVLSTR 138 1
03ALL | ERIS | Thermal | 539753 PRATTENERGY3 115 539756 SKLYVL_GOAB3 115 1 | 26SP | T1 | Single 539754 SEMCRDE3 115 539756 SKLYVL_GOAB3 115 1 | B | 217 | -0.49516 | 100.7798 |  |  |  | Rebuild line 539753 PRATTENERGY3 115 539756 SKLYVL_GOAB3 115 1
03ALL | ERIS | Thermal | 539753 PRATTENERGY3 115 539756 SKLYVL_GOAB3 115 1 | 29SP | T1 | Single 539754 SEMCRDE3 115 539756 SKLYVL_GOAB3 115 1 | B | 217 | -0.49492 | 100.6068 |  |  |  | Rebuild line 539753 PRATTENERGY3 115 539756 SKLYVL_GOAB3 115 1
03ALL | ERIS | Thermal | 539753 PRATTENERGY3 115 539756 SKLYVL_GOAB3 115 1 | 29WP | T1 | Single 539754 SEMCRDE3 115 539756 SKLYVL_GOAB3 115 1 | B | 217 | -0.4943 | 101.0392 |  |  |  | Rebuild line 539753 PRATTENERGY3 115 539756 SKLYVL_GOAB3 115 1
03ALL | ERIS | Thermal | 543098 CTY HIG2 69 543099 HIGNSVL2 69 1 | 29WP | T1 | Single 543064 NORTON5 161 788220 G24-375-TAP 161 1 | B | 106 | 8.8545 | 102.6552 |  |  |  | Rebuild line 543098 CTY HIG2 69 543099 HIGNSVL2 69 1
03ALL | ERIS | Thermal | 543099 HIGNSVL2 69 543102 WHGNSVL2 69 1 | 29WP | T1 | Single 543064 NORTON5 161 788220 G24-375-TAP 161 1 | B | 106 | 8.4942 | 102.3041 |  |  |  | Rebuild line 543099 HIGNSVL2 69 543102 WHGNSVL2 69 1
03ALL | ERIS | Thermal | 543100 AMOCOPL2 69 543102 WHGNSVL2 69 1 | 29WP | T1 | Single 543064 NORTON5 161 788220 G24-375-TAP 161 1 | B | 106 | 7.9869 | 101.8184 |  |  |  | Rebuild line 543100 AMOCOPL2 69 543102 WHGNSVL2 69 1
03ALL | ERIS | Thermal | 547467 ORO110 5 161 547490 FIR417 5 161 1 | 29WP | T1 | Single 547476 ASB3495 161 547491 PUR4215 161 1 | B | 446 | 44.5606 | 107.3133 |  |  |  | Rebuild line 547467 ORO110 5 161 547490 FIR417 5 161 1
03ALL | ERIS | Thermal | 547477 CJ 366 5 161 547490 FIR417 5 161 1 | 29WP | T1 | Single 547476 ASB3495 161 547491 PUR4215 161 1 | B | 446 | 48.4955 | 111.3037 |  |  |  | Rebuild line 547477 CJ 366 5 161 547490 FIR417 5 161 1
03ALL | ERIS | Thermal | 547485 CAR395 5 161 547491 PUR421 5 161 1 | 29WP | T1 | Single 547476 ASB3495 161 547477 CJ3665 161 1 | B | 446 | 50.1418 | 106.7516 |  |  |  | Rebuild line 547485 CAR395 5 161 547491 PUR421 5 161 1
04ALL | ERIS | Thermal | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | 29WP | T1 | Single 507449 NWHOPE3 115 507452 HOPESWI3 115 1 | B | 297 | 44.6255 | 101.8094 |  |  |  | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
04ALL | ERIS | Thermal | 504122 MCNAB 3 115 507453 HOPE 3 115 1 | 29WP | T1 | P12:345:AEPW:TURK7:NWTXARK7::: | B | 329 | 41.4892 | 101.4457 |  |  |  | Rebuild line 504122 MCNAB 3 115 507453 HOPE 3 115 1
04ALL | ERIS | Thermal | 504122 MCNAB 3 115 507456 TURK 3 115 1 | 29WP | T1 | P12:345:AEPW:TURK7:NWTXARK7::: | B | 329 | 44.1512 | 104.1989 |  |  |  | Rebuild line 504122 MCNAB 3 115 507456 TURK 3 115 1
04ALL | ERIS | Thermal | 504122 MCNAB 3 115 507456 TURK 3 115 1 | 26SP | T1 | P12:345:AEPW:TURK7:NWTXARK7::: | B | 329 | 42.4387 | 101.0715 |  |  |  | Rebuild line 504122 MCNAB 3 115 507456 TURK 3 115 1
04ALL | ERIS | Thermal | 505600 TUPELO 4 138 505602 S BROWN4 138 1 | 26SP | T1 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 265 | 37.0741 | 100.0608 |  |  |  | Rebuild line 505600 TUPELO 4 138 505602 S BROWN4 138 1
04ALL | ERIS | Thermal | 505600 TUPELO 4 138 505602 S BROWN4 138 1 | 29WP | T1 | Single 520918 FROGVIL4 138 773820 G23-092-TAP 138 1 | B | 265 | 38.4855 | 100.7106 |  |  |  | Rebuild line 505600 TUPELO 4 138 505602 S BROWN4 138 1
04ALL | ERIS | Thermal | 507448 NHOPE 3 115 507449 NWHOPE 3 115 1 | 29WP | T1 | Single 338875 3PATMOS.W# 115 503912 FULTON3 115 1 | B | 297 | 42.6742 | 106.3857 |  |  |  | Rebuild line 507448 NHOPE 3 115 507449 NWHOPE 3 115 1
04ALL | ERIS | Thermal | 507448 NHOPE 3 115 507449 NWHOPE 3 115 1 | 26SP | T1 | Single 338875 3PATMOS.W# 115 503912 FULTON3 115 1 | B | 297 | 38.1948 | 101.2936 |  |  |  | Rebuild line 507448 NHOPE 3 115 507449 NWHOPE 3 115 1
04ALL | ERIS | Thermal | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | 29WP | T1 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | B | 281 | 52.2387 | 110.8683 |  |  |  | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
04ALL | ERIS | Thermal | 510422 COFFEYT4 138 787350 G24-346-TAP 138 1 | 29WP | T1 | Single 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 395 | 58.8296 | 127.7202 |  |  |  | Rebuild line 510422 COFFEYT4 138 787350 G24-346-TAP 138 1
04ALL | ERIS | Thermal | 510422 COFFEYT4 138 787350 G24-346-TAP 138 1 | 29SP | T1 | Single 512734 FARML4 138 778710 G24-058-TAP 138 1 | B | 395 | 60.3171 | 122.6455 |  |  |  | Rebuild line 510422 COFFEYT4 138 787350 G24-346-TAP 138 1
04ALL | ERIS | Thermal | 510422 COFFEYT4 138 787350 G24-346-TAP 138 1 | 26SP | T1 | Single 512734 FARML4 138 778710 G24-058-TAP 138 1 | B | 395 | 60.4632 | 123.5109 |  |  |  | Rebuild line 510422 COFFEYT4 138 787350 G24-346-TAP 138 1
04ALL | ERIS | Thermal | 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | 29SP | T1 | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | B | 1793 | 58.1584 | 100.6497 |  |  |  | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1
04ALL | ERIS | Thermal | 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | 29WP | T1 | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | B | 1793 | 52.5323 | 100.0766 |  |  |  | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1
04ALL | ERIS | Thermal | 511423 FLE TAP4 138 511467 L.E.S.-4 138 1 | 29SP | T1 | Single 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | B | 211 | 38.3445 | 102.1941 |  |  |  | Rebuild line 511423 FLE TAP4 138 511467 L.E.S.-4 138 1
04ALL | ERIS | Thermal | 511423 FLE TAP4 138 511467 L.E.S.-4 138 1 | 29WP | T1 | Single 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | B | 211 | 36.5673 | 100.265 |  |  |  | Rebuild line 511423 FLE TAP4 138 511467 L.E.S.-4 138 1
04ALL | ERIS | Thermal | 511423 FLE TAP4 138 511586 TONKAWA4 138 1 | 29SP | T1 | Single 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | B | 212 | 36.9907 | 100.5806 |  |  |  | Rebuild line 511423 FLE TAP4 138 511586 TONKAWA4 138 1
04ALL | ERIS | Thermal | 511446 CL-AFTP4 138 511458 ELKCTY-4 138 1 | 29SP | T1 | P42:345:OKGE:SB_GRNT7381:::EHV: | B | 330 | 49.0876 | 102.9549 |  |  |  | Rebuild line 511446 CL-AFTP4 138 511458 ELKCTY-4 138 1
04ALL | ERIS | Thermal | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 29SP | T1 | Single 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | B | 211 | 80.2769 | 110.0272 |  |  |  | Rebuild line 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1
04ALL | ERIS | Thermal | 511477 S.W.S.-4 138 521089 WASHITA4 138 1 | 29SP | T1 | Single 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | B | 472 | 74.946 | 108.6458 |  |  |  | Rebuild line 511477 S.W.S.-4 138 521089 WASHITA4 138 1
04ALL | ERIS | Thermal | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 29WP | T1 | P42:345:OKGE:SB_GRNT7381:::EHV: | B | 386 | 52.535 | 105.6586 |  |  |  | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
04ALL | ERIS | Thermal | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 29SP | T1 | Single 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | B | 211 | 80.3331 | 110.0755 |  |  |  | Rebuild line 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
04ALL | ERIS | Thermal | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 26SP | T1 | System Intact | A | 309 | 61.5596 | 100.3335 |  |  |  | Rebuild line 512654 PENSA 5 161 512669 KETCHUM5 161 1
04ALL | ERIS | Thermal | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 | 29SP | T1 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 265 | 67.3127 | 111.6063 |  |  |  | Rebuild line 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1
04ALL | ERIS | Thermal | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 | 26SP | T1 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 265 | 49.2815 | 107.0006 |  |  |  | Rebuild line 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1
04ALL | ERIS | Thermal | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | 29SP | T1 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 265 | 63.4362 | 107.5211 |  |  |  | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1
04ALL | ERIS | Thermal | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | 26SP | T1 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 265 | 45.4239 | 102.9063 |  |  |  | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1
04ALL | ERIS | Thermal | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 | 29SP | T1 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 265 | 66.5983 | 110.8616 |  |  |  | Rebuild line 515121 MILLCKT4 138 515122 SXMLCKT4 138 1
04ALL | ERIS | Thermal | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 | 26SP | T1 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 265 | 48.5715 | 106.2578 |  |  |  | Rebuild line 515121 MILLCKT4 138 515122 SXMLCKT4 138 1
04ALL | ERIS | Thermal | 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | 29SP | T1 | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | B | 1793 | 57.6213 | 100.2231 |  |  |  | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1
04ALL | ERIS | Thermal | 515802 GRACMNT4 138 521089 WASHITA4 138 1 | 29SP | T1 | Single 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | B | 234 | 69.4977 | 102.4282 |  |  |  | Rebuild line 515802 GRACMNT4 138 521089 WASHITA4 138 1
04ALL | ERIS | Thermal | 520535 BULFTTP4 138 520882 DOVERSW4 138 1 | 26SP | T1 | Single 514827 CTNWOOD4 138 515377 CRESENT4 138 1 | B | 395 | 50.7827 | 100.5516 |  |  |  | Rebuild line 520535 BULFTTP4 138 520882 DOVERSW4 138 1
04ALL | ERIS | Thermal | 520854 CIVIT 4 138 782580 G24-187-TAP 138 1 | 29SP | T1 | P12:138:SWPA:GREASY CREEK-TUPELO BREAKER TO BREAKER::505595 505596 1, 505596 505598 1, 505598 505600 1:: | B | 211 | 19.8519 | 101.0301 |  |  |  | Rebuild line 520854 CIVIT 4 138 782580 G24-187-TAP 138 1
04ALL | ERIS | Thermal | 520999 MOORLND4 138 786210 G24-308-TAP 138 1 | 29WP | T1 | P12:138:OKGE-WFEC:BKRBKR0770:::HV: | B | 265 | 15.2298 | 114.3237 |  |  |  | Rebuild line 520999 MOORLND4 138 786210 G24-308-TAP 138 1
04ALL | ERIS | Thermal | 520999 MOORLND4 138 786210 G24-308-TAP 138 1 | 29SP | T1 | P12:138:OKGE-WFEC:BKRBKR0770:::HV: | B | 265 | 15.5106 | 107.334 |  |  |  | Rebuild line 520999 MOORLND4 138 786210 G24-308-TAP 138 1
04ALL | ERIS | Thermal | 520999 MOORLND4 138 786210 G24-308-TAP 138 1 | 26SP | T1 | P12:138:OKGE-WFEC:BKRBKR0770:::HV: | B | 265 | 11.7529 | 104.3821 |  |  |  | Rebuild line 520999 MOORLND4 138 786210 G24-308-TAP 138 1
04ALL | ERIS | Thermal | 533002 DEARING4 138 533003 LIBERTY4 138 1 | 29WP | T1 | P23:345:WERE:N345-345-20:EHV: | B | 281 | 34.5075 | 100.3456 |  |  |  | Rebuild line 533002 DEARING4 138 533003 LIBERTY4 138 1
04ALL | ERIS | Thermal | 774620 G23-132-TAP 161 780390 G24-114-TAP 161 1 | 29WP | T1 | P23:500:EES-EAI:KEO:B4941::EHV: | B | 309 | 36.5266 | 103.1518 |  |  |  | Rebuild line 774620 G23-132-TAP 161 780390 G24-114-TAP 161 1
05ALL | ERIS | Thermal | 511458 ELKCTY-4 138 511485 CLINTJC4 138 1 | 26SP | T1 | System Intact | A | 191 | 47.0034 | 101.5318 |  |  |  | Rebuild line 511458 ELKCTY-4 138 511485 CLINTJC4 138 1
05ALL | ERIS | Thermal | 523093 HITCHLAND 3 115 3WXFMR 526:H 1003937402 115 2 | 26SP | T1 | Single 523095 HITCHLAND6 230 523093 HITCHLAND3 115 523092 'HITCHLD_TR11' 13 1 | B | 288 | -7.2081 | 100.6071 |  |  |  | Add 3-winding transformer 523093 HITCHLAND 3 115 523095 HITCHLAND 6 230 523098 HITCHLD_TR41 13 M2
05ALL | ERIS | Thermal | 523093 HITCHLAND 3 115 3WXFMR 526:H TP80148301 115 1 | 26SP | T1 | Single 523095 HITCHLAND6 230 523093 HITCHLAND3 115 523098 'HITCHLD_TR41' 13 2 | B | 288 | -7.3128 | 102.4814 |  |  |  | Add 3-winding transformer 523092 HITCHLD_TR11 13 523093 HITCHLAND 3 115 523095 HITCHLAND 6 230 M2
05ALL | ERIS | Thermal | 523095 HITCHLAND 6 230 3WXFMR 526:H 1003937402 115 2 | 26SP | T1 | Single 523095 HITCHLAND6 230 523093 HITCHLAND3 115 523092 'HITCHLD_TR11' 13 1 | B | 288 | -7.2081 | 108.2972 |  |  |  | Add 3-winding transformer 523093 HITCHLAND 3 115 523095 HITCHLAND 6 230 523098 HITCHLD_TR41 13 M2
05ALL | ERIS | Thermal | 523095 HITCHLAND 6 230 3WXFMR 526:H TP80148301 115 1 | 26SP | T1 | Single 523095 HITCHLAND6 230 523093 HITCHLAND3 115 523098 'HITCHLD_TR41' 13 2 | B | 288 | -7.32 | 110.2096 |  |  |  | Add 3-winding transformer 523092 HITCHLD_TR11 13 523093 HITCHLAND 3 115 523095 HITCHLAND 6 230 M2
05ALL | ERIS | Thermal | 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 1 | 26SP | T1 | Single 523186 SPEARMAN3 115 523266 PRINGLE3 115 2 | B | 217 | 27.9611 | 103.9859 |  |  |  | Rebuild line 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 1
05ALL | ERIS | Thermal | 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 1 | 29SP | T1 | Single 523186 SPEARMAN3 115 523266 PRINGLE3 115 2 | B | 217 | 28.5627 | 103.6671 |  |  |  | Rebuild line 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 1
05ALL | ERIS | Thermal | 523216 RB-HOGUE 3 115 523246 DALHART 3 115 1 | 26SP | T1 | Single 523228 DALLAM3 115 523235 HILMRCHZ_TP3 115 1 | B | 82 | 53.8182 | 100.1591 |  |  |  | Rebuild line 523216 RB-HOGUE 3 115 523246 DALHART 3 115 1
05ALL | ERIS | Thermal | 523266 PRINGLE 3 115 3WXFMR 526:ENRCO13617-1 115 1 | 26SP | T1 | MULTIGEN523979 | B | 193 | -2.8843 | 159.152 |  |  |  | Rebuild 3-winding transformer and add 3-winding transformer 523265 PRINGLE_TR 1 13 523266 PRINGLE 3 115 523267 PRINGLE 6 230 1
05ALL | ERIS | Thermal | 523266 PRINGLE 3 115 3WXFMR 526:ENRCO13617-1 115 1 | 29SP | T1 | MULTIGEN523979 | B | 193 | -2.7211 | 157.4431 |  |  |  | Rebuild 3-winding transformer and add 3-winding transformer 523265 PRINGLE_TR 1 13 523266 PRINGLE 3 115 523267 PRINGLE 6 230 1
05ALL | ERIS | Thermal | 523266 PRINGLE 3 115 3WXFMR 526:ENRCO13617-1 115 1 | 29WP | T1 | MULTIGEN523979 | B | 210 | -2.8419 | 148.1894 |  |  |  | Rebuild 3-winding transformer and add 3-winding transformer 523265 PRINGLE_TR 1 13 523266 PRINGLE 3 115 523267 PRINGLE 6 230 1
05ALL | ERIS | Thermal | 523266 PRINGLE 3 115 523377 RIVERVIEW 3 115 1 | 29WP | T1 | MULTIGEN523979 | B | 217 | 12.4482 | 102.7622 |  |  |  | Rebuild line 523266 PRINGLE 3 115 523377 RIVERVIEW 3 115 1
05ALL | ERIS | Thermal | 523267 PRINGLE 6 230 3WXFMR 526:ENRCO13617-1 115 1 | 26SP | T1 | MULTIGEN523979 | B | 193 | -2.9504 | 159.152 |  |  |  | Rebuild 3-winding transformer and add 3-winding transformer 523265 PRINGLE_TR 1 13 523266 PRINGLE 3 115 523267 PRINGLE 6 230 1
05ALL | ERIS | Thermal | 523267 PRINGLE 6 230 3WXFMR 526:ENRCO13617-1 115 1 | 29SP | T1 | MULTIGEN523979 | B | 193 | -2.7834 | 157.4431 |  |  |  | Rebuild 3-winding transformer and add 3-winding transformer 523265 PRINGLE_TR 1 13 523266 PRINGLE 3 115 523267 PRINGLE 6 230 1
05ALL | ERIS | Thermal | 523267 PRINGLE 6 230 3WXFMR 526:ENRCO13617-1 115 1 | 29WP | T1 | MULTIGEN523979 | B | 210 | -2.907 | 148.1894 |  |  |  | Rebuild 3-winding transformer and add 3-winding transformer 523265 PRINGLE_TR 1 13 523266 PRINGLE 3 115 523267 PRINGLE 6 230 1
05ALL | ERIS | Thermal | 524243 OUTPOST 3 115 524266 BUSHLAND 3 115 1 | 29SP | T1 | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | B | 598 | 37.7509 | 100.2086 |  |  |  | Add line and rebuild line 524243 OUTPOST 3 115 524266 BUSHLAND 3 115 M2
05ALL | ERIS | Thermal | 524266 BUSHLAND 3 115 3WXFMR 526:HYUN 201096010 115 1 | 26SP | T1 | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | B | 248 | 41.5801 | 118.0714 |  |  |  | Rebuild 3-winding transformer and add 3-winding transformer 524263 BSHLND_TR1 1 13 524266 BUSHLAND 3 115 524267 BUSHLAND 6 230 1
05ALL | ERIS | Thermal | 524266 BUSHLAND 3 115 3WXFMR 526:HYUN 201096010 115 1 | 29SP | T1 | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | B | 248 | 45.9076 | 122.0969 |  |  |  | Rebuild 3-winding transformer and add 3-winding transformer 524263 BSHLND_TR1 1 13 524266 BUSHLAND 3 115 524267 BUSHLAND 6 230 1
05ALL | ERIS | Thermal | 524266 BUSHLAND 3 115 3WXFMR 526:HYUN 201096010 115 1 | 29WP | T1 | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | B | 273 | 30.0569 | 106.6121 |  |  |  | Rebuild 3-winding transformer and add 3-winding transformer 524263 BSHLND_TR1 1 13 524266 BUSHLAND 3 115 524267 BUSHLAND 6 230 1
05ALL | ERIS | Thermal | 524267 BUSHLAND 6 230 3WXFMR 526:HYUN 201096010 115 1 | 26SP | T1 | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | B | 248 | 42.1938 | 122.2303 |  |  |  | Rebuild 3-winding transformer and add 3-winding transformer 524263 BSHLND_TR1 1 13 524266 BUSHLAND 3 115 524267 BUSHLAND 6 230 1
05ALL | ERIS | Thermal | 524267 BUSHLAND 6 230 3WXFMR 526:HYUN 201096010 115 1 | 29SP | T1 | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | B | 248 | 46.6289 | 127.0248 |  |  |  | Rebuild 3-winding transformer and add 3-winding transformer 524263 BSHLND_TR1 1 13 524266 BUSHLAND 3 115 524267 BUSHLAND 6 230 1
05ALL | ERIS | Thermal | 524267 BUSHLAND 6 230 3WXFMR 526:HYUN 201096010 115 1 | 29WP | T1 | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | B | 273 | 30.3509 | 109.8843 |  |  |  | Rebuild 3-winding transformer and add 3-winding transformer 524263 BSHLND_TR1 1 13 524266 BUSHLAND 3 115 524267 BUSHLAND 6 230 1
05ALL | ERIS | Thermal | 524281 34TH_ST_TP 3 115 524306 COULTER 3 115 1 | 26SP | T1 | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | B | 175 | 6.8467 | 108.9755 |  |  |  | Rebuild line 524281 34TH_ST_TP 3 115 524306 COULTER 3 115 1
05ALL | ERIS | Thermal | 524281 34TH_ST_TP 3 115 524306 COULTER 3 115 1 | 29SP | T1 | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | B | 175 | 10.1537 | 105.2794 |  |  |  | Rebuild line 524281 34TH_ST_TP 3 115 524306 COULTER 3 115 1
05ALL | ERIS | Thermal | 524281 34TH_ST_TP 3 115 524306 COULTER 3 115 1 | 29WP | T1 | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | B | 194 | 7.1101 | 103.8336 |  |  |  | Rebuild line 524281 34TH_ST_TP 3 115 524306 COULTER 3 115 1
05ALL | ERIS | Thermal | 524648 CARGILL 3 115 524655 FRIONA 3 115 1 | 29SP | T1 | P12:230:SPS:K11_K21::1_BUSHL_DFSMTH_PLANTX:HV: | B | 105 | 39.5869 | 100.8077 |  |  |  | Rebuild line 524648 CARGILL 3 115 524655 FRIONA 3 115 1
05ALL | ERIS | Thermal | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 26SP | T1 | P42:345:SPS:TUCO-NR50:::EHV: | B | 546 | 33.7052 | 101.9346 |  |  |  | Rebuild line 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
05ALL | ERIS | Thermal | 527522 ROSWELL_CTY3 115 527534 SW4J795_W 3 115 1 | 29WP | T1 | Single 527482 CHAVES_CNTY3 115 527546 SAMSON3 115 1 | B | 176 | -24.1067 | 100.279 |  |  |  | Rebuild line 527522 ROSWELL_CTY3 115 527534 SW4J795_W 3 115 1
05ALL | ERIS | Thermal | 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 1 | 26SP | T1 | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | B | 429 | -25.7605 | 100.1966 |  |  |  | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2
05ALL | ERIS | Thermal | 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 1 | 29SP | T1 | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | B | 429 | -26.7469 | 104.9468 |  |  |  | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2
05ALL | ERIS | Thermal | 528013 PHANTOM 3 115 528228 WOOD_DRAW 3 115 1 | 26SP | T1 | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | B | 239 | -47.5899 | 100.2913 |  |  |  | Rebuild line 528013 PHANTOM 3 115 528228 WOOD_DRAW 3 115 1
05ALL | ERIS | Thermal | 528015 PHANTOM 7 345 528013 PHANTOM 3 115 4 | 26SP | T1 | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | B | 435 | -128.9108 | 119.7782 |  |  |  | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4
05ALL | ERIS | Thermal | 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 1 | 26SP | T1 | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | B | 429 | -25.7754 | 100.2023 |  |  |  | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2
05ALL | ERIS | Thermal | 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 1 | 29SP | T1 | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | B | 429 | -26.7616 | 104.9538 |  |  |  | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2
05ALL | ERIS | Thermal | 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1 | 29SP | T1 | Single 528554 COOPER_RNCH3 115 528581 BYRD_TP3 115 1 | B | 176 | -2.2775 | 107.0135 |  |  |  | Rebuild line 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1
05ALL | ERIS | Thermal | 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1 | 29WP | T1 | Single 528554 COOPER_RNCH3 115 528581 BYRD_TP3 115 1 | B | 176 | -2.2807 | 106.8879 |  |  |  | Rebuild line 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1
05ALL | ERIS | Thermal | 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1 | 26SP | T1 | Single 528554 COOPER_RNCH3 115 528581 BYRD_TP3 115 1 | B | 176 | -2.471 | 105.4185 |  |  |  | Rebuild line 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1
00NR | NRIS | Thermal | 514893 XEROX 4 138 514896 MORGAN 4 138 1 | 26SP | T2 | Single 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | B | 444 | 71.009 | 100.9319 |  |  |  | Rebuild line 514893 XEROX 4 138 514896 MORGAN 4 138 1
03ALL | ERIS | Thermal | 530624 ST JOHN3 115 539696 ST-JOHN3 115 Z1 | 26SP | T2 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 322 | 14.896 | 100.5537 |  |  |  | Rebuild line 530624 ST JOHN3 115 539696 ST-JOHN3 115 Z1
03ALL | ERIS | Thermal | 530624 ST JOHN3 115 539696 ST-JOHN3 115 Z1 | 29SP | T2 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 322 | 14.9258 | 100.3215 |  |  |  | Rebuild line 530624 ST JOHN3 115 539696 ST-JOHN3 115 Z1
03ALL | ERIS | Thermal | 530624 ST JOHN3 115 539696 ST-JOHN3 115 Z1 | 29WP | T2 | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | B | 322 | 13.576 | 100.9464 |  |  |  | Rebuild line 530624 ST JOHN3 115 539696 ST-JOHN3 115 Z1
03ALL | ERIS | Thermal | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | 29WP | T2 | P23:345:SUNC:HLC_BRK188:::EHV: | B | 260 | 38.807 | 100.1417 |  |  |  | Rebuild line 531405 WALKMYR3 115 539654 CIM-PLT3 115 1
03ALL | ERIS | Thermal | 533075 VIOLA 4 138 539009 CONWAY 4 138 1 | 29WP | T2 | P12:138:ITCGP:FLATRIDGE-THISTLE:::HV: | B | 265 | 11.328 | 100.2531 |  |  |  | Rebuild line 533075 VIOLA 4 138 539009 CONWAY 4 138 1
04ALL | ERIS | Thermal | 511477 S.W.S.-4 138 521089 WASHITA4 138 1 | 29SP | T2 | Single 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | B | 525 | 70.1967 | 101.7367 |  |  |  | Rebuild line 511477 S.W.S.-4 138 521089 WASHITA4 138 1
05ALL | ERIS | Thermal | 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 2 | 26SP | T2 | Single 523186 SPEARMAN3 115 523266 PRINGLE3 115 1 | B | 217 | 25.4207 | 100.0597 |  |  |  | Rebuild line 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 2
05ALL | ERIS | Thermal | 523266 PRINGLE 3 115 3WXFMR 526:ENRCO13617-1 115 1 | 29WP | T2 | MULTIGEN523979 | B | 308 | -1.9372 | 101.2095 |  |  |  | Rebuild 3-winding transformer and add 3-winding transformer 523265 PRINGLE_TR 1 13 523266 PRINGLE 3 115 523267 PRINGLE 6 230 1
05ALL | ERIS | Thermal | 523267 PRINGLE 6 230 3WXFMR 526:ENRCO13617-1 115 1 | 29WP | T2 | MULTIGEN523979 | B | 308 | -1.9816 | 101.2095 |  |  |  | Rebuild 3-winding transformer and add 3-winding transformer 523265 PRINGLE_TR 1 13 523266 PRINGLE 3 115 523267 PRINGLE 6 230 1
05ALL | ERIS | Thermal | 524266 BUSHLAND 3 115 3WXFMR 526:HYUN 201096010 115 1 | 29SP | T2 | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | B | 303 | 38.4738 | 102.5071 |  |  |  | Rebuild 3-winding transformer and add 3-winding transformer 524263 BSHLND_TR1 1 13 524266 BUSHLAND 3 115 524267 BUSHLAND 6 230 1
05ALL | ERIS | Thermal | 524267 BUSHLAND 6 230 3WXFMR 526:HYUN 201096010 115 1 | 29SP | T2 | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | B | 316 | 37.4732 | 102.1997 |  |  |  | Rebuild 3-winding transformer and add 3-winding transformer 524263 BSHLND_TR1 1 13 524266 BUSHLAND 3 115 524267 BUSHLAND 6 230 1
05ALL | ERIS | Thermal | 524281 34TH_ST_TP 3 115 524325 WESTERN 3 115 1 | 26SP | T2 | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | B | 175 | -8.3558 | 101.2368 |  |  |  | Rebuild line 524281 34TH_ST_TP 3 115 524325 WESTERN 3 115 1
05ALL | ERIS | Thermal | 524281 34TH_ST_TP 3 115 524325 WESTERN 3 115 1 | 29WP | T2 | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | B | 194 | -7.455 | 100.8064 |  |  |  | Rebuild line 524281 34TH_ST_TP 3 115 524325 WESTERN 3 115 1
03ALL | ERIS | Thermal | 539652 CMRIVTP3 115 539654 CIM-PLT3 115 1 | 29WP | T3 | Single 539652 CMRIVTP3 115 539672 E-LIBER3 115 1 | B | 176 | 21.8399 | 100.1754 |  |  |  | Rebuild line 539652 CMRIVTP3 115 539654 CIM-PLT3 115 1
00ALL | ERIS | Voltage | BELFELD3 | 29WP | V | P23:345:UMZB:# 7148 #:: TND IN ND. BREAKER FAULT (296):EHV: |  |  |  |  | 1.0584 | 0.9 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | CRESENT4 | 29WP | V | P12:138:OKGE:BKRBKR0990:::HV: |  |  |  |  | 1.0569 | 0.92 | 1.05 | Add 0.4 MVAR switched shunt at CRESENT4 138 kV
00ALL | ERIS | Voltage | CRESENT4 | 29WP | V | P12:138:OKGE:BKRBKR0990:::HV: |  |  |  |  | 1.0569 | 0.92 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | CRESENT4 | 29SP | V | P12:138:OKGE:BKRBKR0990:::HV: |  |  |  |  | 1.0514 | 0.92 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | EHALLTP3 | 29WP | V | P12:115:MIDW-MKEC:ELLSWORTH-BUSHTON:::HV: |  |  |  |  | 1.0534 | 0.9 | 1.05 | None
00ALL | ERIS | Voltage | FRNT2WD7 | 26SP | V | P42:345:OKGE:SB_RARD7383:::EHV: |  |  |  |  | 1.0589 | 0.92 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | FRNT2WD7 | 26SP | V | P42:345:OKGE:SB_RARD7383:::EHV: |  |  |  |  | 1.0589 | 0.92 | 1.05 | Add 38 MVAR switched shunt at FRNT2WD7 345 kV
00ALL | ERIS | Voltage | G15048_1 | 26SP | V | P42:345:OKGE:SB_WONG7313:::EHV: |  |  |  |  | 1.0513 | 0.92 | 1.05 | Add 2 MVAR switched shunt at G15048_1 138 kV
00ALL | ERIS | Voltage | G15052_1 | 26SP | V | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 |  |  |  |  | 1.0569 | 0.95 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | G15052_T | 26SP | V | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 |  |  |  |  | 1.0569 | 0.95 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | G17-140-BUS | 26SP | V | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: |  |  |  |  | 1.2357 | 0.92 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | G17-140-BUS | 29SP | V | P22:345:EES:MUSKOGE7!:::EHV: |  |  |  |  | 1.2197 | 0.92 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | G18-071-TAP | 26SP | V | P42:345:OKGE:SB_RARD7383:::EHV: |  |  |  |  | 1.0579 | 0.92 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | G20-007-TAP | 29WP | V | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: |  |  |  |  | 1.0586 | 0.95 | 1.05 | Add 10 MVAR switched shunt at G20-007-TAP 345 kV
00ALL | ERIS | Voltage | GEN-2016-022 | 26SP | V | P42:345:OKGE:SB_RARD7383:::EHV: |  |  |  |  | 1.055 | 0.92 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | GEN-2017-140 | 26SP | V | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: |  |  |  |  | 1.2356 | 0.92 | 1.05 | Add 4 MVAR switched shunt at GEN-2017-140 345 kV
00ALL | ERIS | Voltage | GEN-2017-140 | 29SP | V | P22:345:EES:MUSKOGE7!:::EHV: |  |  |  |  | 1.2197 | 0.92 | 1.05 | Add 4 MVAR switched shunt at GEN-2017-140 345 kV
00ALL | ERIS | Voltage | GEN-2018-071 | 26SP | V | P42:345:OKGE:SB_RARD7383:::EHV: |  |  |  |  | 1.0579 | 0.92 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | GEN-2020-007 | 29WP | V | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: |  |  |  |  | 1.0586 | 0.95 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | GEN-2024-029 | 29WP | V | P12:138:OKGE:BKRBKR0990:::HV: |  |  |  |  | 1.0568 | 0.92 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | GEN-2024-029 | 29WP | V | P12:138:OKGE:BKRBKR0990:::HV: |  |  |  |  | 1.0568 | 0.92 | 1.05 | Add 0.4 MVAR switched shunt at GEN-2024-029 138 kV
00ALL | ERIS | Voltage | GEN-2024-029 | 29SP | V | P12:138:OKGE:BKRBKR0990:::HV: |  |  |  |  | 1.0514 | 0.92 | 1.05 | Add 0.4 MVAR switched shunt at GEN-2024-029 138 kV
00ALL | ERIS | Voltage | GEN-2024-334 | 26SP | V | P42:345:OKGE:SB_RARD7383:::EHV: |  |  |  |  | 1.055 | 0.92 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | GEN-2024-359 | 29WP | V | P23:345:UMZB:# 7148 #:: TND IN ND. BREAKER FAULT (296):EHV: |  |  |  |  | 1.0584 | 0.9 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | MALTABN5 | 26SP | V | Single 543059 MALTABN5 161 788220 G24-375-TAP 161 1 |  |  |  |  | 0.89521 | 0.93 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | MALTABN5 | 29SP | V | Single 543059 MALTABN5 161 788220 G24-375-TAP 161 1 |  |  |  |  | 0.89491 | 0.93 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | MAURINE4 | 29WP | V | P23:345:UMZB:# 7148 #:: TND IN ND. BREAKER FAULT (296):EHV: |  |  |  |  | 1.0719 | 0.9 | 1.05 | Add 314 MVAR SVC at MAURINE4 230 kV
00ALL | ERIS | Voltage | OMCDLEC7 | 26SP | V | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 |  |  |  |  | 1.0536 | 0.9 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | OPENSKY7 | 26SP | V | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 |  |  |  |  | 1.0554 | 0.92 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | RANCHRD7 | 26SP | V | P42:345:OKGE:SB_RARD7383:::EHV: |  |  |  |  | 1.055 | 0.92 | 1.05 | Add 19 MVAR switched shunt at RANCHRD7 345 kV
00ALL | ERIS | Voltage | RANCHRD7 | 26SP | V | P42:345:OKGE:SB_RARD7383:::EHV: |  |  |  |  | 1.055 | 0.92 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | SWAVCAP5 | 29SP | V | Single 543059 MALTABN5 161 788220 G24-375-TAP 161 1 |  |  |  |  | 0.89553 | 0.93 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | SWAVCAP5 | 26SP | V | Single 543059 MALTABN5 161 788220 G24-375-TAP 161 1 |  |  |  |  | 0.89583 | 0.93 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | SWAVRLY5 | 29SP | V | Single 543059 MALTABN5 161 788220 G24-375-TAP 161 1 |  |  |  |  | 0.89533 | 0.93 | 1.05 | Add 8 MVAR switched shunt at SWAVRLY5 161 kV
00ALL | ERIS | Voltage | SWAVRLY5 | 26SP | V | Single 543059 MALTABN5 161 788220 G24-375-TAP 161 1 |  |  |  |  | 0.89564 | 0.93 | 1.05 | Add 8 MVAR switched shunt at SWAVRLY5 161 kV
00ALL | ERIS | Voltage | TWNLAKE4 | 29WP | V | P12:138:OKGE:BKRBKR0990:::HV: |  |  |  |  | 1.0527 | 0.9 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | TWNLKSW4 | 29WP | V | P12:138:OKGE:BKRBKR0990:::HV: |  |  |  |  | 1.0527 | 0.9 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | TWNLKSW4 | 29WP | V | P12:138:OKGE:BKRBKR0990:::HV: |  |  |  |  | 1.0527 | 0.9 | 1.05 | Add 0.42 MVAR switched shunt at TWNLKSW4 138 kV
00ALL | ERIS | Voltage | WAVERLY7 | 29WP | V | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: |  |  |  |  | 1.0521 | 0.95 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | WHARV4 | 29WP | V | Single 533011 HALSTD4 138 533056 WHARV4 138 1 |  |  |  |  | 1.1283 | 0.93 | 1.05 | Add 54 MVAR SVC at WHARV4 138 kV
00NR | NRIS | Voltage | BISON___-GE4 | 29WP | V | Single 659351 BISON___-GE4 230 661047 HETINGR4 230 1 |  |  |  |  | 1.0571 | 0.9 | 1.05 | Add 0.6 MVAR switched shunt at BISON___-GE4 230 kV
00NR | NRIS | Voltage | CASHION4 | 29WP | V | Single 520545 FOURCTP4 138 520847 TWNLKJT4 138 1 |  |  |  |  | 1.0581 | 0.9 | 1.05 | Add 0.24 MVAR switched shunt at CASHION4 138 kV
00NR | NRIS | Voltage | CASHION4 | 29WP | V | Single 520545 FOURCTP4 138 520847 TWNLKJT4 138 1 |  |  |  |  | 1.0581 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | CASHION4 | 29SP | V | Single 520545 FOURCTP4 138 520847 TWNLKJT4 138 1 |  |  |  |  | 1.0502 | 0.9 | 1.05 | Add 0.24 MVAR switched shunt at CASHION4 138 kV
00NR | NRIS | Voltage | CASHION4 | 26SP | V | Single 520545 FOURCTP4 138 520847 TWNLKJT4 138 1 |  |  |  |  | 1.0529 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | CTNWOOD4 | 29WP | V | P12:138:OKGE:BKRBKR0990:::HV: |  |  |  |  | 1.0531 | 0.92 | 1.05 | Add 5 MVAR switched shunt at CTNWOOD4 138 kV
00NR | NRIS | Voltage | CTNWOOD4 | 29WP | V | P12:138:OKGE:BKRBKR0990:::HV: |  |  |  |  | 1.0531 | 0.92 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | DOVER 4 | 29WP | V | Single 520879 DOVER4 138 520882 DOVERSW4 138 1 |  |  |  |  | 1.055 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | DOVER 4 | 29WP | V | Single 520879 DOVER4 138 520882 DOVERSW4 138 1 |  |  |  |  | 1.055 | 0.9 | 1.05 | Add 0.6 MVAR switched shunt at DOVER 4 138 kV
00NR | NRIS | Voltage | DOVERSW2 | 29WP | V | P12:138:OKGE-WFEC:BKRBKR0770:::HV: |  |  |  |  | 1.0568 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | DOVERSW2 | 29WP | V | P12:138:OKGE-WFEC:BKRBKR0770:::HV: |  |  |  |  | 1.0568 | 0.9 | 1.05 | Add 0.23 MVAR switched shunt at DOVERSW2 69 kV
00NR | NRIS | Voltage | DOVERTP2 | 29WP | V | Single 514772 DOVERTP2 69 515517 TURCRKT2 69 1 |  |  |  |  | 1.0581 | 0.92 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | DOVERTP2 | 26SP | V | Single 514772 DOVERTP2 69 515517 TURCRKT2 69 1 |  |  |  |  | 1.0513 | 0.92 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | FOURCNT4 | 26SP | V | Single 520474 CMBLTP4 138 520545 FOURCTP4 138 1 |  |  |  |  | 1.0521 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | FOURCNT4 | 29WP | V | Single 520474 CMBLTP4 138 520545 FOURCTP4 138 1 |  |  |  |  | 1.0573 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | FOURCTP4 | 26SP | V | Single 520474 CMBLTP4 138 520545 FOURCTP4 138 1 |  |  |  |  | 1.0526 | 0.9 | 1.05 | Add 0.5 MVAR switched shunt at FOURCTP4 138 kV
00NR | NRIS | Voltage | FOURCTP4 | 29WP | V | Single 520474 CMBLTP4 138 520545 FOURCTP4 138 1 |  |  |  |  | 1.0578 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | G17-140-BUS | 29SP | V | P22:345:EES:MUSKOGE7!:::EHV: |  |  |  |  | 1.2187 | 0.92 | 1.05 | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV
00NR | NRIS | Voltage | G17-140-BUS | 26SP | V | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 |  |  |  |  | 1.2244 | 0.92 | 1.05 | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV
00NR | NRIS | Voltage | GEN-2020-007 | 29WP | V | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 |  |  |  |  | 1.052 | 0.95 | 1.05 | Add 7 MVAR switched shunt at GEN-2020-007 345 kV
00NR | NRIS | Voltage | HASTING4 | 29SP | V | System Intact |  |  |  |  | 0.9469 | 0.95 | 1.05 | Add 13 MVAR switched shunt at HASTING4 230 kV
00NR | NRIS | Voltage | HENESEY2 | 29WP | V | P12:138:OKGE-WFEC:BKRBKR0770:::HV: |  |  |  |  | 1.0563 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | JHNCRSOL | 29SP | V | P12:115:SUNC:JOHNSONCORNER-ULYSSESPLANT:::HV: |  |  |  |  | 1.0607 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | LACEY 2 | 29WP | V | P12:138:OKGE-WFEC:BKRBKR0770:::HV: |  |  |  |  | 1.0524 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | LACEY 2 | 29WP | V | P12:138:OKGE-WFEC:BKRBKR0770:::HV: |  |  |  |  | 1.0524 | 0.9 | 1.05 | Add 0.12 MVAR switched shunt at LACEY 2 69 kV
00NR | NRIS | Voltage | MANTER 3 | 29SP | V | P12:115:SUNC:JOHNSONCORNER-ULYSSESPLANT:::HV: |  |  |  |  | 1.06 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | MANTERT3 | 29SP | V | P12:115:SUNC:JOHNSONCORNER-ULYSSESPLANT:::HV: |  |  |  |  | 1.0602 | 0.9 | 1.05 | Add 8.4 MVAR switched shunt at MANTERT3 115 kV
00NR | NRIS | Voltage | MOORHED7 | 29WP | V | P23:345:OTP:DEUEL CO 3:3415::EHV: |  |  |  |  | 1.0537 | 0.9 | 1.05 | Add 5 MVAR switched shunt at MOORHED7 115 kV
00NR | NRIS | Voltage | NP-GLAZIR_G2 | 26SP | V | P23:345:OKGE:IF_MICO7302:::EHV: |  |  |  |  | 0.72197 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | NP-LIPSCOMB2 | 26SP | V | P23:345:OKGE:IF_MICO7302:::EHV: |  |  |  |  | 0.68601 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | NP-LUCKY_G 2 | 26SP | V | P23:345:OKGE:IF_MICO7302:::EHV: |  |  |  |  | 0.80535 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | NP-SUB_A 2 | 26SP | V | Single 523267 PRINGLE6 230 523979 HARRNG_EST6 230 1 |  |  |  |  | 0.85613 | 0.9 | 1.05 | Add 0.08 MVAR switched shunt at NP-SUB_A 2 69 kV
00NR | NRIS | Voltage | NP-SUB_A 2 | 26SP | V | Single 523267 PRINGLE6 230 523979 HARRNG_EST6 230 1 |  |  |  |  | 0.85613 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | NP-VALERO_P2 | 26SP | V | P23:345:OKGE:IF_MICO7302:::EHV: |  |  |  |  | 0.69359 | 0.9 | 1.05 | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV
00NR | NRIS | Voltage | PINE ST4 | 29WP | V | Single 514829 PINEST4 138 514830 FITZGRD4 138 1 |  |  |  |  | 1.0507 | 0.92 | 1.05 | Add 1.2 MVAR switched shunt at PINE ST4 138 kV
00NR | NRIS | Voltage | REDWING2 | 29WP | V | Single 514772 DOVERTP2 69 515517 TURCRKT2 69 1 |  |  |  |  | 1.0582 | 0.92 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | REDWING2 | 26SP | V | Single 514772 DOVERTP2 69 515517 TURCRKT2 69 1 |  |  |  |  | 1.0514 | 0.92 | 1.05 | Add 0.2 MVAR switched shunt at REDWING2 69 kV
00NR | NRIS | Voltage | RICHFLD3 | 29SP | V | P12:115:SUNC:JOHNSONCORNER-ULYSSESPLANT:::HV: |  |  |  |  | 1.0581 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | SEMINOLE 6 | 26SP | V | Single 527149 MUSTANG6 230 527276 SEMINOLE6 230 1 |  |  |  |  | 0.83197 | 0.9 | 1.05 | Add 110 MVAR switched shunt at SEMINOLE 6 230 kV
00NR | NRIS | Voltage | TURCRK 2 | 29WP | V | P12:138:OKGE-WFEC:BKRBKR0770:::HV: |  |  |  |  | 1.0551 | 0.92 | 1.05 | Add 0.21 MVAR switched shunt at TURCRK 2 69 kV
00NR | NRIS | Voltage | TURCRK 2 | 29WP | V | P12:138:OKGE-WFEC:BKRBKR0770:::HV: |  |  |  |  | 1.0551 | 0.92 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | TURCRKT2 | 29WP | V | P12:138:OKGE-WFEC:BKRBKR0770:::HV: |  |  |  |  | 1.0551 | 0.92 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | TWNLAKE4 | 29SP | V | P12:138:WFEC:KNGFSHR_TWINLKS:::: |  |  |  |  | 1.0537 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | TWNLAKE4 | 29SP | V | P12:138:WFEC:KNGFSHR_TWINLKS:::: |  |  |  |  | 1.0537 | 0.9 | 1.05 | Add 0.33 MVAR switched shunt at TWNLAKE4 138 kV
00NR | NRIS | Voltage | TWNLAKE4 | 29WP | V | Single 514827 CTNWOOD4 138 515377 CRESENT4 138 1 |  |  |  |  | 1.0611 | 0.9 | 1.05 | Add 0.33 MVAR switched shunt at TWNLAKE4 138 kV
00NR | NRIS | Voltage | TWNLAKE4 | 29WP | V | Single 514827 CTNWOOD4 138 515377 CRESENT4 138 1 |  |  |  |  | 1.0611 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | TWNLAKE4 | 26SP | V | P12:138:WFEC:KNGFSHR_TWINLKS:::: |  |  |  |  | 1.0564 | 0.9 | 1.05 | Add 0.33 MVAR switched shunt at TWNLAKE4 138 kV
00NR | NRIS | Voltage | TWNLAKE4 | 26SP | V | P12:138:WFEC:KNGFSHR_TWINLKS:::: |  |  |  |  | 1.0564 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | TWNLKJT4 | 29WP | V | Single 520545 FOURCTP4 138 520847 TWNLKJT4 138 1 |  |  |  |  | 1.0586 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | TWNLKJT4 | 29WP | V | Single 520545 FOURCTP4 138 520847 TWNLKJT4 138 1 |  |  |  |  | 1.0586 | 0.9 | 1.05 | Add 0.3 MVAR switched shunt at TWNLKJT4 138 kV
00NR | NRIS | Voltage | TWNLKJT4 | 29SP | V | Single 520545 FOURCTP4 138 520847 TWNLKJT4 138 1 |  |  |  |  | 1.0508 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | TWNLKJT4 | 26SP | V | Single 520545 FOURCTP4 138 520847 TWNLKJT4 138 1 |  |  |  |  | 1.0535 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | 6MILE RD-ER7 | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE HOLT.CO3-GRPRAR1-LNX3-1 :EHV: |  |  |  |  | 0.88464 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | ASHTON-ER8 | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: |  |  |  |  | 0.8877 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | BISON___-GE4 | 29L | V | Single 652411 MICTYE4 230 783451 GEN-2024-216 230 1 |  |  |  |  | 1.1166 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | BOBCAT.C 3 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE SIDNEY__-MB3-SD.LS-LR-MB3-Z :EHV: |  |  |  |  | 1.1498 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | BOBCAT.C 7 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE KEYSTON3-SD.LS-KS-MB3-1 :EHV: |  |  |  |  | 1.0755 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | BRYANT-ER8 | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: |  |  |  |  | 0.88058 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | CHADRON 7 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE KEYSTON3-SD.LS-KS-MB3-1 :EHV: |  |  |  |  | 1.082 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | CHESTER-ER8 | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE HOLT.CO3-GRPRAR1-LNX3-1 :EHV: |  |  |  |  | 0.89168 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | CHRYLK-ER8 | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: |  |  |  |  | 0.88101 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | COLDWATR-TS7 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE KEYSTON3-SD.LS-KS-MB3-1 :EHV: |  |  |  |  | 1.08 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | COVALT__-TS7 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE KEYSTON3-SD.LS-KS-MB3-1 :EHV: |  |  |  |  | 1.0866 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | CRAWFRD7 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE KEYSTON3-SD.LS-KS-MB3-1 :EHV: |  |  |  |  | 1.0992 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | DAKOTAACCESS | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: |  |  |  |  | 0.88715 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | DAYTON__-ER7 | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE HOLT.CO3-GRPRAR1-LNX3-1 :EHV: |  |  |  |  | 0.8966 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | DAYTON__-ER7 | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE HOLT.CO3-GRPRAR1-LNX3-1 :EHV: |  |  |  |  | 0.8966 | 0.9 | 1.05 | Add 24 MVAR switched shunt at DAYTON__-ER7 115 kV
01ALL | ERIS | Voltage | DESMET-ER8 | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: |  |  |  |  | 0.86917 | 0.9 | 1.05 | Add 4.4 MVAR switched shunt at DESMET-ER7 115 kV
01ALL | ERIS | Voltage | DH_CS_EA-TS4 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE SIDNEY__-MB3-SD.LS-LR-MB3-Z :EHV: |  |  |  |  | 1.1354 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | DH_CS_EA-TS4 | 29SP | V | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL_-MB4-1 :HV: |  |  |  |  | 0.88306 | 0.9 | 1.05 | Add 24 MVAR switched shunt at DH_CS_EA-TS4 230 kV
01ALL | ERIS | Voltage | DRYCREEK-BE4 | 29L | V | Single 652411 MICTYE4 230 783451 GEN-2024-216 230 1 |  |  |  |  | 1.1109 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | DRYCREEK-BE7 | 29L | V | Single 652411 MICTYE4 230 783451 GEN-2024-216 230 1 |  |  |  |  | 1.1057 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | DUNLAP 7 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE KEYSTON3-SD.LS-KS-MB3-1 :EHV: |  |  |  |  | 1.0826 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | ELKCRK 7 | 29L | V | Single 652411 MICTYE4 230 783451 GEN-2024-216 230 1 |  |  |  |  | 1.101 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | ELSWRTH7 | 29L | V | Single 652411 MICTYE4 230 783451 GEN-2024-216 230 1 |  |  |  |  | 1.1025 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | FRANKFRT-ER8 | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: |  |  |  |  | 0.89368 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | FREEDOM7 | 29L | V | Single 652411 MICTYE4 230 783451 GEN-2024-216 230 1 |  |  |  |  | 1.1029 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | G24-161-TAP | 29L | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 1.0838 | 0.92 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | G24-282-TAP | 29L | V | Single 652411 MICTYE4 230 783451 GEN-2024-216 230 1 |  |  |  |  | 1.1324 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | GEN-2017-097 | 29L | V | Single 652411 MICTYE4 230 783451 GEN-2024-216 230 1 |  |  |  |  | 1.1062 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | GEN-2017-115 | 29L | V | P55:345:OPPD:S3458 3::FN13:EHV: |  |  |  |  | 1.0733 | 0.95 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | GEN-2024-157 | 29L | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 1.0843 | 0.92 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | GEN-2024-157 | 29L | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 1.0843 | 0.92 | 1.05 | Add 0.9 MVAR switched shunt at GEN-2024-157 138 kV
01ALL | ERIS | Voltage | GEN-2024-161 | 29L | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 1.0838 | 0.92 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | GEN-2024-282 | 29L | V | Single 652411 MICTYE4 230 783451 GEN-2024-216 230 1 |  |  |  |  | 1.1324 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | GEN-2024-283 | 29L | V | Single 652411 MICTYE4 230 783451 GEN-2024-216 230 1 |  |  |  |  | 1.1324 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | GEN-2024-374 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE SIDNEY__-MB3-SD.LS-LR-MB3-Z :EHV: |  |  |  |  | 1.1498 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | GERING TAP | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE KEYSTON3-SD.LS-KS-MB3-1 :EHV: |  |  |  |  | 1.1162 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | GERING-TS7 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE KEYSTON3-SD.LS-KS-MB3-1 :EHV: |  |  |  |  | 1.1189 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | HEMINGF_-TS7 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE KEYSTON3-SD.LS-KS-MB3-1 :EHV: |  |  |  |  | 1.0813 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | HOB-JCT2 | 29L | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 1.0943 | 0.92 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | HRRISBRG-ER7 | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE HOLT.CO3-GRPRAR1-LNX3-1 :EHV: |  |  |  |  | 0.89457 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | KETCHEM7 | 29L | V | Single 645458 S34583 345 645558 S3458-HOLT3 345 Z1 |  |  |  |  | 1.0695 | 0.95 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | LETCHER-ER8 | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: |  |  |  |  | 0.88133 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | LINCOLN-ER7 | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE HOLT.CO3-GRPRAR1-LNX3-1 :EHV: |  |  |  |  | 0.88963 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | LOOMIS-ER8 | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: |  |  |  |  | 0.86693 | 0.9 | 1.05 | Add 5.5 MVAR switched shunt at LOOMIS-ER8 69 kV
01ALL | ERIS | Voltage | LOOMIS-ER8 | 29SP | V | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: |  |  |  |  | 0.89442 | 0.9 | 1.05 | Add 5.5 MVAR switched shunt at LOOMIS-ER8 69 kV
01ALL | ERIS | Voltage | LYNN____-TS7 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE KEYSTON3-SD.LS-KS-MB3-1 :EHV: |  |  |  |  | 1.0894 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | MAURINE4 | 29L | V | Single 652411 MICTYE4 230 783451 GEN-2024-216 230 1 |  |  |  |  | 1.1375 | 0.9 | 1.05 | Add 314 MVAR SVC at MAURINE4 230 kV
01ALL | ERIS | Voltage | MORRILL 7 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE KEYSTON3-SD.LS-KS-MB3-1 :EHV: |  |  |  |  | 1.0977 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | MOS-ASHT-ER8 | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: |  |  |  |  | 0.88774 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | MOS-CHST-ER8 | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE HOLT.CO3-GRPRAR1-LNX3-1 :EHV: |  |  |  |  | 0.8917 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | MOS-LADL-ER8 | 29SP | V | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: |  |  |  |  | 0.89662 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | MOS-LADL-ER8 | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: |  |  |  |  | 0.88082 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | MOS-LMIS-ER8 | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: |  |  |  |  | 0.87203 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | MOS-LMIS-ER8 | 29SP | V | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: |  |  |  |  | 0.8993 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | MOS-MDCY-ER8 | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE HOLT.CO3-GRPRAR1-LNX3-1 :EHV: |  |  |  |  | 0.89343 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | MOS-RDFL-ER8 | 29SP | V | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: |  |  |  |  | 0.89856 | 0.9 | 1.05 | Add 4 MVAR switched shunt at MOS-RDFL-ER8 69 kV
01ALL | ERIS | Voltage | MOS-RDFL-ER8 | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: |  |  |  |  | 0.88277 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | MOS-TULR-ER8 | 29SP | V | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: |  |  |  |  | 0.89611 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | MOS-TULR-ER8 | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: |  |  |  |  | 0.88031 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | NP-GLAZIR_G2 | 26SP | V | P12:230.0:UMZ:# N-1 #:: LINE SIDNEY___TS4-SIDNEY__-MB4-1 :HV: |  |  |  |  | 0.68802 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | NP-LIPSCOMB2 | 26SP | V | P12:230.0:UMZ:# N-1 #:: LINE SIDNEY___TS4-SIDNEY__-MB4-1 :HV: |  |  |  |  | 0.65049 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | NP-LIPS_SHA2 | 26SP | V | P12:230.0:UMZ:# N-1 #:: LINE SIDNEY___TS4-SIDNEY__-MB4-1 :HV: |  |  |  |  | 0.65049 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | NP-LUCKY_CR2 | 26SP | V | P12:230.0:UMZ:# N-1 #:: LINE SIDNEY___TS4-SIDNEY__-MB4-1 :HV: |  |  |  |  | 0.77541 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | NP-LUCKY_G 2 | 26SP | V | P12:230.0:UMZ:# N-1 #:: LINE SIDNEY___TS4-SIDNEY__-MB4-1 :HV: |  |  |  |  | 0.77555 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | NP-SHATTUCK2 | 26SP | V | P12:230.0:UMZ:# N-1 #:: LINE SIDNEY___TS4-SIDNEY__-MB4-1 :HV: |  |  |  |  | 0.62953 | 0.9 | 1.05 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
01ALL | ERIS | Voltage | NP-SUB_A 2 | 26SP | V | P12:230.0:UMZ:# N-1 #:: LINE SIDNEY___TS4-SIDNEY__-MB4-1 :HV: |  |  |  |  | 0.83928 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | NP-VALERO_P2 | 26SP | V | P12:230.0:UMZ:# N-1 #:: LINE SIDNEY___TS4-SIDNEY__-MB4-1 :HV: |  |  |  |  | 0.65838 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | NUNDRWD-LNX3 | 29L | V | Single 652411 MICTYE4 230 783451 GEN-2024-216 230 1 |  |  |  |  | 1.1214 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | NUNDRWD4 | 29L | V | Single 652411 MICTYE4 230 783451 GEN-2024-216 230 1 |  |  |  |  | 1.1213 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | ORLAND-ER8 | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE HOLT.CO3-GRPRAR1-LNX3-1 :EHV: |  |  |  |  | 0.89565 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | ORLAND-ER8 | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE HOLT.CO3-GRPRAR1-LNX3-1 :EHV: |  |  |  |  | 0.89565 | 0.9 | 1.05 | Add 0.5 MVAR switched shunt at ORLAND-ER8 69 kV
01ALL | ERIS | Voltage | OUTLAW_WF7 | 29L | V | P55:345:OPPD:S3458 3::FN13:EHV: |  |  |  |  | 1.0782 | 0.95 | 1.05 | Add 34 MVAR switched shunt at OUTLAW_WF7 345 kV
01ALL | ERIS | Voltage | OUTLAW_WFTP7 | 29L | V | P55:345:OPPD:S3458 3::FN13:EHV: |  |  |  |  | 1.0755 | 0.95 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | RAPIDCTY-RM8 | 29L | V | Single 652411 MICTYE4 230 783451 GEN-2024-216 230 1 |  |  |  |  | 1.1027 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | RCDC.DUM-BE4 | 29L | V | Single 652411 MICTYE4 230 783451 GEN-2024-216 230 1 |  |  |  |  | 1.1108 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | RCDC.E__-BE4 | 29L | V | Single 652411 MICTYE4 230 783451 GEN-2024-216 230 1 |  |  |  |  | 1.1109 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | REDFELD-ER7 | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: |  |  |  |  | 0.88885 | 0.9 | 1.05 | Add 54 MVAR switched shunt at REDFELD-ER7 115 kV
01ALL | ERIS | Voltage | REDFELD-ER7 | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: |  |  |  |  | 0.88885 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | REDFELD-ER8 | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: |  |  |  |  | 0.88825 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | REDFIELD | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: |  |  |  |  | 0.88179 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | REDFIELD | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: |  |  |  |  | 0.88179 | 0.9 | 1.05 | Add 10 MVAR switched shunt at REDFIELD 115 kV
01ALL | ERIS | Voltage | REDFIELD | 29SP | V | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: |  |  |  |  | 0.89706 | 0.9 | 1.05 | Add 10 MVAR switched shunt at REDFIELD 115 kV
01ALL | ERIS | Voltage | REDFIELD-ER8 | 29SP | V | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: |  |  |  |  | 0.89856 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | REDFIELD-ER8 | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: |  |  |  |  | 0.88276 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | RKY_RDG4 | 29L | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 1.0841 | 0.92 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | RUSHMORE-RM7 | 29L | V | Single 652411 MICTYE4 230 783451 GEN-2024-216 230 1 |  |  |  |  | 1.107 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | RUSHMORE-RM8 | 29L | V | Single 652411 MICTYE4 230 783451 GEN-2024-216 230 1 |  |  |  |  | 1.125 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | S3458-HOLT 3 | 29L | V | P55:345:OPPD:S3458 3::FN13:EHV: |  |  |  |  | 1.0734 | 0.95 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | SCOTBLF 7 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE KEYSTON3-SD.LS-KS-MB3-1 :EHV: |  |  |  |  | 1.1168 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | SD.LS-KS-MB3 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE KEYSTON3-SD.LS-KS-MB3-1 :EHV: |  |  |  |  | 1.1515 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | SD.LS-LR-MB3 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE SIDNEY__-MB3-SD.LS-LR-MB3-Z :EHV: |  |  |  |  | 1.2053 | 0.9 | 1.05 | Add 525 MVAR SVC at SD.LS-LR-MB3 345 kV
01ALL | ERIS | Voltage | SHINDLER-ER7 | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE HOLT.CO3-GRPRAR1-LNX3-1 :EHV: |  |  |  |  | 0.88532 | 0.9 | 1.05 | Add 0.4 MVAR switched shunt at SHINDLER-ER7 115 kV
01ALL | ERIS | Voltage | SHINDLER-ER7 | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE HOLT.CO3-GRPRAR1-LNX3-1 :EHV: |  |  |  |  | 0.88532 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | SIDNEY__-MB3 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE KEYSTON3-SD.LS-KS-MB3-1 :EHV: |  |  |  |  | 1.1515 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | STEGALL 4 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE SIDNEY__-MB3-SD.LS-LR-MB3-Z :EHV: |  |  |  |  | 1.1354 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | STEGALL 4 | 29SP | V | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL_-MB4-1 :HV: |  |  |  |  | 0.88306 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | STEGALL-LNX3 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE SIDNEY__-MB3-SD.LS-LR-MB3-Z :EHV: |  |  |  |  | 1.1354 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | STEGALL-LNX3 | 29SP | V | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL_-MB4-1 :HV: |  |  |  |  | 0.88306 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | STEGALL_-MB3 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE SIDNEY__-MB3-SD.LS-LR-MB3-Z :EHV: |  |  |  |  | 1.1498 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | STEGALL_-MB4 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE SIDNEY__-MB3-SD.LS-LR-MB3-Z :EHV: |  |  |  |  | 1.1381 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | STEGALL_-MB4 | 29SP | V | P13:345-230.0:UMZ:# N-1 #:: 3WND STEGALL_-MB3-STEGALL_-MB4-STEGALL_-MB9-1 SGQ KV3A:EHV: |  |  |  |  | 0.88651 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | SW-WILLO-ER8 | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: |  |  |  |  | 0.89316 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | SW145-ER8 | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE HOLT.CO3-GRPRAR1-LNX3-1 :EHV: |  |  |  |  | 0.89889 | 0.9 | 1.05 | Add 14.4 MVAR switched shunt at SW145-ER8 69 kV
01ALL | ERIS | Voltage | SW162-ER8 | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE HOLT.CO3-GRPRAR1-LNX3-1 :EHV: |  |  |  |  | 0.89683 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | SYCAMORE-ER7 | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE HOLT.CO3-GRPRAR1-LNX3-1 :EHV: |  |  |  |  | 0.8883 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | TULARE-ER8 | 29SP | V | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: |  |  |  |  | 0.89068 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | TULARE-ER8 | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: |  |  |  |  | 0.87489 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | UNDERWOOD 2 | 29L | V | Single 652411 MICTYE4 230 783451 GEN-2024-216 230 1 |  |  |  |  | 1.1806 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | VICTRYH4 | 29L | V | Single 652411 MICTYE4 230 783451 GEN-2024-216 230 1 |  |  |  |  | 1.1188 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | VICTRYH4 | 29SP | V | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL_-MB4-1 :HV: |  |  |  |  | 0.88983 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | VICTRYH7 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE KEYSTON3-SD.LS-KS-MB3-1 :EHV: |  |  |  |  | 1.1326 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | WAYSIDE 4 | 26SP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.85079 | 0.9 | 1.05 | Add 60 MVAR switched shunt at WAYSIDE 4 230 kV
01ALL | ERIS | Voltage | WAYSIDE 4 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE SIDNEY__-MB3-SD.LS-LR-MB3-Z :EHV: |  |  |  |  | 1.1432 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | WAYSIDE 7 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE KEYSTON3-SD.LS-KS-MB3-1 :EHV: |  |  |  |  | 1.0704 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | WICKSVL7 | 29L | V | Single 652411 MICTYE4 230 783451 GEN-2024-216 230 1 |  |  |  |  | 1.0981 | 0.9 | 1.05 | Mitigated at another bus
01ALL | ERIS | Voltage | WILLOWLK-ER8 | 26SP | V | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: |  |  |  |  | 0.88362 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | BELFELD3 | 29L | V | Single 652424 BELFELD3 345 800121 MAURINE2 345 1 |  |  |  |  | 1.0542 | 0.9 | 1.05 | Add 25 MVAR switched shunt at BELFELD3 345 kV
01NR | NRIS | Voltage | BOBCAT.C 3 | 29L | V | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: |  |  |  |  | 1.151 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | CHARL_CK-BE4 | 29L | V | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: |  |  |  |  | 1.0689 | 0.9 | 1.05 | Add 18 MVAR switched shunt at CHARL_CK-BE4 230 kV
01NR | NRIS | Voltage | COVALT__-TS7 | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.0657 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | CRAWFRD7 | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.071 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | DRYCREEK-BE4 | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.1028 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | DRYCREEK-BE7 | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.1004 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | DUNLAP 7 | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.0581 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | ELKCRK 7 | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.0978 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | ELSWRTH7 | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.097 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | FREEDOM7 | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.0973 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | GEN-2017-097 | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.0999 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | GEN-2024-359 | 29L | V | Single 652424 BELFELD3 345 800121 MAURINE2 345 1 |  |  |  |  | 1.0542 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | GEN-2024-374 | 29L | V | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: |  |  |  |  | 1.151 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | GERING TAP | 29L | V | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: |  |  |  |  | 1.0901 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | GERING-TS7 | 29L | V | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: |  |  |  |  | 1.0928 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | GRAY CO3 | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.0888 | 0.9 | 1.05 | Add 0.09 MVAR switched shunt at GRAY CO3 115 kV
01NR | NRIS | Voltage | GYCOTAP3 | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.0888 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | HAGGARD3 | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.0888 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | HEMINGF_-TS7 | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.0564 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | LYNN____-TS7 | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.0662 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | MAURINE 2 | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.1289 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | MORRILL 7 | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.0689 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | NUNDRWD-LNX3 | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.1122 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | NUNDRWD4 | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.1123 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | PHILIP 8 | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.075 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | PHILIP_T 4 | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.0874 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | PHILIP__-BE4 | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.0859 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | PHILLIP-WIND | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.0874 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | RAPIDCTY-RM8 | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.0979 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | RCDC.DUM-BE4 | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.1027 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | RCDC.E__-BE4 | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.1027 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | RUSHMORE-RM7 | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.1019 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | RUSHMORE-RM8 | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.1198 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | SCOTBLF 7 | 29L | V | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: |  |  |  |  | 1.0905 | 0.9 | 1.05 | Add 0.7 MVAR switched shunt at SCOTBLF 7 115 kV
01NR | NRIS | Voltage | SCOTBLF 7 | 29L | V | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: |  |  |  |  | 1.0905 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | SD.LS-KS-MB3 | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.1001 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | SD.LS-KS-MB3 | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.1001 | 0.9 | 1.05 | Add 256 MVAR switched shunt at SD.LS-KS-MB3 345 kV
01NR | NRIS | Voltage | SIDNEY__-MB3 | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.1001 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | SIDNEY__-MB4 | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.0581 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | STEGALL 4 | 29L | V | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: |  |  |  |  | 1.1371 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | STEGALL-LNX3 | 29L | V | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: |  |  |  |  | 1.1371 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | STEGALL_-MB3 | 29L | V | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: |  |  |  |  | 1.151 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | STEGALL_-MB3 | 29L | V | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: |  |  |  |  | 1.151 | 0.9 | 1.05 | Add 78 MVAR SVC at STEGALL_-MB3 345 kV
01NR | NRIS | Voltage | STEGALL_-MB4 | 29L | V | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: |  |  |  |  | 1.1398 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | STEGALL_-MB4 | 29L | V | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: |  |  |  |  | 1.1398 | 0.9 | 1.05 | Add 0.7 MVAR switched shunt at STEGALL_-MB4 230 kV
01NR | NRIS | Voltage | UNDERWOOD 2 | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.1626 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | UNDERWOOD 2 | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.1626 | 0.9 | 1.05 | Add 16 MVAR switched shunt at UNDERWOOD 2 345 kV
01NR | NRIS | Voltage | VICTRYH4 | 29L | V | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: |  |  |  |  | 1.118 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | VICTRYH7 | 29L | V | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: |  |  |  |  | 1.1061 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | WALL 7 | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.0907 | 0.9 | 1.05 | Mitigated at another bus
01NR | NRIS | Voltage | WICKSVL7 | 29L | V | P14:345:UMZ:# 7215 #:: PROPER TAKE LINE WITH SIDNEY-LARAMIE RIVER STATION LINE REACTOR:EHV: |  |  |  |  | 1.0963 | 0.9 | 1.05 | Mitigated at another bus
02ALL | ERIS | Voltage | GEN-2024-157 | 29L | V | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 |  |  |  |  | 1.0881 | 0.92 | 1.05 | Mitigated at another bus
02ALL | ERIS | Voltage | NP-GLAZIR_G2 | 26SP | V | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: |  |  |  |  | 0.69387 | 0.9 | 1.05 | Mitigated at another bus
02ALL | ERIS | Voltage | NP-LIPSCOMB2 | 26SP | V | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: |  |  |  |  | 0.65658 | 0.9 | 1.05 | Mitigated at another bus
02ALL | ERIS | Voltage | NP-LIPS_SHA2 | 26SP | V | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: |  |  |  |  | 0.65658 | 0.9 | 1.05 | Mitigated at another bus
02ALL | ERIS | Voltage | NP-LUCKY_CR2 | 26SP | V | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: |  |  |  |  | 0.7806 | 0.9 | 1.05 | Mitigated at another bus
02ALL | ERIS | Voltage | NP-LUCKY_G 2 | 26SP | V | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: |  |  |  |  | 0.78074 | 0.9 | 1.05 | Mitigated at another bus
02ALL | ERIS | Voltage | NP-SHATTUCK2 | 26SP | V | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: |  |  |  |  | 0.63574 | 0.9 | 1.05 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
02ALL | ERIS | Voltage | NP-SUB_A 2 | 26SP | V | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: |  |  |  |  | 0.84398 | 0.9 | 1.05 | Mitigated at another bus
02ALL | ERIS | Voltage | NP-VALERO_P2 | 26SP | V | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: |  |  |  |  | 0.66443 | 0.9 | 1.05 | Mitigated at another bus
02ALL | ERIS | Voltage | RKY_RDG4 | 29L | V | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 |  |  |  |  | 1.0881 | 0.92 | 1.05 | Add 0.5 MVAR switched shunt at RKY_RDG4 138 kV
02NR | NRIS | Voltage | BOBCAT.C 3 | 29L | V | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 |  |  |  |  | 1.0924 | 0.9 | 1.05 | Mitigated at another bus
02NR | NRIS | Voltage | GEN-2024-374 | 29L | V | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 |  |  |  |  | 1.0924 | 0.9 | 1.05 | Mitigated at another bus
02NR | NRIS | Voltage | GRAY CO3 | 29L | V | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: |  |  |  |  | 1.0879 | 0.9 | 1.05 | Add 0.09 MVAR switched shunt at GRAY CO3 115 kV
02NR | NRIS | Voltage | GYCOTAP3 | 29L | V | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: |  |  |  |  | 1.0879 | 0.9 | 1.05 | Mitigated at another bus
02NR | NRIS | Voltage | HAGGARD3 | 29L | V | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: |  |  |  |  | 1.0879 | 0.9 | 1.05 | Mitigated at another bus
02NR | NRIS | Voltage | STEGALL 4 | 29L | V | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 |  |  |  |  | 1.0854 | 0.9 | 1.05 | Mitigated at another bus
02NR | NRIS | Voltage | STEGALL-LNX3 | 29L | V | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 |  |  |  |  | 1.0854 | 0.9 | 1.05 | Mitigated at another bus
02NR | NRIS | Voltage | STEGALL_-MB3 | 29L | V | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 |  |  |  |  | 1.0924 | 0.9 | 1.05 | Add 78 MVAR SVC at STEGALL_-MB3 345 kV
02NR | NRIS | Voltage | STEGALL_-MB3 | 29L | V | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 |  |  |  |  | 1.0924 | 0.9 | 1.05 | Mitigated at another bus
02NR | NRIS | Voltage | STEGALL_-MB4 | 29L | V | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 |  |  |  |  | 1.0869 | 0.9 | 1.05 | Mitigated at another bus
02NR | NRIS | Voltage | UNDERWOOD 2 | 29L | V | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 |  |  |  |  | 1.1269 | 0.9 | 1.05 | Mitigated at another bus
02NR | NRIS | Voltage | UNDERWOOD 2 | 29L | V | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 |  |  |  |  | 1.1269 | 0.9 | 1.05 | Add 16 MVAR switched shunt at UNDERWOOD 2 345 kV
02NR | NRIS | Voltage | VICTRYH4 | 29L | V | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 |  |  |  |  | 1.0744 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | 25MILE 7 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.91478 | 0.92 | 1.05 | None
03ALL | ERIS | Voltage | 25MILZ 7 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.91478 | 0.92 | 1.05 | None
03ALL | ERIS | Voltage | ALXNDR 3 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.89561 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | ANGELUS | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.86111 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | ANGELUS | 29WP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.881 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | ANGELUS | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.86439 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | ARNOLD3 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.86181 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | ARNOLD3 | 29WP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.87716 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | ARNOLD3 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.86915 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | ARNOLD3 | 29L | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.89456 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | ASGI15_001_1 | 26SP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.87707 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | ASGI15_001_1 | 29SP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.88394 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | ASGI15_001_1 | 29WP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.856 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | ATWODSW3 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.89049 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | ATWODSW3 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.89656 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | ATWOOD 3 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.89328 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | ATWOOD 3 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.89806 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | AXTELL 3 | 29SP | V | System Intact |  |  |  |  | 0.93123 | 0.95 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | AXTELL 3 | 29SP | V | System Intact |  |  |  |  | 0.93123 | 0.95 | 1.05 | Add 62 MVAR switched shunt at AXTELL 3 345 kV
03ALL | ERIS | Voltage | BARBER 3 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.86962 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | BARBER 3 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.86962 | 0.9 | 1.05 | Add 32 MVAR switched shunt at BARBER 3 115 kV
03ALL | ERIS | Voltage | BARBER 4 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.87702 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | BEELER 3 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.86277 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | BEELER 3 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.86277 | 0.9 | 1.05 | Add 12 MVAR switched shunt at BEELER 3 115 kV
03ALL | ERIS | Voltage | BEELER 3 | 29WP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.87635 | 0.9 | 1.05 | Add 12 MVAR switched shunt at BEELER 3 115 kV
03ALL | ERIS | Voltage | BEELER 3 | 29WP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.87635 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | BEELER 3 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.87179 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | BEELER 3 | 29L | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.89881 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | BERG -MK7 | 29WP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.89092 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | BEVERLY7 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.88477 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | BEVERLY7 | 29WP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.89232 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | BEVERLY7 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.88232 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | BIGGULCH-MK7 | 29WP | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 0.85544 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | BOBCAT 7 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.91478 | 0.92 | 1.05 | None
03ALL | ERIS | Voltage | BREWSTR3 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.89575 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | BREWSTR3 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.89436 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | BUCKNER7 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.87141 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | CAMBRIG7 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.89904 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | CAMBRIG7 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.89543 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | CENTENNIAL3 | 26SP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.89448 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | CENTENNIAL3 | 29WP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.87421 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | CHADRON 7 | 29WP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.8685 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | CHARLSON-MK7 | 29WP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.884 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | CIMRRN 7 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.87303 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | CIMWD2 7 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.87222 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | CLIFTON3 | 26SP | V | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 |  |  |  |  | 0.89478 | 0.9 | 1.05 | Add 6 MVAR switched shunt at CLIFTON3 115 kV
03ALL | ERIS | Voltage | CLIFTON3 | 29SP | V | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 |  |  |  |  | 0.8918 | 0.9 | 1.05 | Add 6 MVAR switched shunt at CLIFTON3 115 kV
03ALL | ERIS | Voltage | COLBY 2 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.87704 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | COLBY 2 | 29WP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.89443 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | COLBY 2 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.87662 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | COLBY_PUMP3 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.86674 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | COLBY_PUMP3 | 29WP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.88552 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | COLBY_PUMP3 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.86754 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | COLE 2 | 29WP | V | Single 523101 BULL_CREEK3 115 523154 OCHILTREE3 115 1 |  |  |  |  | 1.0531 | 0.9 | 1.05 | Add 5 MVAR switched shunt at COLE 2 69 kV
03ALL | ERIS | Voltage | COVERT 3 | 29SP | V | P12:115:SUNC:RUSSELL-ELLSWORTHTAP:::HV: |  |  |  |  | 0.82951 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | COVERT 3 | 26SP | V | P12:115:SUNC:RUSSELL-ELLSWORTHTAP:::HV: |  |  |  |  | 0.88337 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | CRAWFRD7 | 29WP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.87921 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | DH_CS_EA-TS4 | 29WP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.86979 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | DIGHTON3 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.88593 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | DIGHTON3 | 29WP | V | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: |  |  |  |  | 0.89734 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | DIGHTON3 | 29SP | V | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: |  |  |  |  | 0.89332 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | DRYCREEK-BE4 | 29WP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.89046 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | DRYCREEK-BE7 | 29WP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.89351 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | EAGLEBE8 | 29WP | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 0.89045 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | ELLIS 2 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.85417 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | ELLIS 2 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.85417 | 0.9 | 1.05 | Add 0.04 MVAR switched shunt at ELLIS 2 69 kV
03ALL | ERIS | Voltage | ELLIS 2 | 29WP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.87372 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | ELLIS 2 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.86222 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | ELLIS 2 | 29L | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.89118 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | ELSWRTH7 | 29WP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.88584 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | FAITH 7 | 29WP | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 0.8841 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | FREEDOM7 | 29WP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.88586 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | G-2011-008-1 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.84852 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | G-2011-008-2 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.84912 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | G-2011-008-3 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.85332 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | G19-030-TAP | 26SP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.89627 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | G19-030-TAP | 26SP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.89627 | 0.9 | 1.05 | Add 7 MVAR switched shunt at G19-030-TAP 345 kV
03ALL | ERIS | Voltage | G19-030-TAP | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.83961 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | G20-011-SS1 | 29SP | V | P42:345:NPPD:BKR-AXT-3308:::: |  |  |  |  | 0.89193 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | G20-011-SS2 | 29SP | V | P42:345:NPPD:BKR-AXT-3308:::: |  |  |  |  | 0.89193 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | G20-011-SS3 | 29SP | V | P42:345:NPPD:BKR-AXT-3308:::: |  |  |  |  | 0.89193 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | G20-011-SS4 | 29SP | V | P42:345:NPPD:BKR-AXT-3308:::: |  |  |  |  | 0.89193 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | G21-068-TAP | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.86341 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | G22-015-TAP | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.7971 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | G22-015-TAP | 29WP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.78333 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | G22-015-TAP | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.78559 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | G22-015-TAP | 29L | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.84801 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | G22-015-TAP | 29L | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.84801 | 0.9 | 1.05 | Add 135 MVAR switched shunt at G22-015-TAP 345 kV
03ALL | ERIS | Voltage | G22-075-TAP | 29SP | V | System Intact |  |  |  |  | 0.94761 | 0.95 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | G22-075-TAP | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.88167 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | G24-016-TAP | 29SP | V | System Intact |  |  |  |  | 0.94027 | 0.95 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | G24-161-TAP | 29L | V | P12:345:OKGE-AEP:BKRBKR4291:::EHV: |  |  |  |  | 1.0927 | 0.92 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | G24-282-TAP | 29WP | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 0.88888 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | GANO 3 | 29WP | V | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: |  |  |  |  | 0.89401 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | GEM_SW 3 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.8674 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | GEM_SW 3 | 29WP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.88599 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | GEM_SW 3 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.86816 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | GEN-2011-008 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.84744 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | GEN-2017-011 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.91478 | 0.92 | 1.05 | None
03ALL | ERIS | Voltage | GEN-2017-097 | 29WP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.88868 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | GEN-2019-030 | 26SP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.89779 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | GEN-2019-030 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.84129 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | GEN-2019-058 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.84502 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | GEN-2020-008 | 29WP | V | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 |  |  |  |  | 0.88693 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | GEN-2020-011 | 29SP | V | P42:345:NPPD:BKR-AXT-3308:::: |  |  |  |  | 0.89193 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | GEN-2021-015 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.91478 | 0.92 | 1.05 | None
03ALL | ERIS | Voltage | GEN-2021-021 | 29WP | V | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 |  |  |  |  | 0.88693 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | GEN-2021-021 | 29WP | V | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 |  |  |  |  | 0.88693 | 0.9 | 1.05 | Add 66 MVAR switched shunt at GEN-2021-021 345 kV
03ALL | ERIS | Voltage | GEN-2021-068 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.86341 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | GEN-2021-069 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.86341 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | GEN-2021-070 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.86341 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | GEN-2021-076 | 29SP | V | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 |  |  |  |  | 0.89771 | 0.9 | 1.05 | Add 15 MVAR SVC at GEN-2021-076 345 kV
03ALL | ERIS | Voltage | GEN-2021-076 | 29SP | V | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 |  |  |  |  | 0.89771 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | GEN-2021-076 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.8885 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | GEN-2022-015 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.7971 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | GEN-2022-015 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.7971 | 0.9 | 1.05 | Add 248 MVAR switched shunt at GEN-2022-015 345 kV
03ALL | ERIS | Voltage | GEN-2022-015 | 29WP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.78333 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | GEN-2022-015 | 29WP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.78333 | 0.9 | 1.05 | Add 248 MVAR switched shunt at GEN-2022-015 345 kV
03ALL | ERIS | Voltage | GEN-2022-015 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.78559 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | GEN-2022-015 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.78559 | 0.9 | 1.05 | Add 248 MVAR switched shunt at GEN-2022-015 345 kV
03ALL | ERIS | Voltage | GEN-2022-015 | 29L | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.84801 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | GEN-2022-075 | 29SP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.89876 | 0.9 | 1.05 | Add 15 MVAR switched shunt at GEN-2022-075 345 kV
03ALL | ERIS | Voltage | GEN-2022-075 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.88167 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | GEN-2024-016 | 29SP | V | System Intact |  |  |  |  | 0.94027 | 0.95 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | GEN-2024-157 | 29L | V | P12:345:OKGE-AEP:BKRBKR4291:::EHV: |  |  |  |  | 1.0935 | 0.92 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | GEN-2024-157 | 29L | V | P12:345:OKGE-AEP:BKRBKR4291:::EHV: |  |  |  |  | 1.0935 | 0.92 | 1.05 | Add 0.9 MVAR switched shunt at GEN-2024-157 138 kV
03ALL | ERIS | Voltage | GEN-2024-161 | 29L | V | P12:345:OKGE-AEP:BKRBKR4291:::EHV: |  |  |  |  | 1.0927 | 0.92 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | GEN-2024-189 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.85582 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | GEN-2024-193 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.88915 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | GEN-2024-205 | 26SP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.87044 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | GEN-2024-205 | 29SP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.87842 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | GEN-2024-205 | 29WP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.84611 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | GEN-2024-282 | 29WP | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 0.88945 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | GEN-2024-283 | 29WP | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 0.88966 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | GORDON 7 | 29WP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.87553 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | GOVE 3 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.85964 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | GOVE 3 | 29WP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.87694 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | GOVE 3 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.86465 | 0.9 | 1.05 | Add 30 MVAR switched shunt at GOVE 3 115 kV
03ALL | ERIS | Voltage | GOVE 3 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.86465 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | GOVE 3 | 29L | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.89795 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | GR ISLD-LNX3 | 29SP | V | System Intact |  |  |  |  | 0.94872 | 0.95 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | GR ISLD3 | 29SP | V | System Intact |  |  |  |  | 0.94865 | 0.95 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | GRANT 3 | 29WP | V | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: |  |  |  |  | 0.89473 | 0.9 | 1.05 | Add 2.3 MVAR switched shunt at GRANT 3 115 kV
03ALL | ERIS | Voltage | GRANTTP3 | 29WP | V | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: |  |  |  |  | 0.89492 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | GRINNEL3 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.85521 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | GRINNEL3 | 29WP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.87346 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | GRINNEL3 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.85856 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | GRINNEL3 | 29L | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.89793 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | HARBNGR3 | 29WP | V | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 |  |  |  |  | 0.89104 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | HARBNGR7 | 29WP | V | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 |  |  |  |  | 0.88694 | 0.9 | 1.05 | Add 0.8 MVAR switched shunt at HARBNGR7 345 kV
03ALL | ERIS | Voltage | HARBNGR7 | 29WP | V | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 |  |  |  |  | 0.88694 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | HARDESTY 2 | 29WP | V | Single 523101 BULL_CREEK3 115 523154 OCHILTREE3 115 1 |  |  |  |  | 1.0518 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | HERNDON3 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.8888 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | HERNDON3 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.89641 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | HOXIE 3 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.87441 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | HOXIE 3 | 29WP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.89703 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | HOXIE 3 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.88007 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | HUNTSVL3 | 26SP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.851 | 0.9 | 1.05 | Add 45 MVAR switched shunt at HUNTSVL3 115 kV
03ALL | ERIS | Voltage | HUNTSVL3 | 26SP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.851 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | HUNTSVL3 | 29SP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.86365 | 0.9 | 1.05 | Add 45 MVAR switched shunt at HUNTSVL3 115 kV
03ALL | ERIS | Voltage | HUNTSVL3 | 29SP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.86365 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | HUNTSVL3 | 29WP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.82217 | 0.9 | 1.05 | Add 45 MVAR switched shunt at HUNTSVL3 115 kV
03ALL | ERIS | Voltage | HUNTSVL3 | 29WP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.82217 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | IRONSTAR7 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.8522 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | IRONWOOD WF7 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.84996 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | IRONWOOD7 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.84896 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | IRS7 115 KV | 26SP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.89636 | 0.9 | 1.05 | Add 8 MVAR switched shunt at IRS7 115 KV 115 kV
03ALL | ERIS | Voltage | IRS7 115 KV | 26SP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.89636 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | IRS7 115 KV | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.85033 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | J12_____-MK7 | 29WP | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 0.84448 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | JAGGER 3 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.88659 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | JAGGER 3 | 29WP | V | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: |  |  |  |  | 0.89775 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | JAGGER 3 | 29SP | V | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: |  |  |  |  | 0.89398 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | JOHNSON3 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.89068 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | JOHNSON3 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.89919 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | KEENE -MK7 | 29WP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.88741 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | KEENECRN-MK7 | 29WP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.88348 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | KNOLL N 6 | 29SP | V | System Intact |  |  |  |  | 0.94863 | 0.95 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | KNOLL S 6 | 29SP | V | System Intact |  |  |  |  | 0.94863 | 0.95 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | L11_____-MK7 | 29WP | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 0.85838 | 0.9 | 1.05 | Add 5 MVAR switched shunt at L11_____-MK7 115 kV
03ALL | ERIS | Voltage | LARNED3 | 26SP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.83259 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | LARNED3 | 26SP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.83259 | 0.9 | 1.05 | Add 21 MVAR switched shunt at LARNED3 115 kV
03ALL | ERIS | Voltage | LARNED3 | 29SP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.83039 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | LARNED3 | 29SP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.83039 | 0.9 | 1.05 | Add 21 MVAR switched shunt at LARNED3 115 kV
03ALL | ERIS | Voltage | LARNED3 | 29WP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.83508 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | LEOTI 3 | 26SP | V | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: |  |  |  |  | 0.89453 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | LUDELL 3 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.88972 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | LUDELL 3 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.89622 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | LUDELLT3 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.88972 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | LUDELLT3 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.89622 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | MACON 3 | 29SP | V | System Intact |  |  |  |  | 0.93487 | 0.95 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | MACON 3 | 29SP | V | System Intact |  |  |  |  | 0.93487 | 0.95 | 1.05 | Add 50 MVAR switched shunt at MACON 3 345 kV
03ALL | ERIS | Voltage | MANNGT 3 | 26SP | V | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: |  |  |  |  | 0.89218 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | MANNGT 3 | 29SP | V | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: |  |  |  |  | 0.89861 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | MANNGT 3 | 29WP | V | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: |  |  |  |  | 0.89844 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | MANNING3 | 26SP | V | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: |  |  |  |  | 0.89114 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | MANNING3 | 29SP | V | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: |  |  |  |  | 0.89757 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | MANNING3 | 29WP | V | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: |  |  |  |  | 0.89783 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | MAURINE4 | 29WP | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 0.87794 | 0.9 | 1.05 | Add 314 MVAR SVC at MAURINE4 230 kV
03ALL | ERIS | Voltage | MAURINE8 | 29WP | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 0.86488 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | MCCOOK 7 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.86435 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | MCCOOK 7 | 29WP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.86084 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | MCCOOK 7 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.86511 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | MED-LDG3 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.86943 | 0.9 | 1.05 | Add 20 MVAR switched shunt at MED-LDG3 115 kV
03ALL | ERIS | Voltage | MED-LDG3 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.86943 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | MINGO 7 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.84093 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | MINGO 7 | 29WP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.83446 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | MINGO 7 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.83498 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | MINGO 7 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.83498 | 0.9 | 1.05 | Add 20 MVAR switched shunt at MINGO 7 345 kV
03ALL | ERIS | Voltage | MINGO 7 | 29L | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.88884 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | MOCCASIN-MK7 | 29WP | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 0.83173 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | MOCCASIN-MK7 | 29WP | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 0.83173 | 0.9 | 1.05 | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV
03ALL | ERIS | Voltage | MOUNTAIN-MK7 | 29WP | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 0.86817 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | NATWOOD3 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.89048 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | NATWOOD3 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.89656 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | NESCTY 3 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.86272 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | NESCTY 3 | 29WP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.87508 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | NESCTY 3 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.87159 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | NESCTY 3 | 29L | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.89118 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | NESSCTY3 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.86265 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | NESSCTY3 | 29WP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.87503 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | NESSCTY3 | 29WP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.87503 | 0.9 | 1.05 | Add 24 MVAR switched shunt at NESSCTY3 115 kV
03ALL | ERIS | Voltage | NESSCTY3 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.87152 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | NESSCTY3 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.87152 | 0.9 | 1.05 | Add 24 MVAR switched shunt at NESSCTY3 115 kV
03ALL | ERIS | Voltage | NESSCTY3 | 29L | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.89116 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | NEWELL 7 | 29WP | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 0.87021 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | NRTHFORK-MK7 | 29WP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.88507 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | NUNDRWD-LNX3 | 29WP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.88531 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | NUNDRWD4 | 29WP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.88527 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | OAKDALE -MK7 | 29WP | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 0.88525 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | OBER T 3 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.89179 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | OBERLIN3 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.89162 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | PAULINE3 | 29SP | V | System Intact |  |  |  |  | 0.9373 | 0.95 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | PAWN-ED3 | 26SP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.84452 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | PAWN-ED3 | 29SP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.84251 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | PAWN-ED3 | 29WP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.83653 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | PH RUN 3 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.85382 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | PH RUN 3 | 29WP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.87231 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | PH RUN 3 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.85635 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | PH RUN 3 | 29L | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.89832 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | PILE 3 | 26SP | V | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: |  |  |  |  | 0.88925 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | PILE 3 | 29WP | V | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: |  |  |  |  | 0.88453 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | PILE 3 | 29SP | V | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: |  |  |  |  | 0.89858 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | POSTROCK6 | 29SP | V | System Intact |  |  |  |  | 0.94858 | 0.95 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | POSTROCK7 | 29SP | V | System Intact |  |  |  |  | 0.94227 | 0.95 | 1.05 | Add 210 MVAR SVC at POSTROCK7 345 kV
03ALL | ERIS | Voltage | POSTROCK7 | 29SP | V | System Intact |  |  |  |  | 0.94227 | 0.95 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | POSTROCK7 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.8885 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | POWELL CNR 2 | 29WP | V | Single 788378 ASGI-2024-00 115 788379 A24-06-MPT1 34 788382 'A24-06-TERTI' 13 1 |  |  |  |  | 1.0502 | 0.9 | 1.05 | Add 2 MVAR switched shunt at POWELL CNR 2 69 kV
03ALL | ERIS | Voltage | PRATTENERGY3 | 26SP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.88496 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | PRATTENERGY3 | 29SP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.89103 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | PRATTENERGY3 | 29WP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.86658 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | PRICHRD3 | 26SP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.87707 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | PRICHRD3 | 29SP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.88394 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | PRICHRD3 | 29WP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.856 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | RANSOM 2 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.86137 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | RANSOM 2 | 29WP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.87798 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | RANSOM 2 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.86933 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | RANSOM 2 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.86933 | 0.9 | 1.05 | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV
03ALL | ERIS | Voltage | RANSOM 2 | 29L | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.89347 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | RANSOM 3 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.8621 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | RANSOM 3 | 29WP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.87694 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | RANSOM 3 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.86983 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | RANSOM 3 | 29L | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.8938 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | RAPIDCTY-RM8 | 29WP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.89168 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | RCDC.DUM-BE4 | 29WP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.86672 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | RCDC.E__-BE4 | 29WP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.89048 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | REDHLSW4 | 29L | V | P12:345:OKGE-AEP:BKRBKR4291:::EHV: |  |  |  |  | 1.0705 | 0.9 | 1.05 | Add 6 MVAR switched shunt at REDHLSW4 138 kV
03ALL | ERIS | Voltage | REDHLSW4 | 29L | V | P12:345:OKGE-AEP:BKRBKR4291:::EHV: |  |  |  |  | 1.0705 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | REDWILO3 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.79444 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | REDWILO3 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.79444 | 0.9 | 1.05 | Add 203 MVAR switched shunt at REDWILO3 345 kV
03ALL | ERIS | Voltage | REDWILO3 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.80726 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | REDWILO3 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.80726 | 0.9 | 1.05 | Add 203 MVAR switched shunt at REDWILO3 345 kV
03ALL | ERIS | Voltage | REDWILO3 | 29WP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.79789 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | REDWILO3 | 29WP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.79789 | 0.9 | 1.05 | Add 203 MVAR switched shunt at REDWILO3 345 kV
03ALL | ERIS | Voltage | REDWILO3 | 29L | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.85162 | 0.9 | 1.05 | Add 203 MVAR switched shunt at REDWILO3 345 kV
03ALL | ERIS | Voltage | REDWILO3 | 29L | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.85162 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | REDWILO7 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.8618 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | REDWILO7 | 29WP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.85855 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | REDWILO7 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.85528 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | RKY_RDG4 | 29L | V | GEN-2024-102_POI_531449_Generator_outage |  |  |  |  | 1.0966 | 0.92 | 1.05 | Add 0.5 MVAR switched shunt at RKY_RDG4 138 kV
03ALL | ERIS | Voltage | RKY_RDG4 | 29L | V | GEN-2024-102_POI_531449_Generator_outage |  |  |  |  | 1.0966 | 0.92 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | RUSHMORE-RM7 | 29WP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.89389 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | RUSHMORE-RM8 | 29WP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.89966 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | RUSHVIL7 | 29WP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.86566 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | RUSLSOL3 | 29SP | V | P12:115:SUNC:RUSSELL-ELLSWORTHTAP:::HV: |  |  |  |  | 0.7704 | 0.9 | 1.05 | Add 21 MVAR switched shunt at RUSLSOL3 115 kV
03ALL | ERIS | Voltage | RUSLSOL3 | 26SP | V | P12:115:SUNC:RUSSELL-ELLSWORTHTAP:::HV: |  |  |  |  | 0.84238 | 0.9 | 1.05 | Add 21 MVAR switched shunt at RUSLSOL3 115 kV
03ALL | ERIS | Voltage | RUSSELL3 | 29SP | V | P12:115:SUNC:RUSSELL-ELLSWORTHTAP:::HV: |  |  |  |  | 0.7704 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | RUSSELL3 | 26SP | V | P12:115:SUNC:RUSSELL-ELLSWORTHTAP:::HV: |  |  |  |  | 0.84238 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | RVROAD 3 | 26SP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.89345 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | RVROAD 3 | 29SP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.8994 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | RVROAD 3 | 29WP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.8749 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | SADDLE7 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.84968 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | SADLHRN3 | 26SP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.84797 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | SADLHRN3 | 26SP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.84797 | 0.9 | 1.05 | Add 63 MVAR switched shunt at SADLHRN3 115 kV
03ALL | ERIS | Voltage | SADLHRN3 | 29SP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.85719 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | SADLHRN3 | 29SP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.85719 | 0.9 | 1.05 | Add 63 MVAR switched shunt at SADLHRN3 115 kV
03ALL | ERIS | Voltage | SADLHRN3 | 29WP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.82017 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | SADLHRN3 | 29WP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.82017 | 0.9 | 1.05 | Add 63 MVAR switched shunt at SADLHRN3 115 kV
03ALL | ERIS | Voltage | SANDCREK-MK7 | 29WP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.88288 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | SD.LS-KS-MB3 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.89339 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | SD.LS-LR-MB3 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.89339 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | SD.LS-LR-MB3 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.89339 | 0.9 | 1.05 | Add 525 MVAR SVC at SD.LS-LR-MB3 345 kV
03ALL | ERIS | Voltage | SEGNTP 3 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.86924 | 0.9 | 1.05 | Add 40 MVAR switched shunt at SEGNTP 3 115 kV
03ALL | ERIS | Voltage | SEGNTP 3 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.86924 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | SEGNTP 3 | 29WP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.88988 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | SEGNTP 3 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.87308 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | SEGUIN 3 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.86538 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | SEGUIN 3 | 29WP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.88572 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | SEGUIN 3 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.86899 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | SELKIRK3 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.8937 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | SEWARD 3 | 29WP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.89492 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | SHANNON -RM7 | 29WP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.89096 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | SIDNEY__-MB3 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.89339 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | SLKHILLS 4 | 29L | V | P12:345:OKGE:BKRBKR4890:::EHV: |  |  |  |  | 1.092 | 0.9 | 1.05 | Add 5 MVAR switched shunt at SLKHILLS 4 138 kV
03ALL | ERIS | Voltage | SNDCRKTP-MK7 | 29WP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.88389 | 0.9 | 1.05 | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV
03ALL | ERIS | Voltage | SPERVIL7 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.8498 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | SPRVL 3 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.87056 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | ST-JOHN3 | 26SP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.86964 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | ST-JOHN3 | 29SP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.87766 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | ST-JOHN3 | 29WP | V | Single 539649 SAWYER3 115 539760 BARBER3 115 1 |  |  |  |  | 0.84522 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | STEGALL 4 | 29WP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.86979 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | STEGALL-LNX3 | 29WP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.86979 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | STEGALL_-MB4 | 29WP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.8794 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | STOCKVL7 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.89088 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | STOCKVL7 | 29WP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.89715 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | STOCKVL7 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.88416 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | SULPHUR | 29WP | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 0.86632 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | SUNCITY3 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.88289 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | SWENSON -MK7 | 29WP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.88445 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | TABLEBUT-MK7 | 29WP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.88851 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | TRANSFORMER | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.84502 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | TRIB SW3 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.89906 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | TRIBUNE3 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.89963 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | VICTRYH4 | 29WP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.86956 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | WALDO 3 | 29SP | V | P12:115:SUNC:RUSSELL-ELLSWORTHTAP:::HV: |  |  |  |  | 0.80842 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | WALDO 3 | 26SP | V | P12:115:SUNC:RUSSELL-ELLSWORTHTAP:::HV: |  |  |  |  | 0.86868 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | WALKMYR3 | 29WP | V | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 |  |  |  |  | 0.89392 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | WAYSIDE 4 | 26SP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.87328 | 0.9 | 1.05 | Add 60 MVAR switched shunt at WAYSIDE 4 230 kV
03ALL | ERIS | Voltage | WAYSIDE 4 | 29SP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.89075 | 0.9 | 1.05 | Add 60 MVAR switched shunt at WAYSIDE 4 230 kV
03ALL | ERIS | Voltage | WAYSIDE 4 | 29WP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.74736 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | WAYSIDE 7 | 29WP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.84537 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | WESTPLN7 | 29WP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.85151 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | WHARV4 | 26SP | V | Single 533011 HALSTD4 138 533056 WHARV4 138 1 |  |  |  |  | 1.1271 | 0.93 | 1.05 | Add 54 MVAR SVC at WHARV4 138 kV
03ALL | ERIS | Voltage | WHARV4 | 29WP | V | Single 533011 HALSTD4 138 533056 WHARV4 138 1 |  |  |  |  | 1.1375 | 0.93 | 1.05 | Add 54 MVAR SVC at WHARV4 138 kV
03ALL | ERIS | Voltage | WICKSVL7 | 29WP | V | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: |  |  |  |  | 0.89917 | 0.9 | 1.05 | None
03ALL | ERIS | Voltage | WILCRKXFRP 3 | 29WP | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 0.86634 | 0.9 | 1.05 | Mitigated at another bus
03NR | NRIS | Voltage | BOBCAT.C 3 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE SIDNEY__-MB3-STEGALL_-MB3-1 :EHV: |  |  |  |  | 1.1385 | 0.9 | 1.05 | Mitigated at another bus
03NR | NRIS | Voltage | DRYCREEK-BE4 | 29L | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 1.0742 | 0.9 | 1.05 | Mitigated at another bus
03NR | NRIS | Voltage | DRYCREEK-BE7 | 29L | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 1.0727 | 0.9 | 1.05 | Mitigated at another bus
03NR | NRIS | Voltage | ELKCRK 7 | 29L | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 1.0689 | 0.9 | 1.05 | Mitigated at another bus
03NR | NRIS | Voltage | ELSWRTH7 | 29L | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 1.0691 | 0.9 | 1.05 | Mitigated at another bus
03NR | NRIS | Voltage | FREEDOM7 | 29L | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 1.0695 | 0.9 | 1.05 | Mitigated at another bus
03NR | NRIS | Voltage | GEN-2017-097 | 29L | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 1.0725 | 0.9 | 1.05 | Mitigated at another bus
03NR | NRIS | Voltage | GEN-2024-374 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE SIDNEY__-MB3-STEGALL_-MB3-1 :EHV: |  |  |  |  | 1.1385 | 0.9 | 1.05 | Mitigated at another bus
03NR | NRIS | Voltage | NUNDRWD-LNX3 | 29L | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 1.0833 | 0.9 | 1.05 | Mitigated at another bus
03NR | NRIS | Voltage | NUNDRWD4 | 29L | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 1.0835 | 0.9 | 1.05 | Mitigated at another bus
03NR | NRIS | Voltage | RAPIDCTY-RM8 | 29L | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 1.0698 | 0.9 | 1.05 | Mitigated at another bus
03NR | NRIS | Voltage | RCDC.DUM-BE4 | 29L | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 1.0741 | 0.9 | 1.05 | Mitigated at another bus
03NR | NRIS | Voltage | RCDC.E__-BE4 | 29L | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 1.0742 | 0.9 | 1.05 | Mitigated at another bus
03NR | NRIS | Voltage | RUSHMORE-RM7 | 29L | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 1.074 | 0.9 | 1.05 | Mitigated at another bus
03NR | NRIS | Voltage | RUSHMORE-RM8 | 29L | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 1.0913 | 0.9 | 1.05 | Mitigated at another bus
03NR | NRIS | Voltage | SCOTBLF 7 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE SIDNEY__-MB3-STEGALL_-MB3-1 :EHV: |  |  |  |  | 1.0796 | 0.9 | 1.05 | Mitigated at another bus
03NR | NRIS | Voltage | STEGALL 4 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE SIDNEY__-MB3-STEGALL_-MB3-1 :EHV: |  |  |  |  | 1.1246 | 0.9 | 1.05 | Mitigated at another bus
03NR | NRIS | Voltage | STEGALL-LNX3 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE SIDNEY__-MB3-STEGALL_-MB3-1 :EHV: |  |  |  |  | 1.1246 | 0.9 | 1.05 | Mitigated at another bus
03NR | NRIS | Voltage | STEGALL_-MB3 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE SIDNEY__-MB3-STEGALL_-MB3-1 :EHV: |  |  |  |  | 1.1385 | 0.9 | 1.05 | Add 78 MVAR SVC at STEGALL_-MB3 345 kV
03NR | NRIS | Voltage | STEGALL_-MB3 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE SIDNEY__-MB3-STEGALL_-MB3-1 :EHV: |  |  |  |  | 1.1385 | 0.9 | 1.05 | Mitigated at another bus
03NR | NRIS | Voltage | STEGALL_-MB4 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE SIDNEY__-MB3-STEGALL_-MB3-1 :EHV: |  |  |  |  | 1.1274 | 0.9 | 1.05 | Mitigated at another bus
03NR | NRIS | Voltage | STEGALL_-MB4 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE SIDNEY__-MB3-STEGALL_-MB3-1 :EHV: |  |  |  |  | 1.1274 | 0.9 | 1.05 | Add 0.7 MVAR switched shunt at STEGALL_-MB4 230 kV
03NR | NRIS | Voltage | UNDERWOOD 2 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE SIDNEY__-MB3-STEGALL_-MB3-1 :EHV: |  |  |  |  | 1.1391 | 0.9 | 1.05 | Mitigated at another bus
03NR | NRIS | Voltage | UNDERWOOD 2 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE SIDNEY__-MB3-STEGALL_-MB3-1 :EHV: |  |  |  |  | 1.1391 | 0.9 | 1.05 | Add 16 MVAR switched shunt at UNDERWOOD 2 345 kV
03NR | NRIS | Voltage | VICTRYH4 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE SIDNEY__-MB3-STEGALL_-MB3-1 :EHV: |  |  |  |  | 1.1062 | 0.9 | 1.05 | Mitigated at another bus
03NR | NRIS | Voltage | VICTRYH7 | 29L | V | P12:345.0:UMZ:# N-1 #:: LINE SIDNEY__-MB3-STEGALL_-MB3-1 :EHV: |  |  |  |  | 1.0947 | 0.9 | 1.05 | Mitigated at another bus
03NR | NRIS | Voltage | WALL 7 | 29L | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 1.0701 | 0.9 | 1.05 | Mitigated at another bus
03NR | NRIS | Voltage | WICKSVL7 | 29L | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 1.0715 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | 12&CLAY3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86975 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | 15THSTRT | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89681 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | 15THSTRT | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92218 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | 166TH 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90956 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | 17&FAIR3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87065 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | 19THST 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87004 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | 19THST 3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92948 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | 24-FREY3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89971 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | 27CROCO3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86905 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | 29 GAGE3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87015 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | 29EVENG3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87035 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | 2MADISN3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86958 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | 2WEIRGAT | 29WP | V | P23:345:EES::7ROCKYCRK%:1:EHV: |  |  |  |  | 0.90294 | 0.92 | 1.05 | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
04ALL | ERIS | Voltage | 2WEIRGAT | 29SP | V | P23:345:EES::7ROCKYCRK%:1:EHV: |  |  |  |  | 0.90323 | 0.92 | 1.05 | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
04ALL | ERIS | Voltage | 2WEIRGAT | 26SP | V | Single 509241 CROCKET7 345 783930 G24-232-TAP 345 1 |  |  |  |  | 0.91741 | 0.92 | 1.05 | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
04ALL | ERIS | Voltage | 41CALIF3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86789 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | 4CORNER3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8539 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | 4CORNER3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89125 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | 4VAN 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87015 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | 4VAN N 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87017 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | 4VAN S 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87013 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | 54&MERI3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89135 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | 6 GOLDN3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86922 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | 6TH ST 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87401 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | 87TH 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89058 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | 87TH 7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89348 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | 87TH 7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.93569 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | ADRIAN 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92353 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | AEC 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88667 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | AFTN-EX2 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.91138 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | AFTN-EX2 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.91138 | 0.92 | 1.05 | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV
04ALL | ERIS | Voltage | AFTON 5 | 29WP | V | System Intact |  |  |  |  | 0.93642 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | AFTON 5 | 26SP | V | System Intact |  |  |  |  | 0.9468 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | AFTONTP2 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.91283 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | AIRPORT2 | 26SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.89571 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | AIRPORT2 | 29SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.88538 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | AIRPORT2 | 29WP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.89288 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ALTAMNS2 | 29WP | V | Single 532793 NEOSHO7 345 533023 N34534 138 533801 'N345 2 1 ' 13 2 |  |  |  |  | 0.88805 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ALTAMNS2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87527 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ALTAMNS2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87406 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ALTAMNT2 | 29WP | V | Single 532793 NEOSHO7 345 533023 N34534 138 533801 'N345 2 1 ' 13 2 |  |  |  |  | 0.88492 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ALTAMNT2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.86813 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ALTAMNT2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.86684 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ALTOONA4 | 29WP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.90125 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ALTOONA4 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88812 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ALTOONA4 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88283 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ALXNDR 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.82824 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ALXNDR 3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89313 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | AMELIA 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92247 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | AMOCO 2 | 26SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.89508 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | AMOCO 2 | 29SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.88463 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | AMOCO 2 | 29WP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.89209 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | AMOCO 3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85684 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | AMOCO 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.84172 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | AMOCOTP2 | 26SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.89566 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | AMOCOTP2 | 29SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.88521 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | AMOCOTP2 | 29WP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.89267 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | AND322 2 | 26SP | V | 267142 |  |  |  |  | 1.0502 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ANGELUS | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.84552 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ANGUS 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.83565 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | ANTIOCH5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88297 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | ANTIOCH5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90833 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | ANZIO 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8993 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | ARC250 2 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.92118 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ARC250 2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90644 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ARC250 2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90109 | 0.925 | 1.05 | None
04ALL | ERIS | Voltage | ARKLIN2 | 29WP | V | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: |  |  |  |  | 0.89123 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ARNOLD3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.81496 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ARNOLD3 | 26SP | V | P23:345:SUNC:SB_BRK482:::EHV: |  |  |  |  | 0.86907 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ASG-2018-010 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90828 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | ASG-2018-011 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90919 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | ASG-2018-011 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91864 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | ASPEN 4 | 29L | V | Single 520462 ASPEN4 138 520999 MOORLND4 138 1 |  |  |  |  | 1.0706 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ATL109 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.90919 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ATL109 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92062 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ATLNTIC3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91806 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | ATLNTIC3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87435 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | ATLNTIC7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90703 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ATLNTIC7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86822 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ATWODSW3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.89745 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | AUBURN 6 | 29WP | V | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: |  |  |  |  | 0.92529 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | AUBURN 6 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90689 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | AUBURN 6 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8446 | 0.95 | 1.05 | Add 80 MVAR SVC at AUBURN 6 230 kV
04ALL | ERIS | Voltage | AUBURN 6 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8446 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | AUR124 5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.8847 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | AUR124 5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.8847 | 0.925 | 1.05 | Add 28 MVAR switched shunt at AUR124 5 161 kV
04ALL | ERIS | Voltage | AUR124 5 | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.88989 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | AUR124 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89687 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | AUR124 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89687 | 0.925 | 1.05 | Add 28 MVAR switched shunt at AUR124 5 161 kV
04ALL | ERIS | Voltage | AVOCA 5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.88015 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | AVOCA 5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.88015 | 0.92 | 1.05 | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV
04ALL | ERIS | Voltage | AVOCA 5 | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.89676 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | AVOCA_2 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.90272 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | AVOCA_2 | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.91976 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | AVONDAL5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91318 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | AXTELL 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85808 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | AXTELL 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85808 | 0.9 | 1.05 | Add 62 MVAR switched shunt at AXTELL 3 345 kV
04ALL | ERIS | Voltage | BALDCRK3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87263 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BARBER 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89962 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | BARRY 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91823 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BARRY_CAP 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91923 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BAX488 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.89091 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BAX488 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.89091 | 0.925 | 1.05 | Add 22 MVAR switched shunt at BAX488 5 161 kV
04ALL | ERIS | Voltage | BAX488 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90914 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BAX488 5 | 29SP | V | Single 547469 RIV4525 161 547729 BAX4885 161 1 |  |  |  |  | 0.91875 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BDH509_2 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.90297 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BDH509_2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91987 | 0.925 | 1.05 | None
04ALL | ERIS | Voltage | BDH509_2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.9208 | 0.925 | 1.05 | None
04ALL | ERIS | Voltage | BEARCAT4 | 29L | V | Single 520462 ASPEN4 138 520500 BEARCAT4 138 1 |  |  |  |  | 1.0725 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BEARCRK3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8988 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BEARCRK3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8644 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | BEECRK4 | 29WP | V | P23:345:WERE:N345-345-20:EHV: |  |  |  |  | 0.89489 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BEECRK4 | 29WP | V | P23:345:WERE:N345-345-20:EHV: |  |  |  |  | 0.89489 | 0.93 | 1.05 | Add 0.02 MVAR switched shunt at BEECRK4 138 kV
04ALL | ERIS | Voltage | BEECRK4 | 26SP | V | P23:345:WERE:N345-345-20:EHV: |  |  |  |  | 0.90532 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BEECRK4 | 29SP | V | P23:345:WERE:N345-345-20:EHV: |  |  |  |  | 0.91283 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BEELER 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86475 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BELTONS5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90741 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BELTONS5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92898 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BEMIS 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.81708 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | BEN279_5 | 29WP | V | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: |  |  |  |  | 0.89301 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BENTLEY4 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91075 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BENTLEY4 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90146 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BENTNVL2 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.89473 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BENTVJ_5 | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.91652 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BENTVJ_5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.8894 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BENT_SL5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.88979 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BENT_SL5 | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.91698 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BERG -MK7 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.89668 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BERG 3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90942 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BERG 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86982 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BIG BOW 3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87297 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BIG BOW 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.83948 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | BIGGULCH-MK7 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.87624 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BIGPINEY2 | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.91956 | 0.92 | 1.05 | Add 2 MVAR switched shunt at BIGPINEY2 69 kV
04ALL | ERIS | Voltage | BIGPINEY2 | 29WP | V | P23:500:EES-EAI:KEO:B4921::EHV: |  |  |  |  | 0.90552 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BIRDHOL4 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.89393 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BIRDHOL4 | 26SP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.91873 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BISMARK3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87395 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BLSPE 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91416 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BLSPS 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91573 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BLSPW 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91023 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BLUEMLS2 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.9052 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BLUEVLY5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91299 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BLUMILS5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90976 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BLUVLY-161 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90619 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BNSF 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89404 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BNSF 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92727 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BOL431 5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.89577 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BOL431 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89346 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BOL431 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89609 | 0.925 | 1.05 | None
04ALL | ERIS | Voltage | BONITA 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88257 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BONITA 3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91927 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BRANTLEY4 | 29L | V | Single 520462 ASPEN4 138 520500 BEARCAT4 138 1 |  |  |  |  | 1.0756 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BREWSTR3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.87271 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BRKRIDG5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87424 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BRKRIDG5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90862 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BRMGHAM5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91368 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BRN331 5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.88997 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BRN331 5 | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.9007 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BRN331 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90987 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BRN412 5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.89013 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BRN412 5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.89013 | 0.925 | 1.05 | Add 0.02 MVAR switched shunt at BRN412 5 161 kV
04ALL | ERIS | Voltage | BRN412 5 | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.90081 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BRN412 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90996 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BRN413 5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.89252 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BRN413 5 | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.90517 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BRN413 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91325 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BRUSHCRK_5 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.88895 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BTLRJCT2 | 29L | V | Single 520462 ASPEN4 138 520500 BEARCAT4 138 1 |  |  |  |  | 1.0704 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BUCKEYE_230 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.76006 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BUCKEYE_230 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.83976 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BUCYRUS5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89668 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BUCYRUS5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91321 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BUFFALO2 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.9281 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BUFFALO2 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91634 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BUFFALO4 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.916 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BUFFALO4 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.9004 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BUFFALO7 | 29WP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.92656 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BUFFALO7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8944 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BUFFALO7 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91261 | 0.95 | 1.05 | Add 160 MVAR SVC at BUFFALO7 345 kV
04ALL | ERIS | Voltage | BUFFALO7 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91261 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BUFORD 5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.91018 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BULL SH W5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.90261 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BULL SH5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.90219 | 0.92 | 1.05 | Add 176 MVAR SVC at BULL SH5 161 kV
04ALL | ERIS | Voltage | BULL SH5 | 26SP | V | Single 338814 5SOUTHLAND# 161 505448 NORFORK5 161 1 |  |  |  |  | 0.91479 | 0.92 | 1.05 | Add 176 MVAR SVC at BULL SH5 161 kV
04ALL | ERIS | Voltage | BUNKRDG5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89536 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BUNKRDG5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92336 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BUNKRHL3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88435 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | BURNS 7 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88906 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BURNS 7 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88906 | 0.95 | 1.05 | Add 88 MVAR SVC at BURNS 7 345 kV
04ALL | ERIS | Voltage | BURNS 7 | 29WP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.88983 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BURNS 7 | 29WP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.88983 | 0.95 | 1.05 | Add 88 MVAR SVC at BURNS 7 345 kV
04ALL | ERIS | Voltage | BURNS 7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85233 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BURNS 7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85233 | 0.95 | 1.05 | Add 88 MVAR SVC at BURNS 7 345 kV
04ALL | ERIS | Voltage | BUTLER 2 | 29L | V | Single 520462 ASPEN4 138 520500 BEARCAT4 138 1 |  |  |  |  | 1.0683 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CANEYRV7 | 29WP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.91091 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CANEYRV7 | 26SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.90891 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CANEYRV7 | 26SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.90891 | 0.95 | 1.05 | Add 26 MVAR SVC at CANEYRV7 345 kV
04ALL | ERIS | Voltage | CANEYRV7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90227 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CANEYWF7 | 26SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.90902 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CANEYWF7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90238 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CAR395 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.90737 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CAR395 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91418 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CAR395 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92404 | 0.925 | 1.05 | None
04ALL | ERIS | Voltage | CARACARA2 | 26SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.91212 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CARACARA2 | 29SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.9106 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CARB-KW 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85527 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CARB-KW 3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90148 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CAREY 2 | 26SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.89771 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CAREY 2 | 29SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.88911 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CAREY 2 | 29WP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.89711 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CARLEYRD 5 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.89688 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CAROSEL3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92717 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CARTHAG5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.90258 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CARTHAG5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91062 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CEDAR ST | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.83168 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | CEDARBLF_230 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.78718 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CEDARBLF_230 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86155 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | CEDARNL5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90021 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CEDRCRK5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88348 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CEDRCRK5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92013 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CENTENL5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90795 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CENTENL5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90568 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CENTERPT2 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.90903 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CENTRTN5 | 29WP | V | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: |  |  |  |  | 0.89095 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CENTRTN5 | 26SP | V | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: |  |  |  |  | 0.91883 | 0.92 | 1.05 | Add 0.03 MVAR switched shunt at CENTRTN5 161 kV
04ALL | ERIS | Voltage | CHAMSPR5 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.8951 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CHAMSPR7 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.88146 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CHAMSPR7 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.88146 | 0.92 | 1.05 | Add 37 MVAR switched shunt at CHAMSPR7 345 kV
04ALL | ERIS | Voltage | CHARGER3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90619 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CHARLOT5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90977 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CHARLSON-MK7 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.88988 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CHASE 3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.85659 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CHETOLAH3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.83222 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | CHILD4WT | 26SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.8603 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CHILD4WT | 26SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.8603 | 0.92 | 1.05 | Add 16 MVAR switched shunt at CHILD4WT 138 kV
04ALL | ERIS | Voltage | CHILD4WT | 29WP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.8524 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CHILD4WT | 29WP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.8524 | 0.92 | 1.05 | Add 16 MVAR switched shunt at CHILD4WT 138 kV
04ALL | ERIS | Voltage | CHILD4WT | 29SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.84672 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CHILD4WT | 29SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.84672 | 0.92 | 1.05 | Add 16 MVAR switched shunt at CHILD4WT 138 kV
04ALL | ERIS | Voltage | CHOUTEU5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91486 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CIRCLE 6 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92856 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | CIRRUS7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87136 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | CJ 366 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.91362 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CJ 366 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92247 | 0.925 | 1.05 | None
04ALL | ERIS | Voltage | CKSFORD3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88922 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CLARREC2 | 26SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.91949 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CLAYCM15 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91257 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CLAYCSS3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87768 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CLAYCTR3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88037 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CLAYGEN3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87769 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CLEARVW3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CLEARVW3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92428 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CLIFTON3 | 29SP | V | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 |  |  |  |  | 0.89841 | 0.9 | 1.05 | Add 6 MVAR switched shunt at CLIFTON3 115 kV
04ALL | ERIS | Voltage | CNTRLXN3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86753 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CNTRVIL5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88843 | 0.93 | 1.05 | Add 26 MVAR switched shunt at CNTRVIL5 161 kV
04ALL | ERIS | Voltage | CNTRVIL5 | 29WP | V | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: |  |  |  |  | 0.92177 | 0.93 | 1.05 | Add 26 MVAR switched shunt at CNTRVIL5 161 kV
04ALL | ERIS | Voltage | CNTRVIL5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89865 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | COFFEYT4 | 29WP | V | P23:345:WERE:N345-345-20:EHV: |  |  |  |  | 0.91846 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | COL318_2 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.90097 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | COL318_2 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.90097 | 0.925 | 1.05 | Add 0.03 MVAR switched shunt at COL318_2 69 kV
04ALL | ERIS | Voltage | COL318_2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91799 | 0.925 | 1.05 | None
04ALL | ERIS | Voltage | COL318_2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91888 | 0.925 | 1.05 | None
04ALL | ERIS | Voltage | COLBY 2 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.87335 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | COLBY_PUMP3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.85902 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | COLINE 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88191 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | COLLEGE5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87869 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | COLLEGE5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91451 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | COLLYER3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.81516 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | COMMTP 2 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.88506 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | COMMTP 2 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.89789 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CONCRD6 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89586 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | CONTYLN2 | 29WP | V | P12:138:OKGE:BKRBKR4330:::HV: |  |  |  |  | 0.91393 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CORONAD3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90149 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | COUTYTP2 | 29WP | V | P12:138:OKGE:BKRBKR4330:::HV: |  |  |  |  | 0.91397 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | COVERT 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85106 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | COWSKIN 4 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.88338 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | COWSKIN 4 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.86236 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | COWSKIN2 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.87724 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | COWSKIN2 | 29SP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.89247 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | COWSKIN2 | 29SP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.89247 | 0.9 | 1.05 | Add 4.8 MVAR switched shunt at COWSKIN2 69 kV
04ALL | ERIS | Voltage | COWSKIN2 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.85961 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CPK446 5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.88016 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CPK446 5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.88016 | 0.925 | 1.05 | Add 16 MVAR SVC at CPK446 5 161 kV
04ALL | ERIS | Voltage | CPK446 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88722 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CPK446 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88722 | 0.925 | 1.05 | Add 16 MVAR SVC at CPK446 5 161 kV
04ALL | ERIS | Voltage | CPK446 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.8833 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CPK446 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.8833 | 0.925 | 1.05 | Add 16 MVAR SVC at CPK446 5 161 kV
04ALL | ERIS | Voltage | CRAIG 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88381 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CRAIG 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92083 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CRAIG 7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92531 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CRAIG 7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88442 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CRAIG_CAP 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88477 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CRAIG_CAP 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92184 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CRAWFOR2 | 29WP | V | Single 532793 NEOSHO7 345 533023 N34534 138 533801 'N345 2 1 ' 13 2 |  |  |  |  | 0.92218 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CRAWFOR2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91518 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CRAWFOR2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.9159 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CRAWFRD3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91149 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CRAWFRD3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87102 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CROOKED3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87549 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CROSTWN5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90934 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CUSTER 4 | 29L | V | Single 511561 ELLIS4 138 520459 CUSTER4 138 1 |  |  |  |  | 1.0731 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CUSTER 4 | 29L | V | Single 511561 ELLIS4 138 520459 CUSTER4 138 1 |  |  |  |  | 1.0731 | 0.9 | 1.05 | Add 10 MVAR switched shunt at CUSTER 4 138 kV
04ALL | ERIS | Voltage | DAD368 5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.88249 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | DAD368 5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.88249 | 0.925 | 1.05 | Add 40 MVAR switched shunt at DAD368 5 161 kV
04ALL | ERIS | Voltage | DAD368 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87898 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | DAD368 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87898 | 0.925 | 1.05 | Add 40 MVAR switched shunt at DAD368 5 161 kV
04ALL | ERIS | Voltage | DAD368 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.8816 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | DAD368 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.8816 | 0.925 | 1.05 | Add 40 MVAR switched shunt at DAD368 5 161 kV
04ALL | ERIS | Voltage | DAKOTA_5 | 29WP | V | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: |  |  |  |  | 0.92838 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | DAKOTA_5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90715 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | DAKOTA_5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91996 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | DEC392 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.89656 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | DEC392 5 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.92373 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | DEERCRK3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86927 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | DELWARE7 | 29WP | V | System Intact |  |  |  |  | 0.9472 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | DIXLAND2 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.89988 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | DRAGON 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89562 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | DUNCAN 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91565 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | DURHAM 4 | 29L | V | Single 520462 ASPEN4 138 520500 BEARCAT4 138 1 |  |  |  |  | 1.0778 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | DYESS 2 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.88998 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | DYESS 5 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.89315 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | EABILEN3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88867 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | EAST ST3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.78633 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | EAST ST3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.81541 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | EAST ST3 | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88577 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | EASTFORK3 | 29SP | V | P42:345:NPPD:BKR-AXT-3306:::: |  |  |  |  | 0.87622 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ECENT_1 2 | 29WP | V | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: |  |  |  |  | 0.91384 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ECKLES-161 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91549 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | ECNTRTN5 | 29WP | V | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: |  |  |  |  | 0.89099 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ECNTRTN5 | 26SP | V | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: |  |  |  |  | 0.91879 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | EDUCATE3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87299 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | EDWRDVL5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91842 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | EDWRDVL5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88131 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | EEUREKA3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.8596 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | EEUREKA3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87789 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | EFAIRMNT3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92051 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | EFAYETVL 5 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.89587 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | EFAYTVL2-2 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.89587 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | EFAYVL_1 2 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.89587 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ELDORDJ2 | 29SP | V | P12:138:AEPW-WFEC:LAKEP4WT:RUSSELL4::: |  |  |  |  | 0.89368 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ELDORDO2 | 29SP | V | P12:138:AEPW-WFEC:LAKEP4WT:RUSSELL4::: |  |  |  |  | 0.82096 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ELDORDO2 | 29SP | V | P12:138:AEPW-WFEC:LAKEP4WT:RUSSELL4::: |  |  |  |  | 0.82096 | 0.9 | 1.05 | Add 30 MVAR SVC at ELDORDO2 69 kV
04ALL | ERIS | Voltage | ELDORDO2 | 26SP | V | P12:138:AEPW-WFEC:LAKEP4WT:RUSSELL4::: |  |  |  |  | 0.83402 | 0.9 | 1.05 | Add 30 MVAR SVC at ELDORDO2 69 kV
04ALL | ERIS | Voltage | ELDORDO2 | 29WP | V | P12:138:AEPW-WFEC:LAKEP4WT:RUSSELL4::: |  |  |  |  | 0.85661 | 0.9 | 1.05 | Add 30 MVAR SVC at ELDORDO2 69 kV
04ALL | ERIS | Voltage | ELKRVR17 | 29WP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.90525 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ELKRVR17 | 29WP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.90525 | 0.95 | 1.05 | Add 48 MVAR switched shunt at ELKRVR17 345 kV
04ALL | ERIS | Voltage | ELKRVR17 | 26SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.90266 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ELKRVR17 | 26SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.90266 | 0.95 | 1.05 | Add 48 MVAR switched shunt at ELKRVR17 345 kV
04ALL | ERIS | Voltage | ELKRVR17 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8968 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ELKRVR17 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8968 | 0.95 | 1.05 | Add 48 MVAR switched shunt at ELKRVR17 345 kV
04ALL | ERIS | Voltage | ELLIS 2 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.81001 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ELLIS 2 | 26SP | V | P23:345:SUNC:SB_BRK482:::EHV: |  |  |  |  | 0.86191 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ELLIS 4 | 29L | V | Single 520462 ASPEN4 138 520500 BEARCAT4 138 1 |  |  |  |  | 1.0727 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ELLIS 4 | 29L | V | Single 520462 ASPEN4 138 520500 BEARCAT4 138 1 |  |  |  |  | 1.0727 | 0.92 | 1.05 | Add 8 MVAR switched shunt at ELLIS 4 138 kV
04ALL | ERIS | Voltage | ELLSWTP3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87254 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | ELMCREK6 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89251 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | ELMSPG_2 2 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.89004 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ELMSPRGS 5 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.89004 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | EMANHAT3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88811 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | EMANHAT6 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88667 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | EMANHAT6 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.94536 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | EMCPHER3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92814 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | EMCPHER6 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.93633 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | EMCPHER6 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90815 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | EROGERS5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.88859 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | EROGERS5 | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.91485 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ESTELNE2 | 26SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.90087 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ESTELNE2 | 29SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.89456 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ESTELNE2 | 29WP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.90308 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | EUDORA 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87105 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | EUDORA 3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92527 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | EUREKA 5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.88144 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | EUREKA 5 | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.89125 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | EXPED WF7 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89197 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | EXPED WF7 | 29WP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.89276 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | EXPED WF7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85512 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | FAIRGDS3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87077 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | FAIRGDS3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92985 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | FARMING5 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.90297 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | FARMNGTN 5 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.90272 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | FARM_1 2 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.91037 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | FARM_2 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.90272 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | FIR417 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.90961 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | FIR417 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92035 | 0.925 | 1.05 | None
04ALL | ERIS | Voltage | FLETCHR3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89504 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | FLINTCR7 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.90164 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | FLORENC3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.83824 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | FLORENC3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.85977 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | FLORENC3 | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92869 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | FMC 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87367 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | FOR410 2 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.88952 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | FOR410 2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90901 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | FORBES 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86561 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | FOREST 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8911 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | FOREST 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91994 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | FR4 XMF1 345 | 26SP | V | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 |  |  |  |  | 0.94541 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | FR4345KV-TAP | 26SP | V | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 |  |  |  |  | 0.94534 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | FRANKLIN5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92424 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | FREESTATE3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87048 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | FRLVW 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91989 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | FROSTRD5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90724 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | FROSTRD_CAP5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90823 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | FRSTCRK5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92136 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | G15052_1 | 29WP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.89073 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G15052_1 | 29WP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.89073 | 0.95 | 1.05 | Add 44 MVAR SVC at G15052_1 345 kV
04ALL | ERIS | Voltage | G15052_1 | 26SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.89034 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G15052_1 | 26SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.89034 | 0.95 | 1.05 | Add 44 MVAR SVC at G15052_1 345 kV
04ALL | ERIS | Voltage | G15052_1 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88436 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G15052_1 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88436 | 0.95 | 1.05 | Add 44 MVAR SVC at G15052_1 345 kV
04ALL | ERIS | Voltage | G15052_T | 29WP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.89073 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G15052_T | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88436 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G15052_T | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88436 | 0.95 | 1.05 | Add 44 MVAR SVC at G15052_T 345 kV
04ALL | ERIS | Voltage | G15052_T | 26SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.89034 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G15052_T | 26SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.89034 | 0.95 | 1.05 | Add 44 MVAR SVC at G15052_T 345 kV
04ALL | ERIS | Voltage | G16-111-TAP | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.86009 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G16-111-TAP | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.86009 | 0.95 | 1.05 | Add 415 MVAR SVC at G16-111-TAP 345 kV
04ALL | ERIS | Voltage | G16-111-TAP | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90315 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G16-111-TAP | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90315 | 0.95 | 1.05 | Add 415 MVAR SVC at G16-111-TAP 345 kV
04ALL | ERIS | Voltage | G16-111-TAP | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.83521 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G16-111-TAP | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.83521 | 0.95 | 1.05 | Add 415 MVAR SVC at G16-111-TAP 345 kV
04ALL | ERIS | Voltage | G17-120-TAP | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88413 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | G18-128-TAP | 26SP | V | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 |  |  |  |  | 0.92812 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G18-128-TAP | 26SP | V | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 |  |  |  |  | 0.92812 | 0.95 | 1.05 | Add 27 MVAR switched shunt at G18-128-TAP 345 kV
04ALL | ERIS | Voltage | G18-128-TAP | 29WP | V | Single 515378 WWARD9 765 532828 VIOLA9 765 1 |  |  |  |  | 0.93523 | 0.95 | 1.05 | Add 27 MVAR switched shunt at G18-128-TAP 345 kV
04ALL | ERIS | Voltage | G18-128-TAP | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.94604 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | G19-053-TAP | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.871 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | G19-054-TAP | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86778 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | G20-007-TAP | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92981 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G20-007-TAP | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.85288 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G20-007-TAP | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87172 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G20-011-SS1 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85808 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G20-011-SS2 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85808 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G20-011-SS3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85808 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G20-011-SS4 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85808 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G20-073-TAP | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90488 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | G20-073-TAP | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91806 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | G20-079-TAP | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.90988 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G20-079-TAP | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92105 | 0.925 | 1.05 | None
04ALL | ERIS | Voltage | G21-017-SUB1 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87808 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | G21-029-TAP | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.85405 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G21-029-TAP | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87301 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G21-029-TAP | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.93119 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G21-096-TAP | 29WP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.87785 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G21-096-TAP | 29WP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.87785 | 0.95 | 1.05 | Add 165 MVAR SVC at G21-096-TAP 345 kV
04ALL | ERIS | Voltage | G21-096-TAP | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87777 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G21-096-TAP | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87777 | 0.95 | 1.05 | Add 165 MVAR SVC at G21-096-TAP 345 kV
04ALL | ERIS | Voltage | G21-096-TAP | 26SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.88893 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G21-096-TAP | 26SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.88893 | 0.95 | 1.05 | Add 165 MVAR SVC at G21-096-TAP 345 kV
04ALL | ERIS | Voltage | G22-007-TAP | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.79557 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | G22-007-TAP | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.82451 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | G22-007-TAP | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88928 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | G22-013-TAP | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88936 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G22-013-TAP | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88936 | 0.95 | 1.05 | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV
04ALL | ERIS | Voltage | G22-013-TAP | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.84564 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G22-013-TAP | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.83421 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G22-013-TAP | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.83421 | 0.95 | 1.05 | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV
04ALL | ERIS | Voltage | G22-015-TAP | 29SP | V | P42:345:NPPD:BKR-AXT-3306:::: |  |  |  |  | 0.85223 | 0.9 | 1.05 | Add 135 MVAR switched shunt at G22-015-TAP 345 kV
04ALL | ERIS | Voltage | G22-065-TAP | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8685 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | G22-075-TAP | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.74 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G22-075-TAP | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.74 | 0.9 | 1.05 | Add 27 MVAR switched shunt at G22-075-TAP 345 kV
04ALL | ERIS | Voltage | G22-075-TAP | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8205 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G22-075-TAP | 29WP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87638 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G23-220-TAP | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.83823 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G23-220-TAP | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.83823 | 0.95 | 1.05 | Add 141 MVAR SVC at G23-220-TAP 345 kV
04ALL | ERIS | Voltage | G23-220-TAP | 29WP | V | P23:345:WERE:WAVS-BKRS:EHV: |  |  |  |  | 0.89642 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G23-220-TAP | 29WP | V | P23:345:WERE:WAVS-BKRS:EHV: |  |  |  |  | 0.89642 | 0.95 | 1.05 | Add 141 MVAR SVC at G23-220-TAP 345 kV
04ALL | ERIS | Voltage | G23-220-TAP | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89329 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G23-220-TAP | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89329 | 0.95 | 1.05 | Add 141 MVAR SVC at G23-220-TAP 345 kV
04ALL | ERIS | Voltage | G23-221-TAP | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8388 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G23-221-TAP | 29WP | V | P23:345:WERE:WAVS-BKRS:EHV: |  |  |  |  | 0.89645 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G23-221-TAP | 29WP | V | P23:345:WERE:WAVS-BKRS:EHV: |  |  |  |  | 0.89645 | 0.95 | 1.05 | Add 43 MVAR SVC at G23-221-TAP 345 kV
04ALL | ERIS | Voltage | G23-221-TAP | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89363 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G24-016-TAP | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.77807 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G24-016-TAP | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.77807 | 0.9 | 1.05 | Add 31 MVAR switched shunt at G24-016-TAP 345 kV
04ALL | ERIS | Voltage | G24-016-TAP | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86618 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G24-055-TAP | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92225 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | G24-076-TAP | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88906 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G24-076-TAP | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88906 | 0.95 | 1.05 | Add 260 MVAR SVC at G24-076-TAP 345 kV
04ALL | ERIS | Voltage | G24-076-TAP | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.84618 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G24-076-TAP | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.84618 | 0.95 | 1.05 | Add 260 MVAR SVC at G24-076-TAP 345 kV
04ALL | ERIS | Voltage | G24-076-TAP | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.83511 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G24-076-TAP | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.83511 | 0.95 | 1.05 | Add 260 MVAR SVC at G24-076-TAP 345 kV
04ALL | ERIS | Voltage | G24-084-TAP | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.88582 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G24-084-TAP | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.89144 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G24-084-TAP | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.89144 | 0.925 | 1.05 | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV
04ALL | ERIS | Voltage | G24-084-TAP | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89884 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G24-125-TAP | 29WP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.91973 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G24-125-TAP | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91825 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G24-125-TAP | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91825 | 0.95 | 1.05 | Add 0.06 MVAR switched shunt at G24-125-TAP 345 kV
04ALL | ERIS | Voltage | G24-125-TAP | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91088 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G24-129-TAP | 29WP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.90734 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G24-129-TAP | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89836 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G24-129-TAP | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89699 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G24-139-TAP | 29WP | V | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: |  |  |  |  | 0.9449 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G24-139-TAP | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90947 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G24-139-TAP | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92639 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | G24-207-TAP | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90634 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | G24-217-TAP | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92524 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | G24-228-TAP | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.93434 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | G24-240-TAP | 29WP | V | System Intact |  |  |  |  | 0.94389 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G24-253-TAP | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91551 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | G24-258-TAP | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.93529 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | G24-258-TAP | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92669 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | G24-276-TAP | 29WP | V | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: |  |  |  |  | 0.93958 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G24-276-TAP | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91843 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G24-276-TAP | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85456 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G24-287-TAP | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.93596 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G24-287-TAP | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92288 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G24-287-TAP | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92034 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G24-288-TAP | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87838 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | G24-322-TAP | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.81153 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GALE 2 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92864 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GARDNER5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88624 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GARDNER5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92005 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GATZ 2 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92493 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GB-SHAMROCK | 26SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.86646 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GB-SHAMROCK | 26SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.86646 | 0.92 | 1.05 | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV
04ALL | ERIS | Voltage | GB-SHAMROCK | 29SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.87092 | 0.92 | 1.05 | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV
04ALL | ERIS | Voltage | GB-SHAMROCK | 29SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.87092 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GB-SHAMROCK | 29WP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.87547 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEARY 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90478 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEARY 7 | 29WP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91805 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEARY 7 | 29WP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91805 | 0.95 | 1.05 | Add 111 MVAR SVC at GEARY 7 345 kV
04ALL | ERIS | Voltage | GEARY 7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.83495 | 0.95 | 1.05 | Add 111 MVAR SVC at GEARY 7 345 kV
04ALL | ERIS | Voltage | GEARY 7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.83495 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEARY 7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88551 | 0.95 | 1.05 | Add 111 MVAR SVC at GEARY 7 345 kV
04ALL | ERIS | Voltage | GEARY 7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88551 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEM_SW 3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.86004 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2016-073 | 29WP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.931 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2016-073 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89869 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2016-073 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91698 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2016-111 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.86088 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2016-111 | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90398 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2016-111 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.83598 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2017-004 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87136 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2017-022 | 29WP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.90125 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2017-022 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88812 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2017-022 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88283 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2017-086 | 26SP | V | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 |  |  |  |  | 0.94534 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2017-119 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87808 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2017-120 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88413 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2017-195 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.94745 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2017-195 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.8958 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2017-195 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8625 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2017-220 | 29WP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.92656 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2017-220 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8944 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2017-220 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91261 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2018-031 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90619 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2018-032 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.88886 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2018-032 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87437 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2018-032 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87302 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2018-060 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.80448 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2018-060 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88438 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2018-064 | 29WP | V | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: |  |  |  |  | 0.89846 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2019-016 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.88258 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2019-016 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87906 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2019-016 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88168 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2019-053 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.871 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2019-054 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86778 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2020-007 | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92981 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2020-007 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.85288 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2020-007 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87172 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2020-011 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85808 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2020-057 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90703 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2020-057 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86822 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2020-058 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90703 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2020-058 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86822 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2020-073 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90488 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2020-073 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91806 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2020-079 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.90988 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2020-079 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92105 | 0.925 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2020-088 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.91095 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2020-088 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91667 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2020-090 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.94301 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2020-090 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.9276 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2020-090 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92287 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2021-005 | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90874 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2021-005 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.82867 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2021-005 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.86747 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2021-006 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.88868 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2021-006 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87418 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2021-006 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87283 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2021-029 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.85405 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2021-029 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87301 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2021-029 | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.93119 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2021-030 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.85405 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2021-030 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87301 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2021-030 | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.93119 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2021-035 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86379 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2021-035 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85592 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2021-076 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.73076 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2021-076 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.81571 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2021-076 | 29WP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87375 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2021-096 | 29WP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.87785 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2021-096 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87777 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2021-096 | 26SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.88893 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2021-101 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88132 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2021-103 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91806 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2021-103 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87435 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2021-107 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8599 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2021-107 | 29WP | V | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: |  |  |  |  | 0.9295 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2021-107 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91905 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2022-006 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92275 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2022-006 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92364 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2022-007 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.79557 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2022-007 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.82451 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2022-007 | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88928 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2022-013 | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88936 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2022-013 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.84564 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2022-013 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.83421 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2022-015 | 29SP | V | P42:345:NPPD:BKR-AXT-3306:::: |  |  |  |  | 0.85223 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2022-054 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.94301 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2022-054 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.9276 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2022-054 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92287 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2022-065 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8685 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2022-073 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92242 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2022-075 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.74 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2022-075 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8205 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2022-075 | 29WP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87638 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2022-102 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91811 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2022-142 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91511 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2022-144 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90976 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2023-033 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91359 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2023-061 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.90258 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2023-061 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91062 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2023-171 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.9077 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2023-220 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.83823 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2023-220 | 29WP | V | P23:345:WERE:WAVS-BKRS:EHV: |  |  |  |  | 0.89642 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2023-220 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89329 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2023-221 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8388 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2023-221 | 29WP | V | P23:345:WERE:WAVS-BKRS:EHV: |  |  |  |  | 0.89645 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2023-221 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89363 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-016 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.77807 | 0.9 | 1.05 | Add 138 MVAR switched shunt at GEN-2024-016 345 kV
04ALL | ERIS | Voltage | GEN-2024-016 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86618 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2024-055 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92254 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2024-067 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88168 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2024-074 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91565 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2024-076 | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.8916 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-076 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.84875 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-076 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.83769 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-084 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.88587 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-084 | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.89149 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-084 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.8989 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-090 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92358 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2024-091 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.90216 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-091 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91736 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-121 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.9197 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2024-125 | 29WP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.91999 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-125 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91852 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-125 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91115 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-129 | 29WP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.90754 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-129 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89855 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-129 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89718 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-139 | 29WP | V | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: |  |  |  |  | 0.94496 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-139 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90954 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-139 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92646 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2024-142 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87675 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-142 | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91936 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-142 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85216 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-157 | 29L | V | P12:345:OKGE-AEP:BKRBKR4291:::EHV: |  |  |  |  | 1.0602 | 0.92 | 1.05 | Add 0.7 MVAR switched shunt at GEN-2024-157 138 kV
04ALL | ERIS | Voltage | GEN-2024-157 | 29L | V | P12:345:OKGE-AEP:BKRBKR4291:::EHV: |  |  |  |  | 1.0602 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-167 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91986 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2024-170 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91846 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-170 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89515 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-206 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90619 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2024-207 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90635 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2024-215 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8784 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2024-217 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92524 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2024-228 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.93567 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2024-240 | 29WP | V | System Intact |  |  |  |  | 0.94389 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-249 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8599 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-249 | 29WP | V | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: |  |  |  |  | 0.9295 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-249 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91905 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-253 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91551 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2024-258 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.93537 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2024-258 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92677 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2024-276 | 29WP | V | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: |  |  |  |  | 0.93968 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-276 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91853 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-276 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85465 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-287 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.93596 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-287 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92288 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-287 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92034 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-288 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87857 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2024-319 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88557 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2024-320 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90568 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2024-322 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.81159 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-345 | 29WP | V | System Intact |  |  |  |  | 0.94728 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2024-352 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92268 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2024-352 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.94967 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2024-370 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92358 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GENTRY | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.89933 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GENTRY 5 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.90111 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GIBBS 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89798 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | GLADSTN5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91558 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GLADSTN_CAP5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91663 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GODDARD4 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92911 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GODDARD4 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92104 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GODLNDT3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.86682 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GOODCTY3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.86261 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GOODLND3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.86707 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GORHAM 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.83498 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | GOULD 2 | 29SP | V | P12:138:AEPW-WFEC:LAKEP4WT:RUSSELL4::: |  |  |  |  | 0.88926 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GOVE 3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.80445 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GOVE 3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.80445 | 0.9 | 1.05 | Add 30 MVAR switched shunt at GOVE 3 115 kV
04ALL | ERIS | Voltage | GOVE 3 | 26SP | V | P23:345:SUNC:SB_BRK482:::EHV: |  |  |  |  | 0.86962 | 0.9 | 1.05 | Add 30 MVAR switched shunt at GOVE 3 115 kV
04ALL | ERIS | Voltage | GOVE 3 | 26SP | V | P23:345:SUNC:SB_BRK482:::EHV: |  |  |  |  | 0.86962 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GRAINVL5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.914 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GRAND 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91142 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GRAND W5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91126 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GRANT 3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.84863 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GRANT 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.80861 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | GRANTTP3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.84895 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GRANTTP3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.84895 | 0.9 | 1.05 | Add 21 MVAR switched shunt at GRANTTP3 115 kV
04ALL | ERIS | Voltage | GRANTTP3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.80894 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | GRDVWE 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89976 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GRDVWE 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92521 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GREENHOUSE 5 | 29WP | V | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: |  |  |  |  | 0.89102 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GREENHOUSE 5 | 26SP | V | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: |  |  |  |  | 0.91879 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GREENLD2 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.91849 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GREGGST5 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.90024 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GRHMSUB3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.81691 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GRINNEL3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.83152 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GRINNEL3 | 26SP | V | P23:345:SUNC:SB_BRK482:::EHV: |  |  |  |  | 0.89779 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GRN498 2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92478 | 0.925 | 1.05 | None
04ALL | ERIS | Voltage | GRN498 2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92041 | 0.925 | 1.05 | None
04ALL | ERIS | Voltage | GROVE 4 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.88419 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GROVE 4 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.88419 | 0.92 | 1.05 | Add 16 MVAR SVC at GROVE 4 138 kV
04ALL | ERIS | Voltage | GROVE 4 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.90139 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GROVE 4 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.90139 | 0.92 | 1.05 | Add 16 MVAR SVC at GROVE 4 138 kV
04ALL | ERIS | Voltage | GROVE 4 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.8628 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GROVE 4 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.8628 | 0.92 | 1.05 | Add 16 MVAR SVC at GROVE 4 138 kV
04ALL | ERIS | Voltage | GROVE 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.87052 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GROVE 5 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.89048 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GROVE 5 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.90961 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GRT433 5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.89135 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GRT433 5 | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.9032 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GRT433 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91173 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GRTBEND3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89475 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | GRTBEND6 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8523 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | HALLMRK3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92299 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | HALSTD 4 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89051 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HALSTD 4 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88264 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | HALSTD 4 | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92834 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | HALSTED2 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92583 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | HASKELL3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86521 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HASKELL3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.83539 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | HAWTH 7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.93219 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | HAWTHS_XF5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91566 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | HEDLEY 2 | 26SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.91496 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HEDLEY 2 | 29SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.91809 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HEIZER 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89332 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | HEIZER 6 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85237 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | HERNDON3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.8915 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HESSTON2 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91977 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | HESSTON2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92552 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | HICKMAN5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88619 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | HICKMAN5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91295 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | HICKOCK2 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85498 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HICKOCK2 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.83982 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | HIGHPT 3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.8487 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HIGHPT 3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.8487 | 0.9 | 1.05 | Add 25 MVAR switched shunt at HIGHPT 3 115 kV
04ALL | ERIS | Voltage | HI_BNKS1_WF7 | 29WP | V | P42:345:OKGE:SB_RARD7381:::EHV: |  |  |  |  | 1.0902 | 0.95 | 1.05 | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV
04ALL | ERIS | Voltage | HI_BNKS1_WF7 | 29WP | V | P42:345:OKGE:SB_RARD7381:::EHV: |  |  |  |  | 1.0902 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HI_BNKS2_WF7 | 29WP | V | P42:345:OKGE:SB_RARD7381:::EHV: |  |  |  |  | 1.095 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HI_BNKS2_WF7 | 29WP | V | P42:345:OKGE:SB_RARD7381:::EHV: |  |  |  |  | 1.095 | 0.95 | 1.05 | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV
04ALL | ERIS | Voltage | HLLMRK 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.9177 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | HMLTON 3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89457 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HMLTON 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86003 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | HMLTTAP3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89987 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HMLTTAP3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86557 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | HOC404 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.88456 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HOC404 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.88456 | 0.925 | 1.05 | Add 40 MVAR SVC at HOC404 5 161 kV
04ALL | ERIS | Voltage | HOC404 5 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.90309 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HOC404 5 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.90309 | 0.925 | 1.05 | Add 40 MVAR SVC at HOC404 5 161 kV
04ALL | ERIS | Voltage | HOC404 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91387 | 0.925 | 1.05 | Add 40 MVAR SVC at HOC404 5 161 kV
04ALL | ERIS | Voltage | HOL387 5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.89243 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HOL387 5 | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.90537 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HOL387 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91353 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HOL478_5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.89401 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HOL478_5 | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.90736 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HOL478_5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91517 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HOLLIS 2 | 29SP | V | P12:138:AEPW-WFEC:LAKEP4WT:RUSSELL4::: |  |  |  |  | 0.8743 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HOLLIS 2 | 26SP | V | P12:138:AEPW-WFEC:LAKEP4WT:RUSSELL4::: |  |  |  |  | 0.88535 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HOLLIS 4 | 26SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.85442 | 0.92 | 1.05 | Add 6.3 MVAR switched shunt at HOLLIS 4 138 kV
04ALL | ERIS | Voltage | HOLLIS 4 | 26SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.85442 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HOLLIS 4 | 29SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.8428 | 0.92 | 1.05 | Add 6.3 MVAR switched shunt at HOLLIS 4 138 kV
04ALL | ERIS | Voltage | HOLLIS 4 | 29SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.8428 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HOLLIS 4 | 29WP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.85079 | 0.92 | 1.05 | Add 6.3 MVAR switched shunt at HOLLIS 4 138 kV
04ALL | ERIS | Voltage | HOLLIS 4 | 29WP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.85079 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HOLTP4WT | 26SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.85548 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HOLTP4WT | 29SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.84387 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HOLTP4WT | 29WP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.85127 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HONEYWL5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89406 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | HONEYWL5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91877 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | HOOKRD 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.9183 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | HOXIE 3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.8528 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HOYT 7 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.93481 | 0.95 | 1.05 | Add 122 MVAR switched shunt at HOYT 7 345 kV
04ALL | ERIS | Voltage | HOYT 7 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.93481 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HOYT 7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88072 | 0.95 | 1.05 | Add 122 MVAR switched shunt at HOYT 7 345 kV
04ALL | ERIS | Voltage | HOYT 7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88072 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HOYT 7 | 29WP | V | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 |  |  |  |  | 0.94668 | 0.95 | 1.05 | Add 122 MVAR switched shunt at HOYT 7 345 kV
04ALL | ERIS | Voltage | HOYT 7 | 29WP | V | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 |  |  |  |  | 0.94668 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HSNVL 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92857 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | HUM308_2 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.90852 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HZRNGPL3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89276 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | INDEPCO5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.90692 | 0.92 | 1.05 | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV
04ALL | ERIS | Voltage | INDIANH3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87356 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | INDIAN_CK_5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.9106 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | INDIAN_CK_5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87822 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | IONIA 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87865 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | J12_____-MK7 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.86566 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | JADE 3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.84267 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | JADE 3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.86114 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | JAGGARD3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90568 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | JAY 4 | 29SP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.90875 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | JAY 4 | 29SP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.90875 | 0.92 | 1.05 | Add 24 MVAR SVC at JAY 4 138 kV
04ALL | ERIS | Voltage | JAY 4 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.87109 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | JAY 4 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.87109 | 0.92 | 1.05 | Add 24 MVAR SVC at JAY 4 138 kV
04ALL | ERIS | Voltage | JAY 4 | 26SP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.89511 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | JAY 4 | 26SP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.89511 | 0.92 | 1.05 | Add 24 MVAR SVC at JAY 4 138 kV
04ALL | ERIS | Voltage | JCTCTY 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90049 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | JEC 6 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86535 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | JEC 6 | 29WP | V | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: |  |  |  |  | 0.9333 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | JEC 6 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92499 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | JEC N 7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8599 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | JEC N 7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8599 | 0.95 | 1.05 | Add 36 MVAR switched shunt at JEC N 7 345 kV
04ALL | ERIS | Voltage | JEC N 7 | 29WP | V | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: |  |  |  |  | 0.9295 | 0.95 | 1.05 | Add 36 MVAR switched shunt at JEC N 7 345 kV
04ALL | ERIS | Voltage | JEC N 7 | 29WP | V | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: |  |  |  |  | 0.9295 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | JEC N 7 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91905 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | JEWELL 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88936 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | JHNCRSOL | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89739 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | JHNCRSOL | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86373 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | JOHNSON3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87712 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | JOP145 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.90215 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | JOP145 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91736 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | JOP389 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.89553 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | JOP389 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91207 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | JOP389 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92105 | 0.925 | 1.05 | None
04ALL | ERIS | Voltage | JOP391 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.88867 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | JOP391 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90496 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | JOP391 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91366 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | JOP422 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.89012 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | JOP422 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90649 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | JOP422 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91526 | 0.925 | 1.05 | None
04ALL | ERIS | Voltage | KANARAD3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.85511 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | KANSAS 2 | 29WP | V | P12:161:GRDA:412SUB 5-SILSPWW5:::HV: |  |  |  |  | 0.88152 | 0.9 | 1.05 | Add 8 MVAR switched shunt at KANSAS 2 69 kV
04ALL | ERIS | Voltage | KANSAS 2 | 26SP | V | P12:161:GRDA:412SUB 5-SILSPWW5:::HV: |  |  |  |  | 0.88356 | 0.9 | 1.05 | Add 8 MVAR switched shunt at KANSAS 2 69 kV
04ALL | ERIS | Voltage | KANSAS 2 | 29SP | V | P12:161:GRDA:412SUB 5-SILSPWW5:::HV: |  |  |  |  | 0.88589 | 0.9 | 1.05 | Add 8 MVAR switched shunt at KANSAS 2 69 kV
04ALL | ERIS | Voltage | KANSAS 5 | 29WP | V | P12:161:GRDA:412SUB 5-SILSPWW5:::HV: |  |  |  |  | 0.88152 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | KANSAS 5 | 26SP | V | P12:161:GRDA:412SUB 5-SILSPWW5:::HV: |  |  |  |  | 0.88356 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | KANSAS 5 | 29SP | V | P12:161:GRDA:412SUB 5-SILSPWW5:::HV: |  |  |  |  | 0.88589 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | KAW W 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89682 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | KCI 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92303 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | KEENE -MK7 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.89319 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | KEENE 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87827 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | KEENECRN-MK7 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.88933 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | KERFORD3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92456 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | KNLWRTH5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90986 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | KNLWRTH5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87589 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | KNOLL N 6 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.75905 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | KNOLL N 6 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.83913 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | KNOLL S 6 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.75905 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | KNOLL S 6 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.83913 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | KSU W 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89161 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | L11_____-MK7 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.8791 | 0.9 | 1.05 | Add 5 MVAR switched shunt at L11_____-MK7 115 kV
04ALL | ERIS | Voltage | LABETTE2 | 29WP | V | Single 532793 NEOSHO7 345 533023 N34534 138 533801 'N345 2 1 ' 13 2 |  |  |  |  | 0.89327 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LABETTE2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88794 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LABETTE2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88672 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LABETTS2 | 29WP | V | Single 532793 NEOSHO7 345 533023 N34534 138 533801 'N345 2 1 ' 13 2 |  |  |  |  | 0.89408 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LABETTS2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89002 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LABETTS2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88881 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LACKMAN5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88964 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | LACKMAN5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91403 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | LACROS 3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89549 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | LACROS 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.83351 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | LACYGNE11_7 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.85393 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LACYGNE11_7 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.85393 | 0.95 | 1.05 | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV
04ALL | ERIS | Voltage | LACYGNE11_7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.8728 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LACYGNE11_7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.8728 | 0.95 | 1.05 | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV
04ALL | ERIS | Voltage | LACYGNE11_7 | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.93087 | 0.95 | 1.05 | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV
04ALL | ERIS | Voltage | LACYGNE2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.84089 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LACYGNE2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.86029 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LACYGNE2 | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92527 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | LACYGNE22_7 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.85394 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LACYGNE22_7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87281 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LACYGNE22_7 | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.93088 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LACYGNE_LK2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.83951 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LACYGNE_LK2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.85896 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LACYGNE_LK2 | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92445 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | LAKEP4WT | 26SP | V | P12:138:AEPW-WFEC:LAKEP4WT:RUSSELL4::: |  |  |  |  | 0.85558 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LAKEP4WT | 29SP | V | P12:138:AEPW-WFEC:LAKEP4WT:RUSSELL4::: |  |  |  |  | 0.85923 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LAKEP4WT | 29WP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.878 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LANG 3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.79492 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | LANG 3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.82387 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | LANG 3 | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88869 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | LANG 7 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.72263 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LANG 7 | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.80869 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LANG 7 | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.80869 | 0.95 | 1.05 | Add 174 MVAR SVC at LANG 7 345 kV
04ALL | ERIS | Voltage | LANG 7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.74895 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LAR382 5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.91095 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LAR382 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91667 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LAWHILL6 | 29WP | V | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: |  |  |  |  | 0.93525 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LAWHILL6 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.9384 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LAWHILL6 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87891 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LAXTAP 3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89619 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | LAXTAP 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.83427 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | LBRTYST5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91359 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | LBRTYWT5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91811 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | LEC U3 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87724 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | LEC U4 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87738 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | LEC U5 6 | 29WP | V | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: |  |  |  |  | 0.93524 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LEC U5 6 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.939 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LEC U5 6 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87953 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LEEDS 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90456 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | LEESUM 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92487 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | LENEXA 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88283 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | LENEXA 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91935 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | LEVEE 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88843 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | LEX161 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.9154 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | LH-BEASLEY | 26SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.91202 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LH-BEASLEY | 29SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.91049 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LIBERTY4 | 29WP | V | P23:345:WERE:N345-345-20:EHV: |  |  |  |  | 0.87853 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LIBERTY4 | 29WP | V | P23:345:WERE:N345-345-20:EHV: |  |  |  |  | 0.87853 | 0.93 | 1.05 | Add 32 MVAR SVC at LIBERTY4 138 kV
04ALL | ERIS | Voltage | LIBERTY4 | 26SP | V | P23:345:WERE:N345-345-20:EHV: |  |  |  |  | 0.89198 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LIBERTY4 | 26SP | V | P23:345:WERE:N345-345-20:EHV: |  |  |  |  | 0.89198 | 0.93 | 1.05 | Add 32 MVAR SVC at LIBERTY4 138 kV
04ALL | ERIS | Voltage | LIBERTY4 | 29SP | V | P23:345:WERE:N345-345-20:EHV: |  |  |  |  | 0.89918 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LIBERTY4 | 29SP | V | P23:345:WERE:N345-345-20:EHV: |  |  |  |  | 0.89918 | 0.93 | 1.05 | Add 32 MVAR SVC at LIBERTY4 138 kV
04ALL | ERIS | Voltage | LIN314 2 | 26SP | V | 267142 |  |  |  |  | 1.0589 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LIN314 2 | 26SP | V | 267142 |  |  |  |  | 1.0589 | 0.925 | 1.05 | Add 1.1 MVAR switched shunt at LIN314 2 69 kV
04ALL | ERIS | Voltage | LINCOLN2 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.90287 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LINECRK5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91506 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | LITCH 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92462 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | LITLAXT2 | 29WP | V | MULTIGEN514941 |  |  |  |  | 0.91977 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LITTLAX2 | 29WP | V | MULTIGEN514941 |  |  |  |  | 0.91976 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LITTLEBLUEW3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.81174 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LITTLEBLUEW3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89119 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | LKW400 2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92231 | 0.925 | 1.05 | None
04ALL | ERIS | Voltage | LKWINBG5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92473 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | LKWOOD 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90757 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | LNGVW 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91246 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | LOWELL 5 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.88814 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LTLRLKT2 | 29WP | V | MULTIGEN514941 |  |  |  |  | 0.91593 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LTRVRLK2 | 29WP | V | MULTIGEN514941 |  |  |  |  | 0.9112 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LUDELL 3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.89591 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LUDELLT3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.89592 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LVISTA 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89839 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | LVISTA 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92608 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | LWRNCHL3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87662 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MACOMOC2 | 29WP | V | MULTIGEN514941 |  |  |  |  | 0.91843 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MACON 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.80428 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MACON 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.80428 | 0.9 | 1.05 | Add 50 MVAR switched shunt at MACON 3 345 kV
04ALL | ERIS | Voltage | MACON 3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88415 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MAIN STREET5 | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.89847 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MANTER 3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89641 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MANTER 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8627 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | MANTERT3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89669 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MANTERT3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86299 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | MARMTNE5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91162 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MARMTNE5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92475 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MARMTNW5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91155 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MARMTNW5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92468 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MARTCIT5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89153 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MARTCIT5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91607 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MARTCTY5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89284 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MARTCTY5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91807 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MATTERS3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8899 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MATTISN5 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.89021 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MAYSOTH5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89346 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | MAYWOOD5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89363 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | MCDOWEL3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88967 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MCDOWEL6 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86871 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MCDOWEL6 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.93165 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MERRIAM5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8834 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MERRIAM5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91711 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MERRIAM_CAP5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88437 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MERRIAM_CAP5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91812 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | METRO 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88556 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | MIAMI 2 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.8868 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MIAMI 5 | 29WP | V | System Intact |  |  |  |  | 0.92743 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MIAMI 5 | 29WP | V | System Intact |  |  |  |  | 0.92743 | 0.95 | 1.05 | Add 28 MVAR SVC at MIAMI 5 161 kV
04ALL | ERIS | Voltage | MIAMI 5 | 26SP | V | System Intact |  |  |  |  | 0.93789 | 0.95 | 1.05 | Add 28 MVAR SVC at MIAMI 5 161 kV
04ALL | ERIS | Voltage | MIAMI 5 | 26SP | V | System Intact |  |  |  |  | 0.93789 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MIAMI 5 | 29SP | V | System Intact |  |  |  |  | 0.94817 | 0.95 | 1.05 | Add 28 MVAR SVC at MIAMI 5 161 kV
04ALL | ERIS | Voltage | MIAMI1 2 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.8859 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MIAMI1 2 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.89917 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MIAMI3 2 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.88527 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MIAMI3 2 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.8982 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MIAMI4 2 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.88451 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MIAMI4 2 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.89708 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MID AM 2 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92821 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MID AMJ2 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92826 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MIDLADN3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88132 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MIDLADS3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88132 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MIDLAND6 | 29WP | V | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: |  |  |  |  | 0.93647 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MIDLAND6 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.93764 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MIDLAND6 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87815 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MIDTOWN5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89323 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MIDTOWN5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92214 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MINGO 7 | 29SP | V | P42:345:NPPD:BKR-AXT-3306:::: |  |  |  |  | 0.8753 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MISNJCT5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90998 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MISNJCT5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87715 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MNTCLLO3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89482 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MOBILOL2 | 29WP | V | P12:138:OKGE:BKRBKR4330:::HV: |  |  |  |  | 0.90578 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MOCCASIN-MK7 | 29WP | V | P23:500:EES-EAI:DELL:B8320::EHV: |  |  |  |  | 0.85408 | 0.9 | 1.05 | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV
04ALL | ERIS | Voltage | MOCKBRD3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87158 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MON152 2 | 26SP | V | Single 787110 G24-338-TAP 345 787111 GEN-2024-338 345 1 |  |  |  |  | 1.0511 | 0.925 | 1.05 | Add 2.3 MVAR switched shunt at MON152 2 69 kV
04ALL | ERIS | Voltage | MON383 5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.88995 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MON383 5 | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.89477 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MON383 5 | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.89477 | 0.925 | 1.05 | Add 0.05 MVAR switched shunt at MON383 5 161 kV
04ALL | ERIS | Voltage | MON383 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90499 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MONETT345 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.86343 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MONETT345 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.86343 | 0.9 | 1.05 | Add 129 MVAR SVC at MONETT345 345 kV
04ALL | ERIS | Voltage | MONTGOM4 | 29WP | V | P23:345:WERE:N345-345-20:EHV: |  |  |  |  | 0.8861 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MONTGOM4 | 29WP | V | P23:345:WERE:N345-345-20:EHV: |  |  |  |  | 0.8861 | 0.93 | 1.05 | Add 32 MVAR SVC at MONTGOM4 138 kV
04ALL | ERIS | Voltage | MONTGOM4 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90062 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MONTGOM4 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90062 | 0.93 | 1.05 | Add 32 MVAR SVC at MONTGOM4 138 kV
04ALL | ERIS | Voltage | MONTGOM4 | 26SP | V | P23:345:WERE:N345-345-20:EHV: |  |  |  |  | 0.89651 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MONTGOM4 | 26SP | V | P23:345:WERE:N345-345-20:EHV: |  |  |  |  | 0.89651 | 0.93 | 1.05 | Add 32 MVAR SVC at MONTGOM4 138 kV
04ALL | ERIS | Voltage | MOONLIT3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88029 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MOONLIT3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92319 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MOONLT 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88624 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MOONLT 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92005 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MORRIS 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86145 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MORRIS 3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90396 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MORRIS 6 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85953 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MORRIS 6 | 29WP | V | P23:345:WERE:WAVS-BKRS:EHV: |  |  |  |  | 0.92949 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MORRIS 6 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91849 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MORRIS 7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.84695 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MORRIS 7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.84695 | 0.95 | 1.05 | Add 47 MVAR SVC at MORRIS 7 345 kV
04ALL | ERIS | Voltage | MORRIS 7 | 29WP | V | P23:345:WERE:WAVS-BKRS:EHV: |  |  |  |  | 0.91228 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MORRIS 7 | 29WP | V | P23:345:WERE:WAVS-BKRS:EHV: |  |  |  |  | 0.91228 | 0.95 | 1.05 | Add 47 MVAR SVC at MORRIS 7 345 kV
04ALL | ERIS | Voltage | MORRIS 7 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90467 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MORRIS 7 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90467 | 0.95 | 1.05 | Add 47 MVAR SVC at MORRIS 7 345 kV
04ALL | ERIS | Voltage | MORWODS2 | 29L | V | Single 520462 ASPEN4 138 520500 BEARCAT4 138 1 |  |  |  |  | 1.0706 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MORWODS4 | 29L | V | Single 520462 ASPEN4 138 520500 BEARCAT4 138 1 |  |  |  |  | 1.0734 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MORWOOD4 | 29L | V | Single 520462 ASPEN4 138 520500 BEARCAT4 138 1 |  |  |  |  | 1.0742 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MOUND 2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91575 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MOUND 2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92157 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MOUND 4 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.86813 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MOUND 4 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87457 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MOUND 4 | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91466 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MOUNTAIN-MK7 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.88859 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MUD CRK2 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92764 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MUDCRKJ2 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.9278 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MUND 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91419 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MURLEN 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8728 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MURLEN 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90686 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MUSTNG5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.92755 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MUSTNG5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91105 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MWGRAIN3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92523 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | N HAYS3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.832 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | N TYLER3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87199 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | NASHUA 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92246 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | NASHUA 7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.94791 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | NASHUA-5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92242 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | NASHUA_CAP5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92352 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | NATWOOD3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.8974 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NAVY 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.9113 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | NCFOUND3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90025 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | NCONGRS5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91848 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | NEASTN5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.9147 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | NEASTOTTW5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90474 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | NEASTOTTW5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91625 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | NEASTS5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91477 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | NEASTS_CAP5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91582 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | NEKOMA 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.82731 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEKOMA 3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89095 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | NEO 56 2 | 26SP | V | 267142 |  |  |  |  | 1.0553 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEO SPA5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.88133 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEO SPA5 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.89646 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEO SPA5 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.89646 | 0.92 | 1.05 | Add 4 MVAR switched shunt at NEO SPA5 161 kV
04ALL | ERIS | Voltage | NEO SPA5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91073 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEO184 2 | 26SP | V | 267142 |  |  |  |  | 1.0615 | 0.925 | 1.05 | Add 9 MVAR SVC at NEO184 2 69 kV
04ALL | ERIS | Voltage | NEO184 2 | 26SP | V | 267142 |  |  |  |  | 1.0615 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEO184 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.87801 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEO184 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.87801 | 0.925 | 1.05 | Add 34 MVAR switched shunt at NEO184 5 161 kV
04ALL | ERIS | Voltage | NEO184 5 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.89345 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEO184 5 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.89345 | 0.925 | 1.05 | Add 34 MVAR switched shunt at NEO184 5 161 kV
04ALL | ERIS | Voltage | NEO184 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90879 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEO184 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90879 | 0.925 | 1.05 | Add 34 MVAR switched shunt at NEO184 5 161 kV
04ALL | ERIS | Voltage | NEO398 2 | 26SP | V | 267142 |  |  |  |  | 1.0554 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEOSHO 4 | 29WP | V | Single 532793 NEOSHO7 345 533023 N34534 138 533801 'N345 2 1 ' 13 2 |  |  |  |  | 0.87708 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEOSHO 4 | 29WP | V | Single 532793 NEOSHO7 345 533023 N34534 138 533801 'N345 2 1 ' 13 2 |  |  |  |  | 0.87708 | 0.93 | 1.05 | Add 220 MVAR SVC at NEOSHO 4 138 kV
04ALL | ERIS | Voltage | NEOSHO 4 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87878 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEOSHO 4 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87878 | 0.93 | 1.05 | Add 220 MVAR SVC at NEOSHO 4 138 kV
04ALL | ERIS | Voltage | NEOSHO 4 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87728 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEOSHO 4 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87728 | 0.93 | 1.05 | Add 220 MVAR SVC at NEOSHO 4 138 kV
04ALL | ERIS | Voltage | NEOSHO 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92275 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | NEOSHO 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92364 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | NEOSHO 7 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.88868 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEOSHO 7 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.88868 | 0.95 | 1.05 | Add 160 MVAR SVC at NEOSHO 7 345 kV
04ALL | ERIS | Voltage | NEOSHO 7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87418 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEOSHO 7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87418 | 0.95 | 1.05 | Add 160 MVAR SVC at NEOSHO 7 345 kV
04ALL | ERIS | Voltage | NEOSHO 7 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87283 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEOSHO 7 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87283 | 0.95 | 1.05 | Add 160 MVAR SVC at NEOSHO 7 345 kV
04ALL | ERIS | Voltage | NEOSHON2 | 29WP | V | Single 532793 NEOSHO7 345 533023 N34534 138 533801 'N345 2 1 ' 13 2 |  |  |  |  | 0.89241 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEOSHON2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89075 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEOSHON2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89075 | 0.93 | 1.05 | Add 7 MVAR switched shunt at NEOSHON2 69 kV
04ALL | ERIS | Voltage | NEOSHON2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88953 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEOSHON4 | 29WP | V | Single 532793 NEOSHO7 345 533023 N34534 138 533801 'N345 2 1 ' 13 2 |  |  |  |  | 0.87716 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEOSHON4 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87883 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEOSHON4 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87733 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEOSHOS2 | 29WP | V | Single 532793 NEOSHO7 345 533023 N34534 138 533801 'N345 2 1 ' 13 2 |  |  |  |  | 0.89243 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEOSHOS2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89077 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEOSHOS2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88955 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEOSHOS4 | 29WP | V | Single 532793 NEOSHO7 345 533023 N34534 138 533801 'N345 2 1 ' 13 2 |  |  |  |  | 0.87708 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEOSHOS4 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87878 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEOSHOS4 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87728 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NESCTY 3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.85107 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NESCTY 3 | 26SP | V | P23:345:SUNC:SB_BRK482:::EHV: |  |  |  |  | 0.89006 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NESSCTY3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.85097 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NESSCTY3 | 26SP | V | P23:345:SUNC:SB_BRK482:::EHV: |  |  |  |  | 0.88999 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEVADA 5 | 29WP | V | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: |  |  |  |  | 0.90403 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEVADA 5 | 29WP | V | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: |  |  |  |  | 0.90403 | 0.93 | 1.05 | Add 42 MVAR SVC at NEVADA 5 161 kV
04ALL | ERIS | Voltage | NEVADA 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88457 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEVADA 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.8733 | 0.93 | 1.05 | Add 42 MVAR SVC at NEVADA 5 161 kV
04ALL | ERIS | Voltage | NEVADA 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.8733 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NICHOLS 5 | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.89927 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NINMILE4 | 29L | V | Single 520462 ASPEN4 138 520500 BEARCAT4 138 1 |  |  |  |  | 1.0745 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NINMLTP4 | 29L | V | Single 520462 ASPEN4 138 520500 BEARCAT4 138 1 |  |  |  |  | 1.0744 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NINMLTP4 | 29L | V | Single 520462 ASPEN4 138 520500 BEARCAT4 138 1 |  |  |  |  | 1.0744 | 0.9 | 1.05 | Add 16 MVAR switched shunt at NINMLTP4 138 kV
04ALL | ERIS | Voltage | NINN1WF7 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.93429 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NINN1WF7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91628 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NINN1WF7 | 29WP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.94958 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | NIXA 5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.89333 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NIXA 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89621 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NIXA 5 | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.89528 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NIXA NE2 | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.92808 | 0.93 | 1.05 | Add 30 MVAR switched shunt at NIXA NE2 69 kV
04ALL | ERIS | Voltage | NIXA NE2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92922 | 0.93 | 1.05 | Add 30 MVAR switched shunt at NIXA NE2 69 kV
04ALL | ERIS | Voltage | NKANCTY5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91362 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | NLOUISB5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89619 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | NLOUISB5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91274 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | NMANHT6 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89055 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NMANHT6 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.94862 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | NMEMREC2 | 26SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.91309 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NMEMREC2 | 29SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.91276 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NOL435 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.87068 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NOL435 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.87068 | 0.925 | 1.05 | Add 12 MVAR switched shunt at NOL435 5 161 kV
04ALL | ERIS | Voltage | NOL435 5 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.8911 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NOL435 5 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.8911 | 0.925 | 1.05 | Add 12 MVAR switched shunt at NOL435 5 161 kV
04ALL | ERIS | Voltage | NOL435 5 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.91176 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NORCATR3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8518 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NORTHST3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87415 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | NORTHST3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91557 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | NRAYMORE | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90091 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | NRAYMORE | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92807 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | NRAYMORETP 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90239 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | NRAYMORETP 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92933 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | NRSS7 | 29WP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.90065 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NRSS7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88815 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NRSS7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88815 | 0.95 | 1.05 | Add 12 MVAR SVC at NRSS7 345 kV
04ALL | ERIS | Voltage | NRSS7 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88679 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NRSS7 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88679 | 0.95 | 1.05 | Add 12 MVAR SVC at NRSS7 345 kV
04ALL | ERIS | Voltage | NRTHFORK-MK7 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.89087 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NSI 3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.86193 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NSI TAP3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.86316 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NTHLAND3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88666 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | NWGBEND3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89648 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | OAK432 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.90645 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | OAK432 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91882 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | OAKGRV 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91442 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | OBER T 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87361 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | OBERLIN3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87338 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ODESSA 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91837 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | OG ONEOK3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8175 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | OGALATP3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.81817 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | OLATHE 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8731 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | OLATHE 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90661 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | OPENSKY7 | 26SP | V | P12:345:OKGE:BKRBKR3571:::EHV: |  |  |  |  | 0.9132 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | OPENSKY7 | 29SP | V | P12:345:OKGE:BKRBKR3571:::EHV: |  |  |  |  | 0.91277 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ORDNCE 2 | 29WP | V | Single 532793 NEOSHO7 345 533023 N34534 138 533801 'N345 2 1 ' 13 2 |  |  |  |  | 0.89128 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ORDNCE 2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88539 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ORDNCE 2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88421 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ORDNJCT2 | 29WP | V | Single 532793 NEOSHO7 345 533023 N34534 138 533801 'N345 2 1 ' 13 2 |  |  |  |  | 0.89161 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ORDNJCT2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88594 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ORDNJCT2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88475 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ORO110 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.9057 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ORO110 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91838 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ORRICK 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91986 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | OSAGE 3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.83079 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | OSAGE 3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.85872 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | OSAGE 3 | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92046 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | OSAGE J3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.83192 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | OSAGE J3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.85979 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | OSAGE J3 | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.9211 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | OSAWAT 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90566 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | OSAWTM_CAP5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91256 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | OSAWTM_CAP5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.9067 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | OSBURN | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.89496 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | OTTRCRK3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88136 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | OTTRCRK3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89451 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | OTTRCRK4 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88805 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | OTTRCRK4 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89932 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | OVERLPK5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91232 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | OVERLPK5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87782 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | OXFORD 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.905 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | OXFORD 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87543 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | OZD312 5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.88963 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | OZD312 5 | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.90161 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | OZD312 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91054 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | OZK457 5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.88933 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | OZK457 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.9004 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | OZK457 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.9004 | 0.925 | 1.05 | Add 4 MVAR switched shunt at OZK457 5 161 kV
04ALL | ERIS | Voltage | OZK457 5 | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.89006 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | OZK457 5 | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.89006 | 0.925 | 1.05 | Add 4 MVAR switched shunt at OZK457 5 161 kV
04ALL | ERIS | Voltage | PALMER3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.89672 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | PAOLA 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91112 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | PAOLA 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90547 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | PARALEL3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92537 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | PAULINE3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88467 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | PECULR 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91433 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | PECULR 7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90497 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | PECULR 7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88471 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | PECULRS5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91842 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | PEIL 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89522 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | PENTAGN3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.9028 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | PFEIFER 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.83421 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | PFLUMM 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87999 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | PFLUMM 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91575 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | PH RUN 3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.84105 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | PHILL 7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91846 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | PHILL 7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91846 | 0.95 | 1.05 | Add 0.02 MVAR switched shunt at PHILL 7 345 kV
04ALL | ERIS | Voltage | PHILL 7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89515 | 0.95 | 1.05 | Add 0.02 MVAR switched shunt at PHILL 7 345 kV
04ALL | ERIS | Voltage | PHLBURG3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.80763 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | PHLBURG3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89476 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | PIONTAP3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86482 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | PIONTAP3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.84381 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | PIPER 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8937 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | PK_GOAB3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86954 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | PK_GOAB3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.83299 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | PLAINVL3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.81466 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | PLSNTPR3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86305 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | PLSNTPR3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85244 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | PLSTVAL5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90423 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | PLSTVAL5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92781 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | PLTCTY 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92871 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | PNTPR-GOAB3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86382 | 0.9 | 1.05 | Add 40 MVAR switched shunt at PNTPR-GOAB3 115 kV
04ALL | ERIS | Voltage | PNTPR-GOAB3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86382 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | PNTPR-GOAB3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85321 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | POPE | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92306 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | POSTROCK6 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.75879 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | POSTROCK6 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.83889 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | POSTROCK7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.73076 | 0.9 | 1.05 | Add 210 MVAR SVC at POSTROCK7 345 kV
04ALL | ERIS | Voltage | POSTROCK7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.73076 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | POSTROCK7 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.81571 | 0.9 | 1.05 | Add 210 MVAR SVC at POSTROCK7 345 kV
04ALL | ERIS | Voltage | POSTROCK7 | 29WP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87375 | 0.9 | 1.05 | Add 210 MVAR SVC at POSTROCK7 345 kV
04ALL | ERIS | Voltage | POSTROCK7 | 29WP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87375 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | PRAIRIE3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.79418 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | PRAIRIE3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.82312 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | PRAIRIE3 | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89096 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | PRALEE 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91891 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | PRAXAIR2 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85369 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | PRAXAIR2 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.83851 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | PRGROVE2 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.90582 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | PUCKETT3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86954 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | PUCKETT3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.83299 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | PUR421 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.91692 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | PUR421 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92133 | 0.925 | 1.05 | None
04ALL | ERIS | Voltage | QUARRY 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87878 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | QUARRY 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91293 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | RANDLPH5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91413 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | RANSOM 2 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.81785 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | RANSOM 2 | 26SP | V | P23:345:SUNC:SB_BRK482:::EHV: |  |  |  |  | 0.86921 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | RANSOM 3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.82113 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | RANSOM 3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.82113 | 0.9 | 1.05 | Add 8 MVAR switched shunt at RANSOM 3 115 kV
04ALL | ERIS | Voltage | RANSOM 3 | 26SP | V | P23:345:SUNC:SB_BRK482:::EHV: |  |  |  |  | 0.87214 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | RANSOM 3 | 26SP | V | P23:345:SUNC:SB_BRK482:::EHV: |  |  |  |  | 0.87214 | 0.9 | 1.05 | Add 8 MVAR switched shunt at RANSOM 3 115 kV
04ALL | ERIS | Voltage | RATLIFF2 | 29WP | V | P12:138:OKGE:BKRBKR4330:::HV: |  |  |  |  | 0.91603 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | RAYTOWN5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.9068 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | RDS295 5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.88897 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | RDS295 5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.88897 | 0.925 | 1.05 | Add 0.23 MVAR switched shunt at RDS295 5 161 kV
04ALL | ERIS | Voltage | RDS295 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90596 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | RDS295 5 | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.89672 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | RDS295 5 | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.89672 | 0.925 | 1.05 | Add 0.23 MVAR switched shunt at RDS295 5 161 kV
04ALL | ERIS | Voltage | READING3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.81329 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | READING3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.8418 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | READING3 | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90522 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | REDEL 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89213 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | REDEL 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91518 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | REDHLSW4 | 29L | V | Single 520462 ASPEN4 138 520500 BEARCAT4 138 1 |  |  |  |  | 1.0755 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | REDHLSW4 | 29L | V | Single 520462 ASPEN4 138 520500 BEARCAT4 138 1 |  |  |  |  | 1.0755 | 0.9 | 1.05 | Add 6 MVAR switched shunt at REDHLSW4 138 kV
04ALL | ERIS | Voltage | REDLIN 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.81121 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | REDWILO3 | 29SP | V | P42:345:NPPD:BKR-AXT-3306:::: |  |  |  |  | 0.86866 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | REDWILO3 | 29SP | V | P42:345:NPPD:BKR-AXT-3306:::: |  |  |  |  | 0.86866 | 0.9 | 1.05 | Add 203 MVAR switched shunt at REDWILO3 345 kV
04ALL | ERIS | Voltage | REEDER 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91267 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | REEDER 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87752 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | RICHFLD3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89408 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | RICHFLD3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86028 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | RICHMND5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91542 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | RILEY 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87241 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | RILEY 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90613 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | RIV167 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.9064 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | RIV167 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92141 | 0.925 | 1.05 | None
04ALL | ERIS | Voltage | RIV4525 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.906 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | RIV4525 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92098 | 0.925 | 1.05 | None
04ALL | ERIS | Voltage | RIV452T 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.90642 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | RIV452T 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.9214 | 0.925 | 1.05 | None
04ALL | ERIS | Voltage | RIV453 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.90756 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | RIV453 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92249 | 0.925 | 1.05 | None
04ALL | ERIS | Voltage | RIVRSID5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91367 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | RKY_RDG4 | 29L | V | P12:345:OKGE:BKRBKR4890:::EHV: |  |  |  |  | 1.0728 | 0.92 | 1.05 | Add 0.5 MVAR switched shunt at RKY_RDG4 138 kV
04ALL | ERIS | Voltage | RKY_RDG4 | 29L | V | P12:345:OKGE:BKRBKR4890:::EHV: |  |  |  |  | 1.0728 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | RNM393 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.88778 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | RNM393 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90398 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | RNM393 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91262 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | RNRIDGE5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91796 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | RNRIDGE_CAP5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91901 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | ROC296 2 | 26SP | V | 267142 |  |  |  |  | 1.0567 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ROC296 2 | 26SP | V | 267142 |  |  |  |  | 1.0567 | 0.925 | 1.05 | Add 1.1 MVAR switched shunt at ROC296 2 69 kV
04ALL | ERIS | Voltage | ROEPARK5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88993 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | ROEPARK5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92014 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | RUBART 3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86453 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | RUBART 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86359 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | RUSLPMP3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.83519 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | RUSLSOL3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85879 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | RUSSELL3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85879 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | S ALMA 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8809 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | S GAGEE3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86993 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | S HAYS 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.83653 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | S HAYS6 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.77613 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | S HAYS6 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85162 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | S.OTTWA5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90514 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | S.OTTWA5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91455 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SAILBOA2 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.90671 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SAILBOA2 | 26SP | V | P23:345:WERE:N345-345-20:EHV: |  |  |  |  | 0.9169 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SALICY32 | 29WP | V | Single 505550 SALISAW5 161 512662 SALINT5 161 Z1 |  |  |  |  | 0.89928 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SALINA 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87305 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SALINA 3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91402 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SALINE 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.81866 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | SALISAWK 2 | 29WP | V | Single 505550 SALISAW5 161 512662 SALINT5 161 Z1 |  |  |  |  | 0.89881 | 0.9 | 1.05 | Add 15 MVAR switched shunt at SALISAWK 2 69 kV
04ALL | ERIS | Voltage | SANDCREK-MK7 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.88874 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SAT-TAP3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86372 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SAT-TAP3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.83412 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | SATANTA3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86054 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SATANTA3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85266 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | SATATAP3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86379 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SATATAP3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85592 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | SATMKEC3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86372 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SATMKEC3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.83412 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | SCHILNG3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91106 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SCHILNG3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87113 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SCRANTN3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.85025 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SCRANTN3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87736 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SE1GREE2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92645 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SE1GREE2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.926 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SEFAYTV5 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.90138 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SEGNTP 3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.85081 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SEGNTP 3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.85081 | 0.9 | 1.05 | Add 40 MVAR switched shunt at SEGNTP 3 115 kV
04ALL | ERIS | Voltage | SEGUIN 3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.84825 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SEOTTWA5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90493 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SEOTTWA5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91644 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SEWARD-3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88012 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SEWARD-3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85086 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | SG12COL4 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.9252 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SHALE 7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.93382 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | SHAM 3WT | 26SP | V | P12:138:AEPW-WFEC:LAKEP4WT:RUSSELL4::: |  |  |  |  | 0.91822 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SHAM 4WT | 29SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.85725 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SHAM 4WT | 26SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.86164 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SHAM 4WT | 29WP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.86185 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SHARNSP3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.85671 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SHARNSP3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.85671 | 0.9 | 1.05 | Add 1.1 MVAR switched shunt at SHARNSP3 115 kV
04ALL | ERIS | Voltage | SHAWNEE3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86843 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SHAWNEE5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88868 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SHAWNEE5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92358 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SHERWOD3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87388 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SHIPERD5 | 29WP | V | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: |  |  |  |  | 0.89096 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SHIPERD5 | 26SP | V | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: |  |  |  |  | 0.91884 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SHIPERD7 | 29WP | V | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: |  |  |  |  | 0.89096 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SHIPERD7 | 26SP | V | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: |  |  |  |  | 0.91884 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SHOLCRK5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91511 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SHWNMSN5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88473 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SHWNMSN5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92033 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SIBLEY 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92452 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SIBLEYPL | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.9219 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SIBLEYRD2 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.87338 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SIBLEYRD2 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.89601 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SIBLEYRD2 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.91558 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SIBLEYRD5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.87462 | 0.925 | 1.05 | Add 32 MVAR SVC at SIBLEYRD5 161 kV
04ALL | ERIS | Voltage | SIBLEYRD5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.87462 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SIBLEYRD5 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.89685 | 0.925 | 1.05 | Add 32 MVAR SVC at SIBLEYRD5 161 kV
04ALL | ERIS | Voltage | SIBLEYRD5 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.89685 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SIBLEYRD5 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.91649 | 0.925 | 1.05 | Add 32 MVAR SVC at SIBLEYRD5 161 kV
04ALL | ERIS | Voltage | SIBLEYRD5 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.91649 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SILMCTY2 | 29WP | V | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: |  |  |  |  | 0.89699 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SILMCTY5 | 29WP | V | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: |  |  |  |  | 0.89955 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SILOAM 5 | 29WP | V | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: |  |  |  |  | 0.90124 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SILOAMSP 5 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.89852 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SILSPWW5 | 29WP | V | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: |  |  |  |  | 0.89885 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SLKHILLS 4 | 29L | V | P42:345:OKGE:SB_GRNT7313:::EHV: |  |  |  |  | 1.0578 | 0.9 | 1.05 | Add 5 MVAR switched shunt at SLKHILLS 4 138 kV
04ALL | ERIS | Voltage | SLMNFRK7 | 29SP | V | P42:345:NPPD:BKR-AXT-3306:::: |  |  |  |  | 0.87696 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SMITH-C3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86302 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | SMOKYHL6 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85693 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | SMOKYHLLS3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.9086 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SMOKYHLLS3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86887 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SMTHVL 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92358 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SNDCRKTP-MK7 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.88974 | 0.9 | 1.05 | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV
04ALL | ERIS | Voltage | SO GATE3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90825 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SO GATE3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8683 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SOSPRDL5 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.89388 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SOUTHTN3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88208 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SOUTHTN3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92225 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SPRDALT2 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.88984 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SPRGFLD5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.90425 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SPRGFLD5 | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.90203 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SPRGFLD5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90539 | 0.92 | 1.05 | None
04ALL | ERIS | Voltage | SPRGHL 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88771 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SPRGHL 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91353 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SPRINT15 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87352 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SPRINT15 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90702 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SPRINT25 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87348 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SPRINT25 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90698 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SPRUCE 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92602 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SSLINC2 | 29WP | V | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: |  |  |  |  | 0.88405 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SSLINC2 | 29WP | V | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: |  |  |  |  | 0.88405 | 0.9 | 1.05 | Add 0.04 MVAR switched shunt at SSLINC2 69 kV
04ALL | ERIS | Voltage | SSMOSS2 | 29WP | V | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: |  |  |  |  | 0.89605 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SSNEWN2 | 29WP | V | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: |  |  |  |  | 0.88664 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SSNORT2 | 29WP | V | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: |  |  |  |  | 0.88442 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SSSWES2 | 29WP | V | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: |  |  |  |  | 0.89604 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SSSWTP2 | 29WP | V | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: |  |  |  |  | 0.89676 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | STAGGHL3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89357 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | STHTOWN5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88935 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | STHTOWN5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91795 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | STHTOWN_CAP5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89037 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | STHTOWN_CAP5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91901 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | STILWEL5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89487 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | STILWEL5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91605 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | STILWEL7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89484 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | STILWEL7 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.8757 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | STK324 2 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.90712 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | STK324 2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88909 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | STK324 2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.8829 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | STK324J2 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.90712 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | STK324J2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88909 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | STK324J2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88291 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | STK418 2 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.90421 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | STK418 2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88542 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | STK418 2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87911 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | STL439 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.90305 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | STL439 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91992 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | STROTHR5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91534 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | STULL 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87082 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | STULL T3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87083 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SUB M-161 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.9077 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SUB N-161 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90823 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SUBLETE3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86434 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SUBLETE3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.84332 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | SUMMIT 3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90833 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SUMMIT 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86757 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SUMMIT 6 | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.93873 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SUMMIT 6 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85882 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SUMMIT 6 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89998 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SUMMIT 7 | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90874 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SUMMIT 7 | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90874 | 0.95 | 1.05 | Add 213 MVAR SVC at SUMMIT 7 345 kV
04ALL | ERIS | Voltage | SUMMIT 7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.82867 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SUMMIT 7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.82867 | 0.95 | 1.05 | Add 213 MVAR SVC at SUMMIT 7 345 kV
04ALL | ERIS | Voltage | SUMMIT 7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.86747 | 0.95 | 1.05 | Add 213 MVAR SVC at SUMMIT 7 345 kV
04ALL | ERIS | Voltage | SUMMIT 7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.86747 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SUNSHINE5 | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.91596 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SUNSHINE5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.88892 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SVRCK469 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.89211 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SVRCK469 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90856 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SVRCK469 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91742 | 0.925 | 1.05 | None
04ALL | ERIS | Voltage | SWENSON -MK7 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.89028 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SWISVAL6 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8503 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SWISVAL6 | 29WP | V | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: |  |  |  |  | 0.92224 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SWISVAL6 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91096 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SWISVAL7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.84028 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SWISVAL7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.84028 | 0.95 | 1.05 | Add 114 MVAR SVC at SWISVAL7 345 kV
04ALL | ERIS | Voltage | SWISVAL7 | 29WP | V | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: |  |  |  |  | 0.91123 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SWISVAL7 | 29WP | V | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: |  |  |  |  | 0.91123 | 0.95 | 1.05 | Add 114 MVAR SVC at SWISVAL7 345 kV
04ALL | ERIS | Voltage | SWISVAL7 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89878 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SWISVAL7 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89878 | 0.95 | 1.05 | Add 114 MVAR SVC at SWISVAL7 345 kV
04ALL | ERIS | Voltage | SWITZER5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8711 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SWITZER5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90489 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SWLWRNC3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87051 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SWOPE N5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90141 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SWOPE N5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92888 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SWOPE S5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89869 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SWOPE S5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92646 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SWPINEY5 | 29WP | V | P23:500:EES-EAI:KEO:B4921::EHV: |  |  |  |  | 0.90561 | 0.92 | 1.05 | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV
04ALL | ERIS | Voltage | SYRACUS3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87908 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | TABLEBUT-MK7 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.89433 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | TAYLOR 4 | 29WP | V | P23:345:WERE:N345-345-20:EHV: |  |  |  |  | 0.88594 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | TAYLOR 4 | 29WP | V | P23:345:WERE:N345-345-20:EHV: |  |  |  |  | 0.88594 | 0.93 | 1.05 | Add 13 MVAR switched shunt at TAYLOR 4 138 kV
04ALL | ERIS | Voltage | TAYLOR 4 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89786 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | TAYLOR 4 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89786 | 0.93 | 1.05 | Add 13 MVAR switched shunt at TAYLOR 4 138 kV
04ALL | ERIS | Voltage | TAYLOR 4 | 26SP | V | P23:345:WERE:N345-345-20:EHV: |  |  |  |  | 0.89592 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | TAYLOR 4 | 26SP | V | P23:345:WERE:N345-345-20:EHV: |  |  |  |  | 0.89592 | 0.93 | 1.05 | Add 13 MVAR switched shunt at TAYLOR 4 138 kV
04ALL | ERIS | Voltage | TBBEARD2 | 26SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.90482 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | TBBEARD2 | 29SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.90024 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | TBBEARD2 | 29WP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.90917 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | TCHOPE 3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90056 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | TCHOPE 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85836 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | TCRILEY 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87774 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | TCSEVRN3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.92084 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | TECHILE3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87088 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | TECHILL6 | 29WP | V | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: |  |  |  |  | 0.93965 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | TECHILL6 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91845 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | TECHILL6 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85456 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | TECHILL6 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85456 | 0.95 | 1.05 | Add 13 MVAR switched shunt at TECHILL6 230 kV
04ALL | ERIS | Voltage | TECHILW3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8709 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | TERRACE5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90957 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | THORNTN3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.9257 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | TIFFANY5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91467 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | TIOGA 4 | 29WP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.88131 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | TIOGA 4 | 29WP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.88131 | 0.93 | 1.05 | Add 36 MVAR SVC at TIOGA 4 138 kV
04ALL | ERIS | Voltage | TIOGA 4 | 26SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.87621 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | TIOGA 4 | 26SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.87621 | 0.93 | 1.05 | Add 36 MVAR SVC at TIOGA 4 138 kV
04ALL | ERIS | Voltage | TIOGA 4 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87701 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | TIOGA 4 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87701 | 0.93 | 1.05 | Add 36 MVAR SVC at TIOGA 4 138 kV
04ALL | ERIS | Voltage | TIP292 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.88858 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | TIP292 5 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.9044 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | TIP292 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91427 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | TOMHAWK5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88114 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | TOMHAWK5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91227 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | TONECE5 | 29WP | V | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: |  |  |  |  | 0.89809 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | TONECESTR2 | 29WP | V | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: |  |  |  |  | 0.89175 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | TONGATP3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90288 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | TONNEC2 | 29WP | V | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: |  |  |  |  | 0.89527 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | TONTITN7 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.8792 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | TONTITN7 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.8792 | 0.92 | 1.05 | Add 68 MVAR SVC at TONTITN7 345 kV
04ALL | ERIS | Voltage | TROOST 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90225 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | TROOST 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92912 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | TURNER 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89748 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | TURNER_RD5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90096 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | TURNER_RD5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92387 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | TV1MNDV4 | 26SP | V | P23:345:WERE:N345-345-20:EHV: |  |  |  |  | 0.88673 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | TV1MNDV4 | 26SP | V | P23:345:WERE:N345-345-20:EHV: |  |  |  |  | 0.88673 | 0.93 | 1.05 | Add 42 MVAR switched shunt at TV1MNDV4 138 kV
04ALL | ERIS | Voltage | TV1MNDV4 | 29WP | V | P23:345:WERE:N345-345-20:EHV: |  |  |  |  | 0.87246 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | TV1MNDV4 | 29WP | V | P23:345:WERE:N345-345-20:EHV: |  |  |  |  | 0.87246 | 0.93 | 1.05 | Add 42 MVAR switched shunt at TV1MNDV4 138 kV
04ALL | ERIS | Voltage | TV1MNDV4 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89422 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | TV1MNDV4 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89422 | 0.93 | 1.05 | Add 42 MVAR switched shunt at TV1MNDV4 138 kV
04ALL | ERIS | Voltage | TWA 5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91899 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | TXPLSTE2 | 29WP | V | MULTIGEN514941 |  |  |  |  | 0.91679 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | TXPLSTP2 | 29WP | V | MULTIGEN514941 |  |  |  |  | 0.91679 | 0.92 | 1.05 | Add 12 MVAR switched shunt at TXPLSTP2 69 kV
04ALL | ERIS | Voltage | TXSTELA2 | 29WP | V | MULTIGEN514941 |  |  |  |  | 0.9192 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ULYSPLT3 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85962 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ULYSPLT3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.82499 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | UNIONRG3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90183 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | UNIONRG3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85969 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | UNIONRG6 | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.94003 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | UNIONRG6 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.86911 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | UNIONRG6 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91081 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | VINE2 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.83172 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | VINEDE_N | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.83223 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | VINEDE_S | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.83172 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | VINETAP3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.83223 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | W.GRDNR7 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.94745 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | W.GRDNR7 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.94745 | 0.95 | 1.05 | Add 130 MVAR SVC at W.GRDNR7 345 kV
04ALL | ERIS | Voltage | W.GRDNR7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.8958 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | W.GRDNR7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.8958 | 0.95 | 1.05 | Add 130 MVAR SVC at W.GRDNR7 345 kV
04ALL | ERIS | Voltage | W.GRDNR7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8625 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | W.GRDNR7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8625 | 0.95 | 1.05 | Add 130 MVAR SVC at W.GRDNR7 345 kV
04ALL | ERIS | Voltage | WAGSTAF5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89994 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WAGSTAF5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91075 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WALDO 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.85168 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | WALDRON5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90081 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WASHBURN5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.88339 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WASHBURN5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.88339 | 0.92 | 1.05 | Add 22 MVAR switched shunt at WASHBURN5 161 kV
04ALL | ERIS | Voltage | WASHBURN5 | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.8931 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WASHBURN5 | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.8931 | 0.92 | 1.05 | Add 22 MVAR switched shunt at WASHBURN5 161 kV
04ALL | ERIS | Voltage | WASHBURN5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91876 | 0.92 | 1.05 | None
04ALL | ERIS | Voltage | WATHENA2 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90509 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WAVERLY3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88332 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WAVERLY3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.9273 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WAVERLY7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90818 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WAVERLY7 | 29WP | V | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: |  |  |  |  | 0.93554 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WAVERLY7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89839 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WEDINGTON | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.8972 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WEDINGTON5 | 29WP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.89715 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WELL 4WT | 26SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.85324 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WELL 4WT | 26SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.85324 | 0.92 | 1.05 | Add 0.02 MVAR switched shunt at WELL 4WT 138 kV
04ALL | ERIS | Voltage | WELL 4WT | 29SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.84369 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WELL 4WT | 29WP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.85201 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WELLGS4 | 26SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.85364 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WELLGS4 | 26SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.85364 | 0.92 | 1.05 | Add 21 MVAR switched shunt at WELLGS4 138 kV
04ALL | ERIS | Voltage | WELLGS4 | 29SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.84432 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WELLGS4 | 29SP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.84432 | 0.92 | 1.05 | Add 21 MVAR switched shunt at WELLGS4 138 kV
04ALL | ERIS | Voltage | WELLGS4 | 29WP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.85243 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WELLGS4 | 29WP | V | Single 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 |  |  |  |  | 0.85243 | 0.92 | 1.05 | Add 21 MVAR switched shunt at WELLGS4 138 kV
04ALL | ERIS | Voltage | WEST BELT 5 | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.89879 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WETHRBY5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90815 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WGARDNR5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90042 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WHARV4 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.8826 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WHARV4 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.8826 | 0.93 | 1.05 | Add 54 MVAR SVC at WHARV4 138 kV
04ALL | ERIS | Voltage | WHARV4 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87252 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WHARV4 | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92222 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WICHITA7 | 29WP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.91707 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WICHITA7 | 29WP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.91707 | 0.95 | 1.05 | Add 141 MVAR SVC at WICHITA7 345 kV
04ALL | ERIS | Voltage | WICHITA7 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90253 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WICHITA7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88275 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WICHITA7 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88275 | 0.95 | 1.05 | Add 141 MVAR SVC at WICHITA7 345 kV
04ALL | ERIS | Voltage | WILDHRS2 | 29WP | V | P12:138:OKGE:BKRBKR4330:::HV: |  |  |  |  | 0.90716 | 0.92 | 1.05 | Add 12 MVAR switched shunt at WILDHRS2 69 kV
04ALL | ERIS | Voltage | WILLIAM3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88502 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | WINJT N5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90145 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WINJT N5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92892 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WINJT S5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89872 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WINJT S5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92649 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WJCCTY 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90059 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WJCCTYW3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90056 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WKNNY 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.815 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | WLDHRST2 | 29WP | V | P12:138:OKGE:BKRBKR4330:::HV: |  |  |  |  | 0.91493 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WMBROS 3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.79644 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WMBROS 3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.82488 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WMBROS 3 | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89474 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WMBROSJ3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.79644 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WMBROSJ3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.82488 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WMBROSJ3 | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89474 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WOLCOTT5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89624 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | WOLFCRK7 | 29WP | V | P23:345:WERE:WOLF-345-50:EHV: |  |  |  |  | 0.96033 | 0.99 | 1.03 | None
04ALL | ERIS | Voltage | WOODLND5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.88377 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WOODLND5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92075 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WREN 3 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.87086 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WROGERS 5 | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.9151 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WROGERS 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.88826 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WROGERS 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.88826 | 0.92 | 1.05 | Add 38 MVAR SVC at WROGERS 5 161 kV
04ALL | ERIS | Voltage | WSTELEC5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.9142 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WSTELEC_CAP5 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91519 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WTCLF 3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.84863 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WWR477 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.90301 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WWR477 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91988 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WWUPLNT4 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91053 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WWUPLNT4 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.90122 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | YOST 2 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.91802 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | YOST 2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92356 | 0.93 | 1.05 | None
04NR | NRIS | Voltage | GRAY CO3 | 29L | V | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 |  |  |  |  | 1.0882 | 0.9 | 1.05 | Add 0.09 MVAR switched shunt at GRAY CO3 115 kV
04NR | NRIS | Voltage | GYCOTAP3 | 29L | V | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 |  |  |  |  | 1.0882 | 0.9 | 1.05 | Mitigated at another bus
04NR | NRIS | Voltage | HAGGARD3 | 29L | V | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 |  |  |  |  | 1.0882 | 0.9 | 1.05 | Mitigated at another bus
04NR | NRIS | Voltage | UNDERWOOD 2 | 29L | V | GEN-2024-345_POI_510380_Generator_outage |  |  |  |  | 1.1323 | 0.9 | 1.05 | Add 16 MVAR switched shunt at UNDERWOOD 2 345 kV
05ALL | ERIS | Voltage | A21-003-TAP | 29WP | V | Single 528669 LE-STKLDRTP2 69 528725 LE-PRICE2 69 1 |  |  |  |  | 0.88398 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | ALTUSJT4 | 29L | V | P12:345:OKGE-AEP:BKRBKR4291:::EHV: |  |  |  |  | 1.0697 | 0.92 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | ARNOLD3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.8822 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | ASGI-2021-03 | 29WP | V | Single 528669 LE-STKLDRTP2 69 528725 LE-PRICE2 69 1 |  |  |  |  | 0.88398 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | BLKKET TP4 | 29L | V | P12:345:OKGE-AEP:BKRBKR4291:::EHV: |  |  |  |  | 1.0623 | 0.92 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | BULOJ4 | 29L | V | P12:345:OKGE-AEP:BKRBKR4291:::EHV: |  |  |  |  | 1.06 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | CL-AFTP4 | 29L | V | Single 787920 G24-365-TAP 345 787921 GEN-2024-365 345 1 |  |  |  |  | 1.0726 | 0.92 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | CL-AFTP4 | 29L | V | Single 787920 G24-365-TAP 345 787921 GEN-2024-365 345 1 |  |  |  |  | 1.0726 | 0.92 | 1.05 | Add 7 MVAR switched shunt at CL-AFTP4 138 kV
05ALL | ERIS | Voltage | CLIN-AF4 | 29L | V | Single 787920 G24-365-TAP 345 787921 GEN-2024-365 345 1 |  |  |  |  | 1.0726 | 0.92 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | DEAFSMITH 6 | 29L | V | P12:230:SPS:K11_K21::1_BUSHL_DFSMTH_PLANTX:HV: |  |  |  |  | 1.0903 | 0.9 | 1.05 | Add 18 MVAR switched shunt at DEAFSMITH 6 230 kV
05ALL | ERIS | Voltage | DEMPSEYR POI | 29L | V | P12:230:AEPW:SWEETWT6:CHISHOLM6::: |  |  |  |  | 1.1228 | 0.92 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | DOXEY 4 | 29L | V | P12:345:OKGE-AEP:BKRBKR4291:::EHV: |  |  |  |  | 1.0623 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | DURHAM 4 | 29L | V | P12:345:OKGE-AEP:BKRBKR4291:::EHV: |  |  |  |  | 1.0552 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | ELDORDO2 | 29L | V | Single 787920 G24-365-TAP 345 787921 GEN-2024-365 345 1 |  |  |  |  | 1.0622 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | ELKCITY2 | 29L | V | P12:345:OKGE-AEP:BKRBKR4291:::EHV: |  |  |  |  | 1.0616 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | ELKCTY-4 | 29L | V | P12:345:OKGE-AEP:BKRBKR4291:::EHV: |  |  |  |  | 1.0632 | 0.92 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | ELLIS 2 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.87426 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | ERICK 4 | 29L | V | P12:345:OKGE-AEP:BKRBKR4291:::EHV: |  |  |  |  | 1.0608 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | FALCNRD4 | 29L | V | P12:345:OKGE-AEP:BKRBKR4291:::EHV: |  |  |  |  | 1.0627 | 0.92 | 1.05 | Add 18 MVAR switched shunt at FALCNRD4 138 kV
05ALL | ERIS | Voltage | FALCNRD4 | 29L | V | P12:345:OKGE-AEP:BKRBKR4291:::EHV: |  |  |  |  | 1.0627 | 0.92 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | FARGO 7 | 29WP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 1.0526 | 0.9 | 1.05 | Add 0.8 MVAR switched shunt at FARGO 7 115 kV
05ALL | ERIS | Voltage | G24-158-TAP | 29L | V | P12:345:OKGE-AEP:BKRBKR4291:::EHV: |  |  |  |  | 1.07 | 0.92 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | G24-161-TAP | 29L | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 1.0811 | 0.92 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | G24-161-TAP | 29L | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 1.0811 | 0.92 | 1.05 | Add 0.7 MVAR switched shunt at G24-161-TAP 138 kV
05ALL | ERIS | Voltage | G24-357-TAP | 29L | V | Single 524875 OASIS6 230 787680 G24-357-TAP 230 1 |  |  |  |  | 1.0636 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | GB-AUSTIN 3 | 29L | V | P12:230:AEPW:SWEETWT6:CHISHOLM6::: |  |  |  |  | 1.0561 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | GB-F_ELI_TP3 | 29L | V | P12:230:AEPW:SWEETWT6:CHISHOLM6::: |  |  |  |  | 1.0569 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | GB-F_ELLIOT3 | 29L | V | P12:230:AEPW:SWEETWT6:CHISHOLM6::: |  |  |  |  | 1.0561 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | GB-SHAMROCK | 26SP | V | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 |  |  |  |  | 0.90398 | 0.92 | 1.05 | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV
05ALL | ERIS | Voltage | GB-SHAMROCK | 29SP | V | Single 523770 GRAPEVINE3 115 524088 KIRBY3 115 1 |  |  |  |  | 0.91531 | 0.92 | 1.05 | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV
05ALL | ERIS | Voltage | GEN-2024-079 | 29L | V | Single 524875 OASIS6 230 787680 G24-357-TAP 230 1 |  |  |  |  | 1.0615 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | GEN-2024-080 | 29L | V | Single 524875 OASIS6 230 787680 G24-357-TAP 230 1 |  |  |  |  | 1.0615 | 0.9 | 1.05 | Add 2 MVAR switched shunt at GEN-2024-080 230 kV
05ALL | ERIS | Voltage | GEN-2024-157 | 29L | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 1.0816 | 0.92 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | GEN-2024-157 | 29L | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 1.0816 | 0.92 | 1.05 | Add 0.9 MVAR switched shunt at GEN-2024-157 138 kV
05ALL | ERIS | Voltage | GEN-2024-158 | 29L | V | P12:345:OKGE-AEP:BKRBKR4291:::EHV: |  |  |  |  | 1.07 | 0.92 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | GEN-2024-161 | 29L | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 1.0811 | 0.92 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | GEN-2024-161 | 29L | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 1.0811 | 0.92 | 1.05 | Add 0.7 MVAR switched shunt at GEN-2024-161 138 kV
05ALL | ERIS | Voltage | GEN-2024-357 | 29L | V | Single 524875 OASIS6 230 787680 G24-357-TAP 230 1 |  |  |  |  | 1.0636 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | GOVE 3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.88533 | 0.9 | 1.05 | Add 30 MVAR switched shunt at GOVE 3 115 kV
05ALL | ERIS | Voltage | GOVE 3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.88533 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | GRAPEVINE 6 | 29L | V | P12:230:AEPW:SWEETWT6:CHISHOLM6::: |  |  |  |  | 1.1046 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | HAMJCT 2 | 29L | V | P12:345:OKGE-AEP:BKRBKR4291:::EHV: |  |  |  |  | 1.0634 | 0.92 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | HI_BNKS1_WF7 | 29SP | V | Single 515378 WWARD9 765 532828 VIOLA9 765 1 |  |  |  |  | 1.0809 | 0.95 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | HI_BNKS1_WF7 | 29WP | V | P12:345:WERE:WAVS-WOLF-345:EHV: |  |  |  |  | 1.0781 | 0.95 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | HI_BNKS2_WF7 | 29SP | V | Single 515378 WWARD9 765 532828 VIOLA9 765 1 |  |  |  |  | 1.0858 | 0.95 | 1.05 | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV
05ALL | ERIS | Voltage | HI_BNKS2_WF7 | 29WP | V | P12:345:WERE:WAVS-WOLF-345:EHV: |  |  |  |  | 1.0829 | 0.95 | 1.05 | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV
05ALL | ERIS | Voltage | HOB-JCT2 | 29L | V | Single 787920 G24-365-TAP 345 787921 GEN-2024-365 345 1 |  |  |  |  | 1.0887 | 0.92 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | J12_____-MK7 | 29WP | V | Single 515378 WWARD9 765 532828 VIOLA9 765 1 |  |  |  |  | 0.89451 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | LAKEP4WT | 29L | V | Single 787920 G24-365-TAP 345 787921 GEN-2024-365 345 1 |  |  |  |  | 1.0579 | 0.92 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | LAKEP4WT | 29L | V | Single 787920 G24-365-TAP 345 787921 GEN-2024-365 345 1 |  |  |  |  | 1.0579 | 0.92 | 1.05 | Add 1.2 MVAR switched shunt at LAKEP4WT 138 kV
05ALL | ERIS | Voltage | LE-BRONCO 2 | 29WP | V | Single 528669 LE-STKLDRTP2 69 528725 LE-PRICE2 69 1 |  |  |  |  | 0.88976 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | LE-BRONCOTP2 | 29WP | V | Single 528669 LE-STKLDRTP2 69 528725 LE-PRICE2 69 1 |  |  |  |  | 0.8956 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | LE-LEWIS 2 | 29WP | V | Single 528669 LE-STKLDRTP2 69 528725 LE-PRICE2 69 1 |  |  |  |  | 0.88389 | 0.9 | 1.05 | Add 9.3 MVAR switched shunt at LE-LEWIS 2 69 kV
05ALL | ERIS | Voltage | LE-PRICE 2 | 29WP | V | Single 528669 LE-STKLDRTP2 69 528725 LE-PRICE2 69 1 |  |  |  |  | 0.88355 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | MARTHA 4 | 29L | V | Single 787920 G24-365-TAP 345 787921 GEN-2024-365 345 1 |  |  |  |  | 1.0751 | 0.92 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | MOCCASIN-MK7 | 29WP | V | Single 515378 WWARD9 765 532828 VIOLA9 765 1 |  |  |  |  | 0.88257 | 0.9 | 1.05 | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV
05ALL | ERIS | Voltage | MOORHED7 | 29WP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 1.0518 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NESCTY 3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.89804 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NESSCTY3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.89796 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-BOOKER 2 | 29SP | V | Single 523093 HITCHLAND3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.85057 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-BOOKER 2 | 29SP | V | Single 523093 HITCHLAND3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.85057 | 0.9 | 1.05 | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV
05ALL | ERIS | Voltage | NP-BOOKER 2 | 26SP | V | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.85323 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-BOOKER 2 | 26SP | V | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.85323 | 0.9 | 1.05 | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV
05ALL | ERIS | Voltage | NP-GLAZIR_G2 | 26SP | V | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.62697 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-GLAZIR_G2 | 29SP | V | Single 523267 PRINGLE6 230 523979 HARRNG_EST6 230 1 |  |  |  |  | 0.60619 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-HARBOUR 2 | 29SP | V | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.85924 | 0.9 | 1.05 | Add 7 MVAR switched shunt at NP-HARBOUR 2 69 kV
05ALL | ERIS | Voltage | NP-HARBOUR 2 | 29SP | V | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.85924 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-HARBOUR 2 | 26SP | V | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.8783 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-LIPSCOMB2 | 26SP | V | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.58751 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-LIPSCOMB2 | 29SP | V | Single 523267 PRINGLE6 230 523979 HARRNG_EST6 230 1 |  |  |  |  | 0.56337 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-LIPS_SHA2 | 26SP | V | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.58751 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-LIPS_SHA2 | 26SP | V | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.58751 | 0.9 | 1.05 | Add 0.1 MVAR switched shunt at NP-LIPS_SHA2 69 kV
05ALL | ERIS | Voltage | NP-LIPS_SHA2 | 29SP | V | Single 523267 PRINGLE6 230 523979 HARRNG_EST6 230 1 |  |  |  |  | 0.56337 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-LUCKY_CR2 | 26SP | V | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.71965 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-LUCKY_CR2 | 29SP | V | Single 523267 PRINGLE6 230 523979 HARRNG_EST6 230 1 |  |  |  |  | 0.70742 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-LUCKY_G 2 | 26SP | V | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.7198 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-LUCKY_G 2 | 29SP | V | Single 523267 PRINGLE6 230 523979 HARRNG_EST6 230 1 |  |  |  |  | 0.70759 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-OCHILTRE2 | 29SP | V | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.89471 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-OCHILTRE3 | 29SP | V | Single 523093 HITCHLAND3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.86367 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-OCHILTRE3 | 26SP | V | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.85778 | 0.9 | 1.05 | Add 12 MVAR switched shunt at NP-OCHILTRE3 115 kV
05ALL | ERIS | Voltage | NP-OCHILTRE3 | 26SP | V | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.85778 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-PERDURE 3 | 29SP | V | Single 523093 HITCHLAND3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.87308 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-PERDURE 3 | 26SP | V | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.86614 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-PERDUR_G3 | 29SP | V | Single 523093 HITCHLAND3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.87647 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-PERDUR_G3 | 26SP | V | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.86929 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-PERRYTON2 | 29SP | V | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.85925 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-PERRYTON2 | 26SP | V | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.87562 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-PERYTN_G2 | 29SP | V | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.86163 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-PERYTN_G2 | 29SP | V | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.86163 | 0.9 | 1.05 | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV
05ALL | ERIS | Voltage | NP-PERYTN_G2 | 26SP | V | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.87777 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-PERYTN_G2 | 26SP | V | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.87777 | 0.9 | 1.05 | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV
05ALL | ERIS | Voltage | NP-ROGERS 2 | 29SP | V | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.84406 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-ROGERS 2 | 29SP | V | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.84406 | 0.9 | 1.05 | Add 0.12 MVAR switched shunt at NP-ROGERS 2 69 kV
05ALL | ERIS | Voltage | NP-ROGERS 2 | 26SP | V | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.86205 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-ROGERS-G2 | 29SP | V | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.84771 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-ROGERS-G2 | 26SP | V | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.86533 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-SHATTUCK2 | 26SP | V | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.56561 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-SHATTUCK2 | 26SP | V | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.56561 | 0.9 | 1.05 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
05ALL | ERIS | Voltage | NP-SHATTUCK2 | 29SP | V | Single 523267 PRINGLE6 230 523979 HARRNG_EST6 230 1 |  |  |  |  | 0.53973 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-SHATTUCK2 | 29SP | V | Single 523267 PRINGLE6 230 523979 HARRNG_EST6 230 1 |  |  |  |  | 0.53973 | 0.9 | 1.05 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
05ALL | ERIS | Voltage | NP-SUB_A 2 | 26SP | V | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.78815 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-SUB_A 2 | 29SP | V | Single 523267 PRINGLE6 230 523979 HARRNG_EST6 230 1 |  |  |  |  | 0.78294 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-VALERO-G2 | 29SP | V | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.87188 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-VALERO-G2 | 29SP | V | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.87188 | 0.9 | 1.05 | Add 1.6 MVAR switched shunt at NP-VALERO-G2 69 kV
05ALL | ERIS | Voltage | NP-VALERO-G2 | 26SP | V | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.88695 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-VALERO_P2 | 26SP | V | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 |  |  |  |  | 0.59578 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-VALERO_P2 | 29SP | V | Single 523267 PRINGLE6 230 523979 HARRNG_EST6 230 1 |  |  |  |  | 0.57232 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | OCHILTREE 6 | 26SP | V | System Intact |  |  |  |  | 0.94548 | 0.95 | 1.05 | Add 12 MVAR switched shunt at OCHILTREE 6 230 kV
05ALL | ERIS | Voltage | OCHILTREE 6 | 29WP | V | System Intact |  |  |  |  | 0.94576 | 0.95 | 1.05 | Add 12 MVAR switched shunt at OCHILTREE 6 230 kV
05ALL | ERIS | Voltage | OCHILTREE 6 | 29SP | V | System Intact |  |  |  |  | 0.94577 | 0.95 | 1.05 | Add 12 MVAR switched shunt at OCHILTREE 6 230 kV
05ALL | ERIS | Voltage | OMALTUS4 | 29L | V | Single 787920 G24-365-TAP 345 787921 GEN-2024-365 345 1 |  |  |  |  | 1.0735 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | OMPARK-4 | 29L | V | Single 787920 G24-365-TAP 345 787921 GEN-2024-365 345 1 |  |  |  |  | 1.0725 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | OMPVET-4 | 29L | V | Single 787920 G24-365-TAP 345 787921 GEN-2024-365 345 1 |  |  |  |  | 1.0731 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | POSTROCK7 | 29SP | V | System Intact |  |  |  |  | 0.94856 | 0.95 | 1.05 | Add 210 MVAR SVC at POSTROCK7 345 kV
05ALL | ERIS | Voltage | R-AMOCO2 | 29L | V | Single 787920 G24-365-TAP 345 787921 GEN-2024-365 345 1 |  |  |  |  | 1.0941 | 0.92 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | RANSOM 2 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.88143 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | RANSOM 2 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.88143 | 0.9 | 1.05 | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV
05ALL | ERIS | Voltage | RANSOM 3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.88429 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | REDHLSW4 | 29L | V | Single 787920 G24-365-TAP 345 787921 GEN-2024-365 345 1 |  |  |  |  | 1.0578 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | REDHLSW4 | 29L | V | Single 787920 G24-365-TAP 345 787921 GEN-2024-365 345 1 |  |  |  |  | 1.0578 | 0.9 | 1.05 | Add 6 MVAR switched shunt at REDHLSW4 138 kV
05ALL | ERIS | Voltage | RKY_RDG4 | 29L | V | P52:138:AEPW:NR5O.K.U:::: |  |  |  |  | 1.0856 | 0.92 | 1.05 | Add 0.5 MVAR switched shunt at RKY_RDG4 138 kV
05ALL | ERIS | Voltage | ROSEVLT2 | 29L | V | Single 787920 G24-365-TAP 345 787921 GEN-2024-365 345 1 |  |  |  |  | 1.0964 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | ROSEVLT2 | 29L | V | Single 787920 G24-365-TAP 345 787921 GEN-2024-365 345 1 |  |  |  |  | 1.0964 | 0.9 | 1.05 | Add 0.7 MVAR switched shunt at ROSEVLT2 69 kV
05ALL | ERIS | Voltage | ROSVTAP2 | 29L | V | Single 787920 G24-365-TAP 345 787921 GEN-2024-365 345 1 |  |  |  |  | 1.0941 | 0.92 | 1.05 | Add 0.3 MVAR switched shunt at ROSVTAP2 69 kV
05ALL | ERIS | Voltage | ROSVTAP2 | 29L | V | Single 787920 G24-365-TAP 345 787921 GEN-2024-365 345 1 |  |  |  |  | 1.0941 | 0.92 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | RUSSELL4 | 29L | V | P12:345:OKGE-AEP:BKRBKR4291:::EHV: |  |  |  |  | 1.0658 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | SN_JUAN_SS 6 | 29L | V | Single 524875 OASIS6 230 787680 G24-357-TAP 230 1 |  |  |  |  | 1.0615 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | SN_JUAN_WND6 | 29L | V | Single 524875 OASIS6 230 787680 G24-357-TAP 230 1 |  |  |  |  | 1.0613 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | STLN-DEMARC6 | 29L | V | P12:230:AEPW:SWEETWT6:CHISHOLM6::: |  |  |  |  | 1.1222 | 0.9 | 1.05 | Add 46 MVAR switched shunt at STLN-DEMARC6 230 kV
05ALL | ERIS | Voltage | SWEETWR4 | 29L | V | P12:345:OKGE-AEP:BKRBKR4291:::EHV: |  |  |  |  | 1.0599 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | TOMSTEED2 | 29L | V | Single 787920 G24-365-TAP 345 787921 GEN-2024-365 345 1 |  |  |  |  | 1.0964 | 0.92 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | WHEELER 3 | 29L | V | P12:230:AEPW:SWEETWT6:CHISHOLM6::: |  |  |  |  | 1.057 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | WHEELER 6 | 29L | V | P12:230:AEPW:SWEETWT6:CHISHOLM6::: |  |  |  |  | 1.1201 | 0.9 | 1.05 | Mitigated at another bus
05NR | NRIS | Voltage | GRAY CO3 | 29L | V | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 |  |  |  |  | 1.0859 | 0.9 | 1.05 | Add 0.09 MVAR switched shunt at GRAY CO3 115 kV
05NR | NRIS | Voltage | GYCOTAP3 | 29L | V | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 |  |  |  |  | 1.0859 | 0.9 | 1.05 | Mitigated at another bus
05NR | NRIS | Voltage | HAGGARD3 | 29L | V | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 |  |  |  |  | 1.0859 | 0.9 | 1.05 | Mitigated at another bus
05NR | NRIS | Voltage | UNDERWOOD 2 | 29L | V | Single 778200 G24-041-TAP 345 778201 GEN-2024-041 345 1 |  |  |  |  | 1.1314 | 0.9 | 1.05 | Add 16 MVAR switched shunt at UNDERWOOD 2 345 kV
WECC | ERIS | Non-Converged | None | 26SP, 31WP, 31SP | WECC | None | [7 empty] | None
WECC | ERIS | Thermal | None | 26SP, 31WP, 31SP | WECC | None | [7 empty] | None
WECC | ERIS | Voltage | None | 26SP, 31WP, 31SP | WECC | None | [7 empty] | None
WECC | NRIS | Non-Converged | None | 26SP, 31WP, 31SP | WECC | None | [7 empty] | None
WECC | NRIS | Thermal | None | 26SP, 31WP, 31SP | WECC | None | [7 empty] | None
WECC | NRIS | Voltage | None | 26SP, 31WP, 31SP | WECC | None | [7 empty] | None
03ALL | ERIS | Non-Converged | Non-Converged | 29SP |  | System Intact | [7 empty] | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1
03ALL | ERIS | Non-Converged | Non-Converged | 29SP |  | System Intact | [7 empty] | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY
03ALL | ERIS | Non-Converged | Non-Converged | 29SP |  | System Intact | [7 empty] | Add 641.25 MVAR switched shunt at WWARD9 765 kV
03ALL | ERIS | Non-Converged | Non-Converged | 29SP |  | System Intact | [7 empty] | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV
03ALL | ERIS | Non-Converged | Non-Converged | 29SP |  | System Intact | [7 empty] | Add 375 MVAR switched shunt at WWARD9 765 kV
03ALL | ERIS | Non-Converged | Non-Converged | 26SP |  | System Intact | [7 empty] | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY
03ALL | ERIS | Non-Converged | Non-Converged | 29WP |  | System Intact | [7 empty] | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY
05ALL | ERIS | Non-Converged | Non-Converged | 26SP |  | System Intact | [7 empty] | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1
05ALL | ERIS | Non-Converged | Non-Converged | 26SP |  | System Intact | [7 empty] | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1
05ALL | ERIS | Non-Converged | Non-Converged | 26SP |  | System Intact | [7 empty] | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1
05ALL | ERIS | Non-Converged | Non-Converged | 26SP |  | System Intact | [7 empty] | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1
05ALL | ERIS | Non-Converged | Non-Converged | 26SP |  | System Intact | [7 empty] | Add 641.25 MVAR switched shunt at WWARD9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 26SP |  | System Intact | [7 empty] | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 26SP |  | System Intact | [7 empty] | Add 375 MVAR switched shunt at WWARD9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 26SP |  | System Intact | [7 empty] | Add 150 MVAR switched shunt at MINCO 9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 26SP |  | System Intact | [7 empty] | Add 150 MVAR switched shunt at VIOLA9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 26SP |  | System Intact | [7 empty] | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1
05ALL | ERIS | Non-Converged | Non-Converged | 26SP |  | System Intact | [7 empty] | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1
05ALL | ERIS | Non-Converged | Non-Converged | 29SP |  | System Intact | [7 empty] | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1
05ALL | ERIS | Non-Converged | Non-Converged | 29SP |  | System Intact | [7 empty] | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1
05ALL | ERIS | Non-Converged | Non-Converged | 29SP |  | System Intact | [7 empty] | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1
05ALL | ERIS | Non-Converged | Non-Converged | 29SP |  | System Intact | [7 empty] | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1
05ALL | ERIS | Non-Converged | Non-Converged | 29SP |  | System Intact | [7 empty] | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2
05ALL | ERIS | Non-Converged | Non-Converged | 29SP |  | System Intact | [7 empty] | Add 641.25 MVAR switched shunt at WWARD9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 29SP |  | System Intact | [7 empty] | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 29SP |  | System Intact | [7 empty] | Add 375 MVAR switched shunt at WWARD9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 29SP |  | System Intact | [7 empty] | Add 150 MVAR switched shunt at MINCO 9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 29SP |  | System Intact | [7 empty] | Add 150 MVAR switched shunt at VIOLA9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 29SP |  | System Intact | [7 empty] | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1
05ALL | ERIS | Non-Converged | Non-Converged | 29SP |  | System Intact | [7 empty] | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1
05ALL | ERIS | Non-Converged | Non-Converged | 29WP |  | System Intact | [7 empty] | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1
05ALL | ERIS | Non-Converged | Non-Converged | 29WP |  | System Intact | [7 empty] | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1
05ALL | ERIS | Non-Converged | Non-Converged | 29WP |  | System Intact | [7 empty] | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1
05ALL | ERIS | Non-Converged | Non-Converged | 29WP |  | System Intact | [7 empty] | Add 641.25 MVAR switched shunt at WWARD9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 29WP |  | System Intact | [7 empty] | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 29WP |  | System Intact | [7 empty] | Add 375 MVAR switched shunt at WWARD9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 29WP |  | System Intact | [7 empty] | Add 150 MVAR switched shunt at MINCO 9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 29WP |  | System Intact | [7 empty] | Add 150 MVAR switched shunt at VIOLA9 765 kV
05ALL | ERIS | Non-Converged | Non-Converged | 29WP |  | System Intact | [7 empty] | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1
05ALL | ERIS | Non-Converged | Non-Converged | 29WP |  | System Intact | [7 empty] | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1
00ALL | ERIS | Thermal | 337361 3MINDEN_LA! 115 337363 3SAREPTA! 115 1 | 26S, 29S, 29W | JTIQ Expanded Scope Analysis | P42:345:AEPW:LONGWOOD CB 10280 NBTB+FAULT:::: | B | 176 | N/A | 127.62 |  |  |  | Rebuild the 3MINDEN_LA! to 3SAREPTA! 115kV Line 1
01ALL | ERIS | Thermal | 603022 SOURIS 7 115 603023 MALLARD7 115 1 | 26S | JTIQ Expanded Scope Analysis | System Intact | A | 96.7 | N/A | 102.96 |  |  |  | Rebuild the SOURIS 7 to MALLARD7 115kV Line 1
01ALL | ERIS | Thermal | 603022 SOURIS 7 115 603023 MALLARD7 115 1 | 26S | JTIQ Expanded Scope Analysis | P11:22:GRE:GRE-COAL42G:2 | B | 112.6 | N/A | 118.15 |  |  |  | Rebuild the SOURIS 7 to MALLARD7 115kV Line 1
04ALL | ERIS | Thermal | 337502 3COUCH% 115 337516 3MCNEIL! 115 1 | 26S, 29S, 29W | JTIQ Expanded Scope Analysis | P12:345:AEPW:TURK7:NWTXARK7::: | B | 239 | N/A | 123.66 |  |  |  | Rebuild the 3COUCH% to 3MCNEIL! 115kV Line 1
04ALL | ERIS | Thermal | 337502 3COUCH% 115 338874 3LEWISVILLE# 115 1 | 26S, 29S, 29W | JTIQ Expanded Scope Analysis | P12:345:AEPW:TURK7:NWTXARK7::: | B | 159 | N/A | 141.93 |  |  |  | Rebuild the 3COUCH% to 3LEWISVILLE# 115kV Line 1
04ALL | ERIS | Thermal | 338104 5HARRISON.E! 161 338107 5EVERTON RD 161 1 | 26S, 29S, 29W | JTIQ Expanded Scope Analysis | 774620 G23-132-TAP 161 780390 G24-114-TAP 161 1 | B | 223 | N/A | 110.29 |  |  |  | Rebuild the 5HARRISON.E! to 5EVERTON RD 161kV Line 1
04ALL | ERIS | Thermal | 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | 26S, 29S, 29W | JTIQ Expanded Scope Analysis | 774620 G23-132-TAP 161 780390 G24-114-TAP 161 1 | B | 223 | N/A | 112.99 |  |  |  | Rebuild the 5EVERTON RD to 5ST JOE 161kV Line 1
04ALL | ERIS | Thermal | 338108 5ST JOE 161 338110 5HILLTOP% 161 1 | 26S, 29S, 29W | JTIQ Expanded Scope Analysis | 774620 G23-132-TAP 161 780390 G24-114-TAP 161 1 | B | 223 | N/A | 113.85 |  |  |  | Rebuild the 5ST JOE to 5HILLTOP% 161kV Line 1
04ALL | ERIS | Thermal | 338170 5JONESBORO! 161 338703 5JONSBORO.N# 161 1 | 26S, 29S, 29W | JTIQ Expanded Scope Analysis | P23:500:EES-EAI:DELL:B8320::EHV: | B | 246 | N/A | 133.91 |  |  |  | Rebuild the 5JONESBORO! to 5JONSBORO.N# 161kV Line 1
04ALL | ERIS | Thermal | 338204 5PARAGOULD% 161 338706 5PARGOULD.S# 161 1 | 26S, 29W | JTIQ Expanded Scope Analysis | P23:500:EES-EAI:DELL:B8320::EHV: | B | 247 | N/A | 121.63 |  |  |  | Rebuild the 5PARAGOULD% to 5PARGOULD.S# 161kV Line 1
04ALL | ERIS | Thermal | 338703 5JONSBORO.N# 161 338706 5PARGOULD.S# 161 1 | 26S, 29W | JTIQ Expanded Scope Analysis | P23:500:EES-EAI:DELL:B8320::EHV: | B | 246 | N/A | 126.27 |  |  |  | Rebuild the 5JONSBORO.N# to 5PARGOULD.S# 161kV Line 1
04ALL | ERIS | Thermal | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | 26S, 29S, 29W | JTIQ Expanded Scope Analysis | P12:345:AEPW:TURK7:NWTXARK7::: | B | 159 | N/A | 157.97 |  |  |  | Rebuild the 3LEWISVILLE# to 3PATMOS.W# 115kV Line 1

## Assigned Upgrade Costs
Gen Number | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Length (miles) | Upgrade Rating (MVA) | Allocated Cost | %Allocated | Total Upgrade Cost | PTDF
ASGI-2024-001 | 01 NORTH | TBD | ERIS | Add 4 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 636.5789 | 0.012011 | 5300000 | 0.015111
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 2954856.2888 | 0.19509 | 1514620000 | 0.039995
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 1607409.1115 | 0.12508 | 1285130000 | 0.13139
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 1580719.1812 | 0.12431 | 1271630000 | 0.085335
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 1329577.187 | 0.14169 | 938400000 | 0.080124
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 1261546.1466 | 0.13444 | 938400000 | 0.13454
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 1172433.3727 | 0.16177 | 724760000 | 0.12792
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523092 HITCHLD_TR11 13 523093 HITCHLAND 3 115 523095 HITCHLAND 6 230 M2 | Current Study |  | (250.00, 288.00) | 1090729.0071 | 7.9038 | 13800000 | 0.16017
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523093 HITCHLAND 3 115 523095 HITCHLAND 6 230 523098 HITCHLD_TR41 13 M2 | Current Study |  | (250.00, 288.00) | 1090658.2871 | 7.9033 | 13800000 | 0.15378
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 791186.4503 | 0.073684 | 1073760000 | 0.042073
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 757558.3175 | 0.1569 | 482840000 | 0.13291
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 705709.147 | 0.15036 | 469340000 | 0.0856
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523091 HITCHLD_TR01 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2 | Current Study |  | (560.00, 644.00) | 575646.2086 | 2.3026 | 25000000 | 0.14808
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523094 HITCHLD_TR21 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2 | Current Study |  | (560.00, 644.00) | 575646.2086 | 2.3026 | 25000000 | 0.17023
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add line 523869 CHAN+TASCOS6 230 523959 POTTER_CO 6 230 P2 | Current Study | 41.65 | (496.00, 546.00) | 558816.3601 | 0.50197 | 111325000 | 0.032226
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 501009.0923 | 0.25321 | 197860000 | 0.083428
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add line 523221 XIT_INTG 6 230 523869 CHAN+TASCOS6 230 P2 | Current Study | 32.28 | (495.00, 545.00) | 441181.9694 | 0.50191 | 87900000 | 0.032234
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 263671.3173 | 0.15974 | 165062000 | 0.067004
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 12 MVAR switched shunt at OCHILTREE 6 230 kV | Current Study |  |  | 217541.584 | 5.6874 | 3825000 | 0.08802
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523266 PRINGLE 3 115 523377 RIVERVIEW 3 115 1 | Current Study | 20.25 | (260.00, 260.00) | 193677.1689 | 0.95643 | 20250000 | 0.034801
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 167734.1837 | 0.084496 | 198511000 | 0.030111
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 136694.3816 | 0.16177 | 84500000 | 0.12792
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 126662.1022 | 0.1499 | 84500000 | 0.063524
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 126397.5353 | 0.29076 | 43472000 | 0.059076
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 110849.1447 | 0.088804 | 124824000 | 0.038732
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 73708.342 | 0.090453 | 81488000 | 0.04004
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 38084.8184 | 0.23521 | 16192000 | 0.17582
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 36286.5451 | 0.19509 | 18600000 | 0.039995
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 31273.8116 | 0.056635 | 55220000 | 0.018416
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 30088.9408 | 0.16177 | 18600000 | 0.12792
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 12 MVAR switched shunt at NP-OCHILTRE3 115 kV | Current Study |  |  | 29981.4058 | 1.3551 | 2212500 | 0.00089148
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 27967.3374 | 0.15036 | 18600000 | 0.0856
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 23518.4678 | 0.12644 | 18600000 | 0.13291
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 23182.4749 | 0.12464 | 18600000 | 0.0856
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 22789.9773 | 0.12253 | 18600000 | 0.085335
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 22307.0757 | 0.11993 | 18600000 | 0.080124
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 21402.6512 | 0.11507 | 18600000 | 0.13454
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 21402.6512 | 0.11507 | 18600000 | 0.13454
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 19495.8259 | 0.10482 | 18600000 | 0.13454
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 16825.9754 | 0.090462 | 18600000 | 0.080124
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 14189.6952 | 0.64134 | 2212500 | 0.17582
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 12519.6497 | 0.083811 | 14938000 | 0.059512
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 12119.8332 | 0.083811 | 14460953.1406 | 0.059512
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 8036.6084 | 0.066972 | 12000000 | 0.062115
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 1.6 MVAR switched shunt at NP-VALERO-G2 69 kV | Current Study |  |  | 7195.9749 | 0.52145 | 1380000 | 0.05483
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 7052.9324 | 0.13307 | 5300000 | 0.12705
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 6269.7672 | 0.0074198 | 84500000 | 0.0015187
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 5473.0726 | 0.24737 | 2212500 | 0.17582
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 3880.9258 | 0.23521 | 1650000 | 0.17582
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 2622.3868 | 0.04 | 6556000 | 0.018416
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 2521.3891 | 0.18271 | 1380000 | 0.12705
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 2320.2178 | 0.16813 | 1380000 | 0.17582
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 1985.1243 | 0.089723 | 2212500 | 0.062115
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 1873.6881 | 0.13577 | 1380000 | 0.080198
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 1259.7354 | 0.091285 | 1380000 | 0.062115
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Add line 659131 LARAMIE_-MB3 345 800120 UNDERWOOD 2 345 P2 | Current Study | 206.4 | (1792.00, 1792.00) | 19216703.346 | 2.9571 | 649840000 | 0.021161
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 15120551.8843 | 1.6086 | 940000000 | 0.056963
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Rebuild line 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | Current Study | 84.86 | (1793.00, 1793.00) | 6440553.3483 | 3.4498 | 186692000 | 0.15079
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Rebuild line 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Current Study | 18.19 | (329.00, 329.00) | 4401340.2062 | 24.1965 | 18190000 | 0.23912
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Rebuild line 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Current Study | 12 | (329.00, 329.00) | 2903577.926 | 24.1965 | 12000000 | 0.23912
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2 | Current Study |  | (350.00, 385.00) | 2621420.6487 | 15.6037 | 16800000 | 0.34816
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Rebuild line 531405 WALKMYR3 115 531481 HUGOTON3 115 1 | Current Study | 12.27 | (598.00, 598.00) | 2543225.3492 | 20.7272 | 12270000 | 0.76088
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 2330718.9913 | 1.412 | 165062000 | 0.22266
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Rebuild line 523106 TXPHSF 3 115 539672 E-LIBER3 115 1 | Current Study | 47.28 | (260.00, 260.00) | 2290496.5067 | 4.8445 | 47280000 | 0.034213
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Rebuild line 523961 POTTER_CO 7 345 784950 G24-266_TAP 345 1 | Current Study | 18.24 | (1793.00, 1793.00) | 1367136.2235 | 3.4069 | 40128000 | 0.15079
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Rebuild line 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Current Study | 38.26 | (1793.00, 1793.00) | 1341163.3383 | 1.5934 | 84172000 | 0.096591
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Rebuild line 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Current Study | 37.4 | (1793.00, 1793.00) | 1325498.7575 | 1.611 | 82280000 | 0.096591
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 1181758.0552 | 0.12593 | 938400000 | 0.047382
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 531448 HOLCOMB3 115 531449 HOLCOMB7 345 531450 HOLCTER1 13 M2 | Current Study |  | (336.00, 358.50) | 1022135.8784 | 6.0841 | 16800000 | 0.083246
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 531405 WALKMYR3 115 531510 HARBNGR3 115 M2 | Current Study | 1.28 | (598.00, 598.00) | 934973.3647 | 15.6037 | 5992000 | 0.34816
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 816255.6007 | 0.41119 | 198511000 | 0.034834
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | Current Study | 21.05 | (1793.00, 1793.00) | 692173.5647 | 1.4947 | 46310000 | 0.09924
ASGI-2024-003 | 03 CENTRAL | TBD | NRIS | Add 8.4 MVAR switched shunt at MANTERT3 115 kV | Current Study |  |  | 535347.1801 | 24.1965 | 2212500 | 0.045351
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Add 2.3 MVAR switched shunt at GRANT 3 115 kV | Current Study |  |  | 504096.759 | 22.784 | 2212500 | 0.76088
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | Current Study | 19.2 | (2390.00, 2390.00) | 474474.7327 | 1.1233 | 42240000 | 0.071934
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR switched shunt at GEN-2022-075 345 kV | Current Study |  |  | 458336.4072 | 8.6479 | 5300000 | 0.69632
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | Current Study | 16.04 | (2390.00, 2390.00) | 396384.0996 | 1.1233 | 35288000 | 0.071934
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR SVC at GEN-2021-076 345 kV | Current Study |  |  | 383301.399 | 3.1942 | 12000000 | 0.096591
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Add 7 MVAR switched shunt at G19-030-TAP 345 kV | Current Study |  |  | 374987.4521 | 7.0752 | 5300000 | 0.69632
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Rebuild line 539652 CMRIVTP3 115 539672 E-LIBER3 115 1 | Current Study | 11.74 | (176.00, 176.00) | 267545.5746 | 2.2789 | 11740000 | 0.012357
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | Current Study | 13 | (2390.00, 2390.00) | 258418.5846 | 0.90356 | 28600000 | 0.071607
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 227624.2 | 0.11467 | 198511000 | 0.015362
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Add phase shifting xfmr 523084 SOONER 3 115 523106 TXPHSF 3 115 M2 | Current Study |  | (120.00, 120.00) | 208315.0376 | 4.8445 | 4300000 | 0.017106
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Add 248 MVAR switched shunt at GEN-2022-015 345 kV | Current Study |  |  | 205876.4746 | 3.8845 | 5300000 | 0.69632
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at IRS7 115 KV 115 kV | Current Study |  |  | 191333.8304 | 8.6479 | 2212500 | 0.69632
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MED-LDG3 115 kV | Current Study |  |  | 178479.656 | 8.0669 | 2212500 | 0.69632
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 167646.0543 | 3.1631 | 5300000 | 0.69632
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Add 0.8 MVAR switched shunt at HARBNGR7 345 kV | Current Study |  |  | 141885.1082 | 2.6771 | 5300000 | 0.69632
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 130275.6593 | 0.80457 | 16192000 | 0.22609
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 121634.6843 | 5.4976 | 2212500 | 0.69632
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 117930.6535 | 5.3302 | 2212500 | 0.69632
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Add 66 MVAR switched shunt at GEN-2021-021 345 kV | Current Study |  |  | 98482.6053 | 1.8582 | 5300000 | 0.002414
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 98308.4102 | 0.21411 | 45914000 | 0.027128
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 53652.7452 | 0.21411 | 25058000 | 0.027128
ASGI-2024-003 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 39390.9892 | 0.74323 | 5300000 | 0.079207
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Add 525 MVAR SVC at SD.LS-LR-MB3 345 kV | Current Study |  |  | 37436.0933 | 0.31197 | 12000000 | 0.030988
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 34115.1467 | 0.28429 | 12000000 | 0.099127
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 27178.438 | 0.14612 | 18600000 | 0.06423
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 27178.438 | 0.14612 | 18600000 | 0.06423
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 26808.6207 | 0.50582 | 5300000 | 0.044233
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 26453.6766 | 0.14222 | 18600000 | 0.068632
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 25098.7266 | 0.47356 | 5300000 | 0.040678
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 14313.8628 | 0.095822 | 14938000 | 0.025579
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 13856.7479 | 0.095822 | 14460953.1406 | 0.025579
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 13275.3729 | 0.80457 | 1650000 | 0.22609
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Add 24 MVAR switched shunt at NESSCTY3 115 kV | Current Study |  |  | 11565.7348 | 0.52275 | 2212500 | 0.099127
ASGI-2024-003 | 03 CENTRAL | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 10773.3053 | 0.78067 | 1380000 | 0.12385
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Add 0.04 MVAR switched shunt at ELLIS 2 69 kV | Current Study |  |  | 6254.9006 | 0.45325 | 1380000 | 0.099127
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 5347.5367 | 0.3875 | 1380000 | 0.099127
ASGI-2024-006 | 03 CENTRAL | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 12538150.9187 | 1.3338 | 940000000 | 0.037693
ASGI-2024-006 | 03 CENTRAL | TBD | ERIS | Rebuild line 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | Current Study | 84.86 | (1793.00, 1793.00) | 9011447.4545 | 4.8269 | 186692000 | 0.16836
ASGI-2024-006 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 4113399.774 | 0.43834 | 938400000 | 0.13161
ASGI-2024-006 | 03 CENTRAL | TBD | ERIS | Rebuild line 523961 POTTER_CO 7 345 784950 G24-266_TAP 345 1 | Current Study | 18.24 | (1793.00, 1793.00) | 1912859.9012 | 4.7669 | 40128000 | 0.16836
ASGI-2024-006 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 1874186.5543 | 0.94412 | 198511000 | 0.063825
ASGI-2024-006 | 03 CENTRAL | TBD | ERIS | Add 2 MVAR switched shunt at POWELL CNR 2 69 kV | Current Study |  |  | 1380000 | 100 | 1380000 | 0.0047138
ASGI-2024-006 | 03 CENTRAL | TBD | ERIS | Add 5 MVAR switched shunt at COLE 2 69 kV | Current Study |  |  | 1380000 | 100 | 1380000 | 0.034993
ASGI-2024-006 | 03 CENTRAL | TBD | ERIS | Rebuild line 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Current Study | 38.26 | (1793.00, 1793.00) | 1084109.0788 | 1.288 | 84172000 | 0.062306
ASGI-2024-006 | 03 CENTRAL | TBD | ERIS | Rebuild line 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Current Study | 37.4 | (1793.00, 1793.00) | 1071446.8521 | 1.3022 | 82280000 | 0.062306
ASGI-2024-006 | 03 CENTRAL | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 542997.8952 | 0.24872 | 218320000 | 0.015349
ASGI-2024-006 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR SVC at GEN-2021-076 345 kV | Current Study |  |  | 309836.1924 | 2.582 | 12000000 | 0.062306
ASGI-2024-006 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | Current Study | 21.05 | (1793.00, 1793.00) | 274795.712 | 0.59338 | 46310000 | 0.03144
ASGI-2024-006 | 03 CENTRAL | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 184096.6105 | 0.34436 | 53460000 | 0.02486
ASGI-2024-006 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2 | Current Study |  | (350.00, 385.00) | 176107.3335 | 1.0483 | 16800000 | 0.018665
ASGI-2024-006 | 03 CENTRAL | TBD | ERIS | Rebuild line 539652 CMRIVTP3 115 539654 CIM-PLT3 115 1 | Current Study | 4.08 | (217.00, 217.00) | 100226.5604 | 2.4565 | 4080000 | 0.029713
ASGI-2024-006 | 03 CENTRAL | TBD | ERIS | Add 66 MVAR switched shunt at GEN-2021-021 345 kV | Current Study |  |  | 80739.6468 | 1.5234 | 5300000 | 0.0015793
ASGI-2024-006 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 69785.5255 | 0.37519 | 18600000 | 0.13161
ASGI-2024-006 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 69785.5255 | 0.37519 | 18600000 | 0.13161
ASGI-2024-006 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 63568.1273 | 0.34176 | 18600000 | 0.13161
ASGI-2024-006 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 531405 WALKMYR3 115 531510 HARBNGR3 115 M2 | Current Study | 1.28 | (598.00, 598.00) | 62811.6156 | 1.0483 | 5992000 | 0.018665
ASGI-2024-006 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 52728.0362 | 0.99487 | 5300000 | 0.084608
ASGI-2024-006 | 03 CENTRAL | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 46836.9243 | 0.25877 | 18100000 | 0.0079288
ASGI-2024-006 | 03 CENTRAL | TBD | ERIS | Add 525 MVAR SVC at SD.LS-LR-MB3 345 kV | Current Study |  |  | 34788.5944 | 0.2899 | 12000000 | 0.022979
ASGI-2024-006 | 03 CENTRAL | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 34077.678 | 0.64298 | 5300000 | 0.044868
ASGI-2024-006 | 03 CENTRAL | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 27879.913 | 0.23233 | 12000000 | 0.064645
ASGI-2024-006 | 03 CENTRAL | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 21433.4026 | 0.4044 | 5300000 | 0.02772
ASGI-2024-006 | 03 CENTRAL | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 18798.0364 | 0.35468 | 5300000 | 0.062306
ASGI-2024-006 | 03 CENTRAL | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 18091.9669 | 1.311 | 1380000 | 0.16597
ASGI-2024-006 | 03 CENTRAL | TBD | ERIS | Add 248 MVAR switched shunt at GEN-2022-015 345 kV | Current Study |  |  | 16624.059 | 0.31366 | 5300000 | 0.044868
ASGI-2024-006 | 03 CENTRAL | TBD | ERIS | Add 0.8 MVAR switched shunt at HARBNGR7 345 kV | Current Study |  |  | 16506.8265 | 0.31145 | 5300000 | 0.064645
ASGI-2024-006 | 03 CENTRAL | TBD | ERIS | Add 24 MVAR switched shunt at NESSCTY3 115 kV | Current Study |  |  | 9451.8626 | 0.4272 | 2212500 | 0.064645
ASGI-2024-006 | 03 CENTRAL | TBD | ERIS | Add 0.04 MVAR switched shunt at ELLIS 2 69 kV | Current Study |  |  | 5111.6909 | 0.37041 | 1380000 | 0.064645
ASGI-2024-006 | 03 CENTRAL | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 4370.1661 | 0.31668 | 1380000 | 0.064645
ASGI-2024-007 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at SWAVRLY5 161 kV | Current Study |  |  | 1164023.4346 | 35.8161 | 3250000 | 0.058762
ASGI-2024-008 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at SWAVRLY5 161 kV | Current Study |  |  | 2085976.5654 | 64.1839 | 3250000 | 0.058762
ASGI-2024-020 | 03 CENTRAL | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 842683.4435 | 1.5763 | 53460000 | 0.086484
ASGI-2024-020 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | Current Study | 16.71 | (1793.00, 1793.00) | 362754.17 | 0.98676 | 36762000 | 0.041981
ASGI-2024-020 | 03 CENTRAL | TBD | ERIS | Add 2 MVAR switched shunt at G15048_1 138 kV | Current Study |  |  | 245031.2094 | 10.0732 | 2432500 | 0.013644
ASGI-2024-020 | 03 CENTRAL | TBD | ERIS | Add 10 MVAR switched shunt at G20-007-TAP 345 kV | Current Study |  |  | 71641.4203 | 1.3517 | 5300000 | 0.04029
ASGI-2024-020 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 67787.5788 | 1.279 | 5300000 | 0.082667
ASGI-2024-020 | 03 CENTRAL | TBD | ERIS | Add 38 MVAR switched shunt at FRNT2WD7 345 kV | Current Study |  |  | 16158.5878 | 0.30488 | 5300000 | 0.013644
ASGI-2024-020 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 3118.4584 | 0.189 | 1650000 | 0.017415
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1 | Current Study | 56.1 | (1793.00, 1793.00) | 7016312.8499 | 5.6849 | 123420000 | 0.13589
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 337505 3EMMET 115 507448 NHOPE 3 115 1 | Current Study | 12 | (329.00, 329.00) | 5967372.5424 | 49.7281 | 12000000 | 0.2833
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507449 NWHOPE 3 115 507452 HOPESWI3 115 1 | Current Study | 9.8 | (329.00, 329.00) | 4873354.243 | 49.7281 | 9800000 | 0.2833
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | Current Study | 14.95 | (329.00, 329.00) | 4865242.2979 | 32.5434 | 14950000 | 0.12026
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1 | Current Study | 30.63 | (1793.00, 1793.00) | 1593696.3647 | 2.365 | 67386000 | 0.064539
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 876687.634 | 0.58351 | 150244000 | 0.022039
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 645775.3734 | 0.57253 | 112794000 | 0.081275
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507448 NHOPE 3 115 507449 NWHOPE 3 115 1 | Current Study | 1.2 | (329.00, 329.00) | 596737.2542 | 49.7281 | 1200000 | 0.2833
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 569111.1237 | 0.59605 | 95480000 | 0.040175
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 504856.642 | 0.59605 | 84700000 | 0.040175
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 489492.402 | 0.22421 | 218320000 | 0.011531
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 776060 G23-204-TAP 345 1 | Current Study | 17.82 | (1793.00, 1793.00) | 469849.1505 | 1.1985 | 39204000 | 0.075243
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 451463.3733 | 0.31396 | 143796000 | 0.026135
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 404118.0212 | 0.63892 | 63250000 | 0.057822
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 370194.5672 | 3.085 | 12000000 | 0.076475
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 350311.5593 | 0.17647 | 198511000 | 0.015722
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 288434.7627 | 0.23107 | 124824000 | 0.025196
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 284984.0903 | 0.60645 | 46992000 | 0.040937
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 275081.8651 | 0.29269 | 93984000 | 0.03027
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | Current Study | 7.74 | (1793.00, 1793.00) | 274241.2387 | 1.6105 | 17028000 | 0.075243
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at PHILL 7 345 kV | Current Study |  |  | 232114.424 | 4.3795 | 5300000 | 0.032551
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 217953.6943 | 0.64879 | 33594000 | 0.044122
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 214064.9669 | 1.7839 | 12000000 | 0.10028
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 195783.8607 | 1.6315 | 12000000 | 0.10028
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 190998.1159 | 2.8939 | 6600000 | 0.10028
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | Current Study | 6.93 | (1793.00, 1793.00) | 182719.1141 | 1.1985 | 15246000 | 0.075243
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 177587.2607 | 0.70193 | 25300000 | 0.023962
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 170568.7938 | 1.4214 | 12000000 | 0.10028
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 163849.1481 | 1.3654 | 12000000 | 0.10028
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 156614.2809 | 1.3051 | 12000000 | 0.076475
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 764550 G20-087-TAP 345 1 | Current Study | 14.38 | (1793.00, 1793.00) | 152193.8685 | 0.48108 | 31636000 | 0.027343
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 150043.8972 | 1.2504 | 12000000 | 0.10028
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 149135.6619 | 2.8139 | 5300000 | 0.076475
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1 | Current Study | 11.3 | (1793.00, 1793.00) | 142726.5999 | 0.57412 | 24860000 | 0.029514
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 124011.4472 | 0.48302 | 25674000 | 0.028261
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 120534.2349 | 1.8263 | 6600000 | 0.10028
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 120534.2349 | 1.8263 | 6600000 | 0.10028
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 114543.1582 | 1.7355 | 6600000 | 0.10028
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 108221.1299 | 0.90184 | 12000000 | 0.076475
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 95643.9222 | 2.9429 | 3250000 | 0.10028
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 95643.9222 | 2.9429 | 3250000 | 0.10028
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | Current Study | 8.91 | (2390.00, 2390.00) | 93067.6009 | 0.47479 | 19602000 | 0.027343
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 89267.984 | 0.49848 | 17908000 | 0.029648
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 85489.578 | 1.613 | 5300000 | 0.076475
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 72344.2645 | 0.60287 | 12000000 | 0.034001
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 63612.3516 | 0.5301 | 12000000 | 0.020821
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | Current Study | 5.97 | (2390.00, 2390.00) | 62358.4262 | 0.47479 | 13134000 | 0.027343
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 59235.681 | 1.1177 | 5300000 | 0.10028
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 57886.7302 | 1.7811 | 3250000 | 0.10028
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 56543.683 | 0.4712 | 12000000 | 0.025741
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 56543.683 | 0.4712 | 12000000 | 0.025741
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 56381.5583 | 1.7348 | 3250000 | 0.10028
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 55970.0313 | 0.46642 | 12000000 | 0.026504
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 54880.9033 | 0.45734 | 12000000 | 0.020821
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 53112.7951 | 1.6342 | 3250000 | 0.10028
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 43347.9114 | 1.3338 | 3250000 | 0.10028
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 42572.3752 | 3.085 | 1380000 | 0.076475
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 41194.7304 | 0.27366 | 15053000 | 0.0060326
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 38956.6844 | 0.59025 | 6600000 | 0.040175
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 37171.4292 | 0.31879 | 11660000 | 0.03027
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 36296.4129 | 2.6302 | 1380000 | 0.10028
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 31814.5793 | 0.26512 | 12000000 | 0.01549
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 31291.2855 | 0.5904 | 5300000 | 0.03027
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 29768.9577 | 0.56168 | 5300000 | 0.04489
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 26611.3739 | 0.5021 | 5300000 | 0.026504
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 26605.0821 | 0.1781 | 14938000 | 0.031617
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 26341.8719 | 1.1906 | 2212500 | 0.10028
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 25755.4456 | 0.1781 | 14460953.1406 | 0.031617
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 25539.7068 | 1.1543 | 2212500 | 0.10028
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 21985.6805 | 1.5932 | 1380000 | 0.076475
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 20981.0553 | 0.59605 | 3520000 | 0.040175
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 20370.67 | 0.38435 | 5300000 | 0.03027
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 19371.7171 | 0.59605 | 3250000 | 0.040175
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 18128.917 | 1.3137 | 1380000 | 0.076475
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 18011.6349 | 0.60645 | 2970000 | 0.040937
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 16318.2953 | 0.5021 | 3250000 | 0.026504
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 14732.6983 | 0.64055 | 2300000 | 0.075243
ASGI-2024-023 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 14473.7031 | 0.27309 | 5300000 | 0.077712
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 13813.9231 | 1.001 | 1380000 | 0.081275
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 13341.9518 | 0.60645 | 2200000 | 0.040937
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 13030.3667 | 0.40093 | 3250000 | 0.03027
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 11994.1553 | 0.2263 | 5300000 | 0.0028037
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 9803.2088 | 0.40301 | 2432500 | 0.03027
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 9667.3057 | 0.39742 | 2432500 | 0.03027
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 9552.9227 | 0.39272 | 2432500 | 0.029686
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 6595.8568 | 0.29812 | 2212500 | 0.052971
ASGI-2024-024 | 03 CENTRAL | TBD | ERIS | Rebuild line 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | Current Study | 17.54 | (1793.00, 1793.00) | 1625602.1382 | 4.2127 | 38588000 | 0.051245
ASGI-2024-024 | 03 CENTRAL | TBD | ERIS | Rebuild line 645458 S3458 3 345 778170 G24-040-TAP 345 1 | Current Study | 13.15 | (1793.00, 1793.00) | 976141.0526 | 3.3741 | 28930000 | 0.13246
ASGI-2024-024 | 03 CENTRAL | TBD | ERIS | Rebuild line 640139 COOPER 3 345 778170 G24-040-TAP 345 1 | Current Study | 12.59 | (1793.00, 1793.00) | 934571.5477 | 3.3741 | 27698000 | 0.13246
ASGI-2024-024 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 743374.0931 | 0.079217 | 938400000 | 0.030107
ASGI-2024-024 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 595542.1671 | 0.3 | 198511000 | 0.025672
ASGI-2024-024 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 375016.5669 | 0.2608 | 143796000 | 0.032977
ASGI-2024-024 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 265688.6447 | 0.2827 | 93984000 | 0.044409
ASGI-2024-024 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 209918.5616 | 0.10575 | 198511000 | 0.014311
ASGI-2024-024 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 101303.7609 | 0.22064 | 45914000 | 0.028238
ASGI-2024-024 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 55287.4862 | 0.22064 | 25058000 | 0.028238
ASGI-2024-024 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 35902.1364 | 0.30791 | 11660000 | 0.044409
ASGI-2024-024 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 19691.7295 | 0.10587 | 18600000 | 0.047008
ASGI-2024-024 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 19691.7295 | 0.10587 | 18600000 | 0.047008
ASGI-2024-024 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 15445.8127 | 0.1034 | 14938000 | 0.027882
ASGI-2024-024 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 14952.5488 | 0.1034 | 14460953.1406 | 0.027882
ASGI-2024-024 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 11488.0395 | 0.061764 | 18600000 | 0.030107
ASGI-2024-024 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 6088.3474 | 0.36899 | 1650000 | 0.05663
GEN-2024-003 | 04 SOUTHEAST | TBD | ERIS | Rebuild 3-winding transformer 515336 VBI 2 69 515339 VBI 5 161 515769 VBI 1 13 2 | Current Study |  | (83.00, 83.00) | 2961291.6883 | 48.7455 | 6075000 | 0.035238
GEN-2024-003 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1 | Current Study | 11.3 | (1793.00, 1793.00) | 222438.5599 | 0.89476 | 24860000 | 0.054009
GEN-2024-003 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 75727.1967 | 1.4288 | 5300000 | 0.30077
GEN-2024-003 | 04 SOUTHEAST | TBD | ERIS | Add 38 MVAR switched shunt at FRNT2WD7 345 kV | Current Study |  |  | 31631.2583 | 0.59682 | 5300000 | 0.034386
GEN-2024-003 | 04 SOUTHEAST | TBD | ERIS | Add 19 MVAR switched shunt at RANCHRD7 345 kV | Current Study |  |  | 28959.8061 | 0.54641 | 5300000 | 0.034386
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 530582 S HAYS6 230 539679 GRTBEND6 230 1 | Current Study | 39.2 | (386.00, 386.00) | 8964145.5383 | 12.0356 | 74480000 | 0.20177
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 5684745.9761 | 0.60476 | 940000000 | 0.021362
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 530569 GB STH 2 69 530596 WPRTTS 2 69 1 | Current Study | 5.86 | (69.00, 69.00) | 4981000 | 100 | 4981000 | 0.094051
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 539642 ELLSWTP3 115 539678 GRTBEND3 115 1 | Current Study | 30.21 | (115.00, 115.00) | 4251671.6682 | 14.0737 | 30210000 | 0.071865
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 530679 SEWRDMW3 115 539692 SEWARD 3 115 1 | Current Study | 2.91 | (115.00, 115.00) | 2910000 | 100 | 2910000 | 0.83797
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | Current Study | 13.1 | (297.00, 297.00) | 2874981.22 | 21.9464 | 13100000 | 0.49628
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 | Current Study | 21.74 | (386.00, 386.00) | 2762284.8035 | 6.6874 | 41306000 | 0.091526
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 530618 HUNTSVL3 115 530624 ST JOHN3 115 1 | Current Study | 26.5 | (297.00, 297.00) | 2535263.3189 | 9.567 | 26500000 | 0.16803
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 2278461.8093 | 1.1478 | 198511000 | 0.096991
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 530565 SEWARD 2 69 530569 GB STH 2 69 1 | Current Study | 8.56 | (69.00, 69.00) | 1989326.4152 | 27.3409 | 7276000 | 0.094051
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 539666 GBENDTP3 115 539678 GRTBEND3 115 1 | Current Study | 7.21 | (176.00, 176.00) | 1582343.1934 | 21.9465 | 7210000 | 0.32097
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | Current Study | 84.86 | (1793.00, 1793.00) | 1465166.9244 | 0.7848 | 186692000 | 0.034217
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild 3-winding transformer 530565 SEWARD 2 69 530631 SWRD1 1 12 530679 SEWRDMW3 115 1 | Current Study |  | (87.00, 87.00) | 1280937.6974 | 27.1098 | 4725000 | 0.16203
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 530618 HUNTSVL3 115 530724 CENTENNIAL3 115 1 | Current Study | 12.45 | (297.00, 297.00) | 1191095.4083 | 9.567 | 12450000 | 0.16803
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 530724 CENTENNIAL3 115 533412 ARKVALJ3 115 1 | Current Study | 10.96 | (297.00, 297.00) | 1048546.6406 | 9.567 | 10960000 | 0.16803
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 914842.1879 | 0.41904 | 218320000 | 0.032325
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 530570 GT BND 2 69 530596 WPRTTS 2 69 1 | Current Study | 1.05 | (69.00, 69.00) | 892500 | 100 | 892500 | 0.094051
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 888745.3549 | 0.61806 | 143796000 | 0.077175
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 868660.662 | 0.43759 | 198511000 | 0.058478
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 539649 SAWYER 3 115 539760 BARBER 3 115 1 | Current Study | 19 | (598.00, 598.00) | 859881.8969 | 4.5257 | 19000000 | 0.17365
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 746271.3474 | 0.079526 | 938400000 | 0.029846
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Current Study | 26.47 | (1793.00, 1793.00) | 708139.6114 | 1.216 | 58234000 | 0.052052
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Current Study | 38.26 | (1793.00, 1793.00) | 648010.7972 | 0.76987 | 84172000 | 0.046553
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Current Study | 37.4 | (1793.00, 1793.00) | 640442.1311 | 0.77837 | 82280000 | 0.046553
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add 21 MVAR switched shunt at RUSLSOL3 115 kV | Current Study |  |  | 624646.956 | 28.2326 | 2212500 | 0.035853
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | Current Study | 19.2 | (2390.00, 2390.00) | 537018.1317 | 1.2713 | 42240000 | 0.081213
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 539638 FLATRDG4 138 539674 BARBER 4 138 1 | Current Study | 8.92 | (472.00, 472.00) | 500735.4005 | 4.678 | 10704000 | 0.1616
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 533412 ARKVALJ3 115 533413 CIRCLE 3 115 1 | Current Study | 5.2 | (297.00, 297.00) | 497485.6324 | 9.567 | 5200000 | 0.16803
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 539674 BARBER 4 138 539760 BARBER 3 115 539917 BARBER-1 13 M2 | Current Study |  | (324.00, 324.00) | 486514.2157 | 4.678 | 10400000 | 0.080801
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | Current Study | 16.04 | (2390.00, 2390.00) | 448633.8975 | 1.2713 | 35288000 | 0.081213
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 533413 CIRCLE 3 115 533416 RENO 3 115 2 | Current Study | 5.95 | (217.00, 217.00) | 438313.5089 | 7.3666 | 5950000 | 0.10518
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 366540.4309 | 0.18525 | 197860000 | 0.022889
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 523961 POTTER_CO 7 345 784950 G24-266_TAP 345 1 | Current Study | 18.24 | (1793.00, 1793.00) | 311010.9749 | 0.77505 | 40128000 | 0.034217
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 294708.2641 | 0.55127 | 53460000 | 0.049746
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | Current Study | 13 | (2390.00, 2390.00) | 292482.3093 | 1.0227 | 28600000 | 0.080843
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 284493.3695 | 0.17236 | 165062000 | 0.027111
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 539668 HARPER 4 138 539881 SPRVLSTR 138 1 | Current Study | 12.1 | (281.00, 281.00) | 269621.1707 | 1.8569 | 14520000 | 0.021466
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | Current Study | 19.87 | (1793.00, 1793.00) | 244390.8635 | 0.55907 | 43714000 | 0.023868
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 539009 CONWAY 4 138 539881 SPRVLSTR 138 1 | Current Study | 10.66 | (281.00, 281.00) | 237534.0231 | 1.8569 | 12792000 | 0.021466
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | Current Study | 16.71 | (1793.00, 1793.00) | 215623.0934 | 0.58654 | 36762000 | 0.041042
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR SVC at GEN-2021-076 345 kV | Current Study |  |  | 185200.1845 | 1.5433 | 12000000 | 0.046553
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 176268.1269 | 0.38391 | 45914000 | 0.048519
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 533075 VIOLA 4 138 539009 CONWAY 4 138 1 | Current Study | 5.62 | (281.00, 281.00) | 125229.0066 | 1.8569 | 6744000 | 0.021466
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add 63 MVAR switched shunt at SADLHRN3 115 kV | Current Study |  |  | 100136.2477 | 4.5259 | 2212500 | 0.17366
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add 21 MVAR switched shunt at LARNED3 115 kV | Current Study |  |  | 100131.6788 | 4.5257 | 2212500 | 0.17365
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add 45 MVAR switched shunt at HUNTSVL3 115 kV | Current Study |  |  | 100125.4626 | 4.5254 | 2212500 | 0.17365
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 96199.9984 | 0.38391 | 25058000 | 0.048519
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add 525 MVAR SVC at SD.LS-LR-MB3 345 kV | Current Study |  |  | 70498.6653 | 0.58749 | 12000000 | 0.058209
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 64543.2709 | 0.43207 | 14938000 | 0.11505
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 62482.0736 | 0.43207 | 14460953.1406 | 0.11505
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 58802.537 | 1.1095 | 5300000 | 0.095064
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 57760.7894 | 1.0898 | 5300000 | 0.095064
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 52066.2357 | 0.43389 | 12000000 | 0.15091
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add 7 MVAR switched shunt at G19-030-TAP 345 kV | Current Study |  |  | 43845.6886 | 0.82728 | 5300000 | 0.081214
GEN-2024-007 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 41017.5624 | 0.77392 | 5300000 | 0.082272
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add 66 MVAR switched shunt at GEN-2021-021 345 kV | Current Study |  |  | 40382.6335 | 0.76194 | 5300000 | 0.00098737
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add 248 MVAR switched shunt at GEN-2022-015 345 kV | Current Study |  |  | 28177.3533 | 0.53165 | 5300000 | 0.095064
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 26036.8766 | 0.1608 | 16192000 | 0.045074
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MINGO 7 345 kV | Current Study |  |  | 25662.0401 | 0.48419 | 5300000 | 0.046553
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 22944.9339 | 0.43292 | 5300000 | 0.095064
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 21852.384 | 0.11749 | 18600000 | 0.051514
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 21852.384 | 0.11749 | 18600000 | 0.051514
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 17975.8759 | 0.81247 | 2212500 | 0.065293
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR switched shunt at GEN-2022-075 345 kV | Current Study |  |  | 17675.7243 | 0.3335 | 5300000 | 0.026786
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 13148.0922 | 0.070689 | 18600000 | 0.034027
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add 12 MVAR switched shunt at BEELER 3 115 kV | Current Study |  |  | 11015.5143 | 0.49788 | 2212500 | 0.046198
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add 0.8 MVAR switched shunt at HARBNGR7 345 kV | Current Study |  |  | 10786.0075 | 0.20351 | 5300000 | 0.052801
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 530624 ST JOHN3 115 539696 ST-JOHN3 115 Z1 | Current Study | 0.1 | (326.00, 326.00) | 9567.0314 | 9.567 | 100000 | 0.16803
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at IRS7 115 KV 115 kV | Current Study |  |  | 7378.7811 | 0.3335 | 2212500 | 0.026786
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MED-LDG3 115 kV | Current Study |  |  | 6883.0604 | 0.3111 | 2212500 | 0.026786
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add 40 MVAR switched shunt at SEGNTP 3 115 kV | Current Study |  |  | 4793.9624 | 0.21668 | 2212500 | 0.045075
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 4690.8365 | 0.21202 | 2212500 | 0.026786
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 4547.9907 | 0.20556 | 2212500 | 0.026786
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 3741.752 | 0.16912 | 2212500 | 0.045075
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add 0.04 MVAR switched shunt at ELLIS 2 69 kV | Current Study |  |  | 3682.2135 | 0.26683 | 1380000 | 0.058209
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 2653.2143 | 0.1608 | 1650000 | 0.045074
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 1251.0945 | 0.056547 | 2212500 | 0.01468
GEN-2024-007 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 464.0755 | 0.028126 | 1650000 | 0.0042626
GEN-2024-013 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 514992 TURNER 4 138 516097 NORMHLL4 138 1 | Current Study | 1.89 | (395.00, 395.00) | 1582532.0263 | 69.7765 | 2268000 | 0.023145
GEN-2024-013 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 347572.7085 | 1.9203 | 18100000 | 0.011863
GEN-2024-013 | 04 SOUTHEAST | TBD | ERIS | Add 10 MVAR switched shunt at G20-007-TAP 345 kV | Current Study |  |  | 281679.3204 | 5.3147 | 5300000 | 0.042024
GEN-2024-013 | 04 SOUTHEAST | TBD | ERIS | Add 38 MVAR switched shunt at FRNT2WD7 345 kV | Current Study |  |  | 243596.9475 | 4.5962 | 5300000 | 0.054564
GEN-2024-013 | 04 SOUTHEAST | TBD | ERIS | Add 0.42 MVAR switched shunt at TWNLKSW4 138 kV | Current Study |  |  | 240984.8991 | 9.9069 | 2432500 | 0.079636
GEN-2024-013 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 514959 FOSTER 4 138 515387 NEWDOMI4 138 1 | Current Study | 1.44 | (281.00, 281.00) | 230764.8157 | 13.3544 | 1728000 | 0.026431
GEN-2024-013 | 04 SOUTHEAST | TBD | ERIS | Add 19 MVAR switched shunt at RANCHRD7 345 kV | Current Study |  |  | 223023.7029 | 4.208 | 5300000 | 0.054564
GEN-2024-013 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 41523.037 | 0.78345 | 5300000 | 0.033981
GEN-2024-013 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 28244.6426 | 0.53292 | 5300000 | 0.03669
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 34945040.1396 | 2.3072 | 1514620000 | 0.050678
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 30512101.7791 | 2.3742 | 1285130000 | 0.26722
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 30334912.4631 | 2.3855 | 1271630000 | 0.17546
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 19227799.1496 | 1.7907 | 1073760000 | 0.10955
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526460 AMOCO_SS 6 230 777420 G24-015-TAP 230 1 | Current Study | 25.97 | (519.00, 519.00) | 18612884.6294 | 37.7214 | 49343000 | 0.30717
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 16194271.6342 | 1.7257 | 938400000 | 0.10456
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 15410064.0921 | 2.1262 | 724760000 | 0.18014
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 14405836.8352 | 1.5351 | 938400000 | 0.16461
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 11165805.2572 | 2.3125 | 482840000 | 0.20989
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 10968331.035 | 2.337 | 469340000 | 0.14254
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 9995772.2271 | 2.7274 | 366500000 | 0.064023
GEN-2024-015 | 05 SOUTHWEST | TBD | NRIS | Add 110 MVAR switched shunt at SEMINOLE 6 230 kV | Current Study |  |  | 3825000 | 100 | 3825000 | 0.033336
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 2599950.4454 | 4.7083 | 55220000 | 0.16404
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 2209043.102 | 2.6143 | 84500000 | 0.057332
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1796664.2969 | 2.1262 | 84500000 | 0.18014
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 1791585.4924 | 0.90548 | 197860000 | 0.031965
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 1766691.185 | 2.0908 | 84500000 | 0.094932
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1703874.7618 | 1.365 | 124824000 | 0.063788
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1626829.2507 | 0.81952 | 198511000 | 0.031291
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 1285990.1212 | 0.7791 | 165062000 | 0.035014
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 1177255.305 | 1.4447 | 81488000 | 0.068519
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 925146.1073 | 3.7006 | 25000000 | 0.044836
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 925146.1073 | 3.7006 | 25000000 | 0.039073
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 906376.0842 | 2.085 | 43472000 | 0.045388
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 664045.601 | 2.5058 | 26500000 | 0.028131
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1 | Current Study | 18.95 | (901.00, 901.00) | 527674.6313 | 1.4656 | 36005000 | 0.030575
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 443509.1756 | 2.3845 | 18600000 | 0.17546
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 441330.0809 | 2.3727 | 18600000 | 0.26722
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 437352.8034 | 2.3514 | 18600000 | 0.17546
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 434676.2629 | 2.337 | 18600000 | 0.14254
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 429135.8536 | 2.3072 | 18600000 | 0.050678
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 395478.7683 | 2.1262 | 18600000 | 0.18014
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 271700.5432 | 1.4608 | 18600000 | 0.10456
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 267453.6399 | 1.4379 | 18600000 | 0.18014
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 267453.6399 | 1.4379 | 18600000 | 0.18014
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 257350.5346 | 1.3836 | 18600000 | 0.19029
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528018 RED_BLUFF 3 115 528235 WOLFCAMP_TP3 115 1 | Current Study | 7.81 | (598.00, 598.00) | 257156.0032 | 3.2927 | 7810000 | 0.031532
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 218012.3026 | 3.3254 | 6556000 | 0.16404
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 204940.6529 | 1.1018 | 18600000 | 0.10456
GEN-2024-015 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 182694.2887 | 1.0094 | 18100000 | 0.011045
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | Current Study | 0.78 | (598.00, 598.00) | 149631.2158 | 2.8275 | 5292000 | 0.028529
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 126773.6484 | 0.78294 | 16192000 | 0.062704
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | Current Study | 0.2 | (598.00, 598.00) | 126671.9287 | 2.8275 | 4480000 | 0.028529
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 117765.3134 | 0.78836 | 14938000 | 0.059978
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 114004.4637 | 0.78836 | 14460953.1406 | 0.059978
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 98374.7107 | 1.8561 | 5300000 | 0.18986
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 37748.6566 | 2.7354 | 1380000 | 0.17311
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 36598.3793 | 0.30499 | 12000000 | 0.030307
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 35168.481 | 2.5484 | 1380000 | 0.18986
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 24405.7314 | 1.1031 | 2212500 | 0.0324
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 23385.8254 | 1.6946 | 1380000 | 0.18986
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 18218.3398 | 0.82343 | 2212500 | 0.062704
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 16903.5277 | 1.2249 | 1380000 | 0.0062597
GEN-2024-015 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 14060.2921 | 1.0189 | 1380000 | 0.046066
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 12918.5104 | 0.78294 | 1650000 | 0.062704
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 9040.1733 | 0.4086 | 2212500 | 0.030307
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 5736.7825 | 0.41571 | 1380000 | 0.030307
GEN-2024-016 | 03 CENTRAL | TBD | NRIS | Rebuild line 640066 AXTELL 7 115 640275 MINDEN 7 115 1 | Current Study | 11.61 | (217.00, 217.00) | 11610000 | 100 | 11610000 | 0.022391
GEN-2024-016 | 03 CENTRAL | TBD | NRIS | Rebuild line 640261 LOWELL 7 115 640275 MINDEN 7 115 1 | Current Study | 10.75 | (176.00, 176.00) | 10750000 | 100 | 10750000 | 0.022391
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Rebuild line 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | Current Study | 10.74 | (394.00, 394.00) | 10084654.8733 | 93.8981 | 10740000 | 0.056831
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 9091392.3889 | 4.5798 | 198511000 | 0.1032
GEN-2024-016 | 03 CENTRAL | TBD | NRIS | Rebuild line 640250 KEARNEY7 115 640383 TOWER 7 115 1 | Current Study | 5.92 | (176.00, 176.00) | 5920000 | 100 | 5920000 | 0.021978
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Rebuild line 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | Current Study | 84.86 | (1793.00, 1793.00) | 5890751.7185 | 3.1553 | 186692000 | 0.036686
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Current Study | 26.47 | (1793.00, 1793.00) | 4140901.0098 | 7.1108 | 58234000 | 0.081168
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 3398962.6308 | 1.7122 | 198511000 | 0.061018
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | Current Study | 19.2 | (2390.00, 2390.00) | 2735104.1406 | 6.4752 | 42240000 | 0.1103
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | Current Study | 16.04 | (2390.00, 2390.00) | 2284951.5841 | 6.4752 | 35288000 | 0.1103
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 2249093.7237 | 0.23967 | 938400000 | 0.023987
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 2189997.2722 | 1.523 | 143796000 | 0.050712
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 2130765.1623 | 1.0769 | 197860000 | 0.035482
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Rebuild line 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Current Study | 38.26 | (1793.00, 1793.00) | 1701434.7788 | 2.0214 | 84172000 | 0.032595
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Rebuild line 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Current Study | 37.4 | (1793.00, 1793.00) | 1681562.2833 | 2.0437 | 82280000 | 0.032595
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | Current Study | 13 | (2390.00, 2390.00) | 1489650.9595 | 5.2086 | 28600000 | 0.1098
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 1475693.2995 | 0.89402 | 165062000 | 0.0375
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | Current Study | 16.71 | (1793.00, 1793.00) | 1412152.3054 | 3.8413 | 36762000 | 0.071678
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 1285488.2283 | 24.2545 | 5300000 | 0.55419
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 1262714.4773 | 23.8248 | 5300000 | 0.55419
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Rebuild line 523961 POTTER_CO 7 345 784950 G24-266_TAP 345 1 | Current Study | 18.24 | (1793.00, 1793.00) | 1250429.8346 | 3.1161 | 40128000 | 0.036686
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 1242752.5033 | 0.93478 | 132946000 | 0.019375
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 1190878.8827 | 22.4694 | 5300000 | 0.55419
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | Current Study | 19.87 | (1793.00, 1793.00) | 1093344.1937 | 2.5011 | 43714000 | 0.028475
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 774765.9849 | 1.6874 | 45914000 | 0.05687
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Add 248 MVAR switched shunt at GEN-2022-015 345 kV | Current Study |  |  | 615987.9795 | 11.6224 | 5300000 | 0.55419
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 576805.2599 | 4.8067 | 12000000 | 0.44581
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 501601.5282 | 9.4642 | 5300000 | 0.55419
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 422835.8681 | 1.6874 | 25058000 | 0.05687
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 323647.6398 | 0.6054 | 53460000 | 0.014568
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Add 525 MVAR SVC at SD.LS-LR-MB3 345 kV | Current Study |  |  | 319327.8988 | 2.6611 | 12000000 | 0.07031
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 255978.8154 | 1.7136 | 14938000 | 0.12168
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 247804.1006 | 1.7136 | 14460953.1406 | 0.12168
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Add 7 MVAR switched shunt at G19-030-TAP 345 kV | Current Study |  |  | 223308.5857 | 4.2134 | 5300000 | 0.1103
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 152304.0664 | 0.94061 | 16192000 | 0.07031
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MINGO 7 345 kV | Current Study |  |  | 145341.5824 | 2.7423 | 5300000 | 0.07031
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Add 5 MVAR switched shunt at SLKHILLS 4 138 kV | Current Study |  |  | 118091.122 | 4.8547 | 2432500 | 0.12168
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR switched shunt at GEN-2022-075 345 kV | Current Study |  |  | 93130.85 | 1.7572 | 5300000 | 0.037636
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Add 0.5 MVAR switched shunt at RKY_RDG4 138 kV | Current Study |  |  | 71610.3529 | 2.9439 | 2432500 | 0.12168
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Add 12 MVAR switched shunt at BEELER 3 115 kV | Current Study |  |  | 62868.6132 | 2.8415 | 2212500 | 0.07031
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 57632.5917 | 0.30985 | 18600000 | 0.03623
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 57632.5917 | 0.30985 | 18600000 | 0.03623
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at IRS7 115 KV 115 kV | Current Study |  |  | 38877.7369 | 1.7572 | 2212500 | 0.037636
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 37138.4136 | 0.19967 | 18600000 | 0.02563
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MED-LDG3 115 kV | Current Study |  |  | 36265.8558 | 1.6391 | 2212500 | 0.037636
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 35250.7392 | 1.5933 | 2212500 | 0.1103
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Add 40 MVAR switched shunt at SEGNTP 3 115 kV | Current Study |  |  | 28042.1325 | 1.2674 | 2212500 | 0.07031
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 24715.3431 | 1.1171 | 2212500 | 0.037636
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 23962.7091 | 1.0831 | 2212500 | 0.037636
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 21887.2606 | 0.98925 | 2212500 | 0.07031
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Add 0.04 MVAR switched shunt at ELLIS 2 69 kV | Current Study |  |  | 16678.8052 | 1.2086 | 1380000 | 0.07031
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 15520.1155 | 0.94061 | 1650000 | 0.07031
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Add 0.8 MVAR switched shunt at HARBNGR7 345 kV | Current Study |  |  | 15161.9995 | 0.28608 | 5300000 | 0.019793
GEN-2024-016 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 14735.8808 | 0.27804 | 5300000 | 0.0078818
GEN-2024-016 | 03 CENTRAL | TBD | ERIS | Add 24 MVAR switched shunt at NESSCTY3 115 kV | Current Study |  |  | 8681.8103 | 0.3924 | 2212500 | 0.019793
GEN-2024-017 | 02 NEBRASKA | TBD | NRIS | Rebuild line 645456 S3456 3 345 645458 S3458 3 345 1 | Current Study | 44.95 | (1793.00, 1793.00) | 1915935.8335 | 1.9374 | 98890000 | 0.027583
GEN-2024-017 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | Current Study | 19.87 | (1793.00, 1793.00) | 1095761.8554 | 2.5067 | 43714000 | 0.13809
GEN-2024-017 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2 | Current Study |  | (417.00, 417.00) | 919522.8719 | 5.4734 | 16800000 | 0.018091
GEN-2024-017 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2 | Current Study |  | (417.00, 417.00) | 919522.8719 | 5.4734 | 16800000 | 0.018091
GEN-2024-017 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | Current Study | 16.71 | (1793.00, 1793.00) | 884479.7852 | 2.406 | 36762000 | 0.21723
GEN-2024-017 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2 | Current Study |  | (336.00, 336.00) | 634294.3886 | 3.7756 | 16800000 | 0.0088462
GEN-2024-017 | 02 NEBRASKA | TBD | NRIS | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | Current Study | 17.69 | (160.00, 160.00) | 503390.8869 | 1.8971 | 26535000 | 0.025834
GEN-2024-017 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | Current Study | 10.55 | (297.00, 297.00) | 375355.0766 | 3.5579 | 10550000 | 0.022843
GEN-2024-017 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2 | Current Study |  | (110.00, 120.00) | 227649.9206 | 1.8971 | 12000000 | 0.012917
GEN-2024-017 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659202 LO.KVA2_-BE9 13 M2 | Current Study |  | (500.00, 617.00) | 109713.491 | 0.43885 | 25000000 | 0.0077914
GEN-2024-017 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659201 LO.KU1A_-BE9 13 M2 | Current Study |  | (600.00, 637.40) | 108205.6779 | 0.43282 | 25000000 | 0.0088336
GEN-2024-017 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 51673.7438 | 3.1317 | 1650000 | 0.61242
GEN-2024-018 | 02 NEBRASKA | TBD | NRIS | Rebuild line 645456 S3456 3 345 645458 S3458 3 345 1 | Current Study | 44.95 | (1793.00, 1793.00) | 936657.747 | 0.94717 | 98890000 | 0.02697
GEN-2024-018 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | Current Study | 19.87 | (1793.00, 1793.00) | 475798.1212 | 1.0884 | 43714000 | 0.11992
GEN-2024-018 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | Current Study | 16.71 | (1793.00, 1793.00) | 391506.1035 | 1.065 | 36762000 | 0.19231
GEN-2024-018 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2 | Current Study |  | (336.00, 336.00) | 271580.2478 | 1.6165 | 16800000 | 0.0075752
GEN-2024-018 | 02 NEBRASKA | TBD | NRIS | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | Current Study | 17.69 | (160.00, 160.00) | 235305.6584 | 0.88677 | 26535000 | 0.024152
GEN-2024-018 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | Current Study | 10.55 | (297.00, 297.00) | 187083.5087 | 1.7733 | 10550000 | 0.022771
GEN-2024-018 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2 | Current Study |  | (110.00, 120.00) | 106412.9603 | 0.88677 | 12000000 | 0.012076
GEN-2024-018 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2 | Current Study |  | (417.00, 417.00) | 85945.0937 | 0.51158 | 16800000 | 0.0033818
GEN-2024-018 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2 | Current Study |  | (417.00, 417.00) | 85945.0937 | 0.51158 | 16800000 | 0.0033818
GEN-2024-018 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659202 LO.KVA2_-BE9 13 M2 | Current Study |  | (500.00, 617.00) | 54610.2584 | 0.21844 | 25000000 | 0.0077564
GEN-2024-018 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659201 LO.KU1A_-BE9 13 M2 | Current Study |  | (600.00, 637.40) | 53859.7394 | 0.21544 | 25000000 | 0.0087939
GEN-2024-018 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 13571.6968 | 0.82253 | 1650000 | 0.32169
GEN-2024-019 | 02 NEBRASKA | TBD | NRIS | Rebuild line 645456 S3456 3 345 645458 S3458 3 345 1 | Current Study | 44.95 | (1793.00, 1793.00) | 1873315.494 | 1.8943 | 98890000 | 0.02697
GEN-2024-019 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | Current Study | 19.87 | (1793.00, 1793.00) | 951596.2423 | 2.1769 | 43714000 | 0.11992
GEN-2024-019 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | Current Study | 16.71 | (1793.00, 1793.00) | 783012.207 | 2.1299 | 36762000 | 0.19231
GEN-2024-019 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2 | Current Study |  | (336.00, 336.00) | 543160.4956 | 3.2331 | 16800000 | 0.0075752
GEN-2024-019 | 02 NEBRASKA | TBD | NRIS | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | Current Study | 17.69 | (160.00, 160.00) | 470611.3168 | 1.7735 | 26535000 | 0.024152
GEN-2024-019 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | Current Study | 10.55 | (297.00, 297.00) | 374167.0173 | 3.5466 | 10550000 | 0.022771
GEN-2024-019 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2 | Current Study |  | (110.00, 120.00) | 212825.9206 | 1.7735 | 12000000 | 0.012076
GEN-2024-019 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2 | Current Study |  | (417.00, 417.00) | 171890.1874 | 1.0232 | 16800000 | 0.0033818
GEN-2024-019 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2 | Current Study |  | (417.00, 417.00) | 171890.1874 | 1.0232 | 16800000 | 0.0033818
GEN-2024-019 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659202 LO.KVA2_-BE9 13 M2 | Current Study |  | (500.00, 617.00) | 109220.5169 | 0.43688 | 25000000 | 0.0077564
GEN-2024-019 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659201 LO.KU1A_-BE9 13 M2 | Current Study |  | (600.00, 637.40) | 107719.4789 | 0.43088 | 25000000 | 0.0087939
GEN-2024-019 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 27143.3936 | 1.6451 | 1650000 | 0.32169
GEN-2024-020 | 02 NEBRASKA | TBD | NRIS | Rebuild line 645456 S3456 3 345 645458 S3458 3 345 1 | Current Study | 44.95 | (1793.00, 1793.00) | 12051854.4365 | 12.1871 | 98890000 | 0.027583
GEN-2024-020 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | Current Study | 19.87 | (1793.00, 1793.00) | 6892695.5419 | 15.7677 | 43714000 | 0.13809
GEN-2024-020 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2 | Current Study |  | (417.00, 417.00) | 5784095.4842 | 34.4291 | 16800000 | 0.018091
GEN-2024-020 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2 | Current Study |  | (417.00, 417.00) | 5784095.4842 | 34.4291 | 16800000 | 0.018091
GEN-2024-020 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | Current Study | 16.71 | (1793.00, 1793.00) | 5563663.1653 | 15.1343 | 36762000 | 0.21723
GEN-2024-020 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2 | Current Study |  | (336.00, 336.00) | 3989916.3156 | 23.7495 | 16800000 | 0.0088462
GEN-2024-020 | 02 NEBRASKA | TBD | NRIS | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | Current Study | 17.69 | (160.00, 160.00) | 3166491.0629 | 11.9333 | 26535000 | 0.025834
GEN-2024-020 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | Current Study | 10.55 | (297.00, 297.00) | 2361104.5138 | 22.3801 | 10550000 | 0.022843
GEN-2024-020 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2 | Current Study |  | (110.00, 120.00) | 1431991.436 | 11.9333 | 12000000 | 0.012917
GEN-2024-020 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659202 LO.KVA2_-BE9 13 M2 | Current Study |  | (500.00, 617.00) | 690133.2497 | 2.7605 | 25000000 | 0.0077914
GEN-2024-020 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659201 LO.KU1A_-BE9 13 M2 | Current Study |  | (600.00, 637.40) | 680648.6193 | 2.7226 | 25000000 | 0.0088336
GEN-2024-020 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 325044.5175 | 19.6997 | 1650000 | 0.61242
GEN-2024-021 | 02 NEBRASKA | TBD | NRIS | Rebuild line 645456 S3456 3 345 645458 S3458 3 345 1 | Current Study | 44.95 | (1793.00, 1793.00) | 16687183.0659 | 16.8745 | 98890000 | 0.027583
GEN-2024-021 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | Current Study | 19.87 | (1793.00, 1793.00) | 9543732.2887 | 21.8322 | 43714000 | 0.13809
GEN-2024-021 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2 | Current Study |  | (417.00, 417.00) | 8008747.5936 | 47.6711 | 16800000 | 0.018091
GEN-2024-021 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2 | Current Study |  | (417.00, 417.00) | 8008747.5936 | 47.6711 | 16800000 | 0.018091
GEN-2024-021 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | Current Study | 16.71 | (1793.00, 1793.00) | 7703533.6134 | 20.9552 | 36762000 | 0.21723
GEN-2024-021 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2 | Current Study |  | (336.00, 336.00) | 5524499.5139 | 32.8839 | 16800000 | 0.0088462
GEN-2024-021 | 02 NEBRASKA | TBD | NRIS | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | Current Study | 17.69 | (160.00, 160.00) | 4384372.241 | 16.523 | 26535000 | 0.025834
GEN-2024-021 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | Current Study | 10.55 | (297.00, 297.00) | 3269221.6345 | 30.9879 | 10550000 | 0.022843
GEN-2024-021 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2 | Current Study |  | (110.00, 120.00) | 1982757.373 | 16.523 | 12000000 | 0.012917
GEN-2024-021 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659202 LO.KVA2_-BE9 13 M2 | Current Study |  | (500.00, 617.00) | 955569.1149 | 3.8223 | 25000000 | 0.0077914
GEN-2024-021 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659201 LO.KU1A_-BE9 13 M2 | Current Study |  | (600.00, 637.40) | 942436.5498 | 3.7697 | 25000000 | 0.0088336
GEN-2024-021 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 450061.6397 | 27.2765 | 1650000 | 0.61242
GEN-2024-022 | 02 NEBRASKA | TBD | NRIS | Rebuild line 645456 S3456 3 345 645458 S3458 3 345 1 | Current Study | 44.95 | (1793.00, 1793.00) | 11783758.7529 | 11.916 | 98890000 | 0.02697
GEN-2024-022 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | Current Study | 19.87 | (1793.00, 1793.00) | 5985847.3308 | 13.6932 | 43714000 | 0.11992
GEN-2024-022 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | Current Study | 16.71 | (1793.00, 1793.00) | 4925399.3665 | 13.3981 | 36762000 | 0.19231
GEN-2024-022 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2 | Current Study |  | (336.00, 336.00) | 3416654.7305 | 20.3372 | 16800000 | 0.0075752
GEN-2024-022 | 02 NEBRASKA | TBD | NRIS | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | Current Study | 17.69 | (160.00, 160.00) | 2960296.9931 | 11.1562 | 26535000 | 0.024152
GEN-2024-022 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | Current Study | 10.55 | (297.00, 297.00) | 2353631.2381 | 22.3093 | 10550000 | 0.022771
GEN-2024-022 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2 | Current Study |  | (110.00, 120.00) | 1338743.6939 | 11.1562 | 12000000 | 0.012076
GEN-2024-022 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2 | Current Study |  | (417.00, 417.00) | 1081244.7273 | 6.436 | 16800000 | 0.0033818
GEN-2024-022 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2 | Current Study |  | (417.00, 417.00) | 1081244.7273 | 6.436 | 16800000 | 0.0033818
GEN-2024-022 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659202 LO.KVA2_-BE9 13 M2 | Current Study |  | (500.00, 617.00) | 687032.2835 | 2.7481 | 25000000 | 0.0077564
GEN-2024-022 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659201 LO.KU1A_-BE9 13 M2 | Current Study |  | (600.00, 637.40) | 677590.2702 | 2.7104 | 25000000 | 0.0087939
GEN-2024-022 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 170740.7016 | 10.3479 | 1650000 | 0.32169
GEN-2024-023 | 02 NEBRASKA | TBD | NRIS | Rebuild line 645456 S3456 3 345 645458 S3458 3 345 1 | Current Study | 44.95 | (1793.00, 1793.00) | 8157986.8289 | 8.2496 | 98890000 | 0.02697
GEN-2024-023 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | Current Study | 19.87 | (1793.00, 1793.00) | 4144048.1521 | 9.4799 | 43714000 | 0.11992
GEN-2024-023 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | Current Study | 16.71 | (1793.00, 1793.00) | 3409891.8691 | 9.2756 | 36762000 | 0.19231
GEN-2024-023 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2 | Current Study |  | (336.00, 336.00) | 2365376.3519 | 14.0796 | 16800000 | 0.0075752
GEN-2024-023 | 02 NEBRASKA | TBD | NRIS | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | Current Study | 17.69 | (160.00, 160.00) | 2049436.3798 | 7.7235 | 26535000 | 0.024152
GEN-2024-023 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | Current Study | 10.55 | (297.00, 297.00) | 1629437.011 | 15.4449 | 10550000 | 0.022771
GEN-2024-023 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2 | Current Study |  | (110.00, 120.00) | 926822.5573 | 7.7235 | 12000000 | 0.012076
GEN-2024-023 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2 | Current Study |  | (417.00, 417.00) | 748554.042 | 4.4557 | 16800000 | 0.0033818
GEN-2024-023 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2 | Current Study |  | (417.00, 417.00) | 748554.042 | 4.4557 | 16800000 | 0.0033818
GEN-2024-023 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659202 LO.KVA2_-BE9 13 M2 | Current Study |  | (500.00, 617.00) | 475637.7347 | 1.9026 | 25000000 | 0.0077564
GEN-2024-023 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659201 LO.KU1A_-BE9 13 M2 | Current Study |  | (600.00, 637.40) | 469100.9563 | 1.8764 | 25000000 | 0.0087939
GEN-2024-023 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 118205.1011 | 7.1639 | 1650000 | 0.32169
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1 | Current Study | 30.63 | (1793.00, 1793.00) | 10457896.0962 | 15.5194 | 67386000 | 0.1694
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1 | Current Study | 56.1 | (1793.00, 1793.00) | 7229595.5279 | 5.8577 | 123420000 | 0.05601
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 776060 G23-204-TAP 345 1 | Current Study | 17.82 | (1793.00, 1793.00) | 6282622.1019 | 16.0255 | 39204000 | 0.40244
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | Current Study | 7.74 | (1793.00, 1793.00) | 3667036.6775 | 21.5353 | 17028000 | 0.40244
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 2651118.9378 | 1.7645 | 150244000 | 0.026658
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | Current Study | 6.93 | (1793.00, 1793.00) | 2443241.9285 | 16.0255 | 15246000 | 0.40244
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 2388963.1016 | 2.118 | 112794000 | 0.12027
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 1670317.2278 | 2.6408 | 63250000 | 0.095596
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1612337.9132 | 1.6887 | 95480000 | 0.045527
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1545024.4804 | 0.70769 | 218320000 | 0.014558
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 1430299.7617 | 1.6887 | 84700000 | 0.045527
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1337750.9658 | 0.93031 | 143796000 | 0.030977
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 507454 TURK 4 138 507456 TURK 3 115 507458 TURK1 1 13 M2 | Current Study |  | (257.00, 257.00) | 1310751.6545 | 12.6034 | 10400000 | 0.030847
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1273516.6062 | 1.2681 | 100427000 | 0.010857
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1081793.293 | 0.54495 | 198511000 | 0.01942
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 961652.8398 | 2.0464 | 46992000 | 0.055255
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 933459.7612 | 0.74782 | 124824000 | 0.032616
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 818068.482 | 0.87043 | 93984000 | 0.036008
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 716989.6212 | 0.43438 | 165062000 | 0.01822
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 663123.8578 | 1.9739 | 33594000 | 0.053696
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 619234.7368 | 0.75991 | 81488000 | 0.033638
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 611415.1708 | 2.3815 | 25674000 | 0.055735
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 609495.0216 | 5.0791 | 12000000 | 0.050364
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 764550 G20-087-TAP 345 1 | Current Study | 14.38 | (1793.00, 1793.00) | 577700.5153 | 1.8261 | 31636000 | 0.041515
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 504122 MCNAB 3 115 507453 HOPE 3 115 1 | Current Study | 3.32 | (394.00, 394.00) | 547337.7888 | 16.4861 | 3320000 | 0.061694
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 503767.9515 | 1.0972 | 45914000 | 0.036978
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 477869.7502 | 1.8888 | 25300000 | 0.025792
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at PHILL 7 345 kV | Current Study |  |  | 465068.838 | 8.7749 | 5300000 | 0.026088
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 435941.4659 | 2.4343 | 17908000 | 0.057915
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | Current Study | 8.91 | (2390.00, 2390.00) | 353267.852 | 1.8022 | 19602000 | 0.041515
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 504122 MCNAB 3 115 507456 TURK 3 115 1 | Current Study | 2.65 | (394.00, 394.00) | 333989.6043 | 12.6034 | 2650000 | 0.061694
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1 | Current Study | 11.3 | (1793.00, 1793.00) | 330034.4181 | 1.3276 | 24860000 | 0.027299
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 285156.1895 | 2.3763 | 12000000 | 0.058423
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 278185.8257 | 4.2149 | 6600000 | 0.058423
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 274936.1268 | 1.0972 | 25058000 | 0.036978
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 245539.6474 | 4.6328 | 5300000 | 0.050364
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | Current Study | 5.97 | (2390.00, 2390.00) | 236701.3554 | 1.8022 | 13134000 | 0.041515
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 233767.8476 | 1.9481 | 12000000 | 0.045527
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 232301.7371 | 1.9358 | 12000000 | 0.032142
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 218536.6344 | 1.8211 | 12000000 | 0.058423
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 214295.3086 | 1.7858 | 12000000 | 0.040287
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 196999.2526 | 8.5652 | 2300000 | 0.40244
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 193522.6559 | 1.6127 | 12000000 | 0.014518
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 190350.1666 | 1.5863 | 12000000 | 0.024921
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 189330.1117 | 1.5778 | 12000000 | 0.053516
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 188425.8589 | 1.2517 | 15053000 | 0.011037
GEN-2024-025 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 187794.2119 | 1.0375 | 18100000 | 0.010597
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 176513.6962 | 1.4709 | 12000000 | 0.032142
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 176513.6962 | 1.4709 | 12000000 | 0.032142
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 172632.692 | 1.4386 | 12000000 | 0.0327
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 171311.6926 | 1.4276 | 12000000 | 0.040287
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 168337.6908 | 1.4028 | 12000000 | 0.031544
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 167402.6394 | 1.395 | 12000000 | 0.032142
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 166830.3527 | 2.5277 | 6600000 | 0.058423
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 164559.5469 | 1.3713 | 12000000 | 0.032142
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 164222.6521 | 1.3685 | 12000000 | 0.024921
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 140751.5852 | 2.6557 | 5300000 | 0.050364
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 139303.9054 | 4.2863 | 3250000 | 0.058423
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 139303.9054 | 4.2863 | 3250000 | 0.058423
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 133570.8726 | 1.1131 | 12000000 | 0.0327
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 110685.1255 | 2.0884 | 5300000 | 0.040287
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 110544.4542 | 0.94807 | 11660000 | 0.036008
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 110367.4309 | 1.6722 | 6600000 | 0.045527
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 99773.5637 | 1.8825 | 5300000 | 0.031544
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 98260.2786 | 1.4888 | 6600000 | 0.0327
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 98260.2786 | 1.4888 | 6600000 | 0.0327
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 95731.9042 | 1.8063 | 5300000 | 0.031544
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 93057.5808 | 1.7558 | 5300000 | 0.036008
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 90270.2457 | 1.3677 | 6600000 | 0.036008
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 88724.1213 | 1.674 | 5300000 | 0.053516
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 86275.8606 | 1.6278 | 5300000 | 0.058423
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 84311.1345 | 2.5942 | 3250000 | 0.058423
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 82118.8748 | 2.5267 | 3250000 | 0.058423
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 82079.5167 | 1.5487 | 5300000 | 0.0327
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 80626.6897 | 0.53974 | 14938000 | 0.038326
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 78051.8665 | 0.53974 | 14460953.1406 | 0.038326
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 70916.7499 | 0.43797 | 16192000 | 0.032738
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 70091.9275 | 5.0791 | 1380000 | 0.050364
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV | Current Study |  |  | 64699.1784 | 4.6883 | 1380000 | 0.041211
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 63135.5679 | 1.9426 | 3250000 | 0.058423
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 60882.6369 | 1.8733 | 3250000 | 0.0327
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 60778.6205 | 2.0464 | 2970000 | 0.055255
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 60580.6133 | 1.143 | 5300000 | 0.036008
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 59441.0291 | 1.6887 | 3520000 | 0.045527
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 55741.0968 | 2.2915 | 2432500 | 0.031544
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 54881.6378 | 1.6887 | 3250000 | 0.045527
GEN-2024-025 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 54341.4215 | 1.0253 | 5300000 | 0.11671
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 52865.1685 | 3.8308 | 1380000 | 0.058423
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 52141.5562 | 1.6044 | 3250000 | 0.0327
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 51681.6058 | 1.5902 | 3250000 | 0.0327
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 51678.4055 | 1.5901 | 3250000 | 0.0327
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 51102.8537 | 3.7031 | 1380000 | 0.12027
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 50331.7791 | 1.5487 | 3250000 | 0.0327
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 45021.2004 | 2.0464 | 2200000 | 0.055255
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 43297.8899 | 1.3322 | 3250000 | 0.0327
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 38751.1854 | 1.1923 | 3250000 | 0.036008
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 38678.976 | 0.72979 | 5300000 | 0.0036166
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 30358.2379 | 1.3721 | 2212500 | 0.046228
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 29847.7763 | 2.1629 | 1380000 | 0.050364
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 29433.766 | 1.3303 | 2212500 | 0.046228
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CHILD4WT 138 kV | Current Study |  |  | 29366.8015 | 1.2073 | 2432500 | 0.041515
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 29153.8963 | 1.1985 | 2432500 | 0.036008
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 28749.7322 | 1.1819 | 2432500 | 0.036008
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 28533.0989 | 1.173 | 2432500 | 0.035467
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 23502.0858 | 1.703 | 1380000 | 0.0327
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 19006.6759 | 1.3773 | 1380000 | 0.036008
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 17843.2763 | 0.33667 | 5300000 | 0.032142
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 11796.1677 | 0.53316 | 2212500 | 0.037894
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 7226.571 | 0.43797 | 1650000 | 0.032738
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514827 CTNWOOD4 138 515377 CRESENT4 138 1 | Current Study | 13.6 | (472.00, 472.00) | 9370153.2991 | 57.4152 | 16320000 | 0.59496
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 9135717.0088 | 0.97188 | 940000000 | 0.01831
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520847 TWNLKJT4 138 521073 TWNLKSW4 138 1 | Current Study | 7.45 | (211.00, 211.00) | 6547173.1028 | 73.2346 | 8940000 | 0.19394
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520882 DOVERSW4 138 521016 OKEENE 4 138 1 | Current Study | 27.24 | (211.00, 211.00) | 5974688.5248 | 18.2779 | 32688000 | 0.06057
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515377 CRESENT4 138 521073 TWNLKSW4 138 1 | Current Study | 3.13 | (395.00, 395.00) | 3756000 | 100 | 3756000 | 0.40504
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 532803 BURNS 7 345 1 | Current Study | 50.03 | (1793.00, 1793.00) | 3550017.2872 | 3.2254 | 110066000 | 0.044883
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532803 BURNS 7 345 1 | Current Study | 45.5 | (1793.00, 1793.00) | 3228578.5842 | 3.2254 | 100100000 | 0.044883
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514710 WAUKOMI4 138 514774 HENESEY4 138 1 | Current Study | 11.86 | (395.00, 395.00) | 2965679.2467 | 20.8381 | 14232000 | 0.15099
GEN-2024-029 | 04 SOUTHEAST | TBD | NRIS | Add 0.24 MVAR switched shunt at CASHION4 138 kV | Current Study |  |  | 2432500 | 100 | 2432500 | 0.19414
GEN-2024-029 | 04 SOUTHEAST | TBD | NRIS | Add 0.3 MVAR switched shunt at TWNLKJT4 138 kV | Current Study |  |  | 2432500 | 100 | 2432500 | 0.19414
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520893 EL RENO4 138 520899 SCOTTSW4 138 1 | Current Study | 6.45 | (265.00, 265.00) | 2226720.8534 | 28.769 | 7740000 | 0.093203
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 1884092.5013 | 1.6065 | 117282000 | 0.045073
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 1807384.5256 | 1.203 | 150244000 | 0.036348
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514710 WAUKOMI4 138 514711 WAUKOTP4 138 1 | Current Study | 6.7 | (395.00, 395.00) | 1675383.7229 | 20.8381 | 8040000 | 0.15099
GEN-2024-029 | 04 SOUTHEAST | TBD | NRIS | Add 1.2 MVAR switched shunt at PINE ST4 138 kV | Current Study |  |  | 1401279.9349 | 57.6066 | 2432500 | 0.10554
GEN-2024-029 | 04 SOUTHEAST | TBD | NRIS | Add 0.33 MVAR switched shunt at TWNLAKE4 138 kV | Current Study |  |  | 1395499.8253 | 57.369 | 2432500 | 0.59533
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 1197196.6362 | 2.1518 | 55638000 | 0.064707
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 1152566.6709 | 2.5706 | 44836000 | 0.080467
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1110920.8522 | 1.1062 | 100427000 | 0.018942
GEN-2024-029 | 04 SOUTHEAST | TBD | NRIS | Add 5 MVAR switched shunt at CTNWOOD4 138 kV | Current Study |  |  | 1099431.1104 | 45.1976 | 2432500 | 0.59533
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1083576.5733 | 0.49632 | 218320000 | 0.02042
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 935215.2916 | 1.0399 | 89936000 | 0.016195
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 897389.4927 | 1.6271 | 55154000 | 0.038257
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 890651.9498 | 0.61939 | 143796000 | 0.041248
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 887692.0314 | 0.92972 | 95480000 | 0.050131
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 840756.8137 | 1.2739 | 66000000 | 0.03904
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520535 BULFTTP4 138 520882 DOVERSW4 138 1 | Current Study | 3.3 | (472.00, 472.00) | 825188.9978 | 20.8381 | 3960000 | 0.15099
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 787468.7375 | 0.92972 | 84700000 | 0.050131
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 721471.4925 | 0.57799 | 124824000 | 0.050418
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 707892.4705 | 0.3566 | 198511000 | 0.025416
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514774 HENESEY4 138 520535 BULFTTP4 138 1 | Current Study | 2.53 | (395.00, 395.00) | 632644.8983 | 20.8381 | 3036000 | 0.15099
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 631089.9526 | 1.3745 | 45914000 | 0.092647
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 591812.9733 | 0.29911 | 197860000 | 0.01971
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 470975.4252 | 0.57797 | 81488000 | 0.051169
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 460904.6795 | 0.98082 | 46992000 | 0.052966
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 454033.361 | 0.4831 | 93984000 | 0.039969
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 429544.2326 | 1.6271 | 26400000 | 0.038257
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 428820.8393 | 0.32255 | 132946000 | 0.013371
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 426381.767 | 0.25832 | 165062000 | 0.021671
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 348749.2599 | 1.0381 | 33594000 | 0.056479
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 344423.3139 | 1.3745 | 25058000 | 0.092647
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 342142.9502 | 1.3069 | 26180000 | 0.019689
GEN-2024-029 | 04 SOUTHEAST | TBD | NRIS | Add 0.23 MVAR switched shunt at DOVERSW2 69 kV | Current Study |  |  | 313194.5407 | 22.6953 | 1380000 | 0.022567
GEN-2024-029 | 04 SOUTHEAST | TBD | NRIS | Add 0.12 MVAR switched shunt at LACEY 2 69 kV | Current Study |  |  | 301099.842 | 21.8188 | 1380000 | 0.14855
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 268753.2037 | 0.50272 | 53460000 | 0.024195
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 262188.0058 | 1.0363 | 25300000 | 0.028302
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 122 MVAR switched shunt at HOYT 7 345 kV | Current Study |  |  | 224402.0784 | 4.234 | 5300000 | 0.041677
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 196671.7405 | 1.5964 | 12320000 | 0.045671
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 0.06 MVAR switched shunt at G24-125-TAP 345 kV | Current Study |  |  | 187172.5662 | 3.5316 | 5300000 | 0.03363
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 138 MVAR switched shunt at GEN-2024-016 345 kV | Current Study |  |  | 186167.4883 | 3.5126 | 5300000 | 0.029321
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 185116.8541 | 1.5426 | 12000000 | 0.045671
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 185116.8541 | 1.5426 | 12000000 | 0.045671
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 172094.5404 | 1.4341 | 12000000 | 0.064707
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 165042.44 | 1.3754 | 12000000 | 0.045671
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 164446.448 | 1.0924 | 15053000 | 0.019265
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 137575.6063 | 1.1465 | 12000000 | 0.064707
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 128905.6329 | 1.0742 | 12000000 | 0.072874
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 128703.8319 | 1.0725 | 12000000 | 0.050131
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 127896.887 | 1.0658 | 12000000 | 0.033489
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 125406.9448 | 1.0451 | 12000000 | 0.045671
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 125406.9448 | 1.0451 | 12000000 | 0.045671
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 120269.9044 | 1.0022 | 12000000 | 0.045073
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 118933.8505 | 0.99112 | 12000000 | 0.045671
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 116913.9305 | 0.97428 | 12000000 | 0.045671
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 111458.417 | 0.92882 | 12000000 | 0.045671
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 110341.7263 | 0.91951 | 12000000 | 0.033489
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 107941.5556 | 0.89951 | 12000000 | 0.016195
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 106805.5728 | 2.0152 | 5300000 | 0.033489
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 100500.9588 | 1.8962 | 5300000 | 0.03357
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 95700.6743 | 0.79751 | 12000000 | 0.051169
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 88888.114 | 1.6771 | 5300000 | 0.064707
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 76326.761 | 0.63606 | 12000000 | 0.028915
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 71283.8397 | 1.345 | 5300000 | 0.045073
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 68396.2511 | 1.2905 | 5300000 | 0.045073
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 61352.8955 | 0.52618 | 11660000 | 0.039969
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 60764.1787 | 0.92067 | 6600000 | 0.050131
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 60407.9241 | 1.1398 | 5300000 | 0.072874
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520999 MOORLND4 138 786210 G24-308-TAP 138 1 | Current Study | 1.19 | (395.00, 395.00) | 60310.9444 | 4.2235 | 1428000 | 0.058416
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 59056.2074 | 0.49214 | 12000000 | 0.028915
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 53630.9681 | 0.35902 | 14938000 | 0.050987
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 51918.2565 | 0.35902 | 14460953.1406 | 0.050987
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 51647.6857 | 0.97448 | 5300000 | 0.039969
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 50100.693 | 0.7591 | 6600000 | 0.039969
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 46993.2694 | 0.88667 | 5300000 | 0.03363
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 43444.1977 | 0.65825 | 6600000 | 0.028915
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 43444.1977 | 0.65825 | 6600000 | 0.028915
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 42593.8685 | 0.26306 | 16192000 | 0.039326
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 41284.8317 | 0.62553 | 6600000 | 0.028915
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 39824.5713 | 1.6372 | 2432500 | 0.045073
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 38840.7452 | 0.73284 | 5300000 | 0.033489
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 38152.6413 | 0.71986 | 5300000 | 0.033489
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 36290.1347 | 0.68472 | 5300000 | 0.028915
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 35982.1446 | 0.67891 | 5300000 | 0.033489
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 35795.3527 | 1.6271 | 2200000 | 0.038257
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 33722.4693 | 0.63627 | 5300000 | 0.045671
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 33622.7146 | 0.63439 | 5300000 | 0.039969
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 32725.9735 | 0.92972 | 3520000 | 0.050131
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 30215.7767 | 0.92972 | 3250000 | 0.050131
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 29130.2115 | 0.98082 | 2970000 | 0.052966
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 27087.323 | 0.83346 | 3250000 | 0.050131
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 26918.2761 | 0.82825 | 3250000 | 0.028915
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 26533.1723 | 0.50063 | 5300000 | 0.0049618
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 23053.5482 | 0.70934 | 3250000 | 0.028915
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 22850.1886 | 0.70308 | 3250000 | 0.028915
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 22848.7736 | 0.70304 | 3250000 | 0.028915
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 22253.3845 | 0.68472 | 3250000 | 0.028915
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 21577.9344 | 0.98082 | 2200000 | 0.052966
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 21507.2112 | 0.66176 | 3250000 | 0.039969
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 21205.318 | 1.6065 | 1320000 | 0.045073
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 21138.1651 | 0.9554 | 2212500 | 0.040949
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 20864.135 | 0.64197 | 3250000 | 0.028915
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 19143.4638 | 0.58903 | 3250000 | 0.028915
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 17797.4259 | 0.3358 | 5300000 | 0.039326
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 17305.5474 | 0.14421 | 12000000 | 0.026751
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 16180.6407 | 0.66519 | 2432500 | 0.039969
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 15956.3264 | 0.65596 | 2432500 | 0.039969
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 13300.0975 | 0.96378 | 1380000 | 0.044884
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 12963.5138 | 0.56363 | 2300000 | 0.052966
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 12677.0376 | 0.23919 | 5300000 | 0.045671
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 10548.8539 | 0.76441 | 1380000 | 0.039969
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 6121.0812 | 0.27666 | 2212500 | 0.039326
GEN-2024-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 4340.4078 | 0.26306 | 1650000 | 0.039326
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add line 659131 LARAMIE_-MB3 345 800120 UNDERWOOD 2 345 P2 | Current Study | 206.4 | (1792.00, 1792.00) | 42947283.545 | 6.6089 | 649840000 | 0.025159
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add line 652424 BELFELD3 345 800121 MAURINE 2 345 P2 | Current Study | 154.2 | (1792.00, 1792.00) | 35047726.2213 | 7.1816 | 488020000 | 0.019697
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 33819770.1266 | 3.5978 | 940000000 | 0.067781
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Rebuild line 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Current Study | 75.83 | (1793.00, 1793.00) | 10173825.426 | 6.0985 | 166826000 | 0.091166
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Rebuild line 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | Current Study | 84.86 | (1793.00, 1793.00) | 8976279.4696 | 4.8081 | 186692000 | 0.1118
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 531448 HOLCOMB3 115 531449 HOLCOMB7 345 531450 HOLCTER1 13 M2 | Current Study |  | (336.00, 358.50) | 7891066.2366 | 46.9706 | 16800000 | 0.3419
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Rebuild line 523106 TXPHSF 3 115 539672 E-LIBER3 115 1 | Current Study | 47.28 | (260.00, 260.00) | 5611134.6033 | 11.8679 | 47280000 | 0.044588
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 3988860.6041 | 2.0094 | 198511000 | 0.09056
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Rebuild line 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Current Study | 27.23 | (297.00, 297.00) | 3139600.141 | 11.5299 | 27230000 | 0.066299
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Rebuild line 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Current Study | 38.26 | (1793.00, 1793.00) | 3091787.5265 | 3.6732 | 84172000 | 0.11846
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Rebuild line 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Current Study | 37.4 | (1793.00, 1793.00) | 3055675.9255 | 3.7138 | 82280000 | 0.11846
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 2957228.2697 | 1.7916 | 165062000 | 0.1503
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 2222667.8545 | 1.1234 | 197860000 | 0.074024
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | Current Study | 21.05 | (1793.00, 1793.00) | 1922458.4556 | 4.1513 | 46310000 | 0.14664
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Rebuild line 523961 POTTER_CO 7 345 784950 G24-266_TAP 345 1 | Current Study | 18.24 | (1793.00, 1793.00) | 1905394.7932 | 4.7483 | 40128000 | 0.1118
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | Current Study | 19.2 | (2390.00, 2390.00) | 1454655.3905 | 3.4438 | 42240000 | 0.11733
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1234463.1348 | 0.62186 | 198511000 | 0.044322
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | Current Study | 16.04 | (2390.00, 2390.00) | 1215243.3575 | 3.4438 | 35288000 | 0.11733
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2 | Current Study |  | (350.00, 385.00) | 991746.6775 | 5.9033 | 16800000 | 0.070073
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 938441.3257 | 0.1 | 938400000 | 0.020017
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR SVC at GEN-2021-076 345 kV | Current Study |  |  | 883625.4986 | 7.3635 | 12000000 | 0.11846
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | Current Study | 13 | (2390.00, 2390.00) | 792265.5544 | 2.7702 | 28600000 | 0.11679
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add phase shifting xfmr 523084 SOONER 3 115 523106 TXPHSF 3 115 M2 | Current Study |  | (120.00, 120.00) | 510318.9254 | 11.8679 | 4300000 | 0.022294
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Rebuild line 531405 WALKMYR3 115 531481 HUGOTON3 115 1 | Current Study | 12.27 | (598.00, 598.00) | 463977.1681 | 3.7814 | 12270000 | 0.073848
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add 525 MVAR SVC at SD.LS-LR-MB3 345 kV | Current Study |  |  | 370448.9451 | 3.0871 | 12000000 | 0.16313
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 531405 WALKMYR3 115 531510 HARBNGR3 115 M2 | Current Study | 1.28 | (598.00, 598.00) | 353722.9817 | 5.9033 | 5992000 | 0.070073
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add 66 MVAR switched shunt at GEN-2021-021 345 kV | Current Study |  |  | 228238.9617 | 4.3064 | 5300000 | 0.0029763
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 198221.1872 | 0.43172 | 45914000 | 0.0291
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR switched shunt at GEN-2022-075 345 kV | Current Study |  |  | 187618.8725 | 3.54 | 5300000 | 0.15164
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 176686.5871 | 1.0912 | 16192000 | 0.16313
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MINGO 7 345 kV | Current Study |  |  | 168609.2449 | 3.1813 | 5300000 | 0.16313
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add 7 MVAR switched shunt at G19-030-TAP 345 kV | Current Study |  |  | 153500.1843 | 2.8962 | 5300000 | 0.15164
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 108181.0887 | 0.43172 | 25058000 | 0.0291
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 94625.4102 | 0.63345 | 14938000 | 0.08996
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add 2.3 MVAR switched shunt at GRANT 3 115 kV | Current Study |  |  | 91965.6518 | 4.1566 | 2212500 | 0.073848
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 91603.5362 | 0.63345 | 14460953.1406 | 0.08996
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add 248 MVAR switched shunt at GEN-2022-015 345 kV | Current Study |  |  | 90662.0104 | 1.7106 | 5300000 | 0.16313
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 82385.8154 | 0.68655 | 12000000 | 0.12735
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at IRS7 115 KV 115 kV | Current Study |  |  | 78322.0293 | 3.54 | 2212500 | 0.15164
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 73826.4455 | 1.393 | 5300000 | 0.16313
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MED-LDG3 115 kV | Current Study |  |  | 73060.2049 | 3.3022 | 2212500 | 0.15164
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add 12 MVAR switched shunt at BEELER 3 115 kV | Current Study |  |  | 72933.2186 | 3.2964 | 2212500 | 0.16313
GEN-2024-030 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 70690.4262 | 1.3338 | 5300000 | 0.075621
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add 60 MVAR switched shunt at WAYSIDE 4 230 kV | Current Study |  |  | 64665.111 | 1.6906 | 3825000 | 0.036318
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 56778.8972 | 1.0713 | 5300000 | 0.048956
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add 0.8 MVAR switched shunt at HARBNGR7 345 kV | Current Study |  |  | 53678.5607 | 1.0128 | 5300000 | 0.14015
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 49790.8566 | 2.2504 | 2212500 | 0.15164
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 49164.121 | 0.92762 | 5300000 | 0.043155
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 48274.6208 | 2.1819 | 2212500 | 0.15164
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 40344.5178 | 0.21691 | 18600000 | 0.055685
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 35189.1418 | 0.18919 | 18600000 | 0.044242
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 35189.1418 | 0.18919 | 18600000 | 0.044242
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add 40 MVAR switched shunt at SEGNTP 3 115 kV | Current Study |  |  | 32531.3837 | 1.4703 | 2212500 | 0.16313
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add 24 MVAR switched shunt at NESSCTY3 115 kV | Current Study |  |  | 27930.482 | 1.2624 | 2212500 | 0.12735
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 25391.1814 | 1.1476 | 2212500 | 0.16313
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 20350.1373 | 0.91978 | 2212500 | 0.12735
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add 0.04 MVAR switched shunt at ELLIS 2 69 kV | Current Study |  |  | 19348.907 | 1.4021 | 1380000 | 0.16313
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 18004.7473 | 1.0912 | 1650000 | 0.16313
GEN-2024-030 | 03 CENTRAL | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 12913.9462 | 0.93579 | 1380000 | 0.12735
GEN-2024-030 | 03 CENTRAL | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 12666.5499 | 0.91787 | 1380000 | 0.077466
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Add line 659131 LARAMIE_-MB3 345 800120 UNDERWOOD 2 345 P2 | Current Study | 206.4 | (1792.00, 1792.00) | 60202704.718 | 9.2642 | 649840000 | 0.021161
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 47370150.0135 | 5.0394 | 940000000 | 0.056963
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Rebuild line 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | Current Study | 84.86 | (1793.00, 1793.00) | 20177172.1437 | 10.8077 | 186692000 | 0.15079
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Rebuild line 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Current Study | 18.19 | (329.00, 329.00) | 13788659.7938 | 75.8035 | 18190000 | 0.23912
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Rebuild line 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Current Study | 12 | (329.00, 329.00) | 9096422.074 | 75.8035 | 12000000 | 0.23912
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2 | Current Study |  | (350.00, 385.00) | 8212470.7039 | 48.8838 | 16800000 | 0.34816
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Rebuild line 531405 WALKMYR3 115 531481 HUGOTON3 115 1 | Current Study | 12.27 | (598.00, 598.00) | 7967497.961 | 64.9348 | 12270000 | 0.76088
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 7301751.2257 | 4.4236 | 165062000 | 0.22266
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Rebuild line 523106 TXPHSF 3 115 539672 E-LIBER3 115 1 | Current Study | 47.28 | (260.00, 260.00) | 7175740.9359 | 15.1771 | 47280000 | 0.034213
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Rebuild line 523961 POTTER_CO 7 345 784950 G24-266_TAP 345 1 | Current Study | 18.24 | (1793.00, 1793.00) | 4283008.2191 | 10.6734 | 40128000 | 0.15079
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Rebuild line 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Current Study | 38.26 | (1793.00, 1793.00) | 4201639.5309 | 4.9917 | 84172000 | 0.096591
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Rebuild line 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Current Study | 37.4 | (1793.00, 1793.00) | 4152565.0298 | 5.0469 | 82280000 | 0.096591
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 3702249.5465 | 0.39453 | 938400000 | 0.047382
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 531448 HOLCOMB3 115 531449 HOLCOMB7 345 531450 HOLCTER1 13 M2 | Current Study |  | (336.00, 358.50) | 3202180.0702 | 19.0606 | 16800000 | 0.083246
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 531405 WALKMYR3 115 531510 HARBNGR3 115 M2 | Current Study | 1.28 | (598.00, 598.00) | 2929114.5511 | 48.8838 | 5992000 | 0.34816
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 2557191.7314 | 1.2882 | 198511000 | 0.034834
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | Current Study | 21.05 | (1793.00, 1793.00) | 2168463.5484 | 4.6825 | 46310000 | 0.09924
GEN-2024-032 | 03 CENTRAL | TBD | NRIS | Add 8.4 MVAR switched shunt at MANTERT3 115 kV | Current Study |  |  | 1677152.8199 | 75.8035 | 2212500 | 0.045351
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Add 2.3 MVAR switched shunt at GRANT 3 115 kV | Current Study |  |  | 1579250.4981 | 71.3786 | 2212500 | 0.76088
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | Current Study | 19.2 | (2390.00, 2390.00) | 1486449.6639 | 3.5191 | 42240000 | 0.071934
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR switched shunt at GEN-2022-075 345 kV | Current Study |  |  | 1435891.0001 | 27.0923 | 5300000 | 0.69632
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | Current Study | 16.04 | (2390.00, 2390.00) | 1241804.8234 | 3.5191 | 35288000 | 0.071934
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR SVC at GEN-2021-076 345 kV | Current Study |  |  | 1200818.9193 | 10.0068 | 12000000 | 0.096591
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Add 7 MVAR switched shunt at G19-030-TAP 345 kV | Current Study |  |  | 1174772.7196 | 22.1655 | 5300000 | 0.69632
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Rebuild line 539652 CMRIVTP3 115 539672 E-LIBER3 115 1 | Current Study | 11.74 | (176.00, 176.00) | 838175.3589 | 7.1395 | 11740000 | 0.012357
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | Current Study | 13 | (2390.00, 2390.00) | 809582.0321 | 2.8307 | 28600000 | 0.071607
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 713108.3961 | 0.35923 | 198511000 | 0.015362
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Add phase shifting xfmr 523084 SOONER 3 115 523106 TXPHSF 3 115 M2 | Current Study |  | (120.00, 120.00) | 652616.0327 | 15.1771 | 4300000 | 0.017106
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Add 248 MVAR switched shunt at GEN-2022-015 345 kV | Current Study |  |  | 644976.4241 | 12.1694 | 5300000 | 0.69632
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at IRS7 115 KV 115 kV | Current Study |  |  | 599416.7619 | 27.0923 | 2212500 | 0.69632
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MED-LDG3 115 kV | Current Study |  |  | 559146.7919 | 25.2722 | 2212500 | 0.69632
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 525206.9371 | 9.9096 | 5300000 | 0.69632
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Add 0.8 MVAR switched shunt at HARBNGR7 345 kV | Current Study |  |  | 444502.2188 | 8.3868 | 5300000 | 0.69632
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 408131.7646 | 2.5206 | 16192000 | 0.22609
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 381061.0411 | 17.2231 | 2212500 | 0.69632
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 369456.9345 | 16.6986 | 2212500 | 0.69632
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Add 66 MVAR switched shunt at GEN-2021-021 345 kV | Current Study |  |  | 308529.4653 | 5.8213 | 5300000 | 0.002414
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 307983.7414 | 0.67078 | 45914000 | 0.027128
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 168085.0414 | 0.67078 | 25058000 | 0.027128
GEN-2024-032 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 123405.3546 | 2.3284 | 5300000 | 0.079207
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Add 525 MVAR SVC at SD.LS-LR-MB3 345 kV | Current Study |  |  | 117280.994 | 0.97734 | 12000000 | 0.030988
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 106877.0259 | 0.89064 | 12000000 | 0.099127
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 85145.4825 | 0.45777 | 18600000 | 0.06423
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 85145.4825 | 0.45777 | 18600000 | 0.06423
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 83986.907 | 1.5847 | 5300000 | 0.044233
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 82874.9266 | 0.44556 | 18600000 | 0.068632
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 78630.0959 | 1.4836 | 5300000 | 0.040678
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 44842.9287 | 0.30019 | 14938000 | 0.025579
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 43410.8643 | 0.30019 | 14460953.1406 | 0.025579
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 41589.5141 | 2.5206 | 1650000 | 0.22609
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Add 24 MVAR switched shunt at NESSCTY3 115 kV | Current Study |  |  | 36233.5049 | 1.6377 | 2212500 | 0.099127
GEN-2024-032 | 03 CENTRAL | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 33750.9563 | 2.4457 | 1380000 | 0.12385
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Add 0.04 MVAR switched shunt at ELLIS 2 69 kV | Current Study |  |  | 19595.5533 | 1.42 | 1380000 | 0.099127
GEN-2024-032 | 03 CENTRAL | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 16752.9344 | 1.214 | 1380000 | 0.099127
GEN-2024-034 | 01 NORTH | TBD | ERIS | Rebuild line 652522 SUMMIT-7 115 652531 WATERTN7 115 1 | Current Study | 30.78 | (176.00, 176.00) | 15996166.4991 | 51.9694 | 30780000 | 0.075905
GEN-2024-034 | 01 NORTH | TBD | NRIS | Rebuild line 652296 WARD 4 230 652426 BISMARK4 230 1 | Current Study | 7.74 | (519.00, 519.00) | 5982243.3645 | 40.6789 | 14706000 | 0.037607
GEN-2024-034 | 01 NORTH | TBD | ERIS | Rebuild line 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Current Study | 36.8 | (1793.00, 1793.00) | 3781120.4077 | 4.6704 | 80960000 | 0.074726
GEN-2024-034 | 01 NORTH | TBD | ERIS | Rebuild line 652529 WATERTN3 345 659165 CROCKER_-BE3 345 1 | Current Study | 44.23 | (1793.00, 1793.00) | 1490219.7429 | 1.5315 | 97306000 | 0.041966
GEN-2024-034 | 01 NORTH | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659202 LO.KVA2_-BE9 13 M2 | Current Study |  | (500.00, 617.00) | 1164881.8807 | 4.6595 | 25000000 | 0.029308
GEN-2024-034 | 01 NORTH | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659201 LO.KU1A_-BE9 13 M2 | Current Study |  | (600.00, 637.40) | 1148872.691 | 4.5955 | 25000000 | 0.033229
GEN-2024-034 | 01 NORTH | TBD | ERIS | Rebuild line 652884 NUNDRWD-LNX3 230 785430 G24-282-TAP 230 1 | Current Study | 35.21 | (519.00, 519.00) | 796200.0925 | 1.1902 | 66899000 | 0.019851
GEN-2024-034 | 01 NORTH | TBD | ERIS | Add 24 MVAR switched shunt at DAYTON__-ER7 115 kV | Current Study |  |  | 103331.6964 | 4.6704 | 2212500 | 0.074726
GEN-2024-034 | 01 NORTH | TBD | ERIS | Add 0.4 MVAR switched shunt at SHINDLER-ER7 115 kV | Current Study |  |  | 100527.141 | 4.5436 | 2212500 | 0.079956
GEN-2024-034 | 01 NORTH | TBD | ERIS | Rebuild line 620263 FORMN 7 115 652438 FORMAN 7 115 1 | Current Study | 0.1 | (176.00, 176.00) | 100000 | 100 | 100000 | 0.7517
GEN-2024-034 | 01 NORTH | TBD | ERIS | Add 60 MVAR switched shunt at WAYSIDE 4 230 kV | Current Study |  |  | 83979.6943 | 2.1955 | 3825000 | 0.040428
GEN-2024-034 | 01 NORTH | TBD | ERIS | Add 0.5 MVAR switched shunt at ORLAND-ER8 69 kV | Current Study |  |  | 64450.9564 | 4.6704 | 1380000 | 0.074726
GEN-2024-034 | 01 NORTH | TBD | ERIS | Add 14.4 MVAR switched shunt at SW145-ER8 69 kV | Current Study |  |  | 64450.9564 | 4.6704 | 1380000 | 0.074726
GEN-2024-034 | 01 NORTH | TBD | ERIS | Add 4.4 MVAR switched shunt at DESMET-ER7 115 kV | Current Study |  |  | 50447.4854 | 2.2801 | 2212500 | 0.074726
GEN-2024-034 | 01 NORTH | TBD | ERIS | Add 10 MVAR switched shunt at REDFIELD 115 kV | Current Study |  |  | 33883.9513 | 1.5315 | 2212500 | 0.041966
GEN-2024-034 | 01 NORTH | TBD | ERIS | Add 54 MVAR switched shunt at REDFELD-ER7 115 kV | Current Study |  |  | 33883.9513 | 1.5315 | 2212500 | 0.041966
GEN-2024-034 | 01 NORTH | TBD | ERIS | Add 5.5 MVAR switched shunt at LOOMIS-ER8 69 kV | Current Study |  |  | 32931.9425 | 2.3864 | 1380000 | 0.079956
GEN-2024-034 | 01 NORTH | TBD | ERIS | Add 4 MVAR switched shunt at MOS-RDFL-ER8 69 kV | Current Study |  |  | 21134.3967 | 1.5315 | 1380000 | 0.041966
GEN-2024-034 | 01 NORTH | TBD | ERIS | Rebuild line 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Current Study | 0 | (880.00, 880.00) | 10274.7837 | 4.6704 | 220000 | 0.074726
GEN-2024-034 | 01 NORTH | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 3831.659 | 0.27766 | 1380000 | 0.049773
GEN-2024-034 | 01 NORTH | TBD | ERIS | Rebuild line 652484 NUNDRWD4 230 652884 NUNDRWD-LNX3 230 Z | Current Study | 0.14514 | (519.00, 519.00) | 3282.0315 | 1.1902 | 275765.6361 | 0.019851
GEN-2024-035 | 01 NORTH | TBD | ERIS | Rebuild line 652529 WATERTN3 345 659165 CROCKER_-BE3 345 1 | Current Study | 44.23 | (1793.00, 1793.00) | 28979326.5749 | 29.7816 | 97306000 | 0.52894
GEN-2024-035 | 01 NORTH | TBD | ERIS | Rebuild line 652568 GROTONSOUTH7 115 655481 REDFELD-ER7 115 1 | Current Study | 42.57 | (176.00, 176.00) | 25469977.0312 | 59.8308 | 42570000 | 0.060484
GEN-2024-035 | 01 NORTH | TBD | ERIS | Rebuild line 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | Current Study | 32.97 | (217.00, 217.00) | 20755023.95 | 62.9512 | 32970000 | 0.055972
GEN-2024-035 | 01 NORTH | TBD | ERIS | Rebuild line 652515 HURON 7 115 655481 REDFELD-ER7 115 1 | Current Study | 30.85 | (176.00, 176.00) | 18493414.4864 | 59.9462 | 30850000 | 0.060386
GEN-2024-035 | 01 NORTH | TBD | ERIS | Rebuild line 652512 GROTON 7 115 660001 ABR SIEBRCHT 115 1 | Current Study | 25.8 | (260.00, 260.00) | 15569173.6763 | 60.3456 | 25800000 | 0.078886
GEN-2024-035 | 01 NORTH | TBD | ERIS | Rebuild line 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | Current Study | 21.31 | (217.00, 217.00) | 13414909.3229 | 62.9512 | 21310000 | 0.055972
GEN-2024-035 | 01 NORTH | TBD | ERIS | Rebuild line 652522 SUMMIT-7 115 652531 WATERTN7 115 1 | Current Study | 30.78 | (176.00, 176.00) | 10238507.9786 | 33.2635 | 30780000 | 0.031489
GEN-2024-035 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 652237 WATERT19 13 652529 WATERTN3 345 652530 WATERTN4 230 M2 | Current Study |  | (400.00, 478.00) | 10121919.0886 | 40.4877 | 25000000 | 0.10763
GEN-2024-035 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 659160 GROTON__-BE3 345 659161 GRT.KU2A-BE9 13 659187 GROTON__-BE7 115 M2 | Current Study |  | (400.00, 400.00) | 8924644.9038 | 53.1229 | 16800000 | 0.12545
GEN-2024-035 | 01 NORTH | TBD | ERIS | Rebuild line 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Current Study | 36.8 | (1793.00, 1793.00) | 6980362.1212 | 8.622 | 80960000 | 0.089414
GEN-2024-035 | 01 NORTH | TBD | ERIS | Add line and rebuild line 652568 GROTONSOUTH7 115 659187 GROTON__-BE7 115 M2 | Current Study | 0.1 | (598.00, 598.00) | 2239483.8698 | 51.601 | 4340000 | 0.12545
GEN-2024-035 | 01 NORTH | TBD | ERIS | Rebuild line 652884 NUNDRWD-LNX3 230 785430 G24-282-TAP 230 1 | Current Study | 35.21 | (519.00, 519.00) | 1184724.8687 | 1.7709 | 66899000 | 0.019145
GEN-2024-035 | 01 NORTH | TBD | ERIS | Add 10 MVAR switched shunt at REDFIELD 115 kV | Current Study |  |  | 658918.9916 | 29.7816 | 2212500 | 0.52894
GEN-2024-035 | 01 NORTH | TBD | ERIS | Add 54 MVAR switched shunt at REDFELD-ER7 115 kV | Current Study |  |  | 658918.9916 | 29.7816 | 2212500 | 0.52894
GEN-2024-035 | 01 NORTH | TBD | ERIS | Add 4.4 MVAR switched shunt at DESMET-ER7 115 kV | Current Study |  |  | 550932.4483 | 24.9009 | 2212500 | 0.52894
GEN-2024-035 | 01 NORTH | TBD | ERIS | Add 4 MVAR switched shunt at MOS-RDFL-ER8 69 kV | Current Study |  |  | 410986.7609 | 29.7816 | 1380000 | 0.52894
GEN-2024-035 | 01 NORTH | TBD | ERIS | Add 5.5 MVAR switched shunt at LOOMIS-ER8 69 kV | Current Study |  |  | 336125.2013 | 24.3569 | 1380000 | 0.52894
GEN-2024-035 | 01 NORTH | TBD | ERIS | Add 24 MVAR switched shunt at DAYTON__-ER7 115 kV | Current Study |  |  | 190761.6214 | 8.622 | 2212500 | 0.089414
GEN-2024-035 | 01 NORTH | TBD | ERIS | Add 0.4 MVAR switched shunt at SHINDLER-ER7 115 kV | Current Study |  |  | 183590.3227 | 8.2979 | 2212500 | 0.094643
GEN-2024-035 | 01 NORTH | TBD | ERIS | Rebuild line 652512 GROTON 7 115 652568 GROTONSOUTH7 115 Z | Current Study | 0.25 | (598.00, 598.00) | 153501.0874 | 61.4004 | 250000 | 0.13486
GEN-2024-035 | 01 NORTH | TBD | ERIS | Add 60 MVAR switched shunt at WAYSIDE 4 230 kV | Current Study |  |  | 134682.598 | 3.5211 | 3825000 | 0.042024
GEN-2024-035 | 01 NORTH | TBD | ERIS | Add 0.5 MVAR switched shunt at ORLAND-ER8 69 kV | Current Study |  |  | 118983.5198 | 8.622 | 1380000 | 0.089414
GEN-2024-035 | 01 NORTH | TBD | ERIS | Add 14.4 MVAR switched shunt at SW145-ER8 69 kV | Current Study |  |  | 118983.5198 | 8.622 | 1380000 | 0.089414
GEN-2024-035 | 01 NORTH | TBD | ERIS | Rebuild line 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Current Study | 0 | (880.00, 880.00) | 18968.3753 | 8.622 | 220000 | 0.089414
GEN-2024-035 | 01 NORTH | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 6182.1453 | 0.44798 | 1380000 | 0.05205
GEN-2024-035 | 01 NORTH | TBD | ERIS | Rebuild line 652484 NUNDRWD4 230 652884 NUNDRWD-LNX3 230 Z | Current Study | 0.14514 | (519.00, 519.00) | 4883.5768 | 1.7709 | 275765.6361 | 0.019145
GEN-2024-038 | 02 NEBRASKA | TBD | ERIS | Rebuild line 532913 KELLY 5 161 532920 TECHILL5 161 1 | Current Study | 52.64 | (160.00, 160.00) | 27318155.609 | 34.5975 | 78960000 | 0.052408
GEN-2024-038 | 02 NEBRASKA | TBD | NRIS | Rebuild line 645456 S3456 3 345 645458 S3458 3 345 1 | Current Study | 44.95 | (1793.00, 1793.00) | 12679036.6738 | 12.8214 | 98890000 | 0.037724
GEN-2024-038 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640140 COOPER 5 161 778110 G24-038-TAP 161 1 | Current Study | 11.26 | (446.00, 446.00) | 9562229.7245 | 56.6147 | 16890000 | 0.61929
GEN-2024-038 | 02 NEBRASKA | TBD | ERIS | Rebuild line 646280 S1280 5 161 778110 G24-038-TAP 161 1 | Current Study | 4.25 | (309.00, 309.00) | 6375000 | 100 | 6375000 | 0.38071
GEN-2024-038 | 02 NEBRASKA | TBD | ERIS | Rebuild line 646263 S1263 5 161 646280 S1280 5 161 1 | Current Study | 8 | (309.00, 309.00) | 6071317.8949 | 50.5943 | 12000000 | 0.18023
GEN-2024-038 | 02 NEBRASKA | TBD | ERIS | Rebuild line 533210 ENEMEHA3 115 533212 KINGFISH3 115 1 | Current Study | 16.47 | (115.00, 115.00) | 5591681.8091 | 33.9507 | 16470000 | 0.022873
GEN-2024-038 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 532913 KELLY 5 161 532942 KELLY 1 13 533217 KELLY 3 115 M2 | Current Study |  | (144.00, 144.00) | 4027563.0699 | 33.563 | 12000000 | 0.043427
GEN-2024-038 | 02 NEBRASKA | TBD | ERIS | Rebuild 3-winding transformer 646263 S1263 5 161 647111 W BROCK8 69 648263 S1263T19 13 1 | Current Study |  | (121.00, 121.00) | 3582378.4371 | 58.9692 | 6075000 | 0.053703
GEN-2024-038 | 02 NEBRASKA | TBD | ERIS | Rebuild line 647963 S963 8 69 647977 S977 8 69 1 | Current Study | 8.02 | (106.00, 106.00) | 3112455.2646 | 45.6573 | 6817000 | 0.029893
GEN-2024-038 | 02 NEBRASKA | TBD | ERIS | Rebuild line 533210 ENEMEHA3 115 533217 KELLY 3 115 1 | Current Study | 8.7 | (115.00, 115.00) | 2956268.6625 | 33.9801 | 8700000 | 0.022938
GEN-2024-038 | 02 NEBRASKA | TBD | ERIS | Rebuild line 647401 NCU903 8 69 647977 S977 8 69 1 | Current Study | 6.05 | (106.00, 106.00) | 2347924.4827 | 45.6573 | 5142500 | 0.029893
GEN-2024-038 | 02 NEBRASKA | TBD | NRIS | Rebuild line 647101 AUBRNT 8 69 647975 S975 8 69 1 | Current Study | 14.17 | (106.00, 106.00) | 1420668.5826 | 11.7952 | 12044500 | 0.0040303
GEN-2024-038 | 02 NEBRASKA | TBD | NRIS | Rebuild 3-winding transformer 640234 HUMBOLT5 161 647975 S975 8 69 648275 S975T4 9 13 1 | Current Study |  | (102.00, 102.00) | 716556.2405 | 11.7952 | 6075000 | 0.0040303
GEN-2024-038 | 02 NEBRASKA | TBD | NRIS | Rebuild line 647111 W BROCK8 69 647963 S963 8 69 1 | Current Study | 1.01 | (106.00, 106.00) | 621736.3221 | 72.4212 | 858500 | 0.028322
GEN-2024-038 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659202 LO.KVA2_-BE9 13 M2 | Current Study |  | (500.00, 617.00) | 574103.8947 | 2.2964 | 25000000 | 0.0084259
GEN-2024-038 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659201 LO.KU1A_-BE9 13 M2 | Current Study |  | (600.00, 637.40) | 566213.8775 | 2.2649 | 25000000 | 0.009553
GEN-2024-038 | 02 NEBRASKA | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 4050.1438 | 0.29349 | 1380000 | 0.03069
GEN-2024-039 | 02 NEBRASKA | TBD | ERIS | Rebuild line 532913 KELLY 5 161 532920 TECHILL5 161 1 | Current Study | 52.64 | (160.00, 160.00) | 34470638.7796 | 43.6558 | 78960000 | 0.079355
GEN-2024-039 | 02 NEBRASKA | TBD | NRIS | Rebuild line 645456 S3456 3 345 645458 S3458 3 345 1 | Current Study | 44.95 | (1793.00, 1793.00) | 8187112.0836 | 8.279 | 98890000 | 0.029231
GEN-2024-039 | 02 NEBRASKA | TBD | NRIS | Rebuild line 647101 AUBRNT 8 69 647975 S975 8 69 1 | Current Study | 14.17 | (106.00, 106.00) | 7348909.5296 | 61.0147 | 12044500 | 0.025017
GEN-2024-039 | 02 NEBRASKA | TBD | ERIS | Rebuild line 533210 ENEMEHA3 115 533212 KINGFISH3 115 1 | Current Study | 16.47 | (115.00, 115.00) | 7221027.0081 | 43.8435 | 16470000 | 0.035445
GEN-2024-039 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640140 COOPER 5 161 778110 G24-038-TAP 161 1 | Current Study | 11.26 | (446.00, 446.00) | 6230373.3202 | 36.8879 | 16890000 | 0.48421
GEN-2024-039 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 532913 KELLY 5 161 532942 KELLY 1 13 533217 KELLY 3 115 M2 | Current Study |  | (144.00, 144.00) | 5245728.2653 | 43.7144 | 12000000 | 0.067874
GEN-2024-039 | 02 NEBRASKA | TBD | ERIS | Rebuild line 646263 S1263 5 161 646280 S1280 5 161 1 | Current Study | 8 | (309.00, 309.00) | 5140524.4853 | 42.8377 | 12000000 | 0.18312
GEN-2024-039 | 02 NEBRASKA | TBD | ERIS | Rebuild line 533210 ENEMEHA3 115 533217 KELLY 3 115 1 | Current Study | 8.7 | (115.00, 115.00) | 3813835.2933 | 43.8372 | 8700000 | 0.03551
GEN-2024-039 | 02 NEBRASKA | TBD | NRIS | Rebuild 3-winding transformer 640234 HUMBOLT5 161 647975 S975 8 69 648275 S975T4 9 13 1 | Current Study |  | (102.00, 102.00) | 3706639.9927 | 61.0147 | 6075000 | 0.025017
GEN-2024-039 | 02 NEBRASKA | TBD | ERIS | Rebuild line 647963 S963 8 69 647977 S977 8 69 1 | Current Study | 8.02 | (106.00, 106.00) | 3080581.7383 | 45.1897 | 6817000 | 0.035504
GEN-2024-039 | 02 NEBRASKA | TBD | ERIS | Rebuild 3-winding transformer 646263 S1263 5 161 647111 W BROCK8 69 648263 S1263T19 13 1 | Current Study |  | (121.00, 121.00) | 2360612.1231 | 38.8578 | 6075000 | 0.042465
GEN-2024-039 | 02 NEBRASKA | TBD | ERIS | Rebuild line 647401 NCU903 8 69 647977 S977 8 69 1 | Current Study | 6.05 | (106.00, 106.00) | 2323880.239 | 45.1897 | 5142500 | 0.035504
GEN-2024-039 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659202 LO.KVA2_-BE9 13 M2 | Current Study |  | (500.00, 617.00) | 475969.5669 | 1.9039 | 25000000 | 0.0083828
GEN-2024-039 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659201 LO.KU1A_-BE9 13 M2 | Current Study |  | (600.00, 637.40) | 469428.2281 | 1.8777 | 25000000 | 0.009504
GEN-2024-039 | 02 NEBRASKA | TBD | NRIS | Rebuild line 647111 W BROCK8 69 647963 S963 8 69 1 | Current Study | 1.01 | (106.00, 106.00) | 236763.6779 | 27.5788 | 858500 | 0.012942
GEN-2024-039 | 02 NEBRASKA | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 3355.1473 | 0.24313 | 1380000 | 0.030508
GEN-2024-040 | 02 NEBRASKA | TBD | NRIS | Rebuild line 645456 S3456 3 345 645458 S3458 3 345 1 | Current Study | 44.95 | (1793.00, 1793.00) | 22347871.0635 | 22.5987 | 98890000 | 0.11464
GEN-2024-040 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659202 LO.KVA2_-BE9 13 M2 | Current Study |  | (500.00, 617.00) | 334672.2718 | 1.3387 | 25000000 | 0.0084688
GEN-2024-040 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659201 LO.KU1A_-BE9 13 M2 | Current Study |  | (600.00, 637.40) | 330072.8082 | 1.3203 | 25000000 | 0.0096015
GEN-2024-040 | 02 NEBRASKA | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 2455.9498 | 0.17797 | 1380000 | 0.032086
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 28073345.0053 | 2.2077 | 1271630000 | 0.18187
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 27825293.95 | 2.1652 | 1285130000 | 0.27294
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 21788193.4087 | 1.4385 | 1514620000 | 0.035389
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 11811721.0811 | 1.6297 | 724760000 | 0.15465
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 9884608.0221 | 0.92056 | 1073760000 | 0.063076
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 9074221.9472 | 1.9334 | 469340000 | 0.13208
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 8940332.9669 | 1.8516 | 482840000 | 0.18822
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 4538778.4416 | 0.48367 | 938400000 | 0.058087
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 4462157.6179 | 0.47551 | 938400000 | 0.032268
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 2914257.4886 | 3.4488 | 84500000 | 0.084711
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 2764863.1635 | 0.7544 | 366500000 | 0.019834
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1377132.3353 | 1.6297 | 84500000 | 0.15465
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 1371775.906 | 0.69331 | 197860000 | 0.027412
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1360698.3276 | 0.68545 | 198511000 | 0.029313
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 1267139.0818 | 1.4996 | 84500000 | 0.07626
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1135321.2474 | 0.90954 | 124824000 | 0.047603
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 1004375.9967 | 15.32 | 6556000 | 0.84641
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 999497.3432 | 0.60553 | 165062000 | 0.030479
GEN-2024-041 | 05 SOUTHWEST | TBD | NRIS | Add 16 MVAR switched shunt at UNDERWOOD 2 345 kV | Current Study |  |  | 844048.1215 | 15.9254 | 5300000 | 1
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 791579.2209 | 0.97141 | 81488000 | 0.0516
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 495430.4578 | 0.89719 | 55220000 | 0.03501
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 485431.1264 | 2.6098 | 18600000 | 0.21812
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 0.3 MVAR switched shunt at ROSVTAP2 69 kV | Current Study |  |  | 460000 | 33.3333 | 1380000 | 1
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 412414.3322 | 2.2173 | 18600000 | 0.17776
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 410444.1084 | 2.2067 | 18600000 | 0.18187
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 402467.8247 | 2.1638 | 18600000 | 0.27294
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 7 MVAR switched shunt at CL-AFTP4 138 kV | Current Study |  |  | 392212.1896 | 16.1238 | 2432500 | 1
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 0.7 MVAR switched shunt at GEN-2024-161 138 kV | Current Study |  |  | 360113.3704 | 14.8042 | 2432500 | 0.056211
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 359612.4946 | 1.9334 | 18600000 | 0.13208
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 0.9 MVAR switched shunt at GEN-2024-157 138 kV | Current Study |  |  | 311745.8951 | 12.8159 | 2432500 | 1
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 303132.088 | 1.6297 | 18600000 | 0.15465
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 292294.7982 | 1.5715 | 18600000 | 0.2205
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 292294.7982 | 1.5715 | 18600000 | 0.2205
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 267565.7243 | 1.4385 | 18600000 | 0.035389
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 18 MVAR switched shunt at FALCNRD4 138 kV | Current Study |  |  | 207712.2322 | 8.539 | 2432500 | 0.051143
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 180680.9306 | 0.9714 | 18600000 | 0.10325
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-161-TAP 138 kV | Current Study |  |  | 158179.771 | 6.5028 | 2432500 | 0.056211
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 148031.115 | 0.79587 | 18600000 | 0.12259
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 0.7 MVAR switched shunt at ROSEVLT2 69 kV | Current Study |  |  | 117838.7998 | 8.539 | 1380000 | 0.051143
GEN-2024-041 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 106880.4456 | 0.5905 | 18100000 | 0.0072373
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 98934.6857 | 0.6623 | 14938000 | 0.056434
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 97511.7148 | 0.60222 | 16192000 | 0.054019
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 95775.1944 | 0.6623 | 14460953.1406 | 0.056434
GEN-2024-041 | 05 SOUTHWEST | TBD | NRIS | Add 0.09 MVAR switched shunt at GRAY CO3 115 kV | Current Study |  |  | 63608.6488 | 2.875 | 2212500 | 0.041757
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 58242.0238 | 0.48535 | 12000000 | 0.054019
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 36331.0508 | 1.6421 | 2212500 | 0.054019
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 0.5 MVAR switched shunt at RKY_RDG4 138 kV | Current Study |  |  | 27567.6362 | 1.1333 | 2432500 | 0.056211
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 14013.1606 | 0.63336 | 2212500 | 0.054019
GEN-2024-041 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 10821.056 | 0.78413 | 1380000 | 0.039708
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 9936.6557 | 0.60222 | 1650000 | 0.054019
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 8781.6427 | 0.16569 | 5300000 | 0.018983
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 7039.3995 | 0.31816 | 2212500 | 0.026432
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 5940.6456 | 0.43048 | 1380000 | 0.054019
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 4467.1161 | 0.3237 | 1380000 | 0.026432
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 1218.3958 | 0.08829 | 1380000 | 0.00050534
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 217.2475 | 0.015743 | 1380000 | 0.0011158
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 194.1994 | 0.014072 | 1380000 | 0.0011742
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 28073345.0053 | 2.2077 | 1271630000 | 0.18187
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 27825293.95 | 2.1652 | 1285130000 | 0.27294
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 21788193.4087 | 1.4385 | 1514620000 | 0.035389
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 11811721.0811 | 1.6297 | 724760000 | 0.15465
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 9884608.0221 | 0.92056 | 1073760000 | 0.063076
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 9074221.9472 | 1.9334 | 469340000 | 0.13208
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 8940332.9669 | 1.8516 | 482840000 | 0.18822
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 4538778.4416 | 0.48367 | 938400000 | 0.058087
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 4462157.6179 | 0.47551 | 938400000 | 0.032268
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 2914257.4886 | 3.4488 | 84500000 | 0.084711
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 2764863.1635 | 0.7544 | 366500000 | 0.019834
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1377132.3353 | 1.6297 | 84500000 | 0.15465
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 1371775.906 | 0.69331 | 197860000 | 0.027412
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1360698.3276 | 0.68545 | 198511000 | 0.029313
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 1267139.0818 | 1.4996 | 84500000 | 0.07626
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1135321.2474 | 0.90954 | 124824000 | 0.047603
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 1004375.9967 | 15.32 | 6556000 | 0.84641
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 999497.3432 | 0.60553 | 165062000 | 0.030479
GEN-2024-042 | 05 SOUTHWEST | TBD | NRIS | Add 16 MVAR switched shunt at UNDERWOOD 2 345 kV | Current Study |  |  | 844048.1215 | 15.9254 | 5300000 | 1
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 791579.2209 | 0.97141 | 81488000 | 0.0516
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 495430.4578 | 0.89719 | 55220000 | 0.03501
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 485431.1264 | 2.6098 | 18600000 | 0.21812
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 0.3 MVAR switched shunt at ROSVTAP2 69 kV | Current Study |  |  | 460000 | 33.3333 | 1380000 | 1
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 412414.3322 | 2.2173 | 18600000 | 0.17776
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 410444.1084 | 2.2067 | 18600000 | 0.18187
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 402467.8247 | 2.1638 | 18600000 | 0.27294
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 7 MVAR switched shunt at CL-AFTP4 138 kV | Current Study |  |  | 392212.1896 | 16.1238 | 2432500 | 1
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 0.7 MVAR switched shunt at GEN-2024-161 138 kV | Current Study |  |  | 360113.3704 | 14.8042 | 2432500 | 0.056211
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 359612.4946 | 1.9334 | 18600000 | 0.13208
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 303132.088 | 1.6297 | 18600000 | 0.15465
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 292294.7982 | 1.5715 | 18600000 | 0.2205
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 292294.7982 | 1.5715 | 18600000 | 0.2205
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 267565.7243 | 1.4385 | 18600000 | 0.035389
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 18 MVAR switched shunt at FALCNRD4 138 kV | Current Study |  |  | 207712.2322 | 8.539 | 2432500 | 0.051143
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 180680.9306 | 0.9714 | 18600000 | 0.10325
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-161-TAP 138 kV | Current Study |  |  | 158179.771 | 6.5028 | 2432500 | 0.056211
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 148031.115 | 0.79587 | 18600000 | 0.12259
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 0.7 MVAR switched shunt at ROSEVLT2 69 kV | Current Study |  |  | 117838.7998 | 8.539 | 1380000 | 0.051143
GEN-2024-042 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 106880.4456 | 0.5905 | 18100000 | 0.0072373
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 98934.6857 | 0.6623 | 14938000 | 0.056434
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 97511.7148 | 0.60222 | 16192000 | 0.054019
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 95775.1944 | 0.6623 | 14460953.1406 | 0.056434
GEN-2024-042 | 05 SOUTHWEST | TBD | NRIS | Add 0.09 MVAR switched shunt at GRAY CO3 115 kV | Current Study |  |  | 63608.6488 | 2.875 | 2212500 | 0.041757
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 58242.0238 | 0.48535 | 12000000 | 0.054019
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 36331.0508 | 1.6421 | 2212500 | 0.054019
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 0.5 MVAR switched shunt at RKY_RDG4 138 kV | Current Study |  |  | 27567.6362 | 1.1333 | 2432500 | 0.056211
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 14013.1606 | 0.63336 | 2212500 | 0.054019
GEN-2024-042 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 10821.056 | 0.78413 | 1380000 | 0.039708
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 9936.6557 | 0.60222 | 1650000 | 0.054019
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 8781.6427 | 0.16569 | 5300000 | 0.018983
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 7039.3995 | 0.31816 | 2212500 | 0.026432
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 5940.6456 | 0.43048 | 1380000 | 0.054019
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 4467.1161 | 0.3237 | 1380000 | 0.026432
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 1218.3958 | 0.08829 | 1380000 | 0.00050534
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 217.2475 | 0.015743 | 1380000 | 0.0011158
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 194.1994 | 0.014072 | 1380000 | 0.0011742
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 24899390.5826 | 2.3189 | 1073760000 | 0.15889
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 22522583.187 | 1.7526 | 1285130000 | 0.22092
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 21996820.4562 | 1.7298 | 1271630000 | 0.1425
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 19553796.1351 | 1.291 | 1514620000 | 0.03176
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 17464302.1573 | 1.8611 | 938400000 | 0.12629
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 15343864.605 | 1.6351 | 938400000 | 0.19637
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 12952353.352 | 1.7871 | 724760000 | 0.16958
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 9648165.9347 | 2.6325 | 366500000 | 0.069212
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 7650166.5179 | 1.5844 | 482840000 | 0.16106
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 7445171.7801 | 1.5863 | 469340000 | 0.10837
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 2059314.0475 | 2.4371 | 84500000 | 0.05986
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 1650681.0471 | 0.83427 | 197860000 | 0.032985
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 1525896.1081 | 1.8058 | 84500000 | 0.091833
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1510119.0163 | 1.7871 | 84500000 | 0.16958
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1452494.0504 | 0.73169 | 198511000 | 0.03129
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1284193.3824 | 1.0288 | 124824000 | 0.053846
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 1197598.7763 | 0.72554 | 165062000 | 0.03652
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 897461.9547 | 1.1013 | 81488000 | 0.058502
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 666310.7891 | 1.2066 | 55220000 | 0.047085
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 629767.2892 | 1.4487 | 43472000 | 0.035321
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 547723.483 | 2.9447 | 18600000 | 0.31298
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 397222.0461 | 2.1356 | 18600000 | 0.32896
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 389174.1203 | 1.4686 | 26500000 | 0.018465
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 388441.5533 | 2.0884 | 18600000 | 0.16743
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 343341.2776 | 1.8459 | 18600000 | 0.15427
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 332404.8959 | 1.7871 | 18600000 | 0.16958
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 325768.8878 | 1.7514 | 18600000 | 0.22092
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 321602.7644 | 1.729 | 18600000 | 0.1425
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 295053.0428 | 1.5863 | 18600000 | 0.10837
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 276907.7595 | 1.1076 | 25000000 | 0.013098
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 276907.7595 | 1.1076 | 25000000 | 0.01503
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 260314.9981 | 1.3995 | 18600000 | 0.19637
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 260314.9981 | 1.3995 | 18600000 | 0.19637
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 240126.6378 | 1.291 | 18600000 | 0.03176
GEN-2024-043 | 05 SOUTHWEST | TBD | NRIS | Add 0.09 MVAR switched shunt at GRAY CO3 115 kV | Current Study |  |  | 230546.6179 | 10.4202 | 2212500 | 0.15135
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 18 MVAR switched shunt at FALCNRD4 138 kV | Current Study |  |  | 220318.181 | 9.0573 | 2432500 | 0.054247
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 0.7 MVAR switched shunt at GEN-2024-161 138 kV | Current Study |  |  | 209554.5579 | 8.6148 | 2432500 | 0.03271
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 0.7 MVAR switched shunt at ROSEVLT2 69 kV | Current Study |  |  | 124990.3761 | 9.0573 | 1380000 | 0.054247
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 116850.999 | 0.72166 | 16192000 | 0.064732
GEN-2024-043 | 05 SOUTHWEST | TBD | NRIS | Add 16 MVAR switched shunt at UNDERWOOD 2 345 kV | Current Study |  |  | 115538.2625 | 2.18 | 5300000 | 0.13689
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 104963.5021 | 0.70266 | 14938000 | 0.059873
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 101611.4798 | 0.70266 | 14460953.1406 | 0.059873
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-161-TAP 138 kV | Current Study |  |  | 92046.8239 | 3.784 | 2432500 | 0.03271
GEN-2024-043 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 85771.631 | 0.47388 | 18100000 | 0.0058079
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | Current Study | 0.78 | (598.00, 598.00) | 85132.5476 | 1.6087 | 5292000 | 0.018179
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | Current Study | 0.2 | (598.00, 598.00) | 72069.8816 | 1.6087 | 4480000 | 0.018179
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 69793.0357 | 0.58161 | 12000000 | 0.064732
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 55871.8146 | 0.85222 | 6556000 | 0.047085
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 43536.5078 | 1.9678 | 2212500 | 0.064732
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 16792.3598 | 0.75898 | 2212500 | 0.064732
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 0.5 MVAR switched shunt at RKY_RDG4 138 kV | Current Study |  |  | 16041.9587 | 0.65948 | 2432500 | 0.03271
GEN-2024-043 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 12672.7281 | 0.91831 | 1380000 | 0.046502
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 11907.3708 | 0.72166 | 1650000 | 0.064732
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 9281.7098 | 0.17513 | 5300000 | 0.020063
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 7866.4135 | 0.35554 | 2212500 | 0.029537
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 7118.8407 | 0.51586 | 1380000 | 0.064732
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 4991.929 | 0.36173 | 1380000 | 0.029537
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 2597.481 | 0.18822 | 1380000 | 0.013341
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 990.6523 | 0.071786 | 1380000 | 0.00041088
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 219.3 | 0.015891 | 1380000 | 0.001326
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508813 PLAINDL2 69 778290 G24-044-TAP 69 1 | Current Study | 9.39 | (69.00, 69.00) | 3394134.8968 | 42.525 | 7981500 | 0.30601
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508803 GILLIAM2 69 508815 SUPEROR2 69 1 | Current Study | 6 | (69.00, 69.00) | 2499576.7677 | 49.0113 | 5100000 | 0.23149
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508812 OILCITY2 69 508815 SUPEROR2 69 1 | Current Study | 4.66 | (106.00, 106.00) | 1010119.0382 | 25.5016 | 3961000 | 0.32092
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508805 LIEBERM2 69 508812 OILCITY2 69 1 | Current Study | 3.4 | (106.00, 106.00) | 736996.7231 | 25.5016 | 2890000 | 0.32092
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508830 BALDWIN2 69 508842 WOODLWN2 69 1 | Current Study | 2.73 | (69.00, 69.00) | 606337.6883 | 26.1296 | 2320500 | 0.032559
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 302904.7396 | 0.20161 | 150244000 | 0.025382
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 185492.0435 | 0.19427 | 95480000 | 0.043647
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 174316.0695 | 0.079844 | 218320000 | 0.013687
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 164549.3935 | 0.19427 | 84700000 | 0.043647
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 153551.9801 | 0.10678 | 143796000 | 0.029631
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 131199.8685 | 0.13064 | 100427000 | 0.0093212
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 123485.8645 | 0.062206 | 198511000 | 0.018473
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 121325.4301 | 0.25818 | 46992000 | 0.058093
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 111306.1682 | 0.17598 | 63250000 | 0.053086
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 108832.2688 | 0.096488 | 112794000 | 0.045658
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 106385.1978 | 0.085228 | 124824000 | 0.030977
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | Current Study | 10.42 | (395.00, 395.00) | 104753.1732 | 0.83776 | 12504000 | 0.018796
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 91590.1266 | 0.097453 | 93984000 | 0.033595
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 507454 TURK 4 138 507456 TURK 3 115 507458 TURK1 1 13 M2 | Current Study |  | (257.00, 257.00) | 87824.2694 | 0.84446 | 10400000 | 0.017224
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 82531.6114 | 0.05 | 165062000 | 0.017478
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 79351.6379 | 0.66126 | 12000000 | 0.054642
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508089 WATLANT2 69 779100 G24-071-TAP 69 1 | Current Study | 1.78 | (106.00, 106.00) | 73526.1879 | 4.8596 | 1513000 | 0.11095
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 73481.8926 | 0.21874 | 33594000 | 0.049584
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 70514.8159 | 0.086534 | 81488000 | 0.031921
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at PHILL 7 345 kV | Current Study |  |  | 59925.2836 | 1.1307 | 5300000 | 0.028012
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 55901.8215 | 0.22096 | 25300000 | 0.025143
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 48100.4065 | 0.18735 | 25674000 | 0.036539
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 39148.5913 | 0.32624 | 12000000 | 0.06684
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 38191.6423 | 0.57866 | 6600000 | 0.06684
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 34386.0245 | 0.19201 | 17908000 | 0.038068
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 32762.9831 | 0.27302 | 12000000 | 0.06684
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 31967.4033 | 0.60316 | 5300000 | 0.054642
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 30002.5098 | 0.25002 | 12000000 | 0.06684
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 26893.9137 | 0.22412 | 12000000 | 0.043647
GEN-2024-044 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 25582.501 | 0.14134 | 18100000 | 0.01203
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 24214.5427 | 0.20179 | 12000000 | 0.037936
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 24091.546 | 0.20076 | 12000000 | 0.015061
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 23197.3256 | 0.19331 | 12000000 | 0.054642
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 22903.8454 | 0.34703 | 6600000 | 0.06684
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 504122 MCNAB 3 115 507456 TURK 3 115 1 | Current Study | 2.65 | (394.00, 394.00) | 22378.2994 | 0.84446 | 2650000 | 0.034447
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 21713.3872 | 0.18094 | 12000000 | 0.02369
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 19920.3602 | 0.166 | 12000000 | 0.030228
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 19920.3602 | 0.166 | 12000000 | 0.030228
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 19912.377 | 0.16594 | 12000000 | 0.031432
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 19365.1685 | 0.12865 | 15053000 | 0.0094528
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 19357.56 | 0.16131 | 12000000 | 0.037936
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 19124.7879 | 0.58846 | 3250000 | 0.06684
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 19124.7879 | 0.58846 | 3250000 | 0.06684
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 18974.8554 | 0.15812 | 12000000 | 0.02963
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 18733.0019 | 0.15611 | 12000000 | 0.02369
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 18571.281 | 0.15476 | 12000000 | 0.030228
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 18324.7909 | 0.34575 | 5300000 | 0.054642
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | Current Study | 1.8 | (395.00, 395.00) | 18095.5577 | 0.83776 | 2160000 | 0.018796
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 12697.2644 | 0.19238 | 6600000 | 0.043647
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 12376.4462 | 0.10614 | 11660000 | 0.033595
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 11844.661 | 0.22348 | 5300000 | 0.06684
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 11574.9272 | 0.35615 | 3250000 | 0.06684
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 11333.8655 | 0.17173 | 6600000 | 0.031432
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 11333.8655 | 0.17173 | 6600000 | 0.031432
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 11273.9558 | 0.34689 | 3250000 | 0.06684
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 10620.3397 | 0.32678 | 3250000 | 0.06684
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 10418.63 | 0.19658 | 5300000 | 0.033595
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 10129.5334 | 0.19112 | 5300000 | 0.050916
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 9467.49 | 0.17863 | 5300000 | 0.031432
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 9191.8455 | 0.061533 | 14938000 | 0.036411
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 9125.4384 | 0.66126 | 1380000 | 0.054642
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 8898.3028 | 0.061533 | 14460953.1406 | 0.036411
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 8667.771 | 0.2667 | 3250000 | 0.06684
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 8146.3192 | 0.050311 | 16192000 | 0.031339
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 7668.0398 | 0.25818 | 2970000 | 0.058093
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV | Current Study |  |  | 7552.6181 | 0.54729 | 1380000 | 0.04009
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 7257.7659 | 0.52593 | 1380000 | 0.06684
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 7022.5286 | 0.21608 | 3250000 | 0.031432
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 6838.4164 | 0.19427 | 3520000 | 0.043647
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 6782.5425 | 0.12797 | 5300000 | 0.033595
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 6313.8795 | 0.19427 | 3250000 | 0.043647
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 6014.2857 | 0.18505 | 3250000 | 0.031432
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 5961.2325 | 0.18342 | 3250000 | 0.031432
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 5960.8634 | 0.18341 | 3250000 | 0.031432
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 5805.5363 | 0.17863 | 3250000 | 0.031432
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 5680.0295 | 0.25818 | 2200000 | 0.058093
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 4473.9189 | 0.20221 | 2212500 | 0.056773
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 4338.5424 | 0.13349 | 3250000 | 0.033595
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 4337.6787 | 0.19605 | 2212500 | 0.056773
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 4291.5154 | 0.080972 | 5300000 | 0.0033439
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 3885.9545 | 0.28159 | 1380000 | 0.054642
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 3412.4179 | 0.14837 | 2300000 | 0.058093
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 3264.0399 | 0.13418 | 2432500 | 0.033595
GEN-2024-044 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 3229.2828 | 0.06093 | 5300000 | 0.057796
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 3218.7901 | 0.13232 | 2432500 | 0.033595
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 2931.1861 | 0.1205 | 2432500 | 0.030363
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 2710.8561 | 0.19644 | 1380000 | 0.031432
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 2707.3997 | 0.19619 | 1380000 | 0.053097
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 1543.0224 | 0.069741 | 2212500 | 0.041306
GEN-2024-044 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 830.1276 | 0.050311 | 1650000 | 0.031339
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 36223935.0909 | 2.3916 | 1514620000 | 0.042635
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523095 HITCHLAND 6 230 778320 G24-045-TAP 230 1 | Current Study | 37.8 | (772.00, 772.00) | 24621028.0202 | 34.2816 | 71820000 | 0.51403
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523309 MOORE_CNTY 6 230 778320 G24-045-TAP 230 1 | Current Study | 24.89 | (772.00, 772.00) | 23645500 | 50 | 47291000 | 0.48597
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 22412617.8158 | 2.3884 | 938400000 | 0.11745
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 21779677.5682 | 1.6947 | 1285130000 | 0.15481
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 21509371.2673 | 1.6915 | 1271630000 | 0.10097
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 20490054.7975 | 2.1835 | 938400000 | 0.19002
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add line 523869 CHAN+TASCOS6 230 523959 POTTER_CO 6 230 P2 | Current Study | 41.65 | (496.00, 546.00) | 16589846.3669 | 14.9022 | 111325000 | 0.083193
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 16010997.6333 | 2.2091 | 724760000 | 0.1519
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add line 523221 XIT_INTG 6 230 523869 CHAN+TASCOS6 230 P2 | Current Study | 32.28 | (495.00, 545.00) | 13095637.3066 | 14.8983 | 87900000 | 0.083201
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 11798010.5945 | 1.0988 | 1073760000 | 0.054555
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 9771460.1339 | 2.0237 | 482840000 | 0.14907
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 9185372.0879 | 1.9571 | 469340000 | 0.096883
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523094 HITCHLD_TR21 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2 | Current Study |  | (560.00, 644.00) | 5207116.6631 | 20.8285 | 25000000 | 0.1339
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523091 HITCHLD_TR01 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2 | Current Study |  | (560.00, 644.00) | 5207116.6631 | 20.8285 | 25000000 | 0.11648
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 5003209.1979 | 2.5287 | 197860000 | 0.072447
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 3534390.7851 | 2.1413 | 165062000 | 0.078101
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 2354802.0265 | 1.1862 | 198511000 | 0.036759
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1866727.3305 | 2.2091 | 84500000 | 0.1519
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 1843918.1533 | 2.1822 | 84500000 | 0.080414
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1648542.0851 | 1.3207 | 124824000 | 0.050089
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 1400954.5151 | 3.2227 | 43472000 | 0.056938
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 1127759.6935 | 1.384 | 81488000 | 0.053272
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 588157.4343 | 1.0651 | 55220000 | 0.030117
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 444841.0774 | 2.3916 | 18600000 | 0.042635
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 411099.048 | 1.6444 | 25000000 | 0.01617
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 411099.048 | 1.6444 | 25000000 | 0.014091
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 410900.9272 | 2.2091 | 18600000 | 0.1519
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 376029.2882 | 2.0217 | 18600000 | 0.11745
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 366937.3001 | 2.2662 | 16192000 | 0.1473
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 364017.3879 | 1.9571 | 18600000 | 0.096883
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 347622.2395 | 1.8689 | 18600000 | 0.19002
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 347622.2395 | 1.8689 | 18600000 | 0.19002
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 316651.5494 | 1.7024 | 18600000 | 0.19002
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 315023.4269 | 1.6937 | 18600000 | 0.15481
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 314476.0523 | 1.6907 | 18600000 | 0.10097
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 310110.7951 | 1.6673 | 18600000 | 0.10097
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 283634.6476 | 1.5249 | 18600000 | 0.11745
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 272204.3617 | 0.32214 | 84500000 | 0.0057336
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 173843.54 | 1.1638 | 14938000 | 0.071858
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 168291.8252 | 1.1638 | 14460953.1406 | 0.071858
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 136714.0415 | 6.1792 | 2212500 | 0.1473
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 102674.9734 | 1.9373 | 5300000 | 0.16083
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 78011.4873 | 5.653 | 1380000 | 0.51403
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 75027.3092 | 0.62523 | 12000000 | 0.050425
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 52731.6382 | 2.3834 | 2212500 | 0.1473
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 49318.4617 | 0.75226 | 6556000 | 0.030117
GEN-2024-045 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 46653.154 | 3.3807 | 1380000 | 0.12405
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 37391.7086 | 2.2662 | 1650000 | 0.1473
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 36705.804 | 2.6598 | 1380000 | 0.16083
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 26082.2282 | 1.89 | 1380000 | 0.097076
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 18532.5112 | 0.83763 | 2212500 | 0.050425
GEN-2024-045 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 11760.5031 | 0.85221 | 1380000 | 0.050425
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 36223935.0909 | 2.3916 | 1514620000 | 0.042635
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523095 HITCHLAND 6 230 778320 G24-045-TAP 230 1 | Current Study | 37.8 | (772.00, 772.00) | 24621028.0202 | 34.2816 | 71820000 | 0.51403
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523309 MOORE_CNTY 6 230 778320 G24-045-TAP 230 1 | Current Study | 24.89 | (772.00, 772.00) | 23645500 | 50 | 47291000 | 0.48597
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 22412617.8158 | 2.3884 | 938400000 | 0.11745
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 21779677.5682 | 1.6947 | 1285130000 | 0.15481
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 21509371.2673 | 1.6915 | 1271630000 | 0.10097
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 20490054.7975 | 2.1835 | 938400000 | 0.19002
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add line 523869 CHAN+TASCOS6 230 523959 POTTER_CO 6 230 P2 | Current Study | 41.65 | (496.00, 546.00) | 16589846.3669 | 14.9022 | 111325000 | 0.083193
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 16010997.6333 | 2.2091 | 724760000 | 0.1519
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add line 523221 XIT_INTG 6 230 523869 CHAN+TASCOS6 230 P2 | Current Study | 32.28 | (495.00, 545.00) | 13095637.3066 | 14.8983 | 87900000 | 0.083201
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 11798010.5945 | 1.0988 | 1073760000 | 0.054555
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 9771460.1339 | 2.0237 | 482840000 | 0.14907
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 9185372.0879 | 1.9571 | 469340000 | 0.096883
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523091 HITCHLD_TR01 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2 | Current Study |  | (560.00, 644.00) | 5207116.6631 | 20.8285 | 25000000 | 0.11648
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523094 HITCHLD_TR21 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2 | Current Study |  | (560.00, 644.00) | 5207116.6631 | 20.8285 | 25000000 | 0.1339
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 5003209.1979 | 2.5287 | 197860000 | 0.072447
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 3534390.7851 | 2.1413 | 165062000 | 0.078101
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 2354802.0265 | 1.1862 | 198511000 | 0.036759
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1866727.3305 | 2.2091 | 84500000 | 0.1519
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 1843918.1533 | 2.1822 | 84500000 | 0.080414
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1648542.0851 | 1.3207 | 124824000 | 0.050089
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 1400954.5151 | 3.2227 | 43472000 | 0.056938
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 1127759.6935 | 1.384 | 81488000 | 0.053272
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 588157.4343 | 1.0651 | 55220000 | 0.030117
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 444841.0774 | 2.3916 | 18600000 | 0.042635
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 411099.048 | 1.6444 | 25000000 | 0.014091
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 411099.048 | 1.6444 | 25000000 | 0.01617
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 410900.9272 | 2.2091 | 18600000 | 0.1519
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 376029.2882 | 2.0217 | 18600000 | 0.11745
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 366937.3001 | 2.2662 | 16192000 | 0.1473
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 364017.3879 | 1.9571 | 18600000 | 0.096883
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 347622.2395 | 1.8689 | 18600000 | 0.19002
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 347622.2395 | 1.8689 | 18600000 | 0.19002
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 316651.5494 | 1.7024 | 18600000 | 0.19002
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 315023.4269 | 1.6937 | 18600000 | 0.15481
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 314476.0523 | 1.6907 | 18600000 | 0.10097
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 310110.7951 | 1.6673 | 18600000 | 0.10097
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 283634.6476 | 1.5249 | 18600000 | 0.11745
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 272204.3617 | 0.32214 | 84500000 | 0.0057336
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 173843.54 | 1.1638 | 14938000 | 0.071858
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 168291.8252 | 1.1638 | 14460953.1406 | 0.071858
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 136714.0415 | 6.1792 | 2212500 | 0.1473
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 102674.9734 | 1.9373 | 5300000 | 0.16083
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 78011.4873 | 5.653 | 1380000 | 0.51403
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 75027.3092 | 0.62523 | 12000000 | 0.050425
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 52731.6382 | 2.3834 | 2212500 | 0.1473
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 49318.4617 | 0.75226 | 6556000 | 0.030117
GEN-2024-046 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 46653.154 | 3.3807 | 1380000 | 0.12405
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 37391.7086 | 2.2662 | 1650000 | 0.1473
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 36705.804 | 2.6598 | 1380000 | 0.16083
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 26082.2282 | 1.89 | 1380000 | 0.097076
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 18532.5112 | 0.83763 | 2212500 | 0.050425
GEN-2024-046 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 11760.5031 | 0.85221 | 1380000 | 0.050425
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525481 PLANT_X 6 230 525520 OLSON 6 230 1 | Current Study | 34.94 | (519.00, 519.00) | 66386000 | 100 | 66386000 | 0.49823
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 35605829.2745 | 2.3508 | 1514620000 | 0.048194
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 27849721.0246 | 2.1671 | 1285130000 | 0.22765
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 27260921.8805 | 2.1438 | 1271630000 | 0.14717
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 24917889.6109 | 2.6554 | 938400000 | 0.15016
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 21898196.0723 | 2.3336 | 938400000 | 0.23354
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 16850428.6228 | 2.325 | 724760000 | 0.18385
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 16165159.3196 | 1.5055 | 1073760000 | 0.085961
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524623 DEAFSMITH 6 230 525520 OLSON 6 230 1 | Current Study | 11 | (519.00, 519.00) | 15476146.0993 | 74.0485 | 20900000 | 0.50177
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 11686647.1916 | 3.1887 | 366500000 | 0.069863
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 10861478.4602 | 2.2495 | 482840000 | 0.19056
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 10417956.0925 | 2.2197 | 469340000 | 0.12637
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Current Study | 54.58 | (637.00, 637.00) | 9609965.7145 | 9.2669 | 103702000 | 0.071729
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1 | Current Study | 18.95 | (901.00, 901.00) | 4911031.1381 | 13.6399 | 36005000 | 0.26559
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Rebuild 3-winding transformer and add 3-winding transformer 524263 BSHLND_TR1 1 13 524266 BUSHLAND 3 115 524267 BUSHLAND 6 230 1 | Current Study |  | (323.00, 323.00) | 3612686.7557 | 16.4963 | 21900000 | 0.027952
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 2204818.3195 | 1.1143 | 197860000 | 0.036715
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 2008804.2043 | 2.3773 | 84500000 | 0.10075
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1964596.8578 | 2.325 | 84500000 | 0.18385
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1878005.2399 | 1.5045 | 124824000 | 0.06562
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1820972.3342 | 0.91732 | 198511000 | 0.03269
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 1797971.0694 | 3.256 | 55220000 | 0.10588
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523095 HITCHLAND 6 230 778320 G24-045-TAP 230 1 | Current Study | 37.8 | (772.00, 772.00) | 1578862.6705 | 2.1984 | 71820000 | 0.037907
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 1575609.6112 | 0.95456 | 165062000 | 0.04004
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1531046.6881 | 1.8119 | 84500000 | 0.037087
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 1298488.1049 | 1.5935 | 81488000 | 0.070537
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 1148524.9298 | 4.5941 | 25000000 | 0.051951
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 1148524.9298 | 4.5941 | 25000000 | 0.045273
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 524243 OUTPOST 3 115 524266 BUSHLAND 3 115 M2 | Current Study | 1.93 | (598.00, 598.00) | 1138573.6981 | 16.4963 | 6902000 | 0.027952
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 1074674.6657 | 2.4721 | 43472000 | 0.050229
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523094 HITCHLD_TR21 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2 | Current Study |  | (560.00, 644.00) | 592858.9105 | 2.3714 | 25000000 | 0.017532
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523091 HITCHLD_TR01 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2 | Current Study |  | (560.00, 644.00) | 592858.9105 | 2.3714 | 25000000 | 0.015251
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524243 OUTPOST 3 115 524560 ARNOT 3 115 1 | Current Study | 3.43 | (598.00, 598.00) | 565822.6289 | 16.4963 | 3430000 | 0.055904
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524300 HILLSIDE 3 115 524560 ARNOT 3 115 1 | Current Study | 3.17 | (598.00, 598.00) | 522932.2838 | 16.4963 | 3170000 | 0.055904
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 437250.5477 | 2.3508 | 18600000 | 0.048194
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 432443.8054 | 2.325 | 18600000 | 0.18385
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 418061.6638 | 2.2476 | 18600000 | 0.15016
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 412864.8385 | 2.2197 | 18600000 | 0.12637
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 402821.1404 | 2.1657 | 18600000 | 0.22765
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 398566.1407 | 2.1428 | 18600000 | 0.14717
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 393033.625 | 2.1131 | 18600000 | 0.14717
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 371511.9376 | 1.9974 | 18600000 | 0.23354
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 371511.9376 | 1.9974 | 18600000 | 0.23354
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524300 HILLSIDE 3 115 524306 COULTER 3 115 1 | Current Study | 2.11 | (598.00, 598.00) | 348071.6463 | 16.4963 | 2110000 | 0.055904
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 338412.8439 | 1.8194 | 18600000 | 0.23354
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 315339.194 | 1.6954 | 18600000 | 0.15016
GEN-2024-050 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 179674.9952 | 0.99268 | 18100000 | 0.010139
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 156733.7971 | 0.96797 | 16192000 | 0.072355
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 150764.34 | 2.2996 | 6556000 | 0.10588
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524281 34TH_ST_TP 3 115 524325 WESTERN 3 115 1 | Current Study | 1.11 | (217.00, 217.00) | 147857.2531 | 13.3205 | 1110000 | 0.02158
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 131776.1628 | 0.88215 | 14938000 | 0.06264
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524281 34TH_ST_TP 3 115 524306 COULTER 3 115 1 | Current Study | 0.96 | (217.00, 217.00) | 127876.5432 | 13.3205 | 960000 | 0.02158
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 127567.8749 | 0.88215 | 14460953.1406 | 0.06264
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 111856.3118 | 2.1105 | 5300000 | 0.20149
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 58396.1532 | 2.6394 | 2212500 | 0.072355
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 42606.8964 | 0.35506 | 12000000 | 0.032931
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 39988.0878 | 2.8977 | 1380000 | 0.20149
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 33826.9274 | 2.4512 | 1380000 | 0.14479
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 30528.7841 | 2.2122 | 1380000 | 0.010552
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 26590.6976 | 1.9269 | 1380000 | 0.20149
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 22523.8373 | 1.018 | 2212500 | 0.072355
GEN-2024-050 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 18498.3898 | 1.3405 | 1380000 | 0.056566
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 15971.5146 | 0.96797 | 1650000 | 0.072355
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 10524.3383 | 0.47568 | 2212500 | 0.032931
GEN-2024-050 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 6678.6153 | 0.48396 | 1380000 | 0.032931
GEN-2024-051 | 02 NEBRASKA | TBD | NRIS | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | Current Study | 17.69 | (160.00, 160.00) | 6762519.2788 | 25.4853 | 26535000 | 0.12657
GEN-2024-051 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2 | Current Study |  | (110.00, 120.00) | 3058233.7044 | 25.4853 | 12000000 | 0.063286
GEN-2024-051 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659202 LO.KVA2_-BE9 13 M2 | Current Study |  | (500.00, 617.00) | 306386.9811 | 1.2255 | 25000000 | 0.0079354
GEN-2024-051 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659201 LO.KU1A_-BE9 13 M2 | Current Study |  | (600.00, 637.40) | 302176.2475 | 1.2087 | 25000000 | 0.0089968
GEN-2024-051 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2 | Current Study |  | (336.00, 336.00) | 54517.9561 | 0.32451 | 16800000 | 0.0002773
GEN-2024-051 | 02 NEBRASKA | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 3140.4223 | 0.22757 | 1380000 | 0.041994
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 521098 WSBNKTP4 138 778530 G24-052-TAP 138 1 | Current Study | 9.45 | (472.00, 472.00) | 1991166.0081 | 17.5588 | 11340000 | 0.65991
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505600 TUPELO 4 138 505602 S BROWN4 138 1 | Current Study | 36.9 | (281.00, 281.00) | 1364942.9487 | 3.0825 | 44280000 | 0.094881
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520918 FROGVIL4 138 520948 HUGO PP4 138 1 | Current Study | 6.55 | (717.00, 717.00) | 1264692.0733 | 16.0902 | 7860000 | 0.65991
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520918 FROGVIL4 138 773820 G23-092-TAP 138 1 | Current Study | 6.3 | (717.00, 717.00) | 1216421.3835 | 16.0902 | 7560000 | 0.65991
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1 | Current Study | 56.1 | (1793.00, 1793.00) | 1197282.28 | 0.97009 | 123420000 | 0.066255
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 521098 WSBNKTP4 138 773820 G23-092-TAP 138 1 | Current Study | 3.4 | (472.00, 472.00) | 716398.3521 | 17.5588 | 4080000 | 0.65991
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515150 CANEYCK4 138 515151 LTLCITY4 138 1 | Current Study | 11.79 | (265.00, 265.00) | 638630.0411 | 4.5139 | 14148000 | 0.11595
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1 | Current Study | 30.63 | (1793.00, 1793.00) | 630996.4632 | 0.93639 | 67386000 | 0.073009
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505598 ALLEN 4 138 505600 TUPELO 4 138 1 | Current Study | 19.4 | (211.00, 211.00) | 604137.6589 | 2.5951 | 23280000 | 0.033638
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 521049 SCLMNJC4 138 784980 G24-267-TAP 138 1 | Current Study | 6.96 | (472.00, 472.00) | 529010.264 | 6.3339 | 8352000 | 0.34009
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505596 EXPLOR 4 138 505598 ALLEN 4 138 1 | Current Study | 14.8 | (211.00, 211.00) | 459531.3836 | 2.5875 | 17760000 | 0.033428
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 419471.4195 | 0.37189 | 112794000 | 0.15084
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 417259.6439 | 0.35577 | 117282000 | 0.03565
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 410375.4971 | 0.27314 | 150244000 | 0.029475
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 1 | Current Study |  | (1868.00, 1868.00) | 348407.5418 | 0.56652 | 61500000 | 0.065705
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 2 | Current Study |  | (1868.00, 1868.00) | 348407.5418 | 0.56652 | 61500000 | 0.065705
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515151 LTLCITY4 138 515157 BROWN 4 138 1 | Current Study | 6.37 | (265.00, 265.00) | 345044.3903 | 4.5139 | 7644000 | 0.11595
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 776060 G23-204-TAP 345 1 | Current Study | 17.82 | (1793.00, 1793.00) | 327007.3873 | 0.83412 | 39204000 | 0.14962
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 300114.1367 | 0.47449 | 63250000 | 0.12269
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 252169.2674 | 0.28039 | 89936000 | 0.015596
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 243845.1323 | 0.11169 | 218320000 | 0.016412
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 241971.4552 | 0.25343 | 95480000 | 0.048803
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515044 SEMINOL4 138 515531 VANOSTP4 138 1 | Current Study | 21.55 | (395.00, 395.00) | 238171.0209 | 0.921 | 25860000 | 0.03635
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 231765.3652 | 0.41656 | 55638000 | 0.044738
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 229526.1055 | 0.22855 | 100427000 | 0.013977
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 214652.0974 | 0.25343 | 84700000 | 0.048803
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 205095.7805 | 0.14263 | 143796000 | 0.033923
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 521049 SCLMNJC4 138 769060 G22-104-TAP 138 1 | Current Study | 2.27 | (472.00, 472.00) | 195374.1243 | 7.1723 | 2724000 | 0.34009
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | Current Study | 7.74 | (1793.00, 1793.00) | 190867.4537 | 1.1209 | 17028000 | 0.14962
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 190751.8061 | 0.34585 | 55154000 | 0.029043
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 169699.3035 | 0.085486 | 198511000 | 0.02176
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515178 PARKLN 4 138 515977 LKKONWA4 138 1 | Current Study | 13.56 | (472.00, 472.00) | 169257.8971 | 1.0402 | 16272000 | 0.059916
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 168319.9969 | 0.37541 | 44836000 | 0.041969
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515117 ARBUCKL4 138 515531 VANOSTP4 138 1 | Current Study | 18.2 | (472.00, 472.00) | 164074.3499 | 0.75126 | 21840000 | 0.035275
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 764550 G20-087-TAP 345 1 | Current Study | 14.38 | (1793.00, 1793.00) | 155184.1302 | 0.49053 | 31636000 | 0.079657
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 152933.8885 | 0.077294 | 197860000 | 0.01819
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 148146.4895 | 0.11868 | 124824000 | 0.036974
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 137242.4665 | 0.29205 | 46992000 | 0.056326
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | Current Study | 13.16 | (395.00, 395.00) | 136241.7383 | 0.86273 | 15792000 | 0.040574
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505602 S BROWN4 138 769060 G22-104-TAP 138 1 | Current Study | 1.62 | (717.00, 717.00) | 132808.778 | 6.8317 | 1944000 | 0.34009
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | Current Study | 6.93 | (1793.00, 1793.00) | 127169.5395 | 0.83412 | 15246000 | 0.14962
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 126525.2621 | 0.13462 | 93984000 | 0.039779
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 507454 TURK 4 138 507456 TURK 3 115 507458 TURK1 1 13 M2 | Current Study |  | (257.00, 257.00) | 122791.7538 | 1.1807 | 10400000 | 0.020641
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | Current Study | 13.6 | (1793.00, 1793.00) | 114524.9528 | 0.38277 | 29920000 | 0.034417
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 110513.5802 | 0.066953 | 165062000 | 0.02006
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 110327.9117 | 0.42973 | 25674000 | 0.071837
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 103289.1404 | 0.30746 | 33594000 | 0.059741
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 98378.8468 | 0.12073 | 81488000 | 0.038173
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | Current Study | 8.91 | (2390.00, 2390.00) | 94896.1666 | 0.48411 | 19602000 | 0.079657
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 91305.2123 | 0.34585 | 26400000 | 0.029043
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 78464.3119 | 0.17089 | 45914000 | 0.041139
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 78356.9777 | 0.43755 | 17908000 | 0.074356
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 69951.7441 | 0.27649 | 25300000 | 0.026968
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 67012.7372 | 0.55844 | 12000000 | 0.039553
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | Current Study | 5.97 | (2390.00, 2390.00) | 63583.6268 | 0.48411 | 13134000 | 0.079657
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 | Current Study | 6.08 | (395.00, 395.00) | 62944.5113 | 0.86273 | 7296000 | 0.040574
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 47167.6607 | 0.08823 | 53460000 | 0.015165
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1 | Current Study | 11.3 | (1793.00, 1793.00) | 44781.9706 | 0.18014 | 24860000 | 0.026458
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 43706.5656 | 0.35476 | 12320000 | 0.036249
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 42822.6408 | 0.17089 | 25058000 | 0.041139
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 41138.687 | 0.34282 | 12000000 | 0.036249
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 41138.687 | 0.34282 | 12000000 | 0.036249
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 36677.5317 | 0.30565 | 12000000 | 0.036249
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 35082.6872 | 0.29236 | 12000000 | 0.048803
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 33914.2187 | 0.2253 | 15053000 | 0.01419
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 33315.6893 | 0.27763 | 12000000 | 0.044738
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 504122 MCNAB 3 115 507456 TURK 3 115 1 | Current Study | 2.65 | (394.00, 394.00) | 31288.2834 | 1.1807 | 2650000 | 0.041282
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 29569.8186 | 0.24642 | 12000000 | 0.027653
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 29303.2319 | 0.24419 | 12000000 | 0.059164
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 29105.0268 | 0.24254 | 12000000 | 0.015596
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 27869.2995 | 0.23224 | 12000000 | 0.036249
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 27869.2995 | 0.23224 | 12000000 | 0.036249
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 27369.4807 | 0.22808 | 12000000 | 0.040053
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 26996.5845 | 0.50937 | 5300000 | 0.039553
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 26700.4606 | 0.40455 | 6600000 | 0.040053
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 26635.5012 | 0.22196 | 12000000 | 0.035651
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 26633.1874 | 0.22194 | 12000000 | 0.044738
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 26430.7779 | 0.22026 | 12000000 | 0.036249
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 26069.6975 | 0.21725 | 12000000 | 0.035272
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 25981.8892 | 0.21652 | 12000000 | 0.036249
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 25557.4559 | 0.21298 | 12000000 | 0.048803
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 25511.0575 | 0.21259 | 12000000 | 0.027653
GEN-2024-052 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 24188.5783 | 0.13364 | 18100000 | 0.0097494
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 20170.8738 | 0.16809 | 12000000 | 0.035272
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 17207.802 | 0.32468 | 5300000 | 0.044738
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 17097.1824 | 0.14663 | 11660000 | 0.039779
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 16563.3816 | 0.25096 | 6600000 | 0.048803
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 16012.4882 | 0.24261 | 6600000 | 0.040053
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 15786.8322 | 0.29786 | 5300000 | 0.035651
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 15147.3341 | 0.2858 | 5300000 | 0.035651
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 14838.5321 | 0.22483 | 6600000 | 0.035272
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 14838.5321 | 0.22483 | 6600000 | 0.035272
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 14392.6128 | 0.27156 | 5300000 | 0.039779
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 13961.5138 | 0.21154 | 6600000 | 0.039779
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 13732.1184 | 0.2591 | 5300000 | 0.059164
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 13370.4815 | 0.4114 | 3250000 | 0.040053
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 13370.4815 | 0.4114 | 3250000 | 0.040053
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 12649.7895 | 0.084682 | 14938000 | 0.04295
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 12649.1218 | 0.3892 | 3250000 | 0.035272
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 12649.1218 | 0.3892 | 3250000 | 0.035272
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 12395.0345 | 0.23387 | 5300000 | 0.035272
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 12245.8169 | 0.084682 | 14460953.1406 | 0.04295
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 11425.626 | 0.49677 | 2300000 | 0.16672
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 10958.8823 | 0.067681 | 16192000 | 0.036136
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 10281.4889 | 0.31635 | 3250000 | 0.035272
GEN-2024-052 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 9600.1687 | 0.18114 | 5300000 | 0.14727
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 9369.6108 | 0.17679 | 5300000 | 0.039779
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 9226.606 | 0.17409 | 5300000 | 0.023582
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 9194.0403 | 0.28289 | 3250000 | 0.035272
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 8973.0098 | 0.65022 | 1380000 | 0.15084
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 8920.6066 | 0.25343 | 3520000 | 0.048803
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 8819.7245 | 0.36258 | 2432500 | 0.035651
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 8674.0323 | 0.29205 | 2970000 | 0.056326
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 8280.8145 | 0.15624 | 5300000 | 0.040053
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 8236.3565 | 0.25343 | 3250000 | 0.048803
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 8092.2388 | 0.24899 | 3250000 | 0.040053
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CHILD4WT 138 kV | Current Study |  |  | 7888.6246 | 0.3243 | 2432500 | 0.079657
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 7881.8242 | 0.24252 | 3250000 | 0.040053
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 7874.0277 | 0.24228 | 3250000 | 0.035272
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 7804.5694 | 0.24014 | 3250000 | 0.035272
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 7804.0861 | 0.24013 | 3250000 | 0.035272
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 7706.4648 | 0.55844 | 1380000 | 0.039553
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 7608.7677 | 0.34585 | 2200000 | 0.029043
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 7600.7287 | 0.23387 | 3250000 | 0.035272
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 7383.5881 | 0.22719 | 3250000 | 0.048803
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 6538.5234 | 0.20119 | 3250000 | 0.035272
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 6425.2091 | 0.29205 | 2200000 | 0.056326
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 6169.0809 | 0.1164 | 5300000 | 0.0041202
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 5993.3947 | 0.18441 | 3250000 | 0.039779
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 | Current Study | 0.55 | (395.00, 395.00) | 5693.9936 | 0.86273 | 660000 | 0.040574
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 5086.5234 | 0.20911 | 2432500 | 0.045162
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 5074.034 | 0.36768 | 1380000 | 0.040053
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 4696.2256 | 0.35577 | 1320000 | 0.03565
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 4509.0442 | 0.18537 | 2432500 | 0.039779
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 4446.5347 | 0.1828 | 2432500 | 0.039779
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 4313.936 | 0.3126 | 1380000 | 0.035272
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 3549.1091 | 0.25718 | 1380000 | 0.035272
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 3281.7023 | 0.2378 | 1380000 | 0.039553
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 2939.6394 | 0.21302 | 1380000 | 0.039779
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 2817.2296 | 0.053155 | 5300000 | 0.036249
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 2794.3008 | 0.1263 | 2212500 | 0.030393
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 2709.2085 | 0.12245 | 2212500 | 0.030393
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 1574.8782 | 0.071181 | 2212500 | 0.036136
GEN-2024-052 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 1116.7339 | 0.067681 | 1650000 | 0.036136
GEN-2024-054 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 1039692.9376 | 0.11079 | 938400000 | 0.027721
GEN-2024-054 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 506927.735 | 0.25537 | 198511000 | 0.014386
GEN-2024-054 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 386886.3581 | 0.41165 | 93984000 | 0.042573
GEN-2024-054 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 210694.6867 | 0.14652 | 143796000 | 0.012197
GEN-2024-054 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 92616.1461 | 0.20172 | 45914000 | 0.016996
GEN-2024-054 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 52279.4145 | 0.44837 | 11660000 | 0.042573
GEN-2024-054 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 50546.1382 | 0.20172 | 25058000 | 0.016996
GEN-2024-054 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 25379.8846 | 0.13645 | 18600000 | 0.039887
GEN-2024-054 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 25379.8846 | 0.13645 | 18600000 | 0.039887
GEN-2024-054 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 16067.3255 | 0.086383 | 18600000 | 0.027721
GEN-2024-054 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 3399.5644 | 0.20603 | 1650000 | 0.020817
GEN-2024-055 | 03 CENTRAL | TBD | ERIS | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | Current Study | 11.77 | (446.00, 446.00) | 1621177.1893 | 9.1825 | 17655000 | 0.094728
GEN-2024-055 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 1609245.7683 | 0.17149 | 938400000 | 0.029422
GEN-2024-055 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 789853.542 | 0.84041 | 93984000 | 0.059599
GEN-2024-055 | 03 CENTRAL | TBD | ERIS | Rebuild line 645458 S3458 3 345 778170 G24-040-TAP 345 1 | Current Study | 13.15 | (1793.00, 1793.00) | 692969.801 | 2.3953 | 28930000 | 0.042449
GEN-2024-055 | 03 CENTRAL | TBD | ERIS | Rebuild line 640139 COOPER 3 345 778170 G24-040-TAP 345 1 | Current Study | 12.59 | (1793.00, 1793.00) | 663459.3 | 2.3953 | 27698000 | 0.042449
GEN-2024-055 | 03 CENTRAL | TBD | ERIS | Rebuild line 761278 G17-108-TAP 161 785640 G24-289-TAP 161 1 | Current Study | 4.53 | (364.00, 364.00) | 649505.9094 | 9.5586 | 6795000 | 0.13001
GEN-2024-055 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 609687.8036 | 0.30713 | 198511000 | 0.011865
GEN-2024-055 | 03 CENTRAL | TBD | ERIS | Rebuild line 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 | Current Study | 3.23 | (1793.00, 1793.00) | 294951.3343 | 4.1507 | 7106000 | 0.053471
GEN-2024-055 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 135919.9319 | 0.29603 | 45914000 | 0.017103
GEN-2024-055 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 106731.8087 | 0.91537 | 11660000 | 0.059599
GEN-2024-055 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 74179.5891 | 0.29603 | 25058000 | 0.017103
GEN-2024-055 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 40981.3351 | 0.22033 | 18600000 | 0.044164
GEN-2024-055 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 40981.3351 | 0.22033 | 18600000 | 0.044164
GEN-2024-055 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 24869.1461 | 0.13371 | 18600000 | 0.029422
GEN-2024-055 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 6704.1896 | 0.40631 | 1650000 | 0.02815
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 532803 BURNS 7 345 1 | Current Study | 50.03 | (1793.00, 1793.00) | 2716897.5312 | 2.4684 | 110066000 | 0.042938
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532803 BURNS 7 345 1 | Current Study | 45.5 | (1793.00, 1793.00) | 2470894.2169 | 2.4684 | 100100000 | 0.042938
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 1605646.7047 | 1.369 | 117282000 | 0.048015
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 1535429.8106 | 2.7597 | 55638000 | 0.10374
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 1479610.5592 | 0.98481 | 150244000 | 0.037195
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1005952.0941 | 1.0017 | 100427000 | 0.021441
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 908351.078 | 2.0259 | 44836000 | 0.079271
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 901689.2899 | 0.41301 | 218320000 | 0.02124
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 844838.6872 | 0.93938 | 89936000 | 0.018287
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 773515.2221 | 1.172 | 66000000 | 0.044897
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 768999.6478 | 0.8054 | 95480000 | 0.054285
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 742334.6046 | 1.3459 | 55154000 | 0.039558
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 739627.2375 | 0.51436 | 143796000 | 0.042817
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 682177.107 | 0.8054 | 84700000 | 0.054285
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 604472.5028 | 1.3165 | 45914000 | 0.11092
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 | Current Study | 9.08 | (395.00, 395.00) | 536051.7407 | 4.9197 | 10896000 | 0.044289
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 523220.4932 | 0.41917 | 124824000 | 0.045705
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 404328.1727 | 0.20368 | 198511000 | 0.018146
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 401319.9817 | 0.20283 | 197860000 | 0.016707
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 391584.2051 | 0.41665 | 93984000 | 0.04309
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 355325.6983 | 1.3459 | 26400000 | 0.039558
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 332039.3516 | 0.40747 | 81488000 | 0.045093
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 329896.5887 | 1.3165 | 25058000 | 0.11092
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 327652.1821 | 0.97533 | 33594000 | 0.066328
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 302500.0771 | 0.64373 | 46992000 | 0.043453
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 302294.279 | 0.22738 | 132946000 | 0.011782
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 299776.5958 | 1.1451 | 26180000 | 0.021564
GEN-2024-056 | 04 SOUTHEAST | TBD | NRIS | Add 5 MVAR switched shunt at CTNWOOD4 138 kV | Current Study |  |  | 299004.0728 | 12.292 | 2432500 | 0.20239
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 289432.7256 | 0.17535 | 165062000 | 0.018388
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Current Study | 3.89 | (395.00, 395.00) | 229652.1224 | 4.9197 | 4668000 | 0.044289
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 223761.9562 | 0.88443 | 25300000 | 0.030193
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 220714.6456 | 1.8393 | 12000000 | 0.10373
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 218706.1869 | 0.4091 | 53460000 | 0.024612
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 | Current Study | 3.49 | (395.00, 395.00) | 206037.5083 | 4.9197 | 4188000 | 0.044289
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 122 MVAR switched shunt at HOYT 7 345 kV | Current Study |  |  | 184644.9628 | 3.4839 | 5300000 | 0.042867
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 176443.4312 | 1.4704 | 12000000 | 0.10373
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 0.06 MVAR switched shunt at G24-125-TAP 345 kV | Current Study |  |  | 175610.1118 | 3.3134 | 5300000 | 0.039441
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 167471.5982 | 1.3593 | 12320000 | 0.048613
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 157632.5256 | 1.3136 | 12000000 | 0.048613
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 157632.5256 | 1.3136 | 12000000 | 0.048613
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 148640.3166 | 0.98745 | 15053000 | 0.021767
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 148525.1727 | 1.2377 | 12000000 | 0.048613
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 140538.5629 | 1.1712 | 12000000 | 0.048613
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 114000.761 | 2.151 | 5300000 | 0.10373
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 111495.0396 | 0.92913 | 12000000 | 0.054285
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 106787.756 | 0.8899 | 12000000 | 0.048613
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 106787.756 | 0.8899 | 12000000 | 0.048613
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 104977.1146 | 0.87481 | 12000000 | 0.074183
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 102495.6451 | 0.85413 | 12000000 | 0.048015
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 101275.723 | 0.84396 | 12000000 | 0.048613
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 99555.7008 | 0.82963 | 12000000 | 0.048613
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 97510.5385 | 0.81259 | 12000000 | 0.018288
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 94910.1683 | 0.79092 | 12000000 | 0.048613
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Current Study | 1.46 | (395.00, 395.00) | 86193.3416 | 4.9197 | 1752000 | 0.044289
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 81599.1995 | 0.67999 | 12000000 | 0.030957
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 81223.2409 | 0.67686 | 12000000 | 0.054285
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 78984.1662 | 1.4903 | 5300000 | 0.030957
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 67988.6859 | 1.2828 | 5300000 | 0.028388
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 60749.0559 | 1.1462 | 5300000 | 0.048015
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 59768.883 | 0.49807 | 12000000 | 0.028303
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 58288.2136 | 1.0998 | 5300000 | 0.048015
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 52914.2281 | 0.45381 | 11660000 | 0.04309
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 52639.4934 | 0.79757 | 6600000 | 0.054285
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 49194.511 | 0.9282 | 5300000 | 0.074183
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 46244.9016 | 0.38537 | 12000000 | 0.028303
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 44543.8465 | 0.84045 | 5300000 | 0.04309
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 44090.293 | 0.83189 | 5300000 | 0.039441
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 43209.6336 | 0.65469 | 6600000 | 0.04309
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Current Study | 0.58 | (395.00, 395.00) | 34241.1905 | 4.9197 | 696000 | 0.044289
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 34019.6693 | 0.51545 | 6600000 | 0.028303
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 34019.6693 | 0.51545 | 6600000 | 0.028303
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 33939.0403 | 1.3952 | 2432500 | 0.048015
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 32328.7435 | 0.48983 | 6600000 | 0.028303
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 30865.3575 | 0.20662 | 14938000 | 0.03668
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 29879.6685 | 0.20662 | 14460953.1406 | 0.03668
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 29610.4749 | 1.3459 | 2200000 | 0.039558
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 29230.3825 | 0.55152 | 5300000 | 0.0068327
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 29085.571 | 0.17963 | 16192000 | 0.033568
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 28998.1055 | 0.54713 | 5300000 | 0.04309
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 28723.2566 | 0.54195 | 5300000 | 0.030957
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 28715.689 | 0.54181 | 5300000 | 0.048613
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 28417.5666 | 0.53618 | 5300000 | 0.028303
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 28350.2174 | 0.8054 | 3520000 | 0.054285
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 28214.3945 | 0.53235 | 5300000 | 0.030957
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 26609.2827 | 0.50206 | 5300000 | 0.030957
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 26175.6715 | 0.80541 | 3250000 | 0.054285
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 23465.5185 | 0.72202 | 3250000 | 0.054285
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 23034.9732 | 0.43462 | 5300000 | 0.10373
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 19118.6846 | 0.64373 | 2970000 | 0.043453
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 18549.0192 | 0.57074 | 3250000 | 0.04309
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 18071.4317 | 1.369 | 1320000 | 0.048015
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 17893.2033 | 0.55056 | 3250000 | 0.028303
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 17511.9353 | 0.7915 | 2212500 | 0.042405
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 17425.8663 | 0.53618 | 3250000 | 0.028303
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 14990.5935 | 0.46125 | 3250000 | 0.028303
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 14161.9886 | 0.64373 | 2200000 | 0.043453
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 13955.0875 | 0.57369 | 2432500 | 0.04309
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 13761.6264 | 0.56574 | 2432500 | 0.04309
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 12295.4975 | 0.10246 | 12000000 | 0.023758
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 12153.1372 | 0.2293 | 5300000 | 0.033568
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 10643.2813 | 0.77125 | 1380000 | 0.044898
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 9097.9203 | 0.65927 | 1380000 | 0.04309
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 8508.1956 | 0.36992 | 2300000 | 0.043453
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 4925.7876 | 0.22263 | 2212500 | 0.039559
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 2963.8829 | 0.17963 | 1650000 | 0.033568
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510379 DELWARE4 138 763113 G18-079-TAP 138 1 | Current Study | 12.23 | (395.00, 395.00) | 8923823.0357 | 60.8056 | 14676000 | 0.58243
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 533008 TV1MNDV4 138 533020 NEOSHOS4 138 1 | Current Study | 22.77 | (265.00, 265.00) | 7162185.4149 | 26.2121 | 27324000 | 0.099693
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 533001 ALTOONA4 138 533006 TAYLOR 4 138 1 | Current Study | 21.66 | (265.00, 265.00) | 6969988.2188 | 26.8159 | 25992000 | 0.095219
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512734 FARML 4 138 778710 G24-058-TAP 138 1 | Current Study | 6.69 | (395.00, 395.00) | 5636812.1001 | 70.2144 | 8028000 | 0.41757
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 533002 DEARING4 138 533004 MONTGOM4 138 1 | Current Study | 11.45 | (265.00, 265.00) | 3680134.873 | 26.7841 | 13740000 | 0.090661
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 533002 DEARING4 138 533003 LIBERTY4 138 1 | Current Study | 10.03 | (395.00, 395.00) | 3168782.7186 | 26.3275 | 12036000 | 0.09771
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 533003 LIBERTY4 138 533008 TV1MNDV4 138 1 | Current Study | 8.36 | (265.00, 265.00) | 2629594.6451 | 26.2121 | 10032000 | 0.099693
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 2462443.0213 | 2.452 | 100427000 | 0.03149
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 2462204.4303 | 2.7377 | 89936000 | 0.031978
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 2158152.9076 | 2.2963 | 93984000 | 0.14249
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 2112707.9339 | 2.2127 | 95480000 | 0.089484
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 1874176.393 | 2.2127 | 84700000 | 0.089484
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510422 COFFEYT4 138 533002 DEARING4 138 1 | Current Study | 5.02 | (717.00, 717.00) | 1468944.0025 | 24.3849 | 6024000 | 0.21229
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 1274834.3041 | 0.84851 | 150244000 | 0.019229
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 1274421.5489 | 1.9309 | 66000000 | 0.044382
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1115299.1676 | 0.51086 | 218320000 | 0.015763
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 769349.107 | 0.53503 | 143796000 | 0.026723
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 710808.4375 | 13.4115 | 5300000 | 0.099693
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 625330.1523 | 2.3886 | 26180000 | 0.026989
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 533004 MONTGOM4 138 533006 TAYLOR 4 138 1 | Current Study | 1.88 | (265.00, 265.00) | 604966.6598 | 26.8159 | 2256000 | 0.095219
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 393113.9985 | 3.2759 | 12000000 | 0.089484
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 373572.4238 | 1.4766 | 25300000 | 0.030244
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 365536.0456 | 3.0461 | 12000000 | 0.10528
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 363282.1706 | 2.4134 | 15053000 | 0.031919
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 352977.5919 | 0.30096 | 117282000 | 0.0063332
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 348609.1902 | 2.9051 | 12000000 | 0.09905
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 327612.2278 | 2.7301 | 12000000 | 0.089484
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 327612.2278 | 2.7301 | 12000000 | 0.089484
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 318361.1727 | 2.653 | 12000000 | 0.089484
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 305425.1366 | 2.5452 | 12000000 | 0.089484
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 291628.1956 | 2.5011 | 11660000 | 0.14249
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 284181.7686 | 2.3682 | 12000000 | 0.031978
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 269728.944 | 2.2477 | 12000000 | 0.09905
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 253672.9013 | 2.1139 | 12000000 | 0.089484
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 238142.3866 | 3.6082 | 6600000 | 0.14249
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 223147.9152 | 1.8596 | 12000000 | 0.089484
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 211050.0599 | 1.7588 | 12000000 | 0.089484
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 209223.3658 | 0.37934 | 55154000 | 0.0066896
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 209147.087 | 1.7429 | 12000000 | 0.064275
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 198423.8081 | 3.0064 | 6600000 | 0.09905
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 198423.8081 | 3.0064 | 6600000 | 0.09905
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 188692.3161 | 3.5602 | 5300000 | 0.089484
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 172819.9025 | 1.4402 | 12000000 | 0.031978
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 172819.9025 | 1.4402 | 12000000 | 0.031978
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 165748.8713 | 3.1273 | 5300000 | 0.09905
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 164054.6919 | 3.0954 | 5300000 | 0.095219
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 162835.0861 | 1.357 | 12000000 | 0.031978
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 159818.0189 | 3.0154 | 5300000 | 0.14249
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 154766.6688 | 1.2897 | 12000000 | 0.045212
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 154078.9926 | 1.284 | 12000000 | 0.031978
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 144618.6224 | 2.1912 | 6600000 | 0.089484
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 140279.2337 | 2.6468 | 5300000 | 0.14249
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 137486.1186 | 4.2303 | 3250000 | 0.09905
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 105293.0674 | 3.2398 | 3250000 | 0.09905
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 104364.2576 | 3.2112 | 3250000 | 0.09905
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 104357.7949 | 3.211 | 3250000 | 0.09905
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 102229.696 | 3.1455 | 3250000 | 0.14249
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 101638.4588 | 3.1273 | 3250000 | 0.09905
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 100146.8045 | 0.37934 | 26400000 | 0.0066896
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 98902.5515 | 1.8661 | 5300000 | 0.089484
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 92815.4853 | 2.8559 | 3250000 | 0.09905
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 87434.4377 | 2.6903 | 3250000 | 0.09905
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 84235.6553 | 1.5894 | 5300000 | 0.045212
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 83036.51 | 1.5667 | 5300000 | 0.041041
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 77887.8501 | 2.2127 | 3520000 | 0.089484
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 77639.8765 | 1.1764 | 6600000 | 0.040784
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 76911.0396 | 3.1618 | 2432500 | 0.14249
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 75844.8122 | 3.118 | 2432500 | 0.14249
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 71913.4874 | 2.2127 | 3250000 | 0.089484
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 64467.774 | 1.9836 | 3250000 | 0.089484
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 60427.133 | 1.8593 | 3250000 | 0.035385
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 60427.133 | 1.8593 | 3250000 | 0.035385
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 57686.8121 | 4.1802 | 1380000 | 0.09905
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 56725.8786 | 0.10611 | 53460000 | 0.0038301
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 55456.0243 | 0.46213 | 12000000 | 0.015638
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 50141.6067 | 3.6334 | 1380000 | 0.14249
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 47459.3948 | 3.4391 | 1380000 | 0.09905
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 43921.5862 | 1.3514 | 3250000 | 0.035385
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 41477.4069 | 0.33667 | 12320000 | 0.0072239
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 34043.2611 | 1.0475 | 3250000 | 0.035385
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 17535.1556 | 1.2707 | 1380000 | 0.044382
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 8345.567 | 0.37934 | 2200000 | 0.0066896
GEN-2024-058 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 3972.736 | 0.30096 | 1320000 | 0.0063332
GEN-2024-061 | 03 CENTRAL | TBD | ERIS | Rebuild line 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 | Current Study | 9.08 | (395.00, 395.00) | 8674611.7037 | 79.6128 | 10896000 | 0.43002
GEN-2024-061 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 3860879.3481 | 0.41143 | 938400000 | 0.0349
GEN-2024-061 | 03 CENTRAL | TBD | ERIS | Rebuild line 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Current Study | 3.89 | (395.00, 395.00) | 3716325.9391 | 79.6128 | 4668000 | 0.43002
GEN-2024-061 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 3360025.6378 | 0.35806 | 938400000 | 0.053752
GEN-2024-061 | 03 CENTRAL | TBD | ERIS | Rebuild line 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 | Current Study | 3.49 | (395.00, 395.00) | 3334184.4544 | 79.6128 | 4188000 | 0.43002
GEN-2024-061 | 03 CENTRAL | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1883333.2868 | 0.86265 | 218320000 | 0.026619
GEN-2024-061 | 03 CENTRAL | TBD | ERIS | Rebuild line 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Current Study | 1.46 | (395.00, 395.00) | 1394816.4193 | 79.6128 | 1752000 | 0.43002
GEN-2024-061 | 03 CENTRAL | TBD | ERIS | Rebuild line 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Current Study | 0.58 | (395.00, 395.00) | 554105.1529 | 79.6128 | 696000 | 0.43002
GEN-2024-061 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 550956.7624 | 0.27754 | 198511000 | 0.0093814
GEN-2024-061 | 03 CENTRAL | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 523760.5468 | 0.97972 | 53460000 | 0.035364
GEN-2024-061 | 03 CENTRAL | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 216663.3097 | 1.1649 | 18600000 | 0.11673
GEN-2024-061 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 132943.5681 | 2.5084 | 5300000 | 0.10666
GEN-2024-061 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 127190.1336 | 0.68382 | 18600000 | 0.11993
GEN-2024-061 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 127190.1336 | 0.68382 | 18600000 | 0.11993
GEN-2024-061 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 51925.548 | 0.27917 | 18600000 | 0.053752
GEN-2024-061 | 03 CENTRAL | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 48859.9396 | 0.26269 | 18600000 | 0.0349
GEN-2024-061 | 03 CENTRAL | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 45480.1519 | 0.85812 | 5300000 | 0.029941
GEN-2024-061 | 03 CENTRAL | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 36277.547 | 1.6397 | 2212500 | 0.052707
GEN-2024-061 | 03 CENTRAL | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 25214.0229 | 0.47574 | 5300000 | 0.016305
GEN-2024-061 | 03 CENTRAL | TBD | ERIS | Add 248 MVAR switched shunt at GEN-2022-015 345 kV | Current Study |  |  | 22997.3115 | 0.43391 | 5300000 | 0.031035
GEN-2024-061 | 03 CENTRAL | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 18726.8047 | 0.35334 | 5300000 | 0.031035
GEN-2024-061 | 03 CENTRAL | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 17160.8733 | 0.14301 | 12000000 | 0.019896
GEN-2024-061 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 4733.4079 | 0.28687 | 1650000 | 0.017391
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520882 DOVERSW4 138 521016 OKEENE 4 138 1 | Current Study | 27.24 | (211.00, 211.00) | 26713311.4752 | 81.7221 | 32688000 | 0.17662
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 14368682.2422 | 1.5286 | 940000000 | 0.018781
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520603 NKNGFSH4 138 520882 DOVERSW4 138 1 | Current Study | 9.13 | (211.00, 211.00) | 10956000 | 100 | 10956000 | 0.21743
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514710 WAUKOMI4 138 514774 HENESEY4 138 1 | Current Study | 11.86 | (395.00, 395.00) | 10530004.8039 | 73.9882 | 14232000 | 0.34963
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514827 CTNWOOD4 138 515377 CRESENT4 138 1 | Current Study | 13.6 | (472.00, 472.00) | 6107019.9904 | 37.4205 | 16320000 | 0.25289
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514710 WAUKOMI4 138 514711 WAUKOTP4 138 1 | Current Study | 6.7 | (395.00, 395.00) | 5948653.6413 | 73.9882 | 8040000 | 0.34963
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 532803 BURNS 7 345 1 | Current Study | 50.03 | (1793.00, 1793.00) | 5711510.3579 | 5.1892 | 110066000 | 0.047095
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520405 KGFSJCT4 138 520603 NKNGFSH4 138 1 | Current Study | 4.35 | (211.00, 211.00) | 5220000 | 100 | 5220000 | 0.21743
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532803 BURNS 7 345 1 | Current Study | 45.5 | (1793.00, 1793.00) | 5194357.811 | 5.1892 | 100100000 | 0.047095
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild 3-winding transformer 521015 OKEENE 2 69 521016 OKEENE 4 138 521173 OKENTERT 13 1 | Current Study |  | (103.00, 103.00) | 5057921.6092 | 93.6652 | 5400000 | 0.049851
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520893 EL RENO4 138 520899 SCOTTSW4 138 1 | Current Study | 6.45 | (265.00, 265.00) | 4748023.4985 | 61.344 | 7740000 | 0.12961
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520533 KGFSHSW4 138 520600 EKFSHTP4 138 1 | Current Study | 2.98 | (211.00, 211.00) | 3576000 | 100 | 3576000 | 0.21743
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 2959052.55 | 2.523 | 117282000 | 0.046167
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520535 BULFTTP4 138 520882 DOVERSW4 138 1 | Current Study | 3.3 | (472.00, 472.00) | 2929933.883 | 73.9882 | 3960000 | 0.34963
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 2853857.0131 | 1.8995 | 150244000 | 0.037431
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | Current Study | 12.07 | (395.00, 395.00) | 2461864.6843 | 16.9971 | 14484000 | 0.061912
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520405 KGFSJCT4 138 520600 EKFSHTP4 138 1 | Current Study | 2.03 | (211.00, 211.00) | 2436000 | 100 | 2436000 | 0.21743
GEN-2024-062 | 04 SOUTHEAST | TBD | NRIS | Add 0.5 MVAR switched shunt at FOURCTP4 138 kV | Current Study |  |  | 2432500 | 100 | 2432500 | 0.045995
GEN-2024-062 | 04 SOUTHEAST | TBD | NRIS | Add 0.6 MVAR switched shunt at DOVER 4 138 kV | Current Study |  |  | 2432500 | 100 | 2432500 | 0.20724
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520847 TWNLKJT4 138 521073 TWNLKSW4 138 1 | Current Study | 7.45 | (211.00, 211.00) | 2392826.8972 | 26.7654 | 8940000 | 0.046226
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514774 HENESEY4 138 520535 BULFTTP4 138 1 | Current Study | 2.53 | (395.00, 395.00) | 2246282.6437 | 73.9882 | 3036000 | 0.34963
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 1894599.2753 | 4.2256 | 44836000 | 0.086265
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 1773504.0561 | 3.1876 | 55638000 | 0.062515
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1706844.8973 | 1.6996 | 100427000 | 0.018981
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1701987.047 | 0.77958 | 218320000 | 0.020918
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 1424089.1424 | 2.582 | 55154000 | 0.039594
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1402170.1401 | 0.97511 | 143796000 | 0.042351
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 1386336.3193 | 1.5415 | 89936000 | 0.015657
GEN-2024-062 | 04 SOUTHEAST | TBD | NRIS | Add 0.2 MVAR switched shunt at REDWING2 69 kV | Current Study |  |  | 1380000 | 100 | 1380000 | 0.0023965
GEN-2024-062 | 04 SOUTHEAST | TBD | NRIS | Add 0.21 MVAR switched shunt at TURCRK 2 69 kV | Current Study |  |  | 1380000 | 100 | 1380000 | 0.020073
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1319478.731 | 1.3819 | 95480000 | 0.048597
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 1260002.0071 | 1.9091 | 66000000 | 0.038157
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1184305.2535 | 0.94878 | 124824000 | 0.053975
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 1170505.3259 | 1.3819 | 84700000 | 0.048597
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1109663.4922 | 0.55899 | 198511000 | 0.025983
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 1101572.4166 | 2.3992 | 45914000 | 0.10547
GEN-2024-062 | 04 SOUTHEAST | TBD | NRIS | Add 0.12 MVAR switched shunt at LACEY 2 69 kV | Current Study |  |  | 1078900.158 | 78.1812 | 1380000 | 0.34715
GEN-2024-062 | 04 SOUTHEAST | TBD | NRIS | Add 0.23 MVAR switched shunt at DOVERSW2 69 kV | Current Study |  |  | 1066805.4593 | 77.3047 | 1380000 | 0.050131
GEN-2024-062 | 04 SOUTHEAST | TBD | NRIS | Add 1.2 MVAR switched shunt at PINE ST4 138 kV | Current Study |  |  | 1031220.0651 | 42.3934 | 2432500 | 0.050654
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515376 WWRDEHV4 138 515425 WWDPST 4 138 1 | Current Study | 4.4 | (472.00, 472.00) | 934334.9499 | 17.6957 | 5280000 | 0.073427
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 918453.5077 | 0.46419 | 197860000 | 0.019949
GEN-2024-062 | 04 SOUTHEAST | TBD | NRIS | Add 0.33 MVAR switched shunt at TWNLAKE4 138 kV | Current Study |  |  | 910180.5025 | 37.4175 | 2432500 | 0.25323
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add phase shifting xfmr 514785 WOODWRD4 138 515425 WWDPST 4 138 M2 | Current Study |  | (421.00, 421.00) | 840547.5401 | 17.6957 | 4750000 | 0.036713
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 773480.3779 | 0.9492 | 81488000 | 0.054805
GEN-2024-062 | 04 SOUTHEAST | TBD | NRIS | Add 5 MVAR switched shunt at CTNWOOD4 138 kV | Current Study |  |  | 717076.9515 | 29.479 | 2432500 | 0.25323
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 683948.2507 | 1.4555 | 46992000 | 0.051259
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 681654.1567 | 2.582 | 26400000 | 0.039594
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 675375.5633 | 0.50801 | 132946000 | 0.013734
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 661402.5895 | 0.4007 | 165062000 | 0.021923
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 653728.7822 | 0.69557 | 93984000 | 0.037532
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 601193.5709 | 2.3992 | 25058000 | 0.10547
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 524364.0737 | 2.0029 | 26180000 | 0.01968
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 476171.9632 | 1.4174 | 33594000 | 0.050293
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 435096.7677 | 0.81387 | 53460000 | 0.025546
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 398021.2639 | 1.5732 | 25300000 | 0.02802
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 122 MVAR switched shunt at HOYT 7 345 kV | Current Study |  |  | 353316.2712 | 6.6663 | 5300000 | 0.042796
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 308786.0343 | 2.5064 | 12320000 | 0.046765
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 0.06 MVAR switched shunt at G24-125-TAP 345 kV | Current Study |  |  | 297627.3879 | 5.6156 | 5300000 | 0.034876
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 138 MVAR switched shunt at GEN-2024-016 345 kV | Current Study |  |  | 293349.0233 | 5.5349 | 5300000 | 0.030132
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 290644.154 | 2.422 | 12000000 | 0.046765
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 290644.154 | 2.422 | 12000000 | 0.046765
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 259126.1643 | 2.1594 | 12000000 | 0.046765
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 254937.8212 | 2.1245 | 12000000 | 0.062515
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 252793.6686 | 1.6794 | 15053000 | 0.019314
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 203802.0802 | 1.6984 | 12000000 | 0.062515
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 203710.47 | 1.6976 | 12000000 | 0.075106
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 202656.6837 | 1.6888 | 12000000 | 0.034607
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 196896.1474 | 1.6408 | 12000000 | 0.046765
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 196896.1474 | 1.6408 | 12000000 | 0.046765
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 191307.346 | 1.5942 | 12000000 | 0.048597
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 188889.3027 | 1.5741 | 12000000 | 0.046167
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 186733.0154 | 1.5561 | 12000000 | 0.046765
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 183561.6244 | 1.5297 | 12000000 | 0.046765
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 174996.153 | 1.4583 | 12000000 | 0.046765
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 174839.9734 | 1.457 | 12000000 | 0.034607
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 169236.8258 | 3.1931 | 5300000 | 0.034607
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 160575.9621 | 3.0297 | 5300000 | 0.034981
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 160009.5346 | 1.3334 | 12000000 | 0.015657
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 157168.746 | 1.3097 | 12000000 | 0.054805
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520999 MOORLND4 138 786210 G24-308-TAP 138 1 | Current Study | 1.19 | (395.00, 395.00) | 156940.7388 | 10.9902 | 1428000 | 0.099137
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 131677.2865 | 2.4845 | 5300000 | 0.062515
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 111954.4815 | 2.1123 | 5300000 | 0.046167
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 107419.3935 | 2.0268 | 5300000 | 0.046167
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 105503.6861 | 0.8792 | 12000000 | 0.026067
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 95463.0634 | 1.8012 | 5300000 | 0.075106
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 90320.8055 | 1.3685 | 6600000 | 0.048597
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 88337.4595 | 0.75761 | 11660000 | 0.037532
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 84532.0532 | 0.56589 | 14938000 | 0.052412
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 81832.5117 | 0.56589 | 14460953.1406 | 0.052412
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 81631.2324 | 0.68026 | 12000000 | 0.026067
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 74725.0748 | 1.4099 | 5300000 | 0.034876
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 74363.7177 | 1.4031 | 5300000 | 0.037532
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 72136.3161 | 1.093 | 6600000 | 0.037532
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 66164.824 | 0.40863 | 16192000 | 0.039841
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 62546.2833 | 2.5713 | 2432500 | 0.046167
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 61544.3956 | 1.1612 | 5300000 | 0.034607
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 60454.0731 | 1.1406 | 5300000 | 0.034607
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515785 WINDFRM4 138 520999 MOORLND4 138 1 | Current Study | 0.28 | (395.00, 395.00) | 57118.811 | 16.9996 | 336000 | 0.061925
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 57014.852 | 1.0758 | 5300000 | 0.034607
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 56804.5131 | 2.582 | 2200000 | 0.039594
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 52946.2248 | 0.99899 | 5300000 | 0.046765
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 48644.3772 | 1.3819 | 3520000 | 0.048597
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 48410.8827 | 0.91341 | 5300000 | 0.037532
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 44913.1931 | 1.3819 | 3250000 | 0.048597
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 43227.0664 | 1.4555 | 2970000 | 0.051259
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 40263.0116 | 1.2389 | 3250000 | 0.048597
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 38543.9311 | 0.72724 | 5300000 | 0.0047008
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 33303.9116 | 2.523 | 1320000 | 0.046167
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 33228.1023 | 1.5018 | 2212500 | 0.04198
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 32020.0492 | 1.4555 | 2200000 | 0.051259
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 30966.6573 | 0.95282 | 3250000 | 0.037532
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 27646.3194 | 0.52163 | 5300000 | 0.039841
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 27301.9878 | 0.22752 | 12000000 | 0.027524
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 23297.3187 | 0.95775 | 2432500 | 0.037532
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 22974.345 | 0.94447 | 2432500 | 0.037532
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 21398.108 | 1.5506 | 1380000 | 0.047095
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 20044.0923 | 0.37819 | 5300000 | 0.047095
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 19236.8954 | 0.83639 | 2300000 | 0.051259
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 15188.5216 | 1.1006 | 1380000 | 0.037532
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 9508.4181 | 0.42976 | 2212500 | 0.039841
GEN-2024-062 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 6742.3394 | 0.40863 | 1650000 | 0.039841
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 30941967.2839 | 2.0429 | 1514620000 | 0.04908
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 25485938.568 | 1.9831 | 1285130000 | 0.24413
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 24853944.0473 | 1.9545 | 1271630000 | 0.15724
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 19397498.142 | 2.0671 | 938400000 | 0.13699
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 16717638.7787 | 4.5614 | 366500000 | 0.11711
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 16667525.4451 | 1.7762 | 938400000 | 0.20831
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 14890990.4985 | 1.3868 | 1073760000 | 0.092795
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 14317719.8045 | 1.9755 | 724760000 | 0.18306
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Current Study | 54.58 | (637.00, 637.00) | 11679408.1085 | 11.2625 | 103702000 | 0.10216
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 9659014.87 | 2.0005 | 482840000 | 0.19859
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 9292652.063 | 1.9799 | 469340000 | 0.13209
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524623 DEAFSMITH 6 230 525520 OLSON 6 230 1 | Current Study | 11 | (519.00, 519.00) | 2643566.9737 | 12.6486 | 20900000 | 0.10044
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 1880365.0701 | 3.4052 | 55220000 | 0.12976
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 1776090.3129 | 0.89765 | 197860000 | 0.034659
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 1691932.7905 | 2.0023 | 84500000 | 0.099439
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1669307.5273 | 1.9755 | 84500000 | 0.18306
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1604317.2069 | 1.8986 | 84500000 | 0.045541
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1597187.7676 | 1.2796 | 124824000 | 0.0654
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1529592.5529 | 0.77053 | 198511000 | 0.032179
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 1272474.5861 | 0.77091 | 165062000 | 0.037894
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1 | Current Study | 18.95 | (901.00, 901.00) | 1201501.5413 | 3.337 | 36005000 | 0.076145
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 1174944.2727 | 4.6998 | 25000000 | 0.062281
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 1174944.2727 | 4.6998 | 25000000 | 0.054275
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 1104130.5865 | 1.355 | 81488000 | 0.070288
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 887767.6307 | 2.0422 | 43472000 | 0.048624
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 379976.8863 | 2.0429 | 18600000 | 0.04908
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 368631.1554 | 1.9819 | 18600000 | 0.24413
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 368268.9061 | 1.9799 | 18600000 | 0.13209
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 367445.2072 | 1.9755 | 18600000 | 0.18306
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 363375.1127 | 1.9536 | 18600000 | 0.15724
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 358331.0853 | 1.9265 | 18600000 | 0.15724
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 325442.9036 | 1.7497 | 18600000 | 0.13699
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 282771.4508 | 1.5203 | 18600000 | 0.20831
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 282771.4508 | 1.5203 | 18600000 | 0.20831
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 270363.8891 | 1.0202 | 26500000 | 0.012527
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 257578.5086 | 1.3848 | 18600000 | 0.20831
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 245477.9087 | 1.3198 | 18600000 | 0.13699
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add line 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 P2 | Current Study | 2.51 | (478.00, 478.00) | 236621.4275 | 1.756 | 13475000 | 0.015715
GEN-2024-063 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 158182.0994 | 0.87393 | 18100000 | 0.01046
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 157673.2816 | 2.405 | 6556000 | 0.12976
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 125815.1007 | 0.77702 | 16192000 | 0.068064
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 110611.782 | 0.74047 | 14938000 | 0.061616
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 107079.3812 | 0.74047 | 14460953.1406 | 0.061616
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 94211.9463 | 1.7776 | 5300000 | 0.19888
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 46876.4149 | 2.1187 | 2212500 | 0.068064
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 35112.4425 | 0.2926 | 12000000 | 0.031803
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 33680.3129 | 2.4406 | 1380000 | 0.19888
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 30904.7841 | 2.2395 | 1380000 | 0.15501
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 22396.2451 | 1.6229 | 1380000 | 0.19888
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 19868.0026 | 1.4397 | 1380000 | 0.0080473
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 18080.5872 | 0.8172 | 2212500 | 0.068064
GEN-2024-063 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 14721.7025 | 1.0668 | 1380000 | 0.052755
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 12820.8323 | 0.77702 | 1650000 | 0.068064
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 8673.1317 | 0.39201 | 2212500 | 0.031803
GEN-2024-063 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 5503.8624 | 0.39883 | 1380000 | 0.031803
GEN-2024-065 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640173 FREMONT7 115 643058 FREMONT T1 9 13 647976 S976 8 69 M2 | Current Study |  | (63.00, 63.00) | 8125000 | 100 | 8125000 | 0.11027
GEN-2024-065 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640173 FREMONT7 115 643059 FREMONT T4 9 13 647976 S976 8 69 M2 | Current Study |  | (56.00, 56.00) | 8125000 | 100 | 8125000 | 0.10022
GEN-2024-065 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | Current Study | 23.61 | (386.00, 386.00) | 4380687.7326 | 9.7655 | 44859000 | 0.060583
GEN-2024-065 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659202 LO.KVA2_-BE9 13 M2 | Current Study |  | (500.00, 617.00) | 271439.5423 | 1.0858 | 25000000 | 0.0079677
GEN-2024-065 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659201 LO.KU1A_-BE9 13 M2 | Current Study |  | (600.00, 637.40) | 267709.0978 | 1.0708 | 25000000 | 0.0090334
GEN-2024-065 | 02 NEBRASKA | TBD | ERIS | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1 | Current Study | 0.06 | (140.00, 140.00) | 49023.3531 | 96.1242 | 51000 | 0.42098
GEN-2024-065 | 02 NEBRASKA | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 2933.631 | 0.21258 | 1380000 | 0.044459
GEN-2024-067 | 03 CENTRAL | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 27448195.791 | 12.5725 | 218320000 | 0.20418
GEN-2024-067 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Current Study | 26.47 | (1793.00, 1793.00) | 11196357.2557 | 19.2265 | 58234000 | 0.17326
GEN-2024-067 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 6947175.7054 | 4.8313 | 143796000 | 0.127
GEN-2024-067 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 4641851.9914 | 2.3383 | 198511000 | 0.0416
GEN-2024-067 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 4078229.9498 | 0.43459 | 938400000 | 0.034338
GEN-2024-067 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | Current Study | 19.87 | (1793.00, 1793.00) | 3411776.7591 | 7.8048 | 43714000 | 0.07015
GEN-2024-067 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | Current Study | 16.71 | (1793.00, 1793.00) | 2614127.5038 | 7.111 | 36762000 | 0.10475
GEN-2024-067 | 03 CENTRAL | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 1793090.4205 | 3.3541 | 53460000 | 0.06372
GEN-2024-067 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1624522.4786 | 0.81835 | 198511000 | 0.023024
GEN-2024-067 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 798393.0618 | 1.7389 | 45914000 | 0.046266
GEN-2024-067 | 03 CENTRAL | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 533376.2959 | 24.1074 | 2212500 | 0.40786
GEN-2024-067 | 03 CENTRAL | TBD | ERIS | Add 0.8 MVAR switched shunt at HARBNGR7 345 kV | Current Study |  |  | 525174.2325 | 9.9089 | 5300000 | 0.54124
GEN-2024-067 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 435730.5689 | 1.7389 | 25058000 | 0.046266
GEN-2024-067 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 135402.6807 | 2.5548 | 5300000 | 0.057176
GEN-2024-067 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 120209.3152 | 0.80472 | 14938000 | 0.045112
GEN-2024-067 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 117233.9563 | 0.63029 | 18600000 | 0.058182
GEN-2024-067 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 117233.9563 | 0.63029 | 18600000 | 0.058182
GEN-2024-067 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 116370.416 | 0.80472 | 14460953.1406 | 0.045112
GEN-2024-067 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 65665.1615 | 0.40554 | 16192000 | 0.023932
GEN-2024-067 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 63024.6158 | 0.33884 | 18600000 | 0.034338
GEN-2024-067 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 25204.8597 | 1.5276 | 1650000 | 0.048739
GEN-2024-067 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MED-LDG3 115 kV | Current Study |  |  | 15778.7342 | 0.71316 | 2212500 | 0.012927
GEN-2024-067 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 6691.4227 | 0.40554 | 1650000 | 0.023932
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1 | Current Study | 30.63 | (1793.00, 1793.00) | 11606129.0561 | 17.2234 | 67386000 | 0.188
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 776060 G23-204-TAP 345 1 | Current Study | 17.82 | (1793.00, 1793.00) | 7677906.2299 | 19.5845 | 39204000 | 0.49182
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | Current Study | 6.93 | (1793.00, 1793.00) | 2985852.4227 | 19.5845 | 15246000 | 0.49182
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 2631195.9723 | 1.7513 | 150244000 | 0.026458
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 2190679.0809 | 1.9422 | 112794000 | 0.11028
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1602172.7782 | 1.678 | 95480000 | 0.04524
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 1569574.7982 | 2.4815 | 63250000 | 0.089831
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1530533.6905 | 0.70105 | 218320000 | 0.014421
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 1421282.3032 | 1.678 | 84700000 | 0.04524
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1 | Current Study | 56.1 | (1793.00, 1793.00) | 1410161.8875 | 1.1426 | 123420000 | 0.010925
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1328626.3521 | 0.92397 | 143796000 | 0.030766
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1245367.7078 | 1.2401 | 100427000 | 0.010617
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 507454 TURK 4 138 507456 TURK 3 115 507458 TURK1 1 13 M2 | Current Study |  | (257.00, 257.00) | 1236875.9405 | 11.893 | 10400000 | 0.029108
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1073470.8005 | 0.54076 | 198511000 | 0.019271
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 966700.4792 | 2.0572 | 46992000 | 0.055545
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 925876.4742 | 0.74175 | 124824000 | 0.032351
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 809943.8342 | 0.86179 | 93984000 | 0.03565
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 712302.5056 | 0.43154 | 165062000 | 0.018101
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 655638.5771 | 1.9517 | 33594000 | 0.05309
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 616604.6091 | 5.1384 | 12000000 | 0.050951
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 614250.7399 | 0.75379 | 81488000 | 0.033367
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 582315.7142 | 2.2681 | 25674000 | 0.053082
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 764550 G20-087-TAP 345 1 | Current Study | 14.38 | (1793.00, 1793.00) | 532887.3803 | 1.6844 | 31636000 | 0.038295
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 504122 MCNAB 3 115 507453 HOPE 3 115 1 | Current Study | 3.32 | (394.00, 394.00) | 516489.0999 | 15.5569 | 3320000 | 0.058217
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 499216.3939 | 1.0873 | 45914000 | 0.036644
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | Current Study | 10.42 | (395.00, 395.00) | 477781.1181 | 3.821 | 12504000 | 0.010288
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 476022.6252 | 1.8815 | 25300000 | 0.025692
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at PHILL 7 345 kV | Current Study |  |  | 470328.4308 | 8.8741 | 5300000 | 0.026383
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 415301.7059 | 2.3191 | 17908000 | 0.055173
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | Current Study | 8.91 | (2390.00, 2390.00) | 325864.3107 | 1.6624 | 19602000 | 0.038295
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1 | Current Study | 11.3 | (1793.00, 1793.00) | 322722.6348 | 1.2982 | 24860000 | 0.026694
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 504122 MCNAB 3 115 507456 TURK 3 115 1 | Current Study | 2.65 | (394.00, 394.00) | 315165.5041 | 11.893 | 2650000 | 0.058217
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 290869.1075 | 2.4239 | 12000000 | 0.059594
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 283759.097 | 4.2994 | 6600000 | 0.059594
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 272452.0712 | 1.0873 | 25058000 | 0.036644
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 248403.7981 | 4.6869 | 5300000 | 0.050951
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 232294.0371 | 1.9358 | 12000000 | 0.04524
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 230174.6778 | 1.9181 | 12000000 | 0.031848
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 222914.8732 | 1.8576 | 12000000 | 0.059594
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | Current Study | 5.97 | (2390.00, 2390.00) | 218340.06 | 1.6624 | 13134000 | 0.038295
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 212428.0482 | 1.7702 | 12000000 | 0.039936
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 192247.6093 | 1.6021 | 12000000 | 0.014422
GEN-2024-068 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 190886.8729 | 1.0546 | 18100000 | 0.010771
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 188901.4837 | 1.5742 | 12000000 | 0.024731
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 187914.3748 | 1.566 | 12000000 | 0.053116
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 184280.0963 | 1.2242 | 15053000 | 0.010794
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 174897.4574 | 1.4575 | 12000000 | 0.031848
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 174897.4574 | 1.4575 | 12000000 | 0.031848
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 171523.0658 | 1.4294 | 12000000 | 0.03249
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 170172.6898 | 2.5784 | 6600000 | 0.059594
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 169818.9696 | 1.4152 | 12000000 | 0.039936
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 166767.091 | 1.3897 | 12000000 | 0.03125
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 165869.8255 | 1.3822 | 12000000 | 0.031848
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 163052.7657 | 1.3588 | 12000000 | 0.031848
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 162972.8159 | 1.3581 | 12000000 | 0.024731
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 142393.4127 | 2.6867 | 5300000 | 0.050951
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 142094.7681 | 4.3721 | 3250000 | 0.059594
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 142094.7681 | 4.3721 | 3250000 | 0.059594
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 132712.3229 | 1.1059 | 12000000 | 0.03249
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 109720.6716 | 2.0702 | 5300000 | 0.039936
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 109671.6094 | 1.6617 | 6600000 | 0.04524
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 109446.5819 | 0.93865 | 11660000 | 0.03565
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 99498.1762 | 4.326 | 2300000 | 0.20326
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 97628.6938 | 1.4792 | 6600000 | 0.03249
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 97628.6938 | 1.4792 | 6600000 | 0.03249
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 92133.375 | 1.7384 | 5300000 | 0.03565
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 88060.6769 | 1.6615 | 5300000 | 0.053116
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 88004.3411 | 1.6605 | 5300000 | 0.059594
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 86000.253 | 2.6462 | 3250000 | 0.059594
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 83764.0728 | 2.5774 | 3250000 | 0.059594
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | Current Study | 1.8 | (395.00, 395.00) | 82534.1663 | 3.821 | 2160000 | 0.010288
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 81551.9366 | 1.5387 | 5300000 | 0.03249
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 80006.8199 | 0.53559 | 14938000 | 0.038031
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 77451.7924 | 0.53559 | 14460953.1406 | 0.038031
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 70909.53 | 5.1384 | 1380000 | 0.050951
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 70443.0865 | 0.43505 | 16192000 | 0.032519
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV | Current Study |  |  | 69148.4011 | 5.0108 | 1380000 | 0.044045
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 64400.4478 | 1.9816 | 3250000 | 0.059594
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 61097.6426 | 2.0572 | 2970000 | 0.055545
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 60491.3033 | 1.8613 | 3250000 | 0.03249
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 59978.9541 | 1.1317 | 5300000 | 0.03565
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 59066.2775 | 1.678 | 3520000 | 0.04524
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 55221.0293 | 2.2701 | 2432500 | 0.03125
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 54535.6315 | 1.678 | 3250000 | 0.04524
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 53924.2877 | 3.9076 | 1380000 | 0.059594
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 51806.4074 | 1.594 | 3250000 | 0.03249
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 51349.4134 | 1.58 | 3250000 | 0.03249
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 51346.2336 | 1.5799 | 3250000 | 0.03249
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 50008.263 | 1.5387 | 3250000 | 0.03249
GEN-2024-068 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 49693.8761 | 0.93762 | 5300000 | 0.10673
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 46861.3134 | 3.3957 | 1380000 | 0.11028
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 45257.5131 | 2.0572 | 2200000 | 0.055545
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 43019.5853 | 1.3237 | 3250000 | 0.03249
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 38366.3262 | 1.1805 | 3250000 | 0.03565
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 38237.6574 | 0.72147 | 5300000 | 0.0035753
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 31792.687 | 1.437 | 2212500 | 0.048413
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 30824.5332 | 1.3932 | 2212500 | 0.048413
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 30195.9422 | 2.1881 | 1380000 | 0.050951
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 28864.353 | 1.1866 | 2432500 | 0.03565
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 28464.2028 | 1.1702 | 2432500 | 0.03565
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 27967.3195 | 1.1497 | 2432500 | 0.034764
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CHILD4WT 138 kV | Current Study |  |  | 27088.7717 | 1.1136 | 2432500 | 0.038295
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 23351.0221 | 1.6921 | 1380000 | 0.03249
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 17679.8952 | 0.33358 | 5300000 | 0.031848
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 11953.8665 | 0.54029 | 2212500 | 0.0384
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 7178.3037 | 0.43505 | 1650000 | 0.032519
GEN-2024-069 | 03 CENTRAL | TBD | ERIS | Rebuild line 547476 ASB349 5 161 547477 CJ 366 5 161 1 | Current Study | 12.3 | (551.00, 551.00) | 8183299.2277 | 44.3539 | 18450000 | 0.28384
GEN-2024-069 | 03 CENTRAL | TBD | ERIS | Rebuild line 547476 ASB349 5 161 547491 PUR421 5 161 1 | Current Study | 11.94 | (551.00, 551.00) | 7992093.2794 | 44.6236 | 17910000 | 0.21922
GEN-2024-069 | 03 CENTRAL | TBD | ERIS | Rebuild line 547485 CAR395 5 161 547491 PUR421 5 161 1 | Current Study | 7.89 | (551.00, 551.00) | 5281207.368 | 44.6236 | 11835000 | 0.21922
GEN-2024-069 | 03 CENTRAL | TBD | NRIS | Add 3-winding transformer 505488 CARTHAG5 161 505489 CRG X2 1 13 505490 CARTHG 2 69 M2 | Current Study |  | (84.00, 84.00) | 3885273.3882 | 37.0909 | 10475000 | 0.011647
GEN-2024-069 | 03 CENTRAL | TBD | NRIS | Add 3-winding transformer 505487 CRG X1 1 13 505488 CARTHAG5 161 505490 CARTHG 2 69 M2 | Current Study |  | (84.00, 84.00) | 3885273.3882 | 37.0909 | 10475000 | 0.011876
GEN-2024-069 | 03 CENTRAL | TBD | ERIS | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1 | Current Study | 4.14 | (551.00, 551.00) | 2769208.5186 | 44.5927 | 6210000 | 0.21922
GEN-2024-069 | 03 CENTRAL | TBD | ERIS | Rebuild line 547477 CJ 366 5 161 547490 FIR417 5 161 1 | Current Study | 3.26 | (551.00, 551.00) | 2168906.9498 | 44.3539 | 4890000 | 0.28384
GEN-2024-069 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 1981604.6272 | 0.21117 | 938400000 | 0.027808
GEN-2024-069 | 03 CENTRAL | TBD | ERIS | Rebuild line 547467 ORO110 5 161 547490 FIR417 5 161 1 | Current Study | 2.86 | (551.00, 551.00) | 1902783.3977 | 44.3539 | 4290000 | 0.28384
GEN-2024-069 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1719078.9424 | 1.8291 | 93984000 | 0.099561
GEN-2024-069 | 03 CENTRAL | TBD | ERIS | Rebuild line 533763 HUDSON-2 69 533770 PITTSBG2 69 1 | Current Study | 1.75 | (69.00, 69.00) | 1076005.3384 | 72.3365 | 1487500 | 0.068927
GEN-2024-069 | 03 CENTRAL | TBD | ERIS | Rebuild line 645458 S3458 3 345 778170 G24-040-TAP 345 1 | Current Study | 13.15 | (1793.00, 1793.00) | 708742.1663 | 2.4499 | 28930000 | 0.033323
GEN-2024-069 | 03 CENTRAL | TBD | ERIS | Rebuild line 640139 COOPER 3 345 778170 G24-040-TAP 345 1 | Current Study | 12.59 | (1793.00, 1793.00) | 678559.9904 | 2.4499 | 27698000 | 0.033323
GEN-2024-069 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 232296.7424 | 1.9923 | 11660000 | 0.099561
GEN-2024-069 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 78180.9089 | 1.4751 | 5300000 | 0.055022
GEN-2024-069 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 68898.9188 | 0.034708 | 198511000 | 0.0010291
GEN-2024-069 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 46608.8597 | 0.25059 | 18600000 | 0.038553
GEN-2024-069 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 46608.8597 | 0.25059 | 18600000 | 0.038553
GEN-2024-069 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 30623.5479 | 0.16464 | 18600000 | 0.027808
GEN-2024-069 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 6605.2329 | 0.40032 | 1650000 | 0.021288
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | Current Study | 10.34 | (69.00, 69.00) | 2979017.9072 | 33.8948 | 8789000 | 0.1147
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | Current Study | 8.6 | (69.00, 69.00) | 2477713.153 | 33.8948 | 7310000 | 0.1147
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508089 WATLANT2 69 779100 G24-071-TAP 69 1 | Current Study | 1.78 | (106.00, 106.00) | 1028172.4673 | 67.9559 | 1513000 | 0.74475
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508803 GILLIAM2 69 508815 SUPEROR2 69 1 | Current Study | 6 | (69.00, 69.00) | 876255.833 | 17.1815 | 5100000 | 0.038953
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508813 PLAINDL2 69 778290 G24-044-TAP 69 1 | Current Study | 9.39 | (69.00, 69.00) | 851537.4181 | 10.6689 | 7981500 | 0.036852
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 636880.6648 | 0.4239 | 150244000 | 0.025617
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507452 HOPESWI3 115 507453 HOPE 3 115 1 | Current Study | 6.38 | (260.00, 260.00) | 423879.1192 | 6.6439 | 6380000 | 0.030445
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 337505 3EMMET 115 507448 NHOPE 3 115 1 | Current Study | 12 | (329.00, 329.00) | 400800.1274 | 3.34 | 12000000 | 0.030445
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 390757.2763 | 0.34643 | 112794000 | 0.078687
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 390397.9441 | 0.40888 | 95480000 | 0.044094
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508812 OILCITY2 69 508815 SUPEROR2 69 1 | Current Study | 4.66 | (106.00, 106.00) | 373746.6573 | 9.4357 | 3961000 | 0.056996
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 367690.7373 | 0.16842 | 218320000 | 0.013858
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 346320.7569 | 0.40888 | 84700000 | 0.044094
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 507454 TURK 4 138 507456 TURK 3 115 507458 TURK1 1 13 M2 | Current Study |  | (257.00, 257.00) | 337400.5494 | 3.2442 | 10400000 | 0.031761
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507449 NWHOPE 3 115 507452 HOPESWI3 115 1 | Current Study | 9.8 | (329.00, 329.00) | 327320.1041 | 3.34 | 9800000 | 0.030445
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 322608.0672 | 0.22435 | 143796000 | 0.029881
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 309792.9051 | 0.48979 | 63250000 | 0.070921
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 282475.2307 | 0.28127 | 100427000 | 0.009633
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508805 LIEBERM2 69 508812 OILCITY2 69 1 | Current Study | 3.4 | (106.00, 106.00) | 272690.6942 | 9.4357 | 2890000 | 0.056996
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 259262.2096 | 0.1306 | 198511000 | 0.018617
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 240345.8748 | 0.51146 | 46992000 | 0.055239
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 222754.4357 | 0.17845 | 124824000 | 0.031133
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 194729.791 | 0.20719 | 93984000 | 0.034285
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 172864.509 | 0.10473 | 165062000 | 0.017571
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 165103.4869 | 1.3759 | 12000000 | 0.054572
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | Current Study | 10.42 | (395.00, 395.00) | 164742.6853 | 1.3175 | 12504000 | 0.014189
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 156826.4639 | 0.46683 | 33594000 | 0.050796
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 147681.1403 | 0.18123 | 81488000 | 0.032089
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 504122 MCNAB 3 115 507453 HOPE 3 115 1 | Current Study | 3.32 | (394.00, 394.00) | 140890.206 | 4.2437 | 3320000 | 0.063522
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at PHILL 7 345 kV | Current Study |  |  | 123242.131 | 2.3253 | 5300000 | 0.027653
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 119473.067 | 0.46535 | 25674000 | 0.043563
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 117168.5816 | 0.46312 | 25300000 | 0.025296
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | Current Study | 7.6 | (211.00, 211.00) | 104934.8314 | 1.1506 | 9120000 | 0.029313
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 764550 G20-087-TAP 345 1 | Current Study | 14.38 | (1793.00, 1793.00) | 97731.4997 | 0.30892 | 31636000 | 0.028093
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 504122 MCNAB 3 115 507456 TURK 3 115 1 | Current Study | 2.65 | (394.00, 394.00) | 85972.2554 | 3.2442 | 2650000 | 0.063522
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 85297.6025 | 0.47631 | 17908000 | 0.045327
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1 | Current Study | 0.28 | (69.00, 69.00) | 80669.7306 | 33.8948 | 238000 | 0.1147
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 80346.4872 | 0.66955 | 12000000 | 0.065846
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 78382.496 | 1.1876 | 6600000 | 0.065846
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1 | Current Study | 11.3 | (1793.00, 1793.00) | 75908.1055 | 0.30534 | 24860000 | 0.025115
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 67241.0046 | 0.56034 | 12000000 | 0.065846
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 66513.1798 | 1.255 | 5300000 | 0.054572
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 61575.556 | 0.51313 | 12000000 | 0.065846
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | Current Study | 8.91 | (2390.00, 2390.00) | 59763.4866 | 0.30488 | 19602000 | 0.028093
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 56602.5818 | 0.47169 | 12000000 | 0.044094
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 51250.4284 | 0.42709 | 12000000 | 0.03854
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 49471.7515 | 0.41226 | 12000000 | 0.014845
GEN-2024-071 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 48958.9554 | 0.27049 | 18100000 | 0.011051
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 48265.6621 | 0.40221 | 12000000 | 0.054572
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 47006.6346 | 0.71222 | 6600000 | 0.065846
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 45666.8428 | 0.38056 | 12000000 | 0.023915
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 41989.5227 | 0.34991 | 12000000 | 0.030584
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 41989.5227 | 0.34991 | 12000000 | 0.030584
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 41735.3319 | 0.27726 | 15053000 | 0.0097788
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 41576.5417 | 0.34647 | 12000000 | 0.031502
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 40970.5546 | 0.34142 | 12000000 | 0.03854
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507448 NHOPE 3 115 507449 NWHOPE 3 115 1 | Current Study | 1.2 | (329.00, 329.00) | 40080.0127 | 3.34 | 1200000 | 0.030445
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | Current Study | 5.97 | (2390.00, 2390.00) | 40043.5482 | 0.30488 | 13134000 | 0.028093
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 40005.9192 | 0.33338 | 12000000 | 0.029986
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 39398.5998 | 0.32832 | 12000000 | 0.023915
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 39250.6979 | 1.2077 | 3250000 | 0.065846
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 39250.6979 | 1.2077 | 3250000 | 0.065846
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 39145.8395 | 0.32622 | 12000000 | 0.030584
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 38127.592 | 0.71939 | 5300000 | 0.054572
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | Current Study | 1.8 | (395.00, 395.00) | 28458.4293 | 1.3175 | 2160000 | 0.014189
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 26723.4421 | 0.4049 | 6600000 | 0.044094
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 26471.2286 | 0.49946 | 5300000 | 0.03854
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 26313.5654 | 0.22567 | 11660000 | 0.034285
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 24309.3525 | 0.45867 | 5300000 | 0.065846
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 23755.7652 | 0.73095 | 3250000 | 0.065846
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 23664.8257 | 0.35856 | 6600000 | 0.031502
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 23664.8257 | 0.35856 | 6600000 | 0.031502
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 23138.0674 | 0.71194 | 3250000 | 0.065846
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 22151.0528 | 0.41794 | 5300000 | 0.034285
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 21796.6205 | 0.67067 | 3250000 | 0.065846
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 21304.0253 | 0.40196 | 5300000 | 0.051401
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 19767.8806 | 0.37298 | 5300000 | 0.031502
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 19314.4031 | 0.1293 | 14938000 | 0.036724
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 18986.901 | 1.3759 | 1380000 | 0.054572
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 18697.5952 | 0.1293 | 14460953.1406 | 0.036724
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 18257.9478 | 0.82522 | 2212500 | 0.1147
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV | Current Study |  |  | 18186.4118 | 1.3179 | 1380000 | 0.046337
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 17789.2723 | 0.54736 | 3250000 | 0.065846
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 17075.9699 | 0.10546 | 16192000 | 0.031532
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 15190.3994 | 0.51146 | 2970000 | 0.055239
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 14895.4529 | 1.0794 | 1380000 | 0.065846
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 14662.8629 | 0.45117 | 3250000 | 0.031502
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 14420.3659 | 0.27208 | 5300000 | 0.034285
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 14392.5509 | 0.40888 | 3520000 | 0.044094
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 13288.5785 | 0.40888 | 3250000 | 0.044094
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 13247.0263 | 0.54458 | 2432500 | 0.029986
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 12557.677 | 0.38639 | 3250000 | 0.031502
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 12446.9034 | 0.38298 | 3250000 | 0.031502
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 12446.1326 | 0.38296 | 3250000 | 0.031502
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 12121.8136 | 0.37298 | 3250000 | 0.031502
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 11252.1477 | 0.51146 | 2200000 | 0.055239
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 9224.1765 | 0.28382 | 3250000 | 0.034285
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 9109.3335 | 0.17187 | 5300000 | 0.003407
GEN-2024-071 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 8745.5481 | 0.16501 | 5300000 | 0.075131
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 8624.1051 | 0.38979 | 2212500 | 0.05253
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 8358.7761 | 0.60571 | 1380000 | 0.078687
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 8085.3358 | 0.58589 | 1380000 | 0.054572
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 6939.6764 | 0.28529 | 2432500 | 0.034285
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 6843.4708 | 0.28133 | 2432500 | 0.034285
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 6760.006 | 0.29391 | 2300000 | 0.055239
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 6507.5882 | 0.26753 | 2432500 | 0.032356
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 5660.1993 | 0.41016 | 1380000 | 0.031502
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CHILD4WT 138 kV | Current Study |  |  | 4968.0775 | 0.20424 | 2432500 | 0.028093
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 4244.6035 | 0.080087 | 5300000 | 0.030584
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 3182.7435 | 0.14385 | 2212500 | 0.040897
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 1740.0785 | 0.10546 | 1650000 | 0.031532
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Rebuild line 539663 GLENELD3 115 539693 SMITH-C3 115 1 | Current Study | 30.72 | (176.00, 176.00) | 30720000 | 100 | 30720000 | 0.30693
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Rebuild line 539650 BELOIT 3 115 539657 CONCORD3 115 1 | Current Study | 22.17 | (176.00, 176.00) | 21579838.0188 | 97.338 | 22170000 | 0.69304
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Rebuild line 539656 CLIFTON3 115 539657 CONCORD3 115 1 | Current Study | 23.19 | (176.00, 176.00) | 18576732.5591 | 80.1067 | 23190000 | 0.11122
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Rebuild line 539650 BELOIT 3 115 539663 GLENELD3 115 1 | Current Study | 13.33 | (176.00, 176.00) | 13330000 | 100 | 13330000 | 0.30693
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 7278218.6628 | 3.3337 | 218320000 | 0.12859
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Current Study | 26.47 | (1793.00, 1793.00) | 3282358.5463 | 5.6365 | 58234000 | 0.12064
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 2710850.0459 | 1.3656 | 198511000 | 0.057699
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 2181013.9616 | 1.5167 | 143796000 | 0.094695
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 1510634.9907 | 0.16098 | 938400000 | 0.030208
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | Current Study | 19.87 | (1793.00, 1793.00) | 1132740.0515 | 2.5913 | 43714000 | 0.055314
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 980433.0317 | 0.49389 | 198511000 | 0.033001
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | Current Study | 16.71 | (1793.00, 1793.00) | 891591.0751 | 2.4253 | 36762000 | 0.084854
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 729880.3072 | 0.54901 | 132946000 | 0.021336
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 656612.817 | 0.33186 | 197860000 | 0.020501
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 633293.437 | 1.1846 | 53460000 | 0.05345
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | Current Study | 19.2 | (2390.00, 2390.00) | 620280.7075 | 1.4685 | 42240000 | 0.046902
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | Current Study | 16.04 | (2390.00, 2390.00) | 518192.8411 | 1.4685 | 35288000 | 0.046902
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 470316.1181 | 0.28493 | 165062000 | 0.022409
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | Current Study | 13 | (2390.00, 2390.00) | 337830.5555 | 1.1812 | 28600000 | 0.046689
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 308718.7979 | 0.67238 | 45914000 | 0.042489
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 168486.2055 | 0.67238 | 25058000 | 0.042489
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 140829.174 | 6.3652 | 2212500 | 0.25576
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Add 525 MVAR SVC at SD.LS-LR-MB3 345 kV | Current Study |  |  | 98051.8783 | 0.8171 | 12000000 | 0.04048
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 73039.1281 | 0.48895 | 14938000 | 0.065098
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 70706.6146 | 0.48895 | 14460953.1406 | 0.065098
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 61740.4194 | 0.5145 | 12000000 | 0.089474
GEN-2024-072 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 56869.1627 | 1.073 | 5300000 | 0.057033
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Add 7 MVAR switched shunt at G19-030-TAP 345 kV | Current Study |  |  | 50644.2766 | 0.95555 | 5300000 | 0.046903
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 46766.2652 | 0.28882 | 16192000 | 0.04048
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MINGO 7 345 kV | Current Study |  |  | 44628.1556 | 0.84204 | 5300000 | 0.04048
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 39461.2516 | 0.21216 | 18600000 | 0.046513
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 39461.2516 | 0.21216 | 18600000 | 0.046513
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 38068.4904 | 0.71827 | 5300000 | 0.030772
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR switched shunt at GEN-2022-075 345 kV | Current Study |  |  | 29466.5797 | 0.55597 | 5300000 | 0.022327
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Add 248 MVAR switched shunt at GEN-2022-015 345 kV | Current Study |  |  | 23996.7762 | 0.45277 | 5300000 | 0.04048
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 23345.2236 | 0.12551 | 18600000 | 0.030208
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 23007.5368 | 0.4341 | 5300000 | 0.018933
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 19540.6729 | 0.36869 | 5300000 | 0.04048
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Add 66 MVAR switched shunt at GEN-2021-021 345 kV | Current Study |  |  | 17042.4909 | 0.32156 | 5300000 | 0.00020835
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at IRS7 115 KV 115 kV | Current Study |  |  | 12300.9071 | 0.55597 | 2212500 | 0.022327
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MED-LDG3 115 kV | Current Study |  |  | 11474.5085 | 0.51862 | 2212500 | 0.022327
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Add 12 MVAR switched shunt at BEELER 3 115 kV | Current Study |  |  | 10361.5955 | 0.46832 | 2212500 | 0.021728
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 9521.5516 | 0.57706 | 1650000 | 0.043728
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Add 0.8 MVAR switched shunt at HARBNGR7 345 kV | Current Study |  |  | 8876.8052 | 0.16749 | 5300000 | 0.021728
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 7819.9289 | 0.35344 | 2212500 | 0.022327
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 7581.7957 | 0.34268 | 2212500 | 0.022327
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 6720.6374 | 0.30376 | 2212500 | 0.04048
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Add 0.04 MVAR switched shunt at ELLIS 2 69 kV | Current Study |  |  | 5121.3445 | 0.37111 | 1380000 | 0.04048
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Add 24 MVAR switched shunt at NESSCTY3 115 kV | Current Study |  |  | 5082.8876 | 0.22974 | 2212500 | 0.021728
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 4765.5841 | 0.28882 | 1650000 | 0.04048
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Add 40 MVAR switched shunt at SEGNTP 3 115 kV | Current Study |  |  | 4621.7217 | 0.20889 | 2212500 | 0.021728
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 3703.3897 | 0.16738 | 2212500 | 0.021728
GEN-2024-072 | 03 CENTRAL | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 2350.1255 | 0.1703 | 1380000 | 0.021728
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 61922298.7284 | 4.0883 | 1514620000 | 0.050289
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 56914110.7391 | 5.3004 | 1073760000 | 0.18159
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 53332754.0027 | 4.15 | 1285130000 | 0.26157
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 52988448.9297 | 4.167 | 1271630000 | 0.17164
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 32935226.5668 | 3.5097 | 938400000 | 0.11909
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 29405776.6453 | 3.1336 | 938400000 | 0.18817
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 28039836.4102 | 3.8688 | 724760000 | 0.18356
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 19626638.9766 | 4.0648 | 482840000 | 0.2066
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 19237306.6948 | 4.0988 | 469340000 | 0.14001
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 14419455.9886 | 3.9344 | 366500000 | 0.05172
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 3781787.2237 | 4.4755 | 84500000 | 0.054964
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 3269173.4873 | 3.8688 | 84500000 | 0.18356
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 3256482.8685 | 3.8538 | 84500000 | 0.097992
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 3242303.1036 | 1.6387 | 197860000 | 0.032395
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 3101786.5902 | 2.4849 | 124824000 | 0.065028
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 2923696.4169 | 1.4728 | 198511000 | 0.031492
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 2328500.943 | 1.4107 | 165062000 | 0.035503
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 2147425.1474 | 2.6353 | 81488000 | 0.069992
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 1925317.9529 | 3.4866 | 55220000 | 0.068026
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 1669389.9986 | 3.8401 | 43472000 | 0.046815
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 1621333.726 | 6.1182 | 26500000 | 0.038463
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 1023115.9046 | 5.5006 | 18600000 | 0.29232
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 774713.4042 | 4.1651 | 18600000 | 0.17164
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 771410.269 | 4.1474 | 18600000 | 0.26157
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 763959.5703 | 4.1073 | 18600000 | 0.17164
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 762376.7514 | 4.0988 | 18600000 | 0.14001
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 760424.8962 | 4.0883 | 18600000 | 0.050289
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 741869.5828 | 3.9885 | 18600000 | 0.30719
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 719605.0516 | 3.8688 | 18600000 | 0.18356
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528018 RED_BLUFF 3 115 528235 WOLFCAMP_TP3 115 1 | Current Study | 7.81 | (598.00, 598.00) | 633074.6253 | 8.1059 | 7810000 | 0.04347
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 589867.2747 | 2.3595 | 25000000 | 0.013951
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 589867.2747 | 2.3595 | 25000000 | 0.016009
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 552573.1043 | 2.9708 | 18600000 | 0.11909
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 498881.1417 | 2.6822 | 18600000 | 0.18817
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 498881.1417 | 2.6822 | 18600000 | 0.18817
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | Current Study | 0.78 | (598.00, 598.00) | 370819.3804 | 7.0072 | 5292000 | 0.039592
GEN-2024-073 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 320406.6109 | 1.7702 | 18100000 | 0.010848
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | Current Study | 0.2 | (598.00, 598.00) | 313921.1686 | 7.0072 | 4480000 | 0.039592
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 229785.9941 | 1.4191 | 16192000 | 0.063647
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 211571.1027 | 1.4163 | 14938000 | 0.060342
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 204814.5536 | 1.4163 | 14460953.1406 | 0.060342
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 181330.8288 | 3.4213 | 5300000 | 0.19598
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 161442.6925 | 2.4625 | 6556000 | 0.068026
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 66014.7289 | 0.55012 | 12000000 | 0.030614
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 65686.0938 | 4.7599 | 1380000 | 0.16869
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 64824.89 | 4.6975 | 1380000 | 0.19598
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 43886.46 | 1.9836 | 2212500 | 0.032626
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 43106.3134 | 3.1236 | 1380000 | 0.19598
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 33021.9989 | 1.4925 | 2212500 | 0.063647
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1 | Current Study | 2.13 | (598.00, 598.00) | 30927.3605 | 1.452 | 2130000 | 0.0063338
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 28419.3167 | 2.0594 | 1380000 | 0.0058936
GEN-2024-073 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 25632.4391 | 1.8574 | 1380000 | 0.047029
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 23415.6923 | 1.4191 | 1650000 | 0.063647
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 528184 SENDERO +3 115 528187 SENDERO_345 345 M2 | Current Study |  | (435.00, 435.00) | 22045.6239 | 0.13122 | 16800000 | 0.00020753
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 16306.3119 | 0.73701 | 2212500 | 0.030614
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 10347.7844 | 0.74984 | 1380000 | 0.030614
GEN-2024-073 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528184 SENDERO +3 115 528193 BLACKRIVER 3 115 1 | Current Study | 0.25 | (598.00, 598.00) | 3629.9719 | 1.452 | 250000 | 0.0063338
GEN-2024-074 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 1900687.7938 | 0.20255 | 938400000 | 0.030406
GEN-2024-074 | 03 CENTRAL | TBD | ERIS | Rebuild line 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | Current Study | 17.54 | (1793.00, 1793.00) | 1883896.0645 | 4.8821 | 38588000 | 0.023458
GEN-2024-074 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 1121798.1147 | 0.56511 | 198511000 | 0.019101
GEN-2024-074 | 03 CENTRAL | TBD | ERIS | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | Current Study | 6.07 | (364.00, 364.00) | 1040446.2381 | 11.4272 | 9105000 | 0.091806
GEN-2024-074 | 03 CENTRAL | TBD | ERIS | Rebuild line 645458 S3458 3 345 778170 G24-040-TAP 345 1 | Current Study | 13.15 | (1793.00, 1793.00) | 974469.0283 | 3.3684 | 28930000 | 0.052232
GEN-2024-074 | 03 CENTRAL | TBD | ERIS | Rebuild line 640139 COOPER 3 345 778170 G24-040-TAP 345 1 | Current Study | 12.59 | (1793.00, 1793.00) | 932970.7275 | 3.3684 | 27698000 | 0.052232
GEN-2024-074 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 813158.3147 | 0.86521 | 93984000 | 0.053687
GEN-2024-074 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 561946.9302 | 0.39079 | 143796000 | 0.019519
GEN-2024-074 | 03 CENTRAL | TBD | ERIS | Rebuild line 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 | Current Study | 3.23 | (1793.00, 1793.00) | 242385.0799 | 3.411 | 7106000 | 0.038449
GEN-2024-074 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 222186.272 | 0.48392 | 45914000 | 0.024463
GEN-2024-074 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 121260.2606 | 0.48392 | 25058000 | 0.024463
GEN-2024-074 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 109880.9502 | 0.94238 | 11660000 | 0.053687
GEN-2024-074 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 50307.1253 | 0.27047 | 18600000 | 0.047437
GEN-2024-074 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 50307.1253 | 0.27047 | 18600000 | 0.047437
GEN-2024-074 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 29373.0661 | 0.15792 | 18600000 | 0.030406
GEN-2024-074 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 9432.3607 | 0.57166 | 1650000 | 0.034655
GEN-2024-076 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1613269.9339 | 1.7165 | 93984000 | 0.16387
GEN-2024-076 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 1296649.8151 | 0.13818 | 938400000 | 0.031913
GEN-2024-076 | 03 CENTRAL | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 622568.0857 | 0.28516 | 218320000 | 0.013537
GEN-2024-076 | 03 CENTRAL | TBD | ERIS | Rebuild line 645458 S3458 3 345 778170 G24-040-TAP 345 1 | Current Study | 13.15 | (1793.00, 1793.00) | 491105.7178 | 1.6976 | 28930000 | 0.040497
GEN-2024-076 | 03 CENTRAL | TBD | ERIS | Rebuild line 640139 COOPER 3 345 778170 G24-040-TAP 345 1 | Current Study | 12.59 | (1793.00, 1793.00) | 470191.7101 | 1.6976 | 27698000 | 0.040497
GEN-2024-076 | 03 CENTRAL | TBD | ERIS | Rebuild line 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 | Current Study | 3.23 | (1793.00, 1793.00) | 258176.3443 | 3.6332 | 7106000 | 0.063006
GEN-2024-076 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 254941.5665 | 0.12843 | 198511000 | 0.0066785
GEN-2024-076 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 217998.9185 | 1.8696 | 11660000 | 0.16387
GEN-2024-076 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 98089.4185 | 1.8507 | 5300000 | 0.12107
GEN-2024-076 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 93884.6672 | 0.20448 | 45914000 | 0.015903
GEN-2024-076 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 51238.4456 | 0.20448 | 25058000 | 0.015903
GEN-2024-076 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 34848.4646 | 0.18736 | 18600000 | 0.050554
GEN-2024-076 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 34848.4646 | 0.18736 | 18600000 | 0.050554
GEN-2024-076 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 20038.315 | 0.10773 | 18600000 | 0.031913
GEN-2024-076 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 4713.6768 | 0.28568 | 1650000 | 0.026643
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1 | Current Study | 59.17 | (637.00, 637.00) | 56211500 | 50 | 112423000 | 0.50966
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 33387772.1279 | 2.2044 | 1514620000 | 0.045192
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 25647643.1538 | 2.7331 | 938400000 | 0.15456
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 23336891.677 | 2.4869 | 938400000 | 0.24889
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 22142101.2329 | 1.7229 | 1285130000 | 0.18099
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 21818868.0165 | 1.7158 | 1271630000 | 0.11779
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 15873466.7562 | 2.1902 | 724760000 | 0.17319
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 12620379.8111 | 1.1753 | 1073760000 | 0.067111
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Rebuild 3-winding transformer and add 3-winding transformer 523265 PRINGLE_TR 1 13 523266 PRINGLE 3 115 523267 PRINGLE 6 230 1 | Current Study |  | (312.00, 312.00) | 10950000 | 50 | 21900000 | 0.24517
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 2 | Current Study | 20.02 | (260.00, 260.00) | 10010000 | 50 | 20020000 | 0.10121
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523266 PRINGLE 3 115 523377 RIVERVIEW 3 115 1 | Current Study | 20.25 | (260.00, 260.00) | 9559369.1113 | 47.2068 | 20250000 | 0.17177
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 9479973.1504 | 1.9634 | 482840000 | 0.16632
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 8978166.3094 | 1.9129 | 469340000 | 0.1089
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 1 | Current Study | 17.76 | (260.00, 260.00) | 8880000 | 50 | 17760000 | 0.12746
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 3021781.6003 | 1.5272 | 197860000 | 0.050319
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | Current Study | 13.92 | (519.00, 519.00) | 2880798.628 | 10.8923 | 26448000 | 0.05962
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523092 HITCHLD_TR11 13 523093 HITCHLAND 3 115 523095 HITCHLAND 6 230 M2 | Current Study |  | (250.00, 288.00) | 2826656.1982 | 20.483 | 13800000 | 0.041508
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523093 HITCHLAND 3 115 523095 HITCHLAND 6 230 523098 HITCHLD_TR41 13 M2 | Current Study |  | (250.00, 288.00) | 2826472.9253 | 20.4817 | 13800000 | 0.039854
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | Current Study | 11.15 | (519.00, 519.00) | 2294508.6879 | 10.8308 | 21185000 | 0.058451
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523091 HITCHLD_TR01 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2 | Current Study |  | (560.00, 644.00) | 2252876.3721 | 9.0115 | 25000000 | 0.057954
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523094 HITCHLD_TR21 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2 | Current Study |  | (560.00, 644.00) | 2252876.3721 | 9.0115 | 25000000 | 0.066622
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 2091341.3681 | 1.267 | 165062000 | 0.053145
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1906334.6384 | 0.96032 | 198511000 | 0.034222
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 1863789.1508 | 2.2057 | 84500000 | 0.093473
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1850692.5615 | 2.1902 | 84500000 | 0.17319
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1731069.583 | 1.3868 | 124824000 | 0.060486
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 1472575.4431 | 4.1335 | 35625000 | 0.02874
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 12 MVAR switched shunt at OCHILTREE 6 230 kV | Current Study |  |  | 1342161.5998 | 35.0892 | 3825000 | 0.054306
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523095 HITCHLAND 6 230 778320 G24-045-TAP 230 1 | Current Study | 37.8 | (772.00, 772.00) | 1337991.3347 | 1.863 | 71820000 | 0.032124
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 1170794.0287 | 1.4368 | 81488000 | 0.0636
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 1167236.2059 | 2.685 | 43472000 | 0.054555
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 12 MVAR switched shunt at NP-OCHILTRE3 115 kV | Current Study |  |  | 1016192.4405 | 45.9296 | 2212500 | 0.0030216
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 756810.5478 | 1.3705 | 55220000 | 0.044567
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-LIPS_SHA2 69 kV | Current Study |  |  | 690000 | 50 | 1380000 | 0.00054973
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-ROGERS 2 69 kV | Current Study |  |  | 690000 | 50 | 1380000 | 0.15571
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 7 MVAR switched shunt at NP-HARBOUR 2 69 kV | Current Study |  |  | 690000 | 50 | 1380000 | 0.15571
GEN-2024-077 | 05 SOUTHWEST | TBD | NRIS | Add 0.08 MVAR switched shunt at NP-SUB_A 2 69 kV | Current Study |  |  | 690000 | 50 | 1380000 | 0.0028553
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 1.6 MVAR switched shunt at NP-VALERO-G2 69 kV | Current Study |  |  | 668882.6299 | 48.4698 | 1380000 | 0.50966
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 605622.6923 | 0.71671 | 84500000 | 0.01467
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 594913.3769 | 4.2494 | 14000000 | 0.01437
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 518244.9531 | 2.073 | 25000000 | 0.020429
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 518244.9531 | 2.073 | 25000000 | 0.023442
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 430305.1557 | 2.3135 | 18600000 | 0.15456
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 410012.1229 | 2.2044 | 18600000 | 0.045192
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 407371.3804 | 2.1902 | 18600000 | 0.17319
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 395920.0025 | 2.1286 | 18600000 | 0.24889
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 395920.0025 | 2.1286 | 18600000 | 0.24889
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 360646.3223 | 1.939 | 18600000 | 0.24889
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 355805.7983 | 1.9129 | 18600000 | 0.1089
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 324574.3218 | 1.745 | 18600000 | 0.15456
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 320265.5589 | 1.7219 | 18600000 | 0.18099
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 319001.0249 | 1.7151 | 18600000 | 0.11779
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 314572.9564 | 1.6913 | 18600000 | 0.11779
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 292823.8066 | 21.2191 | 1380000 | 0.10121
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 229460.8655 | 1.4171 | 16192000 | 0.10593
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 140364.6637 | 0.93965 | 14938000 | 0.066722
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 135882.101 | 0.93965 | 14460953.1406 | 0.066722
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 103781.444 | 1.9581 | 5300000 | 0.18695
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 85492.8922 | 3.8641 | 2212500 | 0.10593
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 67259.018 | 4.8738 | 1380000 | 0.50966
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 63460.4442 | 0.96798 | 6556000 | 0.044566
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 53300.4955 | 0.44417 | 12000000 | 0.041196
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 37101.3618 | 2.6885 | 1380000 | 0.18695
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 32975.2541 | 1.4904 | 2212500 | 0.10593
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 26273.3742 | 1.9039 | 1380000 | 0.11246
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 23382.561 | 1.4171 | 1650000 | 0.10593
GEN-2024-077 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 22286.7973 | 1.615 | 1380000 | 0.068151
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 13165.7664 | 0.59506 | 2212500 | 0.041196
GEN-2024-077 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 8354.833 | 0.60542 | 1380000 | 0.041196
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1 | Current Study | 59.17 | (637.00, 637.00) | 56211500 | 50 | 112423000 | 0.50966
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 33387772.1279 | 2.2044 | 1514620000 | 0.045192
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 25647643.1538 | 2.7331 | 938400000 | 0.15456
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 23336891.677 | 2.4869 | 938400000 | 0.24889
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 22142101.2329 | 1.7229 | 1285130000 | 0.18099
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 21818868.0165 | 1.7158 | 1271630000 | 0.11779
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 15873466.7562 | 2.1902 | 724760000 | 0.17319
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 12620379.8111 | 1.1753 | 1073760000 | 0.067111
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Rebuild 3-winding transformer and add 3-winding transformer 523265 PRINGLE_TR 1 13 523266 PRINGLE 3 115 523267 PRINGLE 6 230 1 | Current Study |  | (312.00, 312.00) | 10950000 | 50 | 21900000 | 0.24517
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 2 | Current Study | 20.02 | (260.00, 260.00) | 10010000 | 50 | 20020000 | 0.10121
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523266 PRINGLE 3 115 523377 RIVERVIEW 3 115 1 | Current Study | 20.25 | (260.00, 260.00) | 9559369.1113 | 47.2068 | 20250000 | 0.17177
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 9479973.1504 | 1.9634 | 482840000 | 0.16632
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 8978166.3094 | 1.9129 | 469340000 | 0.1089
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 1 | Current Study | 17.76 | (260.00, 260.00) | 8880000 | 50 | 17760000 | 0.12746
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 3021781.6003 | 1.5272 | 197860000 | 0.050319
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | Current Study | 13.92 | (519.00, 519.00) | 2880798.628 | 10.8923 | 26448000 | 0.05962
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523092 HITCHLD_TR11 13 523093 HITCHLAND 3 115 523095 HITCHLAND 6 230 M2 | Current Study |  | (250.00, 288.00) | 2826656.1982 | 20.483 | 13800000 | 0.041508
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523093 HITCHLAND 3 115 523095 HITCHLAND 6 230 523098 HITCHLD_TR41 13 M2 | Current Study |  | (250.00, 288.00) | 2826472.9253 | 20.4817 | 13800000 | 0.039854
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | Current Study | 11.15 | (519.00, 519.00) | 2294508.6879 | 10.8308 | 21185000 | 0.058451
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523091 HITCHLD_TR01 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2 | Current Study |  | (560.00, 644.00) | 2252876.3721 | 9.0115 | 25000000 | 0.057954
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523094 HITCHLD_TR21 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2 | Current Study |  | (560.00, 644.00) | 2252876.3721 | 9.0115 | 25000000 | 0.066622
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 2091341.3681 | 1.267 | 165062000 | 0.053145
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1906334.6384 | 0.96032 | 198511000 | 0.034222
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 1863789.1508 | 2.2057 | 84500000 | 0.093473
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1850692.5615 | 2.1902 | 84500000 | 0.17319
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1731069.583 | 1.3868 | 124824000 | 0.060486
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 1472575.4431 | 4.1335 | 35625000 | 0.02874
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 12 MVAR switched shunt at OCHILTREE 6 230 kV | Current Study |  |  | 1342161.5998 | 35.0892 | 3825000 | 0.054306
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523095 HITCHLAND 6 230 778320 G24-045-TAP 230 1 | Current Study | 37.8 | (772.00, 772.00) | 1337991.3347 | 1.863 | 71820000 | 0.032124
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 1170794.0287 | 1.4368 | 81488000 | 0.0636
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 1167236.2059 | 2.685 | 43472000 | 0.054555
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 12 MVAR switched shunt at NP-OCHILTRE3 115 kV | Current Study |  |  | 1016192.4405 | 45.9296 | 2212500 | 0.0030216
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 756810.5478 | 1.3705 | 55220000 | 0.044567
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-LIPS_SHA2 69 kV | Current Study |  |  | 690000 | 50 | 1380000 | 0.00054973
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-ROGERS 2 69 kV | Current Study |  |  | 690000 | 50 | 1380000 | 0.15571
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 7 MVAR switched shunt at NP-HARBOUR 2 69 kV | Current Study |  |  | 690000 | 50 | 1380000 | 0.15571
GEN-2024-078 | 05 SOUTHWEST | TBD | NRIS | Add 0.08 MVAR switched shunt at NP-SUB_A 2 69 kV | Current Study |  |  | 690000 | 50 | 1380000 | 0.0028553
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 1.6 MVAR switched shunt at NP-VALERO-G2 69 kV | Current Study |  |  | 668882.6299 | 48.4698 | 1380000 | 0.50966
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 605622.6923 | 0.71671 | 84500000 | 0.01467
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 594913.3769 | 4.2494 | 14000000 | 0.01437
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 518244.9531 | 2.073 | 25000000 | 0.020429
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 518244.9531 | 2.073 | 25000000 | 0.023442
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 430305.1557 | 2.3135 | 18600000 | 0.15456
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 410012.1229 | 2.2044 | 18600000 | 0.045192
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 407371.3804 | 2.1902 | 18600000 | 0.17319
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 395920.0025 | 2.1286 | 18600000 | 0.24889
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 395920.0025 | 2.1286 | 18600000 | 0.24889
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 360646.3223 | 1.939 | 18600000 | 0.24889
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 355805.7983 | 1.9129 | 18600000 | 0.1089
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 324574.3218 | 1.745 | 18600000 | 0.15456
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 320265.5589 | 1.7219 | 18600000 | 0.18099
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 319001.0249 | 1.7151 | 18600000 | 0.11779
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 314572.9564 | 1.6913 | 18600000 | 0.11779
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 292823.8066 | 21.2191 | 1380000 | 0.10121
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 229460.8655 | 1.4171 | 16192000 | 0.10593
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 140364.6637 | 0.93965 | 14938000 | 0.066722
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 135882.101 | 0.93965 | 14460953.1406 | 0.066722
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 103781.444 | 1.9581 | 5300000 | 0.18695
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 85492.8922 | 3.8641 | 2212500 | 0.10593
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 67259.018 | 4.8738 | 1380000 | 0.50966
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 63460.4442 | 0.96798 | 6556000 | 0.044566
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 53300.4955 | 0.44417 | 12000000 | 0.041196
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 37101.3618 | 2.6885 | 1380000 | 0.18695
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 32975.2541 | 1.4904 | 2212500 | 0.10593
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 26273.3742 | 1.9039 | 1380000 | 0.11246
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 23382.561 | 1.4171 | 1650000 | 0.10593
GEN-2024-078 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 22286.7973 | 1.615 | 1380000 | 0.068151
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 13165.7664 | 0.59506 | 2212500 | 0.041196
GEN-2024-078 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 8354.833 | 0.60542 | 1380000 | 0.041196
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524885 SN_JUAN_SS 6 230 785100 G24-271-TAP 230 1 | Current Study | 49.09 | (637.00, 637.00) | 46635500 | 50 | 93271000 | 0.40638
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 30593871.037 | 2.0199 | 1514620000 | 0.049692
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 25865861.0704 | 2.0127 | 1285130000 | 0.25372
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 25394309.8737 | 1.997 | 1271630000 | 0.16451
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 21672101.3584 | 2.0183 | 1073760000 | 0.13829
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 17639138.763 | 1.8797 | 938400000 | 0.12756
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 15293451.2116 | 1.6297 | 938400000 | 0.19573
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 13978356.1115 | 1.9287 | 724760000 | 0.18301
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 13743369.3233 | 3.7499 | 366500000 | 0.098589
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3 | Current Study | 39.39 | (478.00, 544.00) | 13726589.5807 | 12.9894 | 105675000 | 0.17757
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524875 OASIS 6 230 787680 G24-357-TAP 230 1 | Current Study | 26.02 | (901.00, 901.00) | 13416500.6082 | 27.138 | 49438000 | 0.59324
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1 | Current Study | 52.45 | (1046.00, 1046.00) | 12999305.3745 | 13.0443 | 99655000 | 0.34437
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524885 SN_JUAN_SS 6 230 787680 G24-357-TAP 230 1 | Current Study | 20.18 | (901.00, 901.00) | 10405264.4994 | 27.138 | 38342000 | 0.59324
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 9643730.9397 | 1.9973 | 482840000 | 0.20303
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 9350378.6077 | 1.9922 | 469340000 | 0.1361
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Current Study | 54.58 | (637.00, 637.00) | 9036575.4528 | 8.714 | 103702000 | 0.080939
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527799 EDDY_NORTH 6 230 528095 7-RIVERS 6 230 1 | Current Study | 24.1 | (386.00, 386.00) | 3814302.0333 | 8.33 | 45790000 | 0.05194
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527597 TWEEDY 3 115 527798 EDDY_NTH 3 115 1 | Current Study | 44.83 | (394.00, 394.00) | 3573156.2803 | 7.9705 | 44830000 | 0.061309
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528095 7-RIVERS 6 230 528179 PECOS 6 230 1 | Current Study | 20.61 | (386.00, 386.00) | 3458333.5872 | 8.8315 | 39159000 | 0.054587
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1 | Current Study | 9.6 | (901.00, 901.00) | 2914630.3929 | 15.9793 | 18240000 | 0.42817
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add line 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 P2 | Current Study | 2.51 | (478.00, 478.00) | 2902219.5796 | 21.5378 | 13475000 | 0.19737
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 524872 OASIS_TR1 1 13 524874 OASIS 3 115 524875 OASIS 6 230 M2 | Current Study |  | (239.00, 239.00) | 2643882.1838 | 19.1586 | 13800000 | 0.039631
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 527796 EDDY_TR 1 13 527799 EDDY_NORTH 6 230 527802 EDDY_CNTY 7 345 M2 | Current Study |  | (516.00, 558.00) | 2266015.0659 | 9.0641 | 25000000 | 0.12025
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1743591.2175 | 2.0634 | 84500000 | 0.050683
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 1678490.552 | 0.84832 | 197860000 | 0.03354
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 1638226.5716 | 1.9387 | 84500000 | 0.098593
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1629741.0059 | 1.9287 | 84500000 | 0.18301
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1554105.1181 | 1.245 | 124824000 | 0.065163
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524863 FE-CHZPLT 3 115 524874 OASIS 3 115 1 | Current Study | 7.8 | (176.00, 176.00) | 1498409.9623 | 19.2104 | 7800000 | 0.037351
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1477764.7795 | 0.74442 | 198511000 | 0.031834
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524764 NORRIS_TP 3 115 524863 FE-CHZPLT 3 115 1 | Current Study | 7.62 | (176.00, 176.00) | 1463831.2709 | 19.2104 | 7620000 | 0.037351
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 1400157.555 | 2.5356 | 55220000 | 0.098942
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 1203931.4833 | 0.72938 | 165062000 | 0.036713
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 1075068.7152 | 1.3193 | 81488000 | 0.07008
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 849803.9585 | 1.9548 | 43472000 | 0.047662
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 754001.1753 | 3.016 | 25000000 | 0.040927
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 754001.1753 | 3.016 | 25000000 | 0.035666
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1 | Current Study | 18.95 | (901.00, 901.00) | 730566.5635 | 2.0291 | 36005000 | 0.047411
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 583215.9462 | 2.2008 | 26500000 | 0.027671
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 375702.1572 | 2.0199 | 18600000 | 0.049692
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 374126.3923 | 2.0114 | 18600000 | 0.25372
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 371275.4883 | 1.9961 | 18600000 | 0.16451
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 370556.6159 | 1.9922 | 18600000 | 0.1361
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 366121.7954 | 1.9684 | 18600000 | 0.16451
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 358735.8901 | 1.9287 | 18600000 | 0.18301
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 295941.9041 | 1.5911 | 18600000 | 0.12756
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 259459.7141 | 1.3949 | 18600000 | 0.19573
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 259459.7141 | 1.3949 | 18600000 | 0.19573
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 236343.6833 | 1.2707 | 18600000 | 0.19573
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 223225.6378 | 1.2001 | 18600000 | 0.12756
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528018 RED_BLUFF 3 115 528235 WOLFCAMP_TP3 115 1 | Current Study | 7.81 | (598.00, 598.00) | 217911.7374 | 2.7902 | 7810000 | 0.029926
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1 | Current Study | 2.49 | (394.00, 394.00) | 198464.4019 | 7.9705 | 2490000 | 0.061309
GEN-2024-079 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 157470.7063 | 0.87 | 18100000 | 0.010663
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 528184 SENDERO +3 115 528187 SENDERO_345 345 M2 | Current Study |  | (435.00, 435.00) | 134812.5958 | 0.80246 | 16800000 | 0.0025381
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 118824.8741 | 0.73385 | 16192000 | 0.065825
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 117406.6887 | 1.7908 | 6556000 | 0.098942
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | Current Study | 0.78 | (598.00, 598.00) | 114946.5628 | 2.1721 | 5292000 | 0.024545
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 106875.6271 | 0.71546 | 14938000 | 0.060964
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 103462.5409 | 0.71546 | 14460953.1406 | 0.060964
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | Current Study | 0.2 | (598.00, 598.00) | 97309.2595 | 2.1721 | 4480000 | 0.024545
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 91221.419 | 1.7212 | 5300000 | 0.19719
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 44271.9859 | 2.001 | 2212500 | 0.065825
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 33636.4409 | 0.2803 | 12000000 | 0.031197
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 32611.214 | 2.3631 | 1380000 | 0.19719
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 31561.2293 | 2.287 | 1380000 | 0.16211
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1 | Current Study | 2.13 | (598.00, 598.00) | 30785.8326 | 1.4453 | 2130000 | 0.01261
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 21685.3312 | 1.5714 | 1380000 | 0.19719
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 17076.0393 | 0.7718 | 2212500 | 0.065825
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 16765.7889 | 1.2149 | 1380000 | 0.0069537
GEN-2024-079 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 13584.4496 | 0.98438 | 1380000 | 0.049848
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 12108.513 | 0.73385 | 1650000 | 0.065825
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 8308.5442 | 0.37553 | 2212500 | 0.031197
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 5272.4997 | 0.38207 | 1380000 | 0.031197
GEN-2024-079 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528184 SENDERO +3 115 528193 BLACKRIVER 3 115 1 | Current Study | 0.25 | (598.00, 598.00) | 3613.3606 | 1.4453 | 250000 | 0.01261
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524885 SN_JUAN_SS 6 230 785100 G24-271-TAP 230 1 | Current Study | 49.09 | (637.00, 637.00) | 46635500 | 50 | 93271000 | 0.40638
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 30593871.037 | 2.0199 | 1514620000 | 0.049692
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 25865861.0704 | 2.0127 | 1285130000 | 0.25372
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 25394309.8737 | 1.997 | 1271630000 | 0.16451
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 21672101.3584 | 2.0183 | 1073760000 | 0.13829
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 17639138.763 | 1.8797 | 938400000 | 0.12756
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 15293451.2116 | 1.6297 | 938400000 | 0.19573
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 13978356.1115 | 1.9287 | 724760000 | 0.18301
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 13743369.3233 | 3.7499 | 366500000 | 0.098589
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3 | Current Study | 39.39 | (478.00, 544.00) | 13726589.5807 | 12.9894 | 105675000 | 0.17757
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524875 OASIS 6 230 787680 G24-357-TAP 230 1 | Current Study | 26.02 | (901.00, 901.00) | 13416500.6082 | 27.138 | 49438000 | 0.59324
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1 | Current Study | 52.45 | (1046.00, 1046.00) | 12999305.3745 | 13.0443 | 99655000 | 0.34437
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524885 SN_JUAN_SS 6 230 787680 G24-357-TAP 230 1 | Current Study | 20.18 | (901.00, 901.00) | 10405264.4994 | 27.138 | 38342000 | 0.59324
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 9643730.9397 | 1.9973 | 482840000 | 0.20303
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 9350378.6077 | 1.9922 | 469340000 | 0.1361
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Current Study | 54.58 | (637.00, 637.00) | 9036575.4528 | 8.714 | 103702000 | 0.080939
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527799 EDDY_NORTH 6 230 528095 7-RIVERS 6 230 1 | Current Study | 24.1 | (386.00, 386.00) | 3814302.0333 | 8.33 | 45790000 | 0.05194
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527597 TWEEDY 3 115 527798 EDDY_NTH 3 115 1 | Current Study | 44.83 | (394.00, 394.00) | 3573156.2803 | 7.9705 | 44830000 | 0.061309
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528095 7-RIVERS 6 230 528179 PECOS 6 230 1 | Current Study | 20.61 | (386.00, 386.00) | 3458333.5872 | 8.8315 | 39159000 | 0.054587
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1 | Current Study | 9.6 | (901.00, 901.00) | 2914630.3929 | 15.9793 | 18240000 | 0.42817
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add line 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 P2 | Current Study | 2.51 | (478.00, 478.00) | 2902219.5796 | 21.5378 | 13475000 | 0.19737
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 524872 OASIS_TR1 1 13 524874 OASIS 3 115 524875 OASIS 6 230 M2 | Current Study |  | (239.00, 239.00) | 2643882.1838 | 19.1586 | 13800000 | 0.039631
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 527796 EDDY_TR 1 13 527799 EDDY_NORTH 6 230 527802 EDDY_CNTY 7 345 M2 | Current Study |  | (516.00, 558.00) | 2266015.0659 | 9.0641 | 25000000 | 0.12025
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1743591.2175 | 2.0634 | 84500000 | 0.050683
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 1678490.552 | 0.84832 | 197860000 | 0.03354
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 1638226.5716 | 1.9387 | 84500000 | 0.098593
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1629741.0059 | 1.9287 | 84500000 | 0.18301
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1554105.1181 | 1.245 | 124824000 | 0.065163
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524863 FE-CHZPLT 3 115 524874 OASIS 3 115 1 | Current Study | 7.8 | (176.00, 176.00) | 1498409.9623 | 19.2104 | 7800000 | 0.037351
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1477764.7795 | 0.74442 | 198511000 | 0.031834
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524764 NORRIS_TP 3 115 524863 FE-CHZPLT 3 115 1 | Current Study | 7.62 | (176.00, 176.00) | 1463831.2709 | 19.2104 | 7620000 | 0.037351
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 1400157.555 | 2.5356 | 55220000 | 0.098942
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 1203931.4833 | 0.72938 | 165062000 | 0.036713
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 1075068.7152 | 1.3193 | 81488000 | 0.07008
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 849803.9585 | 1.9548 | 43472000 | 0.047662
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 754001.1753 | 3.016 | 25000000 | 0.040927
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 754001.1753 | 3.016 | 25000000 | 0.035666
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1 | Current Study | 18.95 | (901.00, 901.00) | 730566.5635 | 2.0291 | 36005000 | 0.047411
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 583215.9462 | 2.2008 | 26500000 | 0.027671
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 375702.1572 | 2.0199 | 18600000 | 0.049692
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 374126.3923 | 2.0114 | 18600000 | 0.25372
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 371275.4883 | 1.9961 | 18600000 | 0.16451
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 370556.6159 | 1.9922 | 18600000 | 0.1361
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 366121.7954 | 1.9684 | 18600000 | 0.16451
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 358735.8901 | 1.9287 | 18600000 | 0.18301
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 295941.9041 | 1.5911 | 18600000 | 0.12756
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 259459.7141 | 1.3949 | 18600000 | 0.19573
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 259459.7141 | 1.3949 | 18600000 | 0.19573
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 236343.6833 | 1.2707 | 18600000 | 0.19573
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 223225.6378 | 1.2001 | 18600000 | 0.12756
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528018 RED_BLUFF 3 115 528235 WOLFCAMP_TP3 115 1 | Current Study | 7.81 | (598.00, 598.00) | 217911.7374 | 2.7902 | 7810000 | 0.029926
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1 | Current Study | 2.49 | (394.00, 394.00) | 198464.4019 | 7.9705 | 2490000 | 0.061309
GEN-2024-080 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 157470.7063 | 0.87 | 18100000 | 0.010663
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 528184 SENDERO +3 115 528187 SENDERO_345 345 M2 | Current Study |  | (435.00, 435.00) | 134812.5958 | 0.80246 | 16800000 | 0.0025381
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 118824.8741 | 0.73385 | 16192000 | 0.065825
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 117406.6887 | 1.7908 | 6556000 | 0.098942
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | Current Study | 0.78 | (598.00, 598.00) | 114946.5628 | 2.1721 | 5292000 | 0.024545
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 106875.6271 | 0.71546 | 14938000 | 0.060964
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 103462.5409 | 0.71546 | 14460953.1406 | 0.060964
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | Current Study | 0.2 | (598.00, 598.00) | 97309.2595 | 2.1721 | 4480000 | 0.024545
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 91221.419 | 1.7212 | 5300000 | 0.19719
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 44271.9859 | 2.001 | 2212500 | 0.065825
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 33636.4409 | 0.2803 | 12000000 | 0.031197
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 32611.214 | 2.3631 | 1380000 | 0.19719
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 31561.2293 | 2.287 | 1380000 | 0.16211
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1 | Current Study | 2.13 | (598.00, 598.00) | 30785.8326 | 1.4453 | 2130000 | 0.01261
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 21685.3312 | 1.5714 | 1380000 | 0.19719
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 17076.0393 | 0.7718 | 2212500 | 0.065825
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 16765.7889 | 1.2149 | 1380000 | 0.0069537
GEN-2024-080 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 13584.4496 | 0.98438 | 1380000 | 0.049848
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 12108.513 | 0.73385 | 1650000 | 0.065825
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 8308.5442 | 0.37553 | 2212500 | 0.031197
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 5272.4997 | 0.38207 | 1380000 | 0.031197
GEN-2024-080 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528184 SENDERO +3 115 528193 BLACKRIVER 3 115 1 | Current Study | 0.25 | (598.00, 598.00) | 3613.3606 | 1.4453 | 250000 | 0.01261
GEN-2024-081 | 01 NORTH | TBD | ERIS | Rebuild line 659070 W.BANK.S-BE3 345 779400 G24-081-TAP 345 1 | Current Study | 18.38 | (1793.00, 1793.00) | 20218000 | 50 | 40436000 | 0.42982
GEN-2024-081 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2 | Current Study |  | (600.00, 637.00) | 12500000 | 50 | 25000000 | 0.085487
GEN-2024-081 | 01 NORTH | TBD | ERIS | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | Current Study | 9 | (1793.00, 1793.00) | 9900000 | 50 | 19800000 | 0.57018
GEN-2024-081 | 01 NORTH | TBD | ERIS | Add 2-winding transformer 655943 W.BANK.S-MW7 115 659070 W.BANK.S-BE3 345 M2 | Current Study |  | (435.00, 435.00) | 8400000 | 50 | 16800000 | 0.031731
GEN-2024-081 | 01 NORTH | TBD | ERIS | Rebuild line 655943 W.BANK.S-MW7 115 655945 WHEELS_T-MW7 115 1 | Current Study | 11.73 | (394.00, 394.00) | 5865000 | 50 | 11730000 | 0.018307
GEN-2024-081 | 01 NORTH | TBD | ERIS | Rebuild line 655942 N.TWELVE-MW7 115 655959 EPPING -MW7 115 1 | Current Study | 9 | (260.00, 260.00) | 4500000 | 50 | 9000000 | 0.024777
GEN-2024-081 | 01 NORTH | TBD | ERIS | Add 314 MVAR SVC at MAURINE4 230 kV | Current Study |  |  | 3044937.5258 | 35.4063 | 8600000 | 0.36636
GEN-2024-081 | 01 NORTH | TBD | ERIS | Rebuild line 655945 WHEELS_T-MW7 115 655959 EPPING -MW7 115 1 | Current Study | 2.6 | (260.00, 260.00) | 1300000 | 50 | 2600000 | 0.024777
GEN-2024-081 | 01 NORTH | TBD | ERIS | Rebuild line 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | Current Study | 1.04 | (772.00, 772.00) | 988000 | 50 | 1976000 | 0.12691
GEN-2024-081 | 01 NORTH | TBD | ERIS | Rebuild line 652391 WILLISTON27 115 652421 WILISTN7 115 Z1 | Current Study | 0.035484 | (217.00, 217.00) | 17741.9356 | 50 | 35483.8712 | 0.046857
GEN-2024-082 | 01 NORTH | TBD | ERIS | Rebuild line 659070 W.BANK.S-BE3 345 779400 G24-081-TAP 345 1 | Current Study | 18.38 | (1793.00, 1793.00) | 20218000 | 50 | 40436000 | 0.42982
GEN-2024-082 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2 | Current Study |  | (600.00, 637.00) | 12500000 | 50 | 25000000 | 0.085487
GEN-2024-082 | 01 NORTH | TBD | ERIS | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | Current Study | 9 | (1793.00, 1793.00) | 9900000 | 50 | 19800000 | 0.57018
GEN-2024-082 | 01 NORTH | TBD | ERIS | Add 2-winding transformer 655943 W.BANK.S-MW7 115 659070 W.BANK.S-BE3 345 M2 | Current Study |  | (435.00, 435.00) | 8400000 | 50 | 16800000 | 0.031731
GEN-2024-082 | 01 NORTH | TBD | ERIS | Rebuild line 655943 W.BANK.S-MW7 115 655945 WHEELS_T-MW7 115 1 | Current Study | 11.73 | (394.00, 394.00) | 5865000 | 50 | 11730000 | 0.018307
GEN-2024-082 | 01 NORTH | TBD | ERIS | Rebuild line 655942 N.TWELVE-MW7 115 655959 EPPING -MW7 115 1 | Current Study | 9 | (260.00, 260.00) | 4500000 | 50 | 9000000 | 0.024777
GEN-2024-082 | 01 NORTH | TBD | ERIS | Add 314 MVAR SVC at MAURINE4 230 kV | Current Study |  |  | 3044937.5258 | 35.4063 | 8600000 | 0.36636
GEN-2024-082 | 01 NORTH | TBD | ERIS | Rebuild line 655945 WHEELS_T-MW7 115 655959 EPPING -MW7 115 1 | Current Study | 2.6 | (260.00, 260.00) | 1300000 | 50 | 2600000 | 0.024777
GEN-2024-082 | 01 NORTH | TBD | ERIS | Rebuild line 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | Current Study | 1.04 | (772.00, 772.00) | 988000 | 50 | 1976000 | 0.12691
GEN-2024-082 | 01 NORTH | TBD | ERIS | Rebuild line 652391 WILLISTON27 115 652421 WILISTN7 115 Z1 | Current Study | 0.035484 | (217.00, 217.00) | 17741.9356 | 50 | 35483.8712 | 0.046857
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1 | Current Study | 56.1 | (1793.00, 1793.00) | 8891909.0269 | 7.2046 | 123420000 | 0.082666
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1 | Current Study | 30.63 | (1793.00, 1793.00) | 4950685.9919 | 7.3468 | 67386000 | 0.096233
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 2811385.148 | 2.4925 | 112794000 | 0.16984
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 776060 G23-204-TAP 345 1 | Current Study | 17.82 | (1793.00, 1793.00) | 2509800.8141 | 6.4019 | 39204000 | 0.19292
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 2392693.5249 | 2.0401 | 117282000 | 0.034344
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 2366495.0841 | 1.5751 | 150244000 | 0.028555
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 1857944.997 | 2.9375 | 63250000 | 0.1276
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 1471267.5288 | 1.6359 | 89936000 | 0.015287
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | Current Study | 7.74 | (1793.00, 1793.00) | 1464918.865 | 8.603 | 17028000 | 0.19292
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1412635.2201 | 1.4795 | 95480000 | 0.047866
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1398507.4886 | 0.64058 | 218320000 | 0.015813
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1269550.1648 | 1.2642 | 100427000 | 0.012988
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 1253144.1469 | 1.4795 | 84700000 | 0.047866
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1186215.7021 | 0.82493 | 143796000 | 0.032962
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 1086588.8324 | 1.9701 | 55154000 | 0.027793
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | Current Study | 6.93 | (1793.00, 1793.00) | 976033.6499 | 6.4019 | 15246000 | 0.19292
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 974307.8403 | 0.49081 | 198511000 | 0.020989
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 967941.4471 | 2.1588 | 44836000 | 0.040546
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 883140.7245 | 0.44635 | 197860000 | 0.017647
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 507454 TURK 4 138 507456 TURK 3 115 507458 TURK1 1 13 M2 | Current Study |  | (257.00, 257.00) | 880399.912 | 8.4654 | 10400000 | 0.024863
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 764550 G20-087-TAP 345 1 | Current Study | 14.38 | (1793.00, 1793.00) | 847854.9435 | 2.68 | 31636000 | 0.073115
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 847159.4752 | 0.67868 | 124824000 | 0.035521
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 807059.0901 | 1.7174 | 46992000 | 0.055647
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 733698.8686 | 0.78066 | 93984000 | 0.038753
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 661048.5968 | 2.5748 | 25674000 | 0.072311
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 638690.2072 | 0.38694 | 165062000 | 0.019477
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | Current Study | 13.6 | (1793.00, 1793.00) | 624859.5745 | 2.0884 | 29920000 | 0.031548
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 598464.7699 | 1.7815 | 33594000 | 0.058152
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515178 PARKLN 4 138 515977 LKKONWA4 138 1 | Current Study | 13.56 | (472.00, 472.00) | 567946.0446 | 3.4903 | 16272000 | 0.033776
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 562564.364 | 0.69036 | 81488000 | 0.036672
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 520106.3418 | 1.9701 | 26400000 | 0.027793
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | Current Study | 8.91 | (2390.00, 2390.00) | 518469.1493 | 2.645 | 19602000 | 0.073115
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | Current Study | 13.16 | (395.00, 395.00) | 498088.1395 | 3.1541 | 15792000 | 0.02492
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 470472.7139 | 2.6272 | 17908000 | 0.075003
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 449780.6426 | 0.97962 | 45914000 | 0.039618
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 433883.8407 | 3.6157 | 12000000 | 0.043023
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 411020.2279 | 1.6246 | 25300000 | 0.026621
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | Current Study | 5.97 | (2390.00, 2390.00) | 347391.7869 | 2.645 | 13134000 | 0.073115
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1 | Current Study | 11.3 | (1793.00, 1793.00) | 293681.5077 | 1.1813 | 24860000 | 0.02915
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 250783.9797 | 2.0356 | 12320000 | 0.034942
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 245472.0421 | 0.97962 | 25058000 | 0.039618
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 | Current Study | 6.08 | (395.00, 395.00) | 230119.7484 | 3.1541 | 7296000 | 0.02492
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 504122 MCNAB 3 115 507456 TURK 3 115 1 | Current Study | 2.65 | (394.00, 394.00) | 224332.6699 | 8.4654 | 2650000 | 0.049726
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 210452.0685 | 1.7538 | 12000000 | 0.034942
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 204813.5751 | 1.7068 | 12000000 | 0.047866
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 191654.421 | 1.5971 | 12000000 | 0.043237
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 188108.1024 | 1.2496 | 15053000 | 0.013222
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 185822.7332 | 1.5485 | 12000000 | 0.045686
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 181280.4784 | 2.7467 | 6600000 | 0.045686
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 174793.3641 | 3.298 | 5300000 | 0.043023
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 170449.6884 | 1.4204 | 12000000 | 0.026779
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 169811.6188 | 1.4151 | 12000000 | 0.015287
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 169113.6611 | 1.4093 | 12000000 | 0.057362
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 159911.2988 | 1.3326 | 12000000 | 0.034942
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 159911.2988 | 1.3326 | 12000000 | 0.034942
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 153212.1421 | 1.2768 | 12000000 | 0.043237
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 152736.0495 | 1.2728 | 12000000 | 0.034344
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 152046.7152 | 1.2671 | 12000000 | 0.034561
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 151657.2032 | 1.2638 | 12000000 | 0.034942
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 149205.0446 | 1.2434 | 12000000 | 0.047866
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 149081.5242 | 1.2423 | 12000000 | 0.034942
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 147053.7189 | 1.2254 | 12000000 | 0.026779
GEN-2024-083 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 146634.0424 | 0.81013 | 18100000 | 0.0099292
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 117642.911 | 0.98036 | 12000000 | 0.034561
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 108715.4102 | 1.6472 | 6600000 | 0.045686
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 99143.7059 | 0.85029 | 11660000 | 0.038753
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 98990.9382 | 1.8678 | 5300000 | 0.043237
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 96697.4215 | 1.4651 | 6600000 | 0.047866
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505602 S BROWN4 138 769060 G22-104-TAP 138 1 | Current Study | 1.62 | (717.00, 717.00) | 92316.1471 | 4.7488 | 1944000 | 0.039715
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 90777.733 | 2.7932 | 3250000 | 0.045686
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 90777.733 | 2.7932 | 3250000 | 0.045686
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 90526.4881 | 1.708 | 5300000 | 0.034344
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 89630.1602 | 3.897 | 2300000 | 0.21972
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 86859.4121 | 1.6389 | 5300000 | 0.034344
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 86543.0088 | 1.3113 | 6600000 | 0.034561
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 86543.0088 | 1.3113 | 6600000 | 0.034561
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 83460.3411 | 1.5747 | 5300000 | 0.038753
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 80960.4703 | 1.2267 | 6600000 | 0.038753
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 79250.2621 | 1.4953 | 5300000 | 0.057362
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 73773.6763 | 2.27 | 3250000 | 0.034561
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 73773.6763 | 2.27 | 3250000 | 0.034561
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 72632.8926 | 0.48623 | 14938000 | 0.041431
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 72291.7586 | 1.364 | 5300000 | 0.034561
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 70313.3523 | 0.48623 | 14460953.1406 | 0.041431
GEN-2024-083 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 64517.7561 | 1.2173 | 5300000 | 0.16628
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 63285.2188 | 0.39084 | 16192000 | 0.035058
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 60138.9877 | 4.3579 | 1380000 | 0.16984
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 59964.8928 | 1.8451 | 3250000 | 0.034561
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 56221.8771 | 1.0608 | 5300000 | 0.045686
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 54941.5584 | 1.6905 | 3250000 | 0.045686
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 54332.7971 | 1.0251 | 5300000 | 0.038753
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 53622.5488 | 1.6499 | 3250000 | 0.034561
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 53512.967 | 1.6466 | 3250000 | 0.045686
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 52558.9384 | 0.99168 | 5300000 | 0.022568
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 52078.7178 | 1.4795 | 3520000 | 0.047866
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 51007.9481 | 1.7174 | 2970000 | 0.055647
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 50574.9774 | 2.0791 | 2432500 | 0.034344
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 49896.6417 | 3.6157 | 1380000 | 0.043023
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 48084.0482 | 1.4795 | 3250000 | 0.047866
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 45923.8181 | 1.413 | 3250000 | 0.034561
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 45518.7155 | 1.4006 | 3250000 | 0.034561
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 45515.8968 | 1.4005 | 3250000 | 0.034561
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 44329.852 | 1.364 | 3250000 | 0.034561
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 43342.1951 | 1.9701 | 2200000 | 0.027793
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 43105.5656 | 1.3263 | 3250000 | 0.047866
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CHILD4WT 138 kV | Current Study |  |  | 43099.8272 | 1.7718 | 2432500 | 0.073115
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 38134.7349 | 1.1734 | 3250000 | 0.034561
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 37783.6653 | 1.7174 | 2200000 | 0.055647
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 35333.2033 | 0.66666 | 5300000 | 0.0039645
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 34754.6876 | 1.0694 | 3250000 | 0.038753
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 34449.7173 | 2.4964 | 1380000 | 0.045686
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 28376.3511 | 1.1666 | 2432500 | 0.042327
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 26929.5838 | 2.0401 | 1320000 | 0.034344
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 26147.1888 | 1.0749 | 2432500 | 0.038753
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 25784.707 | 1.06 | 2432500 | 0.038753
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 25160.2383 | 1.8232 | 1380000 | 0.034561
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 21247.8648 | 1.5397 | 1380000 | 0.043023
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 | Current Study | 0.55 | (395.00, 395.00) | 20816.7536 | 3.1541 | 660000 | 0.02492
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 20699.5262 | 1.5 | 1380000 | 0.034561
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 18948.7373 | 0.85644 | 2212500 | 0.034625
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 18371.7086 | 0.83036 | 2212500 | 0.034625
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 17046.4742 | 1.2353 | 1380000 | 0.038753
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 16164.9863 | 0.305 | 5300000 | 0.034942
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 9094.5875 | 0.41105 | 2212500 | 0.035058
GEN-2024-083 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 6448.9014 | 0.39084 | 1650000 | 0.035058
GEN-2024-084 | 03 CENTRAL | TBD | ERIS | Rebuild line 547473 RDS295 5 161 779490 G24-084-TAP 161 1 | Current Study | 18.76 | (246.00, 246.00) | 28140000 | 100 | 28140000 | 0.38865
GEN-2024-084 | 03 CENTRAL | TBD | ERIS | Rebuild line 547468 AUR124 5 161 779490 G24-084-TAP 161 1 | Current Study | 4.95 | (246.00, 246.00) | 7425000 | 100 | 7425000 | 0.61135
GEN-2024-084 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 1280094.9854 | 0.13641 | 938400000 | 0.024525
GEN-2024-084 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 181652.9746 | 0.091508 | 198511000 | 0.0037043
GEN-2024-084 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 60938.7915 | 1.1498 | 5300000 | 0.058553
GEN-2024-084 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 25949.1732 | 0.13951 | 18600000 | 0.029304
GEN-2024-084 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 25949.1732 | 0.13951 | 18600000 | 0.029304
GEN-2024-084 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 19782.4781 | 0.10636 | 18600000 | 0.024525
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Rebuild line 530582 S HAYS6 230 539679 GRTBEND6 230 1 | Current Study | 39.2 | (386.00, 386.00) | 23036819.5488 | 30.9302 | 74480000 | 0.25926
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Rebuild line 539678 GRTBEND3 115 539684 OTISSUB3 115 1 | Current Study | 20.83 | (176.00, 176.00) | 20830000 | 100 | 20830000 | 1
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 11612676.165 | 1.2354 | 940000000 | 0.021819
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Rebuild line 539642 ELLSWTP3 115 539678 GRTBEND3 115 1 | Current Study | 30.21 | (115.00, 115.00) | 11430172.0593 | 37.8357 | 30210000 | 0.096601
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Rebuild line 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 | Current Study | 21.74 | (386.00, 386.00) | 5827159.2069 | 14.1073 | 41306000 | 0.096539
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 5137256.437 | 2.5879 | 198511000 | 0.10934
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Rebuild line 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | Current Study | 84.86 | (1793.00, 1793.00) | 3315625.7976 | 1.776 | 186692000 | 0.038716
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1952865.3241 | 0.98376 | 198511000 | 0.065733
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Rebuild line 530618 HUNTSVL3 115 530624 ST JOHN3 115 1 | Current Study | 26.5 | (297.00, 297.00) | 1925878.1798 | 7.2675 | 26500000 | 0.063821
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1792930.9062 | 1.2469 | 143796000 | 0.077845
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1741816.9654 | 0.79783 | 218320000 | 0.030773
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add 21 MVAR switched shunt at RUSLSOL3 115 kV | Current Study |  |  | 1587853.044 | 71.7674 | 2212500 | 0.04557
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Current Study | 26.47 | (1793.00, 1793.00) | 1490750.5392 | 2.5599 | 58234000 | 0.054789
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | Current Study | 19.2 | (2390.00, 2390.00) | 1444576.2233 | 3.4199 | 42240000 | 0.10923
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Rebuild line 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Current Study | 38.26 | (1793.00, 1793.00) | 1377561.361 | 1.6366 | 84172000 | 0.049482
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Rebuild line 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Current Study | 37.4 | (1793.00, 1793.00) | 1361471.657 | 1.6547 | 82280000 | 0.049482
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 1315027.7664 | 0.14014 | 938400000 | 0.026297
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | Current Study | 16.04 | (2390.00, 2390.00) | 1206823.0532 | 3.4199 | 35288000 | 0.10923
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 915923.5218 | 0.46291 | 197860000 | 0.028598
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Rebuild line 530618 HUNTSVL3 115 530724 CENTENNIAL3 115 1 | Current Study | 12.45 | (297.00, 297.00) | 904799.3712 | 7.2675 | 12450000 | 0.063821
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Rebuild line 530724 CENTENNIAL3 115 533412 ARKVALJ3 115 1 | Current Study | 10.96 | (297.00, 297.00) | 796514.1453 | 7.2675 | 10960000 | 0.063821
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | Current Study | 13 | (2390.00, 2390.00) | 786776.0226 | 2.751 | 28600000 | 0.10873
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Rebuild line 539649 SAWYER 3 115 539760 BARBER 3 115 1 | Current Study | 19 | (598.00, 598.00) | 741358.3088 | 3.9019 | 19000000 | 0.074856
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Rebuild line 533413 CIRCLE 3 115 533416 RENO 3 115 2 | Current Study | 5.95 | (217.00, 217.00) | 729083.0109 | 12.2535 | 5950000 | 0.087479
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Rebuild line 523961 POTTER_CO 7 345 784950 G24-266_TAP 345 1 | Current Study | 18.24 | (1793.00, 1793.00) | 703807.8697 | 1.7539 | 40128000 | 0.038716
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 697508.1916 | 0.42257 | 165062000 | 0.033235
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 567136.9582 | 1.0609 | 53460000 | 0.047866
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | Current Study | 19.87 | (1793.00, 1793.00) | 501462.8922 | 1.1471 | 43714000 | 0.024488
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Rebuild line 539638 FLATRDG4 138 539674 BARBER 4 138 1 | Current Study | 8.92 | (472.00, 472.00) | 473431.2836 | 4.4229 | 10704000 | 0.076395
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | Current Study | 16.71 | (1793.00, 1793.00) | 461533.8036 | 1.2555 | 36762000 | 0.043925
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 539674 BARBER 4 138 539760 BARBER 3 115 539917 BARBER-1 13 M2 | Current Study |  | (324.00, 324.00) | 459985.552 | 4.4229 | 10400000 | 0.038198
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR SVC at GEN-2021-076 345 kV | Current Study |  |  | 393701.2067 | 3.2808 | 12000000 | 0.049482
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Rebuild line 533412 ARKVALJ3 115 533413 CIRCLE 3 115 1 | Current Study | 5.2 | (297.00, 297.00) | 377908.1711 | 7.2675 | 5200000 | 0.063821
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 330002.3502 | 0.71874 | 45914000 | 0.045418
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 180101.9056 | 0.71874 | 25058000 | 0.045418
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add 525 MVAR SVC at SD.LS-LR-MB3 345 kV | Current Study |  |  | 153149.3354 | 1.2762 | 12000000 | 0.063226
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 145664.619 | 0.97513 | 14938000 | 0.12983
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 141012.8015 | 0.97513 | 14460953.1406 | 0.12983
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 136920.7112 | 2.5834 | 5300000 | 0.11068
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 134495.0195 | 2.5376 | 5300000 | 0.11068
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 131466.4082 | 1.0956 | 12000000 | 0.19052
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add 7 MVAR switched shunt at G19-030-TAP 345 kV | Current Study |  |  | 117944.528 | 2.2254 | 5300000 | 0.10923
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add 63 MVAR switched shunt at SADLHRN3 115 kV | Current Study |  |  | 86340.2493 | 3.9024 | 2212500 | 0.074866
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add 21 MVAR switched shunt at LARNED3 115 kV | Current Study |  |  | 86329.6155 | 3.9019 | 2212500 | 0.074856
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add 45 MVAR switched shunt at HUNTSVL3 115 kV | Current Study |  |  | 86324.2561 | 3.9017 | 2212500 | 0.074856
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add 66 MVAR switched shunt at GEN-2021-021 345 kV | Current Study |  |  | 85903.0079 | 1.6208 | 5300000 | 0.0010502
GEN-2024-085 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 79117.7943 | 1.4928 | 5300000 | 0.079346
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 65240.1239 | 0.40292 | 16192000 | 0.05647
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MINGO 7 345 kV | Current Study |  |  | 62258.0319 | 1.1747 | 5300000 | 0.056471
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR switched shunt at GEN-2022-075 345 kV | Current Study |  |  | 43523.0236 | 0.82119 | 5300000 | 0.032978
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 42183.9694 | 0.2268 | 18600000 | 0.049722
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 42183.9694 | 0.2268 | 18600000 | 0.049722
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 34092.5167 | 1.5409 | 2212500 | 0.061916
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add 248 MVAR switched shunt at GEN-2022-015 345 kV | Current Study |  |  | 33476.4463 | 0.63163 | 5300000 | 0.056471
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 27260.007 | 0.51434 | 5300000 | 0.056471
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add 12 MVAR switched shunt at BEELER 3 115 kV | Current Study |  |  | 26930.1879 | 1.2172 | 2212500 | 0.056471
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 26799.2031 | 0.14408 | 18600000 | 0.034677
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at IRS7 115 KV 115 kV | Current Study |  |  | 18168.8094 | 0.82119 | 2212500 | 0.032978
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add 0.8 MVAR switched shunt at HARBNGR7 345 kV | Current Study |  |  | 18093.4473 | 0.34139 | 5300000 | 0.044287
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MED-LDG3 115 kV | Current Study |  |  | 16948.1939 | 0.76602 | 2212500 | 0.032978
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add 40 MVAR switched shunt at SEGNTP 3 115 kV | Current Study |  |  | 12012.0337 | 0.54292 | 2212500 | 0.056471
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 11550.27 | 0.52205 | 2212500 | 0.032978
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 11198.5401 | 0.50615 | 2212500 | 0.032978
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 9375.5534 | 0.42375 | 2212500 | 0.056471
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add 0.04 MVAR switched shunt at ELLIS 2 69 kV | Current Study |  |  | 7999.138 | 0.57965 | 1380000 | 0.063226
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Rebuild line 530624 ST JOHN3 115 539696 ST-JOHN3 115 Z1 | Current Study | 0.1 | (326.00, 326.00) | 7267.4648 | 7.2675 | 100000 | 0.063821
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 6648.1105 | 0.40292 | 1650000 | 0.05647
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 3127.6521 | 0.14136 | 2212500 | 0.01835
GEN-2024-085 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 226.8743 | 0.01375 | 1650000 | 0.0010419
GEN-2024-088 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 47368.8092 | 0.89375 | 5300000 | 0.05242
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 17221597.414 | 1.3401 | 1285130000 | 0.21657
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 16567979.7266 | 1.3029 | 1271630000 | 0.1376
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3 | Current Study | 39.39 | (478.00, 544.00) | 15415525.761 | 14.5877 | 105675000 | 0.25567
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 15066542.0826 | 0.99474 | 1514620000 | 0.031374
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 13733955.358 | 1.4636 | 938400000 | 0.12733
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 13443499.8048 | 3.6681 | 366500000 | 0.12364
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 12457335.2055 | 1.1602 | 1073760000 | 0.10191
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 11672637.6801 | 1.2439 | 938400000 | 0.19152
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 9970701.5433 | 1.3757 | 724760000 | 0.16736
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Current Study | 54.58 | (637.00, 637.00) | 9860772.5508 | 9.5088 | 103702000 | 0.11323
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 5904050.4857 | 1.2228 | 482840000 | 0.15936
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 5672334.8725 | 1.2086 | 469340000 | 0.10585
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add 2 MVAR switched shunt at GEN-2024-080 230 kV | Current Study |  |  | 3825000 | 100 | 3825000 | 0.12741
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524662 PARMER_CO 3 115 524668 DS-#20 +3 115 1 | Current Study | 7.6 | (176.00, 176.00) | 3386299.1626 | 44.5566 | 7600000 | 0.058119
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1 | Current Study | 52.45 | (1046.00, 1046.00) | 3003931.7654 | 3.0143 | 99655000 | 0.10202
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add 18 MVAR switched shunt at DEAFSMITH 6 230 kV | Current Study |  |  | 1855866.8788 | 48.5194 | 3825000 | 0.077662
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1535189.3867 | 1.8168 | 84500000 | 0.057211
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 1327416.8033 | 0.67089 | 197860000 | 0.034007
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 1178264.5267 | 1.3944 | 84500000 | 0.090912
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1162487.2791 | 1.3757 | 84500000 | 0.16736
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1141666.3367 | 0.57511 | 198511000 | 0.031531
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 1137380.2537 | 2.0597 | 55220000 | 0.10304
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1 | Current Study | 9.6 | (901.00, 901.00) | 1011179.8804 | 5.5437 | 18240000 | 0.19044
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 992323.5011 | 0.79498 | 124824000 | 0.053343
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 961196.0506 | 0.58232 | 165062000 | 0.037579
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527597 TWEEDY 3 115 527798 EDDY_NTH 3 115 1 | Current Study | 44.83 | (394.00, 394.00) | 833548.2623 | 1.8594 | 44830000 | 0.018336
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524623 DEAFSMITH 6 230 525520 OLSON 6 230 1 | Current Study | 11 | (519.00, 519.00) | 819122.3299 | 3.9192 | 20900000 | 0.040858
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1 | Current Study | 18.95 | (901.00, 901.00) | 781957.6539 | 2.1718 | 36005000 | 0.065058
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 698945.0213 | 2.7958 | 25000000 | 0.048639
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 698945.0213 | 2.7958 | 25000000 | 0.042387
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 692083.4016 | 0.84931 | 81488000 | 0.057839
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add line 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 P2 | Current Study | 2.51 | (478.00, 478.00) | 637714.9467 | 4.7326 | 13475000 | 0.055601
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524648 CARGILL 3 115 524655 FRIONA 3 115 1 | Current Study | 1.27 | (115.00, 115.00) | 565868.4127 | 44.5566 | 1270000 | 0.058119
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 493554.7774 | 1.1353 | 43472000 | 0.035489
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 524872 OASIS_TR1 1 13 524874 OASIS 3 115 524875 OASIS 6 230 M2 | Current Study |  | (239.00, 239.00) | 316938.0939 | 2.2967 | 13800000 | 0.0060908
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 300884.842 | 1.6177 | 18600000 | 0.16627
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 258894.239 | 0.97696 | 26500000 | 0.015748
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 255884.7739 | 1.3757 | 18600000 | 0.16736
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 249094.9013 | 1.3392 | 18600000 | 0.21657
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 242230.8302 | 1.3023 | 18600000 | 0.1376
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 238868.4124 | 1.2842 | 18600000 | 0.1376
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 224795.3054 | 1.2086 | 18600000 | 0.10585
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 198031.1176 | 1.0647 | 18600000 | 0.19152
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 198031.1176 | 1.0647 | 18600000 | 0.19152
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 185021.7762 | 0.99474 | 18600000 | 0.031374
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 180387.9415 | 0.96983 | 18600000 | 0.19152
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 173805.0245 | 0.93444 | 18600000 | 0.12733
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add 0.7 MVAR switched shunt at GEN-2024-161 138 kV | Current Study |  |  | 169441.0833 | 6.9657 | 2432500 | 0.033908
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add 18 MVAR switched shunt at FALCNRD4 138 kV | Current Study |  |  | 166553.8193 | 6.847 | 2432500 | 0.052576
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 95372.1593 | 1.4547 | 6556000 | 0.10304
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add 0.7 MVAR switched shunt at ROSEVLT2 69 kV | Current Study |  |  | 94488.9088 | 6.847 | 1380000 | 0.052576
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 93855.5756 | 0.57964 | 16192000 | 0.066658
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 82480.3806 | 0.55215 | 14938000 | 0.060318
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 79846.3596 | 0.55215 | 14460953.1406 | 0.060318
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-161-TAP 138 kV | Current Study |  |  | 74426.9832 | 3.0597 | 2432500 | 0.033908
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 56058.2758 | 0.46715 | 12000000 | 0.066658
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | Current Study | 0.78 | (598.00, 598.00) | 53925.246 | 1.019 | 5292000 | 0.014763
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1 | Current Study | 2.49 | (394.00, 394.00) | 46297.9071 | 1.8594 | 2490000 | 0.018336
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | Current Study | 0.2 | (598.00, 598.00) | 45651.0019 | 1.019 | 4480000 | 0.014763
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 34968.8409 | 1.5805 | 2212500 | 0.066658
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 13487.746 | 0.60962 | 2212500 | 0.066658
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add 0.5 MVAR switched shunt at RKY_RDG4 138 kV | Current Study |  |  | 12971.1655 | 0.53324 | 2432500 | 0.033908
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 9564.0872 | 0.57964 | 1650000 | 0.066658
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 7221.9445 | 0.13626 | 5300000 | 0.020014
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 6235.6355 | 0.28184 | 2212500 | 0.030018
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 5717.9048 | 0.41434 | 1380000 | 0.066658
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 3957.0574 | 0.28674 | 1380000 | 0.030018
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 2793.5617 | 0.20243 | 1380000 | 0.018395
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 805.843 | 0.058394 | 1380000 | 0.0004285
GEN-2024-089 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 177.3023 | 0.012848 | 1380000 | 0.0013744
GEN-2024-090 | 03 CENTRAL | TBD | ERIS | Rebuild line 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 | Current Study | 7.49 | (364.00, 364.00) | 3210000 | 28.5714 | 11235000 | 0.18905
GEN-2024-090 | 03 CENTRAL | TBD | ERIS | Rebuild line 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | Current Study | 17.54 | (1793.00, 1793.00) | 1378447.9335 | 3.5722 | 38588000 | 0.034329
GEN-2024-090 | 03 CENTRAL | TBD | ERIS | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | Current Study | 2.29 | (446.00, 446.00) | 981428.5714 | 28.5714 | 3435000 | 0.81095
GEN-2024-090 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 959792.6039 | 0.10228 | 938400000 | 0.030709
GEN-2024-090 | 03 CENTRAL | TBD | ERIS | Rebuild line 645458 S3458 3 345 778170 G24-040-TAP 345 1 | Current Study | 13.15 | (1793.00, 1793.00) | 739213.6466 | 2.5552 | 28930000 | 0.079244
GEN-2024-090 | 03 CENTRAL | TBD | ERIS | Rebuild line 640139 COOPER 3 345 778170 G24-040-TAP 345 1 | Current Study | 12.59 | (1793.00, 1793.00) | 707733.8259 | 2.5552 | 27698000 | 0.079244
GEN-2024-090 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 641829.4309 | 0.32332 | 198511000 | 0.021858
GEN-2024-090 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 382011.4969 | 0.40646 | 93984000 | 0.050443
GEN-2024-090 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 372775.4941 | 0.25924 | 143796000 | 0.025896
GEN-2024-090 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 121972.2084 | 0.26565 | 45914000 | 0.026859
GEN-2024-090 | 03 CENTRAL | TBD | ERIS | Rebuild line 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 | Current Study | 3.23 | (1793.00, 1793.00) | 115316.9811 | 1.6228 | 7106000 | 0.036585
GEN-2024-090 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 66567.487 | 0.26565 | 25058000 | 0.026859
GEN-2024-090 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 51620.6813 | 0.44272 | 11660000 | 0.050443
GEN-2024-090 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 25669.1326 | 0.13801 | 18600000 | 0.048409
GEN-2024-090 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 25669.1326 | 0.13801 | 18600000 | 0.048409
GEN-2024-090 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 16507.8818 | 0.11051 | 14938000 | 0.023541
GEN-2024-090 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 15980.7006 | 0.11051 | 14460953.1406 | 0.023541
GEN-2024-090 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 14832.5526 | 0.079745 | 18600000 | 0.030709
GEN-2024-090 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 5992.5564 | 0.36319 | 1650000 | 0.044034
GEN-2024-091 | 03 CENTRAL | TBD | NRIS | Add 3-winding transformer 505487 CRG X1 1 13 505488 CARTHAG5 161 505490 CARTHG 2 69 M2 | Current Study |  | (84.00, 84.00) | 1864437.8296 | 17.7989 | 10475000 | 0.012993
GEN-2024-091 | 03 CENTRAL | TBD | NRIS | Add 3-winding transformer 505488 CARTHAG5 161 505489 CRG X2 1 13 505490 CARTHG 2 69 M2 | Current Study |  | (84.00, 84.00) | 1864437.8296 | 17.7989 | 10475000 | 0.012743
GEN-2024-091 | 03 CENTRAL | TBD | ERIS | Rebuild line 547554 BAX492 2 69 547601 HOC404 2 69 1 | Current Study | 3.59 | (106.00, 106.00) | 1273813.8795 | 41.7439 | 3051500 | 0.022823
GEN-2024-091 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 784148.7169 | 0.083562 | 938400000 | 0.025089
GEN-2024-091 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 482641.405 | 0.51354 | 93984000 | 0.063731
GEN-2024-091 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 156396.8647 | 0.078785 | 198511000 | 0.0053261
GEN-2024-091 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 65218.6606 | 0.55934 | 11660000 | 0.063731
GEN-2024-091 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 38283.8308 | 0.72234 | 5300000 | 0.061431
GEN-2024-091 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 16244.9502 | 0.087338 | 18600000 | 0.030636
GEN-2024-091 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 16244.9502 | 0.087338 | 18600000 | 0.030636
GEN-2024-091 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 12118.167 | 0.065151 | 18600000 | 0.025089
GEN-2024-091 | 03 CENTRAL | TBD | ERIS | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1 | Current Study | 4.14 | (551.00, 551.00) | 4301.0881 | 0.069261 | 6210000 | 0.00077632
GEN-2024-091 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 2546.6583 | 0.15434 | 1650000 | 0.018713
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 24153031.201 | 1.5947 | 1514620000 | 0.049161
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 20015212.3887 | 1.5574 | 1285130000 | 0.24602
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 19494040.3733 | 1.533 | 1271630000 | 0.15825
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 15079399.2929 | 1.6069 | 938400000 | 0.13665
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3 | Current Study | 39.39 | (478.00, 544.00) | 15078701.6998 | 14.2689 | 105675000 | 0.24444
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 13465862.9144 | 3.6742 | 366500000 | 0.12105
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 13423338.1082 | 1.2501 | 1073760000 | 0.10734
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 12902198.4177 | 1.3749 | 938400000 | 0.20692
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 11171290.6066 | 1.5414 | 724760000 | 0.18328
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Current Study | 54.58 | (637.00, 637.00) | 9732446.1451 | 9.385 | 103702000 | 0.10924
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 7559072.2348 | 1.5655 | 482840000 | 0.19943
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 7270741.7784 | 1.5491 | 469340000 | 0.13262
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524662 PARMER_CO 3 115 524668 DS-#20 +3 115 1 | Current Study | 7.6 | (176.00, 176.00) | 4213700.8374 | 55.4434 | 7600000 | 0.070688
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1 | Current Study | 52.45 | (1046.00, 1046.00) | 3238865.845 | 3.2501 | 99655000 | 0.10752
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524863 FE-CHZPLT 3 115 524874 OASIS 3 115 1 | Current Study | 7.8 | (176.00, 176.00) | 2238917.0303 | 28.7041 | 7800000 | 0.069937
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524764 NORRIS_TP 3 115 524863 FE-CHZPLT 3 115 1 | Current Study | 7.62 | (176.00, 176.00) | 2187249.7143 | 28.7041 | 7620000 | 0.069937
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1 | Current Study | 9.6 | (901.00, 901.00) | 1709993.136 | 9.375 | 18240000 | 0.31479
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 1375757.4746 | 0.69532 | 197860000 | 0.03445
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 1325822.6348 | 2.401 | 55220000 | 0.1174
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 1320210.7613 | 1.5624 | 84500000 | 0.099566
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1302464.3417 | 1.5414 | 84500000 | 0.18328
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1279184.6869 | 1.5138 | 84500000 | 0.046596
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1246403.9761 | 0.99853 | 124824000 | 0.06549
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1190224.8989 | 0.59958 | 198511000 | 0.032131
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 986020.4835 | 0.59736 | 165062000 | 0.03768
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527597 TWEEDY 3 115 527798 EDDY_NTH 3 115 1 | Current Study | 44.83 | (394.00, 394.00) | 893458.7105 | 1.993 | 44830000 | 0.019211
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 861877.4952 | 1.0577 | 81488000 | 0.070405
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1 | Current Study | 18.95 | (901.00, 901.00) | 837076.3735 | 2.3249 | 36005000 | 0.068073
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 802311.9241 | 3.2092 | 25000000 | 0.054573
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 802311.9241 | 3.2092 | 25000000 | 0.047558
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524648 CARGILL 3 115 524655 FRIONA 3 115 1 | Current Study | 1.27 | (115.00, 115.00) | 704131.5873 | 55.4434 | 1270000 | 0.070688
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524623 DEAFSMITH 6 230 525520 OLSON 6 230 1 | Current Study | 11 | (519.00, 519.00) | 696827.0757 | 3.3341 | 20900000 | 0.033974
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 690541.0285 | 1.5885 | 43472000 | 0.048534
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add line 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 P2 | Current Study | 2.51 | (478.00, 478.00) | 669948.0042 | 4.9718 | 13475000 | 0.057094
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 296606.6606 | 1.5947 | 18600000 | 0.049161
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 289502.0267 | 1.5565 | 18600000 | 0.24602
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 288140.3611 | 1.5491 | 18600000 | 0.13262
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 286696.293 | 1.5414 | 18600000 | 0.18328
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 285011.0672 | 1.5323 | 18600000 | 0.15825
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 281054.8149 | 1.511 | 18600000 | 0.15825
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 273800.1138 | 1.0332 | 26500000 | 0.016279
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 252995.6933 | 1.3602 | 18600000 | 0.13665
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 218891.1231 | 1.1768 | 18600000 | 0.20692
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 218891.1231 | 1.1768 | 18600000 | 0.20692
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 199389.4677 | 1.072 | 18600000 | 0.20692
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 190831.7957 | 1.026 | 18600000 | 0.13665
GEN-2024-092 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 123614.1215 | 0.68295 | 18100000 | 0.010489
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 111173.521 | 1.6958 | 6556000 | 0.1174
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 97295.5737 | 0.60089 | 16192000 | 0.067542
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 86028.8907 | 0.57591 | 14938000 | 0.061494
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 83281.5476 | 0.57591 | 14460953.1406 | 0.061494
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 73513.3369 | 1.387 | 5300000 | 0.19913
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | Current Study | 0.78 | (598.00, 598.00) | 57174.5919 | 1.0804 | 5292000 | 0.015299
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1 | Current Study | 2.49 | (394.00, 394.00) | 49625.5228 | 1.993 | 2490000 | 0.019211
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | Current Study | 0.2 | (598.00, 598.00) | 48401.7709 | 1.0804 | 4480000 | 0.015299
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 36250.559 | 1.6384 | 2212500 | 0.067542
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 27248.8095 | 0.22707 | 12000000 | 0.03167
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 26280.6607 | 1.9044 | 1380000 | 0.19913
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 24271.413 | 1.7588 | 1380000 | 0.15622
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 17475.7318 | 1.2664 | 1380000 | 0.19913
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 14727.68 | 1.0672 | 1380000 | 0.0076547
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 13982.1144 | 0.63196 | 2212500 | 0.067542
GEN-2024-092 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 11353.6977 | 0.82273 | 1380000 | 0.052208
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 9914.6305 | 0.60089 | 1650000 | 0.067542
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 6730.7341 | 0.30421 | 2212500 | 0.03167
GEN-2024-092 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 4271.2409 | 0.30951 | 1380000 | 0.03167
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 35984271.7943 | 2.3758 | 1514620000 | 0.048706
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 28727188.2374 | 2.2354 | 1285130000 | 0.23482
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 28306260.4185 | 2.226 | 1271630000 | 0.15281
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 22904318.0534 | 2.4408 | 938400000 | 0.13803
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 20304317.3199 | 2.1637 | 938400000 | 0.21655
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 16701556.7654 | 2.3044 | 724760000 | 0.18222
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 12879950.5112 | 1.1995 | 1073760000 | 0.068491
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 11070426.5681 | 2.2928 | 482840000 | 0.19423
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 10693368.8227 | 2.2784 | 469340000 | 0.12971
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 9341703.0851 | 2.5489 | 366500000 | 0.055845
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 2465277.8026 | 4.4645 | 55220000 | 0.14517
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 2154961.3543 | 1.0891 | 197860000 | 0.035885
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 1967394.4149 | 2.3283 | 84500000 | 0.098669
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1947239.8403 | 2.3044 | 84500000 | 0.18222
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1856931.5464 | 1.4876 | 124824000 | 0.064883
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1805248.4369 | 0.90939 | 198511000 | 0.032408
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 1718794.347 | 6.8752 | 25000000 | 0.077746
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 1718794.347 | 6.8752 | 25000000 | 0.067753
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1675808.6709 | 1.9832 | 84500000 | 0.040594
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 1540324.5035 | 0.93318 | 165062000 | 0.039143
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523095 HITCHLAND 6 230 778320 G24-045-TAP 230 1 | Current Study | 37.8 | (772.00, 772.00) | 1506811.1849 | 2.098 | 71820000 | 0.036178
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 1282177.4221 | 1.5735 | 81488000 | 0.069651
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 1047189.8646 | 2.4089 | 43472000 | 0.048944
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1 | Current Study | 18.95 | (901.00, 901.00) | 855415.8929 | 2.3758 | 36005000 | 0.046261
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523091 HITCHLD_TR01 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2 | Current Study |  | (560.00, 644.00) | 567855.1359 | 2.2714 | 25000000 | 0.014608
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523094 HITCHLD_TR21 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2 | Current Study |  | (560.00, 644.00) | 567855.1359 | 2.2714 | 25000000 | 0.016793
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 441897.9383 | 2.3758 | 18600000 | 0.048706
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 428623.2075 | 2.3044 | 18600000 | 0.18222
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 423779.4778 | 2.2784 | 18600000 | 0.12971
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 415512.9136 | 2.2339 | 18600000 | 0.23482
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 413849.4297 | 2.225 | 18600000 | 0.15281
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 408104.7659 | 2.1941 | 18600000 | 0.15281
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 384278.8239 | 2.066 | 18600000 | 0.13803
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 344471.1265 | 1.852 | 18600000 | 0.21655
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 344471.1265 | 1.852 | 18600000 | 0.21655
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 313781.1783 | 1.687 | 18600000 | 0.21655
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 289857.1792 | 1.5584 | 18600000 | 0.13803
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 206719.667 | 3.1531 | 6556000 | 0.14517
GEN-2024-099 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 183480.6384 | 1.0137 | 18100000 | 0.010354
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 152891.9933 | 0.94424 | 16192000 | 0.070581
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 130618.2236 | 0.8744 | 14938000 | 0.062089
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 126446.9146 | 0.8744 | 14460953.1406 | 0.062089
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 109550.4849 | 2.067 | 5300000 | 0.19734
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 56964.7687 | 2.5747 | 2212500 | 0.070581
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 41954.9008 | 0.34962 | 12000000 | 0.032427
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 39163.7659 | 2.838 | 1380000 | 0.19734
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 35256.352 | 2.5548 | 1380000 | 0.1509
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 29629.4659 | 2.1471 | 1380000 | 0.010241
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 26042.552 | 1.8871 | 1380000 | 0.19734
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 21971.7415 | 0.99307 | 2212500 | 0.070581
GEN-2024-099 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 17825.7407 | 1.2917 | 1380000 | 0.054509
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 15580.0265 | 0.94424 | 1650000 | 0.070581
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 10363.2888 | 0.4684 | 2212500 | 0.032427
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 6576.4152 | 0.47655 | 1380000 | 0.032427
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add line 659131 LARAMIE_-MB3 345 800120 UNDERWOOD 2 345 P2 | Current Study | 206.4 | (1792.00, 1792.00) | 112386619.7564 | 17.2945 | 649840000 | 0.024659
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 102352254.9182 | 10.8885 | 940000000 | 0.076829
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add line 652424 BELFELD3 345 800121 MAURINE 2 345 P2 | Current Study | 154.2 | (1792.00, 1792.00) | 97881684.2055 | 20.0569 | 488020000 | 0.020603
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add line 652424 BELFELD3 345 659183 CHARL_CK-BE3 345 P2 | Current Study | 40.74 | (531.00, 531.00) | 32500722.14 | 23.846 | 136294000 | 0.019527
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Rebuild line 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | Current Study | 84.86 | (1793.00, 1793.00) | 21275165.6601 | 11.3959 | 186692000 | 0.099247
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 13365024.1691 | 6.7326 | 198511000 | 0.11364
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 11302982.8332 | 5.7126 | 197860000 | 0.14099
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Rebuild line 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Current Study | 38.26 | (1793.00, 1793.00) | 8209320.9174 | 9.753 | 84172000 | 0.1178
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Rebuild line 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Current Study | 37.4 | (1793.00, 1793.00) | 8113437.3165 | 9.8608 | 82280000 | 0.1178
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 7572983.57 | 4.588 | 165062000 | 0.14415
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | Current Study | 21.05 | (1793.00, 1793.00) | 6077709.8008 | 13.124 | 46310000 | 0.17362
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Rebuild line 523961 POTTER_CO 7 345 784950 G24-266_TAP 345 1 | Current Study | 18.24 | (1793.00, 1793.00) | 4516079.2967 | 11.2542 | 40128000 | 0.099247
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | Current Study | 19.2 | (2390.00, 2390.00) | 4222239.5572 | 9.9958 | 42240000 | 0.12755
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 4016476.3718 | 2.0233 | 198511000 | 0.05401
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | Current Study | 16.04 | (2390.00, 2390.00) | 3527329.2967 | 9.9958 | 35288000 | 0.12755
GEN-2024-102 | 03 CENTRAL | TBD | NRIS | Add 78 MVAR SVC at STEGALL_-MB3 345 kV | Current Study |  |  | 2835588.3259 | 23.6299 | 12000000 | 0.030966
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | Current Study | 13 | (2390.00, 2390.00) | 2299606.4809 | 8.0406 | 28600000 | 0.12696
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add 525 MVAR SVC at SD.LS-LR-MB3 345 kV | Current Study |  |  | 1702034.8427 | 14.1836 | 12000000 | 0.28072
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add 5 MVAR switched shunt at SLKHILLS 4 138 kV | Current Study |  |  | 1295633.2958 | 53.2634 | 2432500 | 1
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 942479.2711 | 2.0527 | 45914000 | 0.05182
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 861250.507 | 0.091779 | 938400000 | 0.0068803
GEN-2024-102 | 03 CENTRAL | TBD | NRIS | Add 0.7 MVAR switched shunt at STEGALL_-MB4 230 kV | Current Study |  |  | 859361.809 | 22.467 | 3825000 | 0.046207
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 811790.0549 | 5.0135 | 16192000 | 0.28072
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add 0.5 MVAR switched shunt at RKY_RDG4 138 kV | Current Study |  |  | 785670.8945 | 32.2989 | 2432500 | 1
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MINGO 7 345 kV | Current Study |  |  | 774678.4367 | 14.6166 | 5300000 | 0.28072
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 514366.9812 | 2.0527 | 25058000 | 0.05182
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 484867.8066 | 4.0406 | 12000000 | 0.28072
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR switched shunt at GEN-2022-075 345 kV | Current Study |  |  | 477995.1485 | 9.0188 | 5300000 | 0.14469
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add 248 MVAR switched shunt at GEN-2022-015 345 kV | Current Study |  |  | 416548.3602 | 7.8594 | 5300000 | 0.28072
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add 7 MVAR switched shunt at G19-030-TAP 345 kV | Current Study |  |  | 391071.2307 | 7.3787 | 5300000 | 0.14469
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 339197.0315 | 6.3999 | 5300000 | 0.28072
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add 12 MVAR switched shunt at BEELER 3 115 kV | Current Study |  |  | 335093.0832 | 15.1455 | 2212500 | 0.28072
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 304179.794 | 2.0363 | 14938000 | 0.10831
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 294465.775 | 2.0363 | 14460953.1406 | 0.10831
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add 0.9 MVAR switched shunt at GEN-2024-157 138 kV | Current Study |  |  | 280388.5827 | 11.5268 | 2432500 | 0.28072
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Rebuild line 531405 WALKMYR3 115 531481 HUGOTON3 115 1 | Current Study | 12.27 | (598.00, 598.00) | 230971.2837 | 1.8824 | 12270000 | 0.013769
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add 60 MVAR switched shunt at WAYSIDE 4 230 kV | Current Study |  |  | 208858.5801 | 5.4604 | 3825000 | 0.043934
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at IRS7 115 KV 115 kV | Current Study |  |  | 199540.4276 | 9.0188 | 2212500 | 0.14469
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MED-LDG3 115 kV | Current Study |  |  | 186134.9182 | 8.4129 | 2212500 | 0.14469
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add 6 MVAR switched shunt at REDHLSW4 138 kV | Current Study |  |  | 167346.1327 | 6.8796 | 2432500 | 0.037003
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2 | Current Study |  | (350.00, 385.00) | 163813.5513 | 0.97508 | 16800000 | 0.004335
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add 40 MVAR switched shunt at SEGNTP 3 115 kV | Current Study |  |  | 149466.0716 | 6.7555 | 2212500 | 0.28072
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add 0.8 MVAR switched shunt at HARBNGR7 345 kV | Current Study |  |  | 140753.2617 | 2.6557 | 5300000 | 0.13764
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 135749.0815 | 2.5613 | 5300000 | 0.043837
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 126851.7798 | 5.7334 | 2212500 | 0.14469
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 122988.8775 | 5.5588 | 2212500 | 0.14469
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 116660.2742 | 5.2728 | 2212500 | 0.28072
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 98312.8813 | 1.855 | 5300000 | 0.032321
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add 0.04 MVAR switched shunt at ELLIS 2 69 kV | Current Study |  |  | 88898.9273 | 6.442 | 1380000 | 0.28072
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 86679.7314 | 0.46602 | 18600000 | 0.044808
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 84662.2371 | 0.45517 | 18600000 | 0.039866
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 84662.2371 | 0.45517 | 18600000 | 0.039866
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 82723.1714 | 5.0135 | 1650000 | 0.28072
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add 24 MVAR switched shunt at NESSCTY3 115 kV | Current Study |  |  | 80595.7759 | 3.6427 | 2212500 | 0.13764
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 58722.0482 | 2.6541 | 2212500 | 0.13764
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 531405 WALKMYR3 115 531510 HARBNGR3 115 M2 | Current Study | 1.28 | (598.00, 598.00) | 58426.8333 | 0.97508 | 5992000 | 0.004335
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add 66 MVAR switched shunt at GEN-2021-021 345 kV | Current Study |  |  | 55089.2907 | 1.0394 | 5300000 | 0.00026906
GEN-2024-102 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 49277.2146 | 0.92976 | 5300000 | 0.019743
GEN-2024-102 | 03 CENTRAL | TBD | NRIS | Add 16 MVAR switched shunt at UNDERWOOD 2 345 kV | Current Study |  |  | 40714.4851 | 0.7682 | 5300000 | 0.030111
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 37264.2877 | 2.7003 | 1380000 | 0.13764
GEN-2024-102 | 03 CENTRAL | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 24378.5839 | 1.7666 | 1380000 | 0.055841
GEN-2024-102 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR SVC at GEN-2021-076 345 kV | Current Study |  |  | 17496.5777 | 0.1458 | 12000000 | 0.00087851
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 34976752.5157 | 2.7217 | 1285130000 | 0.21416
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 34450282.4598 | 9.3998 | 366500000 | 0.15427
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 33363327.1578 | 2.6237 | 1271630000 | 0.13492
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 30697015.5533 | 2.0267 | 1514620000 | 0.031123
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 30275446.6428 | 3.2263 | 938400000 | 0.13666
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 29448579.7626 | 2.7426 | 1073760000 | 0.1173
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 25400217.5456 | 2.7068 | 938400000 | 0.20292
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 20694468.4961 | 2.8554 | 724760000 | 0.16913
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Current Study | 54.58 | (637.00, 637.00) | 14913943.9075 | 14.3815 | 103702000 | 0.083385
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 12023649.7071 | 2.4902 | 482840000 | 0.15801
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 11466397.1848 | 2.4431 | 469340000 | 0.10418
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 3094308.4267 | 3.6619 | 84500000 | 0.056146
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 2733218.9129 | 1.3814 | 197860000 | 0.034093
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 2472463.6438 | 2.926 | 84500000 | 0.092884
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 2412774.695 | 2.8554 | 84500000 | 0.16913
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 2354056.7717 | 1.1859 | 198511000 | 0.031655
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 2069621.0293 | 1.658 | 124824000 | 0.054169
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 1980754.9022 | 1.2 | 165062000 | 0.037704
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 18 MVAR switched shunt at DEAFSMITH 6 230 kV | Current Study |  |  | 1969133.1212 | 51.4806 | 3825000 | 0.040121
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 1685910.6946 | 3.0531 | 55220000 | 0.074366
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 6 MVAR switched shunt at REDHLSW4 138 kV | Current Study |  |  | 1524459.3341 | 62.6705 | 2432500 | 1
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 1445596.6102 | 1.774 | 81488000 | 0.058822
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 1038348.5435 | 2.3885 | 43472000 | 0.036353
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 978099.0132 | 3.9124 | 25000000 | 0.03314
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 978099.0132 | 3.9124 | 25000000 | 0.02888
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1 | Current Study | 18.95 | (901.00, 901.00) | 799770.2504 | 2.2213 | 36005000 | 0.032398
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 630353.1833 | 3.389 | 18600000 | 0.1696
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 7 MVAR switched shunt at CL-AFTP4 138 kV | Current Study |  |  | 628323.9278 | 25.8304 | 2432500 | 1
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 531095.9684 | 2.8554 | 18600000 | 0.16913
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 505907.2341 | 2.7199 | 18600000 | 0.21416
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 487785.8718 | 2.6225 | 18600000 | 0.13492
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 481014.8927 | 2.5861 | 18600000 | 0.13492
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 454414.6837 | 2.4431 | 18600000 | 0.10418
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 452637.3311 | 1.7081 | 26500000 | 0.013406
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 430925.1778 | 2.3168 | 18600000 | 0.20292
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 430925.1778 | 2.3168 | 18600000 | 0.20292
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 392532.7833 | 2.1104 | 18600000 | 0.20292
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 392255.3988 | 2.1089 | 18600000 | 0.13992
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 376968.8036 | 2.0267 | 18600000 | 0.031123
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 18 MVAR switched shunt at FALCNRD4 138 kV | Current Study |  |  | 360267.9362 | 14.8106 | 2432500 | 0.055372
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 0.7 MVAR switched shunt at GEN-2024-161 138 kV | Current Study |  |  | 329006.8731 | 13.5255 | 2432500 | 0.032057
GEN-2024-109 | 05 SOUTHWEST | TBD | NRIS | Add 0.09 MVAR switched shunt at GRAY CO3 115 kV | Current Study |  |  | 254179.3179 | 11.4883 | 2212500 | 0.10416
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 0.7 MVAR switched shunt at ROSEVLT2 69 kV | Current Study |  |  | 204386.3317 | 14.8106 | 1380000 | 0.055372
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 193389.4531 | 1.1944 | 16192000 | 0.066874
GEN-2024-109 | 05 SOUTHWEST | TBD | NRIS | Add 16 MVAR switched shunt at UNDERWOOD 2 345 kV | Current Study |  |  | 175243.4189 | 3.3065 | 5300000 | 0.1296
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 170038.0925 | 1.1383 | 14938000 | 0.060545
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 164607.9051 | 1.1383 | 14460953.1406 | 0.060545
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-161-TAP 138 kV | Current Study |  |  | 144516.2444 | 5.9411 | 2432500 | 0.032057
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 141367.7992 | 2.1563 | 6556000 | 0.074366
GEN-2024-109 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 132419.1038 | 0.7316 | 18100000 | 0.0055971
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 115508.1009 | 0.96257 | 12000000 | 0.066874
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | Current Study | 0.78 | (598.00, 598.00) | 98491.1196 | 1.8611 | 5292000 | 0.013128
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | Current Study | 0.2 | (598.00, 598.00) | 83378.7256 | 1.8611 | 4480000 | 0.013128
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 72053.3114 | 3.2566 | 2212500 | 0.066874
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 27791.5063 | 1.2561 | 2212500 | 0.066874
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 0.5 MVAR switched shunt at RKY_RDG4 138 kV | Current Study |  |  | 25186.3511 | 1.0354 | 2432500 | 0.032057
GEN-2024-109 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 21662.3548 | 1.5697 | 1380000 | 0.049619
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 19706.8057 | 1.1944 | 1650000 | 0.066874
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 14934.344 | 0.28178 | 5300000 | 0.020151
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 12852.3591 | 0.5809 | 2212500 | 0.030124
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 11781.7453 | 0.85375 | 1380000 | 0.066874
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 8155.9486 | 0.59101 | 1380000 | 0.030124
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 5143.37 | 0.37271 | 1380000 | 0.01649
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 1689.1613 | 0.1224 | 1380000 | 0.00043732
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 364.9167 | 0.026443 | 1380000 | 0.0013773
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 2550250.2804 | 1.6974 | 150244000 | 0.025644
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1 | Current Study | 11.3 | (1793.00, 1793.00) | 2187798.9821 | 8.8005 | 24860000 | 0.18097
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 2036800.5427 | 2.2647 | 89936000 | 0.017635
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1932240.7844 | 2.0237 | 95480000 | 0.05456
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 1736889.1835 | 2.6317 | 66000000 | 0.040325
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 1714084.5668 | 2.0237 | 84700000 | 0.05456
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 1632283.4448 | 2.9338 | 55638000 | 0.044111
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1575007.0008 | 1.5683 | 100427000 | 0.013428
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1558843.3248 | 0.71402 | 218320000 | 0.014688
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1306700.407 | 0.90872 | 143796000 | 0.030258
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1145295.2822 | 1.2186 | 93984000 | 0.050411
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 1135962.5707 | 2.5336 | 44836000 | 0.039654
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 1028042.3137 | 3.0602 | 33594000 | 0.083245
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 844865.8183 | 0.4256 | 198511000 | 0.015167
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 840428.2212 | 0.7451 | 112794000 | 0.042309
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 68 MVAR SVC at TONTITN7 345 kV | Current Study |  |  | 820169.3806 | 6.8347 | 12000000 | 0.031084
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 2.3 MVAR switched shunt at MON152 2 69 kV | Current Study |  |  | 802793.6892 | 58.1735 | 1380000 | 1
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 668005.2925 | 5.5667 | 12000000 | 0.055199
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 656971.1437 | 0.52632 | 124824000 | 0.022955
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 540804.2965 | 1.1779 | 45914000 | 0.039696
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 522544.6796 | 2.0654 | 25300000 | 0.028203
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 447396.3457 | 3.7283 | 12000000 | 0.091663
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 436460.1801 | 6.613 | 6600000 | 0.091663
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 389776.0253 | 3.2481 | 12000000 | 0.091663
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 374420.5974 | 3.1202 | 12000000 | 0.091663
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 342873.4681 | 2.8573 | 12000000 | 0.091663
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 295149.0626 | 1.1779 | 25058000 | 0.039696
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 269110.9495 | 5.0776 | 5300000 | 0.055199
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 261748.799 | 3.9659 | 6600000 | 0.091663
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 235084.3737 | 1.959 | 12000000 | 0.017636
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 234635.6151 | 1.9553 | 12000000 | 0.044111
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 233209.9009 | 1.5493 | 15053000 | 0.013661
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 227469.6647 | 1.8956 | 12000000 | 0.031473
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 218561.1272 | 6.725 | 3250000 | 0.091663
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 218561.1272 | 6.725 | 3250000 | 0.091663
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 215122.7006 | 1.7927 | 12000000 | 0.040748
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 195281.8705 | 1.6273 | 12000000 | 0.055199
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 176187.2423 | 1.4682 | 12000000 | 0.023067
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 172842.0623 | 1.4404 | 12000000 | 0.031473
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 172842.0623 | 1.4404 | 12000000 | 0.031473
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 169998.793 | 1.4167 | 12000000 | 0.03264
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 164769.7358 | 1.3731 | 12000000 | 0.030875
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 161136.5694 | 1.3428 | 12000000 | 0.031473
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 154762.1558 | 1.3273 | 11660000 | 0.050411
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 154263.4484 | 2.9106 | 5300000 | 0.055199
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 152003.7346 | 1.2667 | 12000000 | 0.023067
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 135362.6756 | 2.554 | 5300000 | 0.091663
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 132280.1148 | 4.0702 | 3250000 | 0.091663
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 132265.2549 | 2.004 | 6600000 | 0.05456
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 130280.4324 | 2.4581 | 5300000 | 0.050411
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 128840.5647 | 3.9643 | 3250000 | 0.091663
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 126378.1687 | 1.9148 | 6600000 | 0.050411
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 122445.0378 | 1.8552 | 6600000 | 0.040748
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 122445.0378 | 1.8552 | 6600000 | 0.040748
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 121370.9359 | 3.7345 | 3250000 | 0.091663
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 121191.0456 | 2.2866 | 5300000 | 0.044111
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 107903.5183 | 0.8992 | 12000000 | 0.021015
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 104378.3976 | 3.2116 | 3250000 | 0.040748
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 104378.3976 | 3.2116 | 3250000 | 0.040748
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 102281.7121 | 1.9298 | 5300000 | 0.040748
GEN-2024-113 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 100938.5339 | 1.9045 | 5300000 | 0.21678
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 99056.6693 | 3.0479 | 3250000 | 0.091663
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 97658.8407 | 1.8426 | 5300000 | 0.030875
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 93702.8451 | 1.768 | 5300000 | 0.030875
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 90454.2649 | 1.7067 | 5300000 | 0.05456
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 84841.0942 | 2.6105 | 3250000 | 0.040748
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 84812.741 | 1.6002 | 5300000 | 0.050411
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 82942.9067 | 6.0104 | 1380000 | 0.091663
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 76820.6086 | 5.5667 | 1380000 | 0.055199
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 75867.6536 | 2.3344 | 3250000 | 0.040748
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 71234.6833 | 2.0237 | 3520000 | 0.05456
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 65770.615 | 2.0237 | 3250000 | 0.05456
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 64975.1345 | 1.9992 | 3250000 | 0.040748
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 64401.9767 | 1.9816 | 3250000 | 0.040748
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 64397.9887 | 1.9815 | 3250000 | 0.040748
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 63543.0297 | 0.42538 | 14938000 | 0.030205
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 62719.9178 | 1.9298 | 3250000 | 0.040748
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 61513.7753 | 0.42538 | 14460953.1406 | 0.030205
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 60195.2438 | 2.7207 | 2212500 | 0.091663
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 60018.9612 | 0.37067 | 16192000 | 0.027707
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 58362.1726 | 2.6378 | 2212500 | 0.091663
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 54559.6517 | 2.2429 | 2432500 | 0.030875
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 54251.5843 | 1.6693 | 3250000 | 0.050411
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 48761.4325 | 0.92003 | 5300000 | 0.0045593
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 40815.3982 | 1.6779 | 2432500 | 0.050411
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 40249.5692 | 1.6547 | 2432500 | 0.050411
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 35597.8647 | 2.5796 | 1380000 | 0.040748
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 32713.1016 | 2.3705 | 1380000 | 0.055199
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 29286.6438 | 2.1222 | 1380000 | 0.040748
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 26609.3093 | 1.9282 | 1380000 | 0.050411
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 17977.7838 | 1.3027 | 1380000 | 0.042309
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 17472.121 | 0.32966 | 5300000 | 0.031473
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 14420.8968 | 0.65179 | 2212500 | 0.046325
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 6116.0626 | 0.37067 | 1650000 | 0.027707
GEN-2024-114 | 04 SOUTHEAST | TBD | ERIS | Add line 505418 JONESBO5 161 774620 G23-132-TAP 161 P2 | Current Study | 9.8 | (237.00, 237.00) | 26780000 | 100 | 26780000 | 0.39858
GEN-2024-114 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 774620 G23-132-TAP 161 780390 G24-114-TAP 161 1 | Current Study | 9.3 | (364.00, 364.00) | 13950000 | 100 | 13950000 | 0.80285
GEN-2024-114 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 338758 5HEBER.N# 161 505422 GREERSF5 161 1 | Current Study | 1.4851 | (309.00, 309.00) | 2227580.5943 | 100 | 2227580.5943 | 0.1957
GEN-2024-114 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at PHILL 7 345 kV | Current Study |  |  | 668807.4983 | 12.619 | 5300000 | 0.056557
GEN-2024-114 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 109845.0325 | 1.6643 | 6600000 | 0.034777
GEN-2024-114 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 38275.4782 | 1.73 | 2212500 | 0.18536
GEN-2024-114 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 22704.5903 | 0.42839 | 5300000 | 0.073511
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 533008 TV1MNDV4 138 533020 NEOSHOS4 138 1 | Current Study | 22.77 | (265.00, 265.00) | 7792272.3378 | 28.5181 | 27324000 | 0.14462
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532996 TIOGA 4 138 533001 ALTOONA4 138 1 | Current Study | 16.38 | (134.00, 134.00) | 7746735.6798 | 39.4116 | 19656000 | 0.032207
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 533001 ALTOONA4 138 533006 TAYLOR 4 138 1 | Current Study | 21.66 | (265.00, 265.00) | 7350397.366 | 28.2795 | 25992000 | 0.13389
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 533002 DEARING4 138 533004 MONTGOM4 138 1 | Current Study | 11.45 | (265.00, 265.00) | 3884411.6256 | 28.2708 | 13740000 | 0.12759
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 533002 DEARING4 138 533003 LIBERTY4 138 1 | Current Study | 10.03 | (395.00, 395.00) | 3423454.4385 | 28.4435 | 12036000 | 0.14075
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 533003 LIBERTY4 138 533008 TV1MNDV4 138 1 | Current Study | 8.36 | (265.00, 265.00) | 2860930.9066 | 28.5181 | 10032000 | 0.14462
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510422 COFFEYT4 138 787350 G24-346-TAP 138 1 | Current Study | 6.1 | (525.00, 525.00) | 2630192.9857 | 35.9316 | 7320000 | 0.49388
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510379 DELWARE4 138 763113 G18-079-TAP 138 1 | Current Study | 12.23 | (395.00, 395.00) | 2199925.3134 | 14.99 | 14676000 | 0.19144
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1901583.6264 | 1.8935 | 100427000 | 0.032424
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1817998.0286 | 1.9041 | 95480000 | 0.10267
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 1804029.2668 | 2.0059 | 89936000 | 0.03124
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 1612740.1867 | 1.9041 | 84700000 | 0.10267
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510422 COFFEYT4 138 533002 DEARING4 138 1 | Current Study | 5.02 | (717.00, 717.00) | 1569315.3859 | 26.0511 | 6024000 | 0.3024
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 1471598.8905 | 1.2548 | 117282000 | 0.035205
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 1402240.4876 | 0.93331 | 150244000 | 0.0282
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 533680 CHRYJCT2 69 533697 LIBERT-2 69 1 | Current Study | 3.84 | (106.00, 106.00) | 1249611.4148 | 38.2847 | 3264000 | 0.01757
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 1137982.1251 | 1.7242 | 66000000 | 0.052841
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1004348.6363 | 0.46004 | 218320000 | 0.018927
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 773305.8478 | 14.5907 | 5300000 | 0.14461
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 721202.1038 | 0.50155 | 143796000 | 0.033401
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 691136.2806 | 1.2531 | 55154000 | 0.029464
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 533004 MONTGOM4 138 533006 TAYLOR 4 138 1 | Current Study | 1.88 | (265.00, 265.00) | 637984.6283 | 28.2795 | 2256000 | 0.13389
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 510323.1639 | 1.9493 | 26180000 | 0.029367
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 438424.1639 | 0.46649 | 93984000 | 0.038595
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 355727.7162 | 1.406 | 25300000 | 0.038399
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 338276.6246 | 2.819 | 12000000 | 0.10267
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 330819.1211 | 1.2531 | 26400000 | 0.029464
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 282345.8629 | 1.8757 | 15053000 | 0.033077
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 281912.0128 | 2.3493 | 12000000 | 0.10267
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 281912.0128 | 2.3493 | 12000000 | 0.10267
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 262819.9063 | 2.1902 | 12000000 | 0.10267
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 218286.8408 | 1.8191 | 12000000 | 0.10267
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 215045.0058 | 1.792 | 12000000 | 0.081467
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 208218.2423 | 1.7352 | 12000000 | 0.03124
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 192019.9327 | 1.6002 | 12000000 | 0.10267
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 533683 COFFSUB2 69 533685 CRA S 2 69 1 | Current Study | 0.58 | (140.00, 140.00) | 190371.2375 | 38.6149 | 493000 | 0.021438
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 181609.6658 | 1.5134 | 12000000 | 0.10267
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 179720.6188 | 0.33618 | 53460000 | 0.01618
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 172991.0124 | 3.264 | 5300000 | 0.13387
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 166386.498 | 1.3866 | 12000000 | 0.081467
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 162370.7118 | 3.0636 | 5300000 | 0.10267
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 154177.2784 | 1.2514 | 12320000 | 0.035803
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 145726.1979 | 1.2144 | 12000000 | 0.05596
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 145120.4663 | 1.2093 | 12000000 | 0.035804
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 145120.4663 | 1.2093 | 12000000 | 0.035804
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 136736.0083 | 1.1395 | 12000000 | 0.035804
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 129383.3345 | 1.0782 | 12000000 | 0.035804
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 124445.0709 | 1.8855 | 6600000 | 0.10267
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 122400.8149 | 1.8546 | 6600000 | 0.081467
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 122400.8149 | 1.8546 | 6600000 | 0.081467
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 121649.1891 | 2.2953 | 5300000 | 0.14461
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 106240.2474 | 0.88534 | 12000000 | 0.043533
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 102244.7715 | 1.9291 | 5300000 | 0.081467
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 93939.5691 | 0.78283 | 12000000 | 0.035206
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 92565.4652 | 0.77138 | 12000000 | 0.036055
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 85106.156 | 1.6058 | 5300000 | 0.10267
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 67022.9688 | 1.9041 | 3520000 | 0.10267
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 64378.7169 | 1.9809 | 3250000 | 0.081467
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 64374.7303 | 1.9808 | 3250000 | 0.081467
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 62854.4297 | 0.95234 | 6600000 | 0.044023
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 62704.1041 | 1.1831 | 5300000 | 0.044874
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 62697.2655 | 1.9291 | 3250000 | 0.081467
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 61881.9271 | 1.9041 | 3250000 | 0.10267
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 60152.9983 | 1.135 | 5300000 | 0.081467
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 59243.6464 | 0.50809 | 11660000 | 0.038595
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 57792.2449 | 0.4816 | 12000000 | 0.02173
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 57731.0366 | 2.3733 | 2432500 | 0.14461
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 57254.677 | 1.7617 | 3250000 | 0.081467
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 56382.7934 | 1.7349 | 3250000 | 0.044023
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 56382.7934 | 1.7349 | 3250000 | 0.044023
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 55474.8522 | 1.7069 | 3250000 | 0.10267
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 55264.6411 | 1.0427 | 5300000 | 0.03642
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 54196.1439 | 2.228 | 2432500 | 0.13387
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 53935.294 | 1.6595 | 3250000 | 0.081467
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 48376.0871 | 0.73297 | 6600000 | 0.038593
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 45829.1945 | 1.4101 | 3250000 | 0.044023
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 40981.9496 | 1.261 | 3250000 | 0.044023
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 35776.7008 | 1.1008 | 3250000 | 0.044874
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 35585.008 | 2.5786 | 1380000 | 0.081467
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 31764.773 | 0.97738 | 3250000 | 0.044023
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 29276.0665 | 2.1215 | 1380000 | 0.081467
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 27568.2601 | 1.2531 | 2200000 | 0.029464
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 23688.2952 | 0.72887 | 3250000 | 0.044023
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 16562.7337 | 1.2548 | 1320000 | 0.035205
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 15658.1859 | 1.1347 | 1380000 | 0.052842
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 10185.7329 | 0.7381 | 1380000 | 0.038593
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 512636 CATSAGR4 138 512638 CATSAGR5 161 512834 CATTER2 1 13 M2 | Current Study |  | (150.00, 188.00) | 7971532.8002 | 64.2866 | 12400000 | 0.040951
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 512623 CATSAGD4 138 512638 CATSAGR5 161 512833 CATTER1 1 13 M2 | Current Study |  | (150.00, 188.00) | 7971532.8002 | 64.2866 | 12400000 | 0.040311
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 547469 RIV4525 161 547729 BAX488 5 161 1 | Current Study | 5.19 | (364.00, 364.00) | 3958049.968 | 50.842 | 7785000 | 0.029032
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | Current Study | 1.8 | (395.00, 395.00) | 2160000 | 100 | 2160000 | 0.6305
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 2107598.6558 | 1.797 | 117282000 | 0.038005
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 547487 HOC404 5 161 547729 BAX488 5 161 1 | Current Study | 2.6 | (364.00, 364.00) | 1982838.1342 | 50.842 | 3900000 | 0.029032
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 1944915.5905 | 1.2945 | 150244000 | 0.029483
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 1744658.2039 | 1.9399 | 89936000 | 0.022773
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1713980.7573 | 1.7067 | 100427000 | 0.022029
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1645421.1337 | 1.7233 | 95480000 | 0.070042
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 1459647.7799 | 1.7233 | 84700000 | 0.070042
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 1368667.1132 | 2.0737 | 66000000 | 0.047904
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 1332414.3626 | 2.3948 | 55638000 | 0.054283
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1261511.358 | 0.57783 | 218320000 | 0.01792
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 990770.6732 | 0.68901 | 143796000 | 0.034587
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 950886.8406 | 1.0118 | 93984000 | 0.063096
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 917297.7961 | 1.6632 | 55154000 | 0.029476
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 898829.8819 | 2.6756 | 33594000 | 0.10972
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 68 MVAR SVC at TONTITN7 345 kV | Current Study |  |  | 854714.1714 | 7.1226 | 12000000 | 0.048834
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 830621.5508 | 1.8526 | 44836000 | 0.043711
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 38 MVAR SVC at WROGERS 5 161 kV | Current Study |  |  | 726492.2326 | 11.0075 | 6600000 | 0.048834
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 37 MVAR switched shunt at CHAMSPR7 345 kV | Current Study |  |  | 565000.3098 | 10.6604 | 5300000 | 0.048834
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 549946.9837 | 0.27704 | 198511000 | 0.014883
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 517772.3832 | 1.9777 | 26180000 | 0.022459
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 439073.5362 | 1.6632 | 26400000 | 0.029476
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR SVC at JAY 4 138 kV | Current Study |  |  | 436594.0749 | 8.2376 | 5300000 | 0.046059
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 419523.0375 | 0.25416 | 165062000 | 0.016072
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 413741.7365 | 0.33146 | 124824000 | 0.021794
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 411146.1119 | 0.89547 | 45914000 | 0.045496
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 400066.6858 | 1.5813 | 25300000 | 0.032552
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 253640.0256 | 1.685 | 15053000 | 0.022398
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at CENTRTN5 161 kV | Current Study |  |  | 246813.258 | 7.5943 | 3250000 | 0.048834
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 232661.7752 | 0.43521 | 53460000 | 0.015788
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 230727.4172 | 1.9227 | 12000000 | 0.065886
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510422 COFFEYT4 138 787350 G24-346-TAP 138 1 | Current Study | 6.1 | (525.00, 525.00) | 227100.2422 | 3.1025 | 7320000 | 0.032143
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 224386.8814 | 0.89547 | 25058000 | 0.045496
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 220538.3031 | 1.7901 | 12320000 | 0.038603
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 207581.2828 | 1.7298 | 12000000 | 0.038603
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 207581.2828 | 1.7298 | 12000000 | 0.038603
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 201365.7851 | 1.678 | 12000000 | 0.022773
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 191530.2638 | 1.5961 | 12000000 | 0.054282
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 185070.7845 | 1.5423 | 12000000 | 0.038603
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 178520.4301 | 1.4877 | 12000000 | 0.065886
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 173792.0738 | 1.4483 | 12000000 | 0.070042
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 164370.0214 | 1.3698 | 12000000 | 0.070042
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 153112.8885 | 1.2759 | 12000000 | 0.054282
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 143173.7052 | 1.1931 | 12000000 | 0.041442
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 140625.4152 | 1.1719 | 12000000 | 0.038603
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 140625.4152 | 1.1719 | 12000000 | 0.038603
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 4.8 MVAR switched shunt at COWSKIN2 69 kV | Current Study |  |  | 136211.6264 | 9.8704 | 1380000 | 0.046059
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 134537.3366 | 1.1211 | 12000000 | 0.038005
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 131327.0391 | 1.9898 | 6600000 | 0.065886
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 131327.0391 | 1.9898 | 6600000 | 0.065886
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 131101.7508 | 1.0925 | 12000000 | 0.038603
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 130730.8857 | 1.0894 | 12000000 | 0.025802
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 128492.014 | 1.102 | 11660000 | 0.063096
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 124984.196 | 1.0415 | 12000000 | 0.038603
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 124799.5129 | 1.8909 | 6600000 | 0.065886
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 112786.7296 | 0.93989 | 12000000 | 0.025802
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 112631.8849 | 1.7065 | 6600000 | 0.070042
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 111949.8687 | 3.4446 | 3250000 | 0.065886
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 111949.8687 | 3.4446 | 3250000 | 0.065886
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 109701.0924 | 2.0698 | 5300000 | 0.065886
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 108165.9224 | 2.0409 | 5300000 | 0.063096
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 104926.0503 | 1.5898 | 6600000 | 0.063096
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 98926.8101 | 1.8665 | 5300000 | 0.054282
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 90995.3551 | 2.7999 | 3250000 | 0.065886
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 89571.1166 | 0.74643 | 12000000 | 0.026298
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 81370.9929 | 2.5037 | 3250000 | 0.065886
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 80528.8883 | 1.5194 | 5300000 | 0.011351
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 79740.131 | 1.5045 | 5300000 | 0.038005
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | Current Study | 0 | (275.00, 275.00) | 77143.8658 | 64.2866 | 120000 | 0.081902
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | Current Study | 0 | (424.00, 424.00) | 77143.8658 | 64.2866 | 120000 | 0.12292
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 77027.2916 | 1.4533 | 5300000 | 0.070042
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 76509.9923 | 1.4436 | 5300000 | 0.038005
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 70416.1646 | 1.3286 | 5300000 | 0.063096
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 69688.3449 | 2.1443 | 3250000 | 0.065886
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 69073.611 | 2.1253 | 3250000 | 0.065886
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 69069.3337 | 2.1252 | 3250000 | 0.065886
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 67269.5378 | 2.0698 | 3250000 | 0.065886
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 64539.7268 | 1.2177 | 5300000 | 0.065886
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 63069.9891 | 1.9406 | 3250000 | 0.065886
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 61430.042 | 1.8902 | 3250000 | 0.065886
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 60660.687 | 1.7233 | 3520000 | 0.070042
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 57868.5891 | 1.7806 | 3250000 | 0.065886
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 56007.6669 | 1.7233 | 3250000 | 0.070042
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 50208.7959 | 1.5449 | 3250000 | 0.070042
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 47033.88 | 1.4472 | 3250000 | 0.065886
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 44548.8985 | 1.8314 | 2432500 | 0.038005
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 41779.2881 | 0.25802 | 16192000 | 0.029076
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 41453.1318 | 0.2775 | 14938000 | 0.029706
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 40129.321 | 0.2775 | 14460953.1406 | 0.029706
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 38682.8993 | 0.72987 | 5300000 | 0.020867
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 38180.0868 | 2.7667 | 1380000 | 0.065886
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 36589.4614 | 1.6632 | 2200000 | 0.029476
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 33887.1703 | 1.3931 | 2432500 | 0.063096
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 33417.3882 | 1.3738 | 2432500 | 0.063096
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 31411.0582 | 2.2762 | 1380000 | 0.065886
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 23720.8628 | 1.797 | 1320000 | 0.038005
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 22092.5003 | 1.6009 | 1380000 | 0.063096
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 19208.6698 | 1.3919 | 1380000 | 0.032002
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 18832.2509 | 1.3647 | 1380000 | 0.047905
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 14215.4302 | 0.26822 | 5300000 | 0.038603
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 4257.4003 | 0.25802 | 1650000 | 0.029076
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 11841298.8116 | 1.2597 | 940000000 | 0.017889
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520842 CANADNS4 138 520976 LIL AXE4 138 1 | Current Study | 11.08 | (265.00, 265.00) | 9061415.4982 | 68.1514 | 13296000 | 0.54072
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520973 LEXNGTN4 138 520976 LIL AXE4 138 1 | Current Study | 9.71 | (265.00, 265.00) | 7539440.2659 | 64.7051 | 11652000 | 0.54072
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520888 PAYNESW4 138 521023 PAOLI 4 138 1 | Current Study | 12 | (265.00, 265.00) | 5437868.6147 | 37.763 | 14400000 | 0.22859
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 532803 BURNS 7 345 1 | Current Study | 50.03 | (1793.00, 1793.00) | 4303457.3511 | 3.9099 | 110066000 | 0.041012
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532803 BURNS 7 345 1 | Current Study | 45.5 | (1793.00, 1793.00) | 3913797.9107 | 3.9099 | 100100000 | 0.041012
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520861 COLE 4 138 520868 CRINER 4 138 1 | Current Study | 10.06 | (211.00, 211.00) | 3251185.7039 | 26.9316 | 12072000 | 0.089937
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520400 NOBLE4 138 520975 LIDDELL4 138 1 | Current Study | 5.73 | (265.00, 265.00) | 3250221.0721 | 47.2691 | 6876000 | 0.15235
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 2293336.8011 | 1.9554 | 117282000 | 0.041355
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 1 | Current Study |  | (1868.00, 1868.00) | 2234968.9885 | 3.6341 | 61500000 | 0.088957
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 2 | Current Study |  | (1868.00, 1868.00) | 2234968.9885 | 3.6341 | 61500000 | 0.088957
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 2212573.1146 | 1.4727 | 150244000 | 0.03354
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520868 CRINER 4 138 520888 PAYNESW4 138 1 | Current Study | 6.54 | (211.00, 211.00) | 2113593.8871 | 26.9316 | 7848000 | 0.089937
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1339604.0509 | 1.3339 | 100427000 | 0.017217
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1326160.311 | 0.60744 | 218320000 | 0.018838
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 1274986.2421 | 2.2916 | 55638000 | 0.051943
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 1229178.0158 | 1.3667 | 89936000 | 0.016044
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1179355.5865 | 1.2352 | 95480000 | 0.050203
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514948 CEDARLN4 138 766111 G21-088-TAP 138 1 | Current Study | 2.86 | (395.00, 395.00) | 1152257.1492 | 33.5739 | 3432000 | 0.2892
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2 | Current Study |  | (478.00, 478.00) | 1111551.6749 | 6.1412 | 18100000 | 0.051644
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1091041.7272 | 0.75874 | 143796000 | 0.038087
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 1088179.163 | 1.6488 | 66000000 | 0.038087
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 1080034.0164 | 1.9582 | 55154000 | 0.034706
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 1046202.5364 | 1.2352 | 84700000 | 0.050203
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 1001585.394 | 2.2339 | 44836000 | 0.052708
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 965314.4846 | 0.48628 | 198511000 | 0.026124
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 856787.0336 | 0.6864 | 124824000 | 0.045131
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 825474.6989 | 0.4172 | 197860000 | 0.020722
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 727890.569 | 1.549 | 46992000 | 0.06305
GEN-2024-119 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 514992 TURNER 4 138 516097 NORMHLL4 138 1 | Current Study | 1.89 | (395.00, 395.00) | 685467.9737 | 30.2235 | 2268000 | 0.024987
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 610804.602 | 0.6499 | 93984000 | 0.04053
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 594789.5382 | 0.36034 | 165062000 | 0.022786
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511425 TUTCONT4 138 514898 CIMARON4 138 1 | Current Study | 14.65 | (395.00, 395.00) | 583197.1787 | 3.3174 | 17580000 | 0.029131
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 569330.6303 | 0.69867 | 81488000 | 0.046624
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 561866.8936 | 0.42263 | 132946000 | 0.013206
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 529570.2338 | 0.83727 | 63250000 | 0.045691
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 516968.8152 | 1.9582 | 26400000 | 0.034706
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 481640.5229 | 1.4337 | 33594000 | 0.058795
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | Current Study | 13.6 | (1793.00, 1793.00) | 480838.8566 | 1.6071 | 29920000 | 0.030498
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 472057.2563 | 1.0281 | 45914000 | 0.052236
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 426669.9706 | 1.6298 | 26180000 | 0.018508
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 341627.9113 | 1.3503 | 25300000 | 0.027797
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 338395.5595 | 1.318 | 25674000 | 0.046503
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 307854.4612 | 0.57586 | 53460000 | 0.020891
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 280830.3268 | 5.2987 | 5300000 | 0.052236
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 257629.7149 | 1.0281 | 25058000 | 0.052236
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR SVC at JAY 4 138 kV | Current Study |  |  | 248537.791 | 4.6894 | 5300000 | 0.02622
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 138 MVAR switched shunt at GEN-2024-016 345 kV | Current Study |  |  | 240807.5503 | 4.5435 | 5300000 | 0.028588
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 239707.0456 | 1.3385 | 17908000 | 0.048008
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 239672.7633 | 1.9454 | 12320000 | 0.041953
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 225591.3652 | 1.8799 | 12000000 | 0.041953
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 225591.3652 | 1.8799 | 12000000 | 0.041953
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 0.06 MVAR switched shunt at G24-125-TAP 345 kV | Current Study |  |  | 212704.8332 | 4.0133 | 5300000 | 0.028808
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 201127.8203 | 1.6761 | 12000000 | 0.041953
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 198368.3012 | 1.3178 | 15053000 | 0.017517
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 183276.4494 | 1.5273 | 12000000 | 0.051943
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 170991.1546 | 1.4249 | 12000000 | 0.050203
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 161315.3702 | 1.3443 | 12000000 | 0.031839
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 158154.4875 | 1.318 | 12000000 | 0.067393
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 152826.3001 | 1.2736 | 12000000 | 0.041953
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 152826.3001 | 1.2736 | 12000000 | 0.041953
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 146514.6342 | 1.221 | 12000000 | 0.051943
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 146393.695 | 1.2199 | 12000000 | 0.041355
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 144937.9087 | 1.2078 | 12000000 | 0.041953
GEN-2024-119 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 514959 FOSTER 4 138 515387 NEWDOMI4 138 1 | Current Study | 1.44 | (281.00, 281.00) | 143077.4912 | 8.2799 | 1728000 | 0.040846
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 142476.3473 | 1.1873 | 12000000 | 0.041953
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 141870.2001 | 1.1823 | 12000000 | 0.016044
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 139173.1796 | 1.1598 | 12000000 | 0.031839
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at CENTRTN5 161 kV | Current Study |  |  | 137687.7449 | 4.2365 | 3250000 | 0.027243
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 135828.0237 | 1.1319 | 12000000 | 0.041953
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 134713.0561 | 2.5418 | 5300000 | 0.031839
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 128305.5849 | 2.4209 | 5300000 | 0.032305
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 124565.683 | 1.038 | 12000000 | 0.050203
GEN-2024-119 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 123777.287 | 0.68385 | 18100000 | 0.010529
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514947 CANADN-4 138 766111 G21-088-TAP 138 1 | Current Study | 0.3 | (395.00, 395.00) | 120866.1345 | 33.5739 | 360000 | 0.2892
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 120086.9242 | 1.0007 | 12000000 | 0.034292
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520400 NOBLE4 138 520842 CANADNS4 138 1 | Current Study | 0.18 | (265.00, 265.00) | 102101.1855 | 47.2691 | 216000 | 0.15235
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 94663.6533 | 1.7861 | 5300000 | 0.051943
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 92914.7027 | 0.77429 | 12000000 | 0.034292
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511501 TUTTLE4 138 511575 LEONARD4 138 1 | Current Study | 2.12 | (395.00, 395.00) | 91981.2778 | 3.6156 | 2544000 | 0.029131
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 86767.3816 | 1.6371 | 5300000 | 0.041355
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 83252.5807 | 1.5708 | 5300000 | 0.041355
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 82537.1749 | 0.70787 | 11660000 | 0.04053
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 80729.0422 | 1.2232 | 6600000 | 0.050203
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 74114.5601 | 1.3984 | 5300000 | 0.067393
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 72102.6877 | 0.48268 | 14938000 | 0.051669
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 69800.0795 | 0.48268 | 14460953.1406 | 0.051669
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 69480.8593 | 1.311 | 5300000 | 0.04053
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 68351.9123 | 1.0356 | 6600000 | 0.034292
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 68351.9123 | 1.0356 | 6600000 | 0.034292
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 67399.7131 | 1.0212 | 6600000 | 0.04053
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 64954.5244 | 0.98416 | 6600000 | 0.034292
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 59184.0816 | 0.36551 | 16192000 | 0.041189
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 58266.6575 | 1.7928 | 3250000 | 0.034292
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 58266.6575 | 1.7928 | 3250000 | 0.034292
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 57096.2347 | 1.0773 | 5300000 | 0.034292
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 53403.6356 | 1.0076 | 5300000 | 0.028808
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 48989.5363 | 0.92433 | 5300000 | 0.031839
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 48474.8548 | 1.9928 | 2432500 | 0.041355
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 48121.6361 | 0.90796 | 5300000 | 0.031839
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 47360.4414 | 1.4572 | 3250000 | 0.034292
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 46004.3197 | 1.549 | 2970000 | 0.06305
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | Current Study | 1.06 | (395.00, 395.00) | 45990.6389 | 3.6156 | 1272000 | 0.029131
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 45384.0051 | 0.8563 | 5300000 | 0.031839
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 45232.1352 | 0.85344 | 5300000 | 0.04053
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 43478.547 | 1.2352 | 3520000 | 0.050203
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 43080.7346 | 1.9582 | 2200000 | 0.034706
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 42351.2402 | 1.3031 | 3250000 | 0.034292
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 41095.6524 | 0.77539 | 5300000 | 0.041953
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 40143.5643 | 1.2352 | 3250000 | 0.050203
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 36270.7609 | 1.116 | 3250000 | 0.034292
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 35987.2163 | 1.1073 | 3250000 | 0.050203
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 35950.8098 | 1.1062 | 3250000 | 0.034292
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 35948.5836 | 1.1061 | 3250000 | 0.034292
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 35011.8421 | 1.0773 | 3250000 | 0.034292
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 34077.2738 | 1.549 | 2200000 | 0.06305
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 33434.1845 | 1.3745 | 2432500 | 0.062653
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 32826.0988 | 1.01 | 3250000 | 0.034292
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 31972.554 | 0.98377 | 3250000 | 0.034292
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 31565.7948 | 0.59558 | 5300000 | 0.0044494
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 30118.9211 | 0.92674 | 3250000 | 0.034292
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CHILD4WT 138 kV | Current Study |  |  | 29398.0475 | 1.2086 | 2432500 | 0.062653
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 28933.3296 | 0.89026 | 3250000 | 0.04053
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 25811.3315 | 1.9554 | 1320000 | 0.041355
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 24729.4641 | 0.46659 | 5300000 | 0.041189
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 22528.4955 | 0.18774 | 12000000 | 0.02625
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 21767.5739 | 0.89486 | 2432500 | 0.04053
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 21465.8073 | 0.88246 | 2432500 | 0.04053
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 20472.8036 | 0.89012 | 2300000 | 0.06305
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 19871.6271 | 1.44 | 1380000 | 0.034292
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 18124.1025 | 1.3133 | 1380000 | 0.030195
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 16348.5442 | 1.1847 | 1380000 | 0.034292
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 16122.8435 | 1.1683 | 1380000 | 0.041013
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 15448.7836 | 0.29149 | 5300000 | 0.041953
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 14191.2154 | 1.0283 | 1380000 | 0.04053
GEN-2024-119 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 12706.4747 | 0.23974 | 5300000 | 0.04114
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 10264.7077 | 0.74382 | 1380000 | 0.036418
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 8505.222 | 0.38442 | 2212500 | 0.041189
GEN-2024-119 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 6030.9866 | 0.36551 | 1650000 | 0.041189
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 532803 BURNS 7 345 1 | Current Study | 50.03 | (1793.00, 1793.00) | 4354878.7214 | 3.9566 | 110066000 | 0.041502
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532803 BURNS 7 345 1 | Current Study | 45.5 | (1793.00, 1793.00) | 3960563.2985 | 3.9566 | 100100000 | 0.041502
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 2376631.7114 | 2.0264 | 117282000 | 0.042857
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 2269595.5158 | 1.5106 | 150244000 | 0.034405
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 1 | Current Study |  | (1868.00, 1868.00) | 2029626.0687 | 3.3002 | 61500000 | 0.080784
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 2 | Current Study |  | (1868.00, 1868.00) | 2029626.0687 | 3.3002 | 61500000 | 0.080784
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 1541179.0435 | 2.77 | 55638000 | 0.062788
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1435287.7043 | 1.4292 | 100427000 | 0.018447
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1369562.6672 | 0.62732 | 218320000 | 0.019454
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 1289801.4429 | 2.8767 | 44836000 | 0.067876
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 1282890.0065 | 1.4264 | 89936000 | 0.016745
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1219180.4578 | 1.2769 | 95480000 | 0.051898
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 1133278.9714 | 1.7171 | 66000000 | 0.039665
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1121977.921 | 0.78026 | 143796000 | 0.039167
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 1115820.9188 | 2.0231 | 55154000 | 0.035856
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 1081531.0513 | 1.2769 | 84700000 | 0.051898
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 932607.166 | 0.4698 | 198511000 | 0.025239
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 851883.8528 | 0.68247 | 124824000 | 0.044873
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 782410.4393 | 0.39544 | 197860000 | 0.019641
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 661574.0004 | 1.4078 | 46992000 | 0.057306
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 650062.034 | 0.69167 | 93984000 | 0.043135
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 622601.9779 | 1.356 | 45914000 | 0.068895
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 564094.865 | 0.34175 | 165062000 | 0.02161
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 559313.4777 | 0.68638 | 81488000 | 0.045804
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 551371.2982 | 0.41473 | 132946000 | 0.012959
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 534098.565 | 2.0231 | 26400000 | 0.035856
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at TXPLSTP2 69 kV | Current Study |  |  | 531481.6452 | 38.5132 | 1380000 | 0.4106
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 528519.9178 | 1.5733 | 33594000 | 0.064517
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 447202.4402 | 1.7082 | 26180000 | 0.019398
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 349943.4625 | 1.3832 | 25300000 | 0.028473
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 339790.9213 | 1.356 | 25058000 | 0.068895
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 322411.3961 | 0.60309 | 53460000 | 0.021878
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 122 MVAR switched shunt at HOYT 7 345 kV | Current Study |  |  | 283219.8046 | 5.3438 | 5300000 | 0.039649
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 248253.6778 | 2.015 | 12320000 | 0.043455
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 138 MVAR switched shunt at GEN-2024-016 345 kV | Current Study |  |  | 238355.8411 | 4.4973 | 5300000 | 0.028297
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 233668.2385 | 1.9472 | 12000000 | 0.043455
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 233668.2385 | 1.9472 | 12000000 | 0.043455
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 0.06 MVAR switched shunt at G24-125-TAP 345 kV | Current Study |  |  | 227610.1446 | 4.2945 | 5300000 | 0.030826
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 221540.9814 | 1.8462 | 12000000 | 0.062788
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 212502.0418 | 1.4117 | 15053000 | 0.018765
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 208328.8225 | 1.7361 | 12000000 | 0.043455
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 194850.2041 | 0.75894 | 25674000 | 0.026777
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 177104.0195 | 1.4759 | 12000000 | 0.062788
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 176765.2802 | 1.473 | 12000000 | 0.051898
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 161925.8347 | 1.3494 | 12000000 | 0.069
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 161887.181 | 1.3491 | 12000000 | 0.031952
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 158297.9575 | 1.3191 | 12000000 | 0.043455
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 158297.9575 | 1.3191 | 12000000 | 0.043455
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 151710.8447 | 1.2643 | 12000000 | 0.042857
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 150127.1372 | 1.2511 | 12000000 | 0.043455
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 148069.669 | 1.2339 | 12000000 | 0.016746
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 147577.4442 | 1.2298 | 12000000 | 0.043455
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 140691.0899 | 1.1724 | 12000000 | 0.043455
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 139666.5035 | 1.1639 | 12000000 | 0.031952
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 135190.5703 | 2.5508 | 5300000 | 0.031952
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 128772.0871 | 1.0731 | 12000000 | 0.051898
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 126671.5556 | 2.39 | 5300000 | 0.031893
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 117837.2411 | 0.98198 | 12000000 | 0.033649
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 114427.5696 | 2.159 | 5300000 | 0.062788
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 91174.0582 | 0.75978 | 12000000 | 0.033649
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 89918.8504 | 1.6966 | 5300000 | 0.042857
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 87841.977 | 0.75336 | 11660000 | 0.043135
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 86276.3888 | 1.6279 | 5300000 | 0.042857
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 83455.1459 | 1.2645 | 6600000 | 0.051898
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 75881.8937 | 1.4317 | 5300000 | 0.069
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 73946.4759 | 1.3952 | 5300000 | 0.043135
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 71731.5719 | 1.0868 | 6600000 | 0.043135
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 69910.9945 | 0.46801 | 14938000 | 0.050099
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 67678.3783 | 0.46801 | 14460953.1406 | 0.050099
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 67071.422 | 1.0162 | 6600000 | 0.033649
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 67071.422 | 1.0162 | 6600000 | 0.033649
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 63737.6801 | 0.96572 | 6600000 | 0.033649
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 57175.1023 | 1.7592 | 3250000 | 0.033649
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 57175.1023 | 1.7592 | 3250000 | 0.033649
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 57145.9005 | 1.0782 | 5300000 | 0.030826
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 56136.6313 | 0.34669 | 16192000 | 0.039068
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 56026.6059 | 1.0571 | 5300000 | 0.033649
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 50235.5048 | 2.0652 | 2432500 | 0.042857
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 49163.1884 | 0.92761 | 5300000 | 0.031952
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 48292.2117 | 0.91117 | 5300000 | 0.031952
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 48139.2577 | 0.90829 | 5300000 | 0.043135
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 46473.2008 | 1.4299 | 3250000 | 0.033649
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 45544.8767 | 0.85934 | 5300000 | 0.031952
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 44946.745 | 1.2769 | 3520000 | 0.051898
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 44508.2138 | 2.0231 | 2200000 | 0.035856
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 42567.0047 | 0.80315 | 5300000 | 0.043455
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 41812.9635 | 1.4078 | 2970000 | 0.057306
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 41557.841 | 1.2787 | 3250000 | 0.033649
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 41499.1547 | 1.2769 | 3250000 | 0.051898
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 37202.4529 | 1.1447 | 3250000 | 0.051898
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 35591.2722 | 1.0951 | 3250000 | 0.033649
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 35525.8875 | 0.6703 | 5300000 | 0.0050077
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 35277.3149 | 1.0855 | 3250000 | 0.033649
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 35275.1304 | 1.0854 | 3250000 | 0.033649
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 34355.9376 | 1.0571 | 3250000 | 0.033649
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 32211.1416 | 0.99111 | 3250000 | 0.033649
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 31373.5869 | 0.96534 | 3250000 | 0.033649
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 30972.5656 | 1.4078 | 2200000 | 0.057306
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 30792.9088 | 0.94747 | 3250000 | 0.043135
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 29554.6796 | 0.90937 | 3250000 | 0.033649
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 26748.8094 | 2.0264 | 1320000 | 0.042857
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 23456.1269 | 0.44257 | 5300000 | 0.039068
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 23166.6015 | 0.95238 | 2432500 | 0.043135
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 22845.44 | 0.93918 | 2432500 | 0.043135
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 22162.7251 | 0.18469 | 12000000 | 0.025824
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 19499.3562 | 1.413 | 1380000 | 0.033649
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 18607.5767 | 0.80903 | 2300000 | 0.057306
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 17638.3852 | 1.2781 | 1380000 | 0.029386
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 16977.4777 | 0.69794 | 2432500 | 0.031814
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 16315.4957 | 1.1823 | 1380000 | 0.041503
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 16042.274 | 1.1625 | 1380000 | 0.033649
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 16001.8981 | 0.30192 | 5300000 | 0.043455
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 15103.3015 | 1.0944 | 1380000 | 0.043135
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 9437.6386 | 0.42656 | 2212500 | 0.045704
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 5720.4448 | 0.34669 | 1650000 | 0.039068
GEN-2024-121 | 03 CENTRAL | TBD | ERIS | Rebuild line 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | Current Study | 17.54 | (1793.00, 1793.00) | 2846554.4602 | 7.3768 | 38588000 | 0.035623
GEN-2024-121 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 2006384.0362 | 0.21381 | 938400000 | 0.032259
GEN-2024-121 | 03 CENTRAL | TBD | ERIS | Rebuild line 645458 S3458 3 345 778170 G24-040-TAP 345 1 | Current Study | 13.15 | (1793.00, 1793.00) | 1556927.137 | 5.3817 | 28930000 | 0.083871
GEN-2024-121 | 03 CENTRAL | TBD | ERIS | Rebuild line 640139 COOPER 3 345 778170 G24-040-TAP 345 1 | Current Study | 12.59 | (1793.00, 1793.00) | 1490624.5365 | 5.3817 | 27698000 | 0.083871
GEN-2024-121 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 1349480.5103 | 0.6798 | 198511000 | 0.023094
GEN-2024-121 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 889814.8074 | 0.6188 | 143796000 | 0.031062
GEN-2024-121 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 744935.789 | 0.79262 | 93984000 | 0.04943
GEN-2024-121 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 475947.9451 | 0.23976 | 198511000 | 0.012881
GEN-2024-121 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 277777.6163 | 0.605 | 45914000 | 0.030738
GEN-2024-121 | 03 CENTRAL | TBD | ERIS | Rebuild line 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 | Current Study | 3.23 | (1793.00, 1793.00) | 228393.8381 | 3.2141 | 7106000 | 0.036412
GEN-2024-121 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 151599.7628 | 0.605 | 25058000 | 0.030738
GEN-2024-121 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 100662.1353 | 0.86331 | 11660000 | 0.04943
GEN-2024-121 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 55555.4851 | 0.29869 | 18600000 | 0.052649
GEN-2024-121 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 55555.4851 | 0.29869 | 18600000 | 0.052649
GEN-2024-121 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 34806.7481 | 0.23301 | 14938000 | 0.024943
GEN-2024-121 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 33695.1903 | 0.23301 | 14460953.1406 | 0.024943
GEN-2024-121 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 31006.4868 | 0.1667 | 18600000 | 0.032259
GEN-2024-121 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 13661.424 | 0.82797 | 1650000 | 0.050445
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | Current Study | 7.6 | (211.00, 211.00) | 5298489.5193 | 58.0975 | 9120000 | 0.69379
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 1340325.3688 | 0.8921 | 150244000 | 0.02527
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | Current Study | 10.42 | (395.00, 395.00) | 1220531.5503 | 9.7611 | 12504000 | 0.049276
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 820721.166 | 0.85957 | 95480000 | 0.043452
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 770287.4702 | 0.35282 | 218320000 | 0.013609
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 728059.0989 | 0.85957 | 84700000 | 0.043452
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 679723.9877 | 0.4727 | 143796000 | 0.029512
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 574318.1205 | 0.57188 | 100427000 | 0.0091807
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 546576.0076 | 0.27534 | 198511000 | 0.018398
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 544588.5203 | 1.1589 | 46992000 | 0.058671
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 470997.2722 | 0.37733 | 124824000 | 0.030857
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 448406.9646 | 0.70894 | 63250000 | 0.048119
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 403906.1332 | 0.42976 | 93984000 | 0.033334
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 391039.6901 | 0.34668 | 112794000 | 0.036911
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 365583.5414 | 0.22148 | 165062000 | 0.017419
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 353880.4485 | 2.949 | 12000000 | 0.054829
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 323620.85 | 0.96333 | 33594000 | 0.049134
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 312109.463 | 0.38301 | 81488000 | 0.03179
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at PHILL 7 345 kV | Current Study |  |  | 268020.5112 | 5.057 | 5300000 | 0.02819
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 247785.5654 | 0.97939 | 25300000 | 0.025076
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | Current Study | 1.8 | (395.00, 395.00) | 210840.383 | 9.7611 | 2160000 | 0.049276
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 201649.4674 | 0.78542 | 25674000 | 0.034466
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 175450.5425 | 1.4621 | 12000000 | 0.0674
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 171161.8257 | 2.5934 | 6600000 | 0.0674
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 146832.4396 | 1.2236 | 12000000 | 0.0674
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 144240.3543 | 0.80545 | 17908000 | 0.03593
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 142563.3967 | 2.6899 | 5300000 | 0.054829
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 134460.9462 | 1.1205 | 12000000 | 0.0674
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 118993.8062 | 0.99162 | 12000000 | 0.043452
GEN-2024-122 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 115856.1202 | 0.64009 | 18100000 | 0.012258
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 107875.9645 | 0.89897 | 12000000 | 0.015174
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 106933.9825 | 0.89112 | 12000000 | 0.037694
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 103451.9288 | 0.8621 | 12000000 | 0.054829
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 102647.1701 | 1.5553 | 6600000 | 0.0674
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 96045.3356 | 0.80038 | 12000000 | 0.023577
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 88197.3955 | 0.73498 | 12000000 | 0.031324
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 88016.9349 | 0.73347 | 12000000 | 0.030051
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 88016.9349 | 0.73347 | 12000000 | 0.030051
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 85710.7321 | 2.6373 | 3250000 | 0.0674
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 85710.7321 | 2.6373 | 3250000 | 0.0674
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 85485.0331 | 0.71238 | 12000000 | 0.037694
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 84672.8297 | 0.5625 | 15053000 | 0.0092996
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 83829.3187 | 0.69858 | 12000000 | 0.029453
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 82862.1273 | 0.69052 | 12000000 | 0.023577
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 82056.1081 | 0.6838 | 12000000 | 0.030051
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 81722.1344 | 1.5419 | 5300000 | 0.054829
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 56179.8417 | 0.85121 | 6600000 | 0.043452
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 54579.273 | 0.46809 | 11660000 | 0.033334
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 53083.7033 | 1.0016 | 5300000 | 0.0674
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 51874.849 | 1.5961 | 3250000 | 0.0674
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 50525.9982 | 1.5546 | 3250000 | 0.0674
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 50200.8081 | 0.76062 | 6600000 | 0.031324
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 50200.8081 | 0.76062 | 6600000 | 0.031324
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 47596.7154 | 1.4645 | 3250000 | 0.0674
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 45945.4376 | 0.8669 | 5300000 | 0.033334
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 44807.9533 | 0.84543 | 5300000 | 0.050676
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 41934.1175 | 0.79121 | 5300000 | 0.031324
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 40696.2516 | 2.949 | 1380000 | 0.054829
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 40668.1338 | 0.27225 | 14938000 | 0.036247
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 39369.392 | 0.27225 | 14460953.1406 | 0.036247
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 38845.973 | 1.1953 | 3250000 | 0.0674
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 36070.3197 | 0.22277 | 16192000 | 0.031222
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV | Current Study |  |  | 35510.7856 | 2.5732 | 1380000 | 0.042411
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 34419.2183 | 1.1589 | 2970000 | 0.058671
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 32526.8146 | 2.357 | 1380000 | 0.0674
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 31104.7111 | 0.95707 | 3250000 | 0.031324
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 30257.0015 | 0.85957 | 3520000 | 0.043452
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 29910.5432 | 0.56435 | 5300000 | 0.033334
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 27936.1556 | 0.85957 | 3250000 | 0.043452
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 26638.9257 | 0.81966 | 3250000 | 0.031324
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 26403.9387 | 0.81243 | 3250000 | 0.031324
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 26402.3037 | 0.81238 | 3250000 | 0.031324
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 25714.3174 | 0.79121 | 3250000 | 0.031324
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 25495.7172 | 1.1589 | 2200000 | 0.058671
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 20446.704 | 0.92414 | 2212500 | 0.058379
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 19824.059 | 0.896 | 2212500 | 0.058379
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 19132.672 | 0.5887 | 3250000 | 0.033334
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 18916.4823 | 0.35691 | 5300000 | 0.0033164
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 17329.993 | 1.2558 | 1380000 | 0.054829
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 15317.1811 | 0.66596 | 2300000 | 0.058671
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 14394.1903 | 0.59174 | 2432500 | 0.033334
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 14194.6418 | 0.58354 | 2432500 | 0.033334
GEN-2024-122 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 14067.1851 | 0.26542 | 5300000 | 0.056647
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 12780.8158 | 0.52542 | 2432500 | 0.029788
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 12007.1275 | 0.87008 | 1380000 | 0.031324
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 11054.5399 | 0.80105 | 1380000 | 0.04878
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 6899.3318 | 0.31183 | 2212500 | 0.041556
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 3675.644 | 0.22277 | 1650000 | 0.031222
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509106 HEMPHIL4 138 509107 SIXMILE4 138 1 | Current Study | 9.32 | (211.00, 211.00) | 1503501.5695 | 13.4433 | 11184000 | 0.095368
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 937752.562 | 0.62415 | 150244000 | 0.023574
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 583129.6138 | 0.61073 | 95480000 | 0.041164
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 528436.8493 | 0.24205 | 218320000 | 0.012448
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 517292.3993 | 0.61073 | 84700000 | 0.041164
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 478927.17 | 0.33306 | 143796000 | 0.027725
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 381280.9076 | 0.19207 | 198511000 | 0.017112
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 367122.4429 | 0.78124 | 46992000 | 0.052735
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 323808.3443 | 0.25941 | 124824000 | 0.028286
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 312796.9202 | 0.27732 | 112794000 | 0.039368
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 310281.1378 | 0.49056 | 63250000 | 0.044395
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 282752.1748 | 0.30085 | 93984000 | 0.031114
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 268372.6164 | 2.2364 | 12000000 | 0.055441
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 225094.3764 | 0.67004 | 33594000 | 0.045567
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at PHILL 7 345 kV | Current Study |  |  | 218180.0742 | 4.1166 | 5300000 | 0.030597
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 214694.6193 | 0.26347 | 81488000 | 0.029157
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 179675.6475 | 0.71018 | 25300000 | 0.024244
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 136049.258 | 1.1337 | 12000000 | 0.069685
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 132723.6671 | 2.011 | 6600000 | 0.069685
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 129939.0258 | 0.50611 | 25674000 | 0.029612
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 113857.9806 | 0.94882 | 12000000 | 0.069685
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 113537.5504 | 0.94615 | 12000000 | 0.055441
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 108115.9242 | 2.0399 | 5300000 | 0.055441
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 104264.7786 | 0.86887 | 12000000 | 0.069685
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 93187.9482 | 0.52037 | 17908000 | 0.03095
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 79595.4867 | 1.206 | 6600000 | 0.069685
GEN-2024-123 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 78649.6505 | 0.43453 | 18100000 | 0.011095
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 78454.9271 | 0.65379 | 12000000 | 0.055441
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 75252.867 | 0.62711 | 12000000 | 0.035369
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 67145.4514 | 0.55955 | 12000000 | 0.021977
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 66462.499 | 2.045 | 3250000 | 0.069685
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 66462.499 | 2.045 | 3250000 | 0.069685
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 61975.6845 | 1.1694 | 5300000 | 0.055441
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 60621.5421 | 0.50518 | 12000000 | 0.027597
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 60621.5421 | 0.50518 | 12000000 | 0.027597
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 60599.7967 | 0.505 | 12000000 | 0.028697
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 60158.5546 | 0.50132 | 12000000 | 0.035369
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV | Current Study |  |  | 59888.3433 | 4.3397 | 1380000 | 0.095368
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 57929.0489 | 0.48274 | 12000000 | 0.021977
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 57633.0646 | 0.48028 | 12000000 | 0.026999
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 49968.8791 | 0.33195 | 15053000 | 0.0073174
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 41162.5883 | 0.77665 | 5300000 | 0.069685
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 40225.2089 | 1.2377 | 3250000 | 0.069685
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 39916.2731 | 0.60479 | 6600000 | 0.041164
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 39179.2722 | 1.2055 | 3250000 | 0.069685
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 38207.9074 | 0.32768 | 11660000 | 0.031114
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 36907.8244 | 1.1356 | 3250000 | 0.069685
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 34492.6146 | 0.52262 | 6600000 | 0.028697
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 34492.6146 | 0.52262 | 6600000 | 0.028697
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 32163.8234 | 0.60686 | 5300000 | 0.031114
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 31381.3215 | 0.5921 | 5300000 | 0.047321
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 30862.8509 | 2.2364 | 1380000 | 0.055441
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 30122.254 | 0.92684 | 3250000 | 0.069685
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 29479.4446 | 0.24566 | 12000000 | 0.014353
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 28812.6308 | 0.54363 | 5300000 | 0.028697
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 28427.0931 | 0.1903 | 14938000 | 0.033782
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 27684.3013 | 1.2513 | 2212500 | 0.10539
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 27519.2704 | 0.1903 | 14460953.1406 | 0.033782
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 26841.2564 | 1.2132 | 2212500 | 0.10539
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 25300.0895 | 0.15625 | 16192000 | 0.029199
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 25222.2018 | 1.8277 | 1380000 | 0.069685
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 23202.9634 | 0.78124 | 2970000 | 0.052735
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 21497.8659 | 0.61073 | 3520000 | 0.041164
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 21371.8235 | 0.65759 | 3250000 | 0.028697
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 20938.6934 | 0.39507 | 5300000 | 0.031114
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 19848.885 | 0.61073 | 3250000 | 0.041164
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 18303.4144 | 0.56318 | 3250000 | 0.028697
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 18140.8332 | 0.55818 | 3250000 | 0.028697
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 17668.1227 | 0.54363 | 3250000 | 0.028697
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 17187.3803 | 0.78124 | 2200000 | 0.052735
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 13393.7104 | 0.41211 | 3250000 | 0.031114
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 13142.5615 | 0.95236 | 1380000 | 0.055441
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 12877.5436 | 0.24297 | 5300000 | 0.0030102
GEN-2024-123 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 10765.7973 | 0.20313 | 5300000 | 0.057804
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 10325.7379 | 0.44895 | 2300000 | 0.052735
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 10076.5651 | 0.41425 | 2432500 | 0.031114
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 9936.8724 | 0.4085 | 2432500 | 0.031114
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 9209.6583 | 0.37861 | 2432500 | 0.02862
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 8250.0111 | 0.59783 | 1380000 | 0.028697
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 7655.2463 | 0.55473 | 1380000 | 0.04504
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 5561.5873 | 0.25137 | 2212500 | 0.044665
GEN-2024-123 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 2578.1341 | 0.15625 | 1650000 | 0.029199
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 52076443.6012 | 3.4383 | 1514620000 | 0.050348
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 48088273.2765 | 4.4785 | 1073760000 | 0.18266
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 44956858.4575 | 3.4982 | 1285130000 | 0.26249
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 44686611.6967 | 3.5141 | 1271630000 | 0.17232
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 27339970.4845 | 2.9135 | 938400000 | 0.11768
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 24429684.7498 | 2.6033 | 938400000 | 0.1861
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 23529464.3075 | 3.2465 | 724760000 | 0.18337
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 16522493.9701 | 3.4219 | 482840000 | 0.20706
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 16204630.8446 | 3.4526 | 469340000 | 0.1404
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 11958670.1803 | 3.2629 | 366500000 | 0.051064
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 3203637.9587 | 3.7913 | 84500000 | 0.05543
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 2743307.7626 | 3.2465 | 84500000 | 0.18337
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 2729259.2344 | 3.2299 | 84500000 | 0.09777
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 2716990.857 | 1.3732 | 197860000 | 0.032317
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 2602009.6873 | 2.0845 | 124824000 | 0.064941
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 2453436.4425 | 1.2359 | 198511000 | 0.03146
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 1951279.1356 | 1.1821 | 165062000 | 0.035419
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 1801315.6011 | 2.2105 | 81488000 | 0.069894
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 1638493.8004 | 2.9672 | 55220000 | 0.068919
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 1424128.9026 | 5.3741 | 26500000 | 0.04022
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 1398346.9886 | 3.2167 | 43472000 | 0.046683
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 848723.0364 | 4.563 | 18600000 | 0.28868
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 653337.0531 | 3.5126 | 18600000 | 0.17232
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 650260.4811 | 3.496 | 18600000 | 0.26249
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 644268.0501 | 3.4638 | 18600000 | 0.17232
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 642191.4469 | 3.4526 | 18600000 | 0.1404
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 639514.7634 | 3.4383 | 18600000 | 0.050348
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 615971.5166 | 3.3117 | 18600000 | 0.30364
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 603852.3596 | 3.2465 | 18600000 | 0.18337
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528018 RED_BLUFF 3 115 528235 WOLFCAMP_TP3 115 1 | Current Study | 7.81 | (598.00, 598.00) | 556294.0302 | 7.1228 | 7810000 | 0.045474
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 487290.9886 | 1.9492 | 25000000 | 0.015744
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 487290.9886 | 1.9492 | 25000000 | 0.01372
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 458698.2978 | 2.4661 | 18600000 | 0.11768
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 414459.6882 | 2.2283 | 18600000 | 0.1861
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 414459.6882 | 2.2283 | 18600000 | 0.1861
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | Current Study | 0.78 | (598.00, 598.00) | 326308.2557 | 6.1661 | 5292000 | 0.041476
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | Current Study | 0.2 | (598.00, 598.00) | 276239.7932 | 6.1661 | 4480000 | 0.041476
GEN-2024-124 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 269700.6999 | 1.4901 | 18100000 | 0.010871
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 192558.8445 | 1.1892 | 16192000 | 0.063495
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 177552.0824 | 1.1886 | 14938000 | 0.060285
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 171881.9349 | 1.1886 | 14460953.1406 | 0.060285
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 151973.4195 | 2.8674 | 5300000 | 0.19554
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 137391.7749 | 2.0957 | 6556000 | 0.068919
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 55400.2076 | 4.0145 | 1380000 | 0.16937
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 55370.4536 | 0.46142 | 12000000 | 0.030569
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 54329.7589 | 3.9369 | 1380000 | 0.19554
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 36834.1392 | 1.6648 | 2212500 | 0.032599
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 36127.4136 | 2.6179 | 1380000 | 0.19554
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 27672.1738 | 1.2507 | 2212500 | 0.063495
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1 | Current Study | 2.13 | (598.00, 598.00) | 26806.9995 | 1.2585 | 2130000 | 0.0065357
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 23795.8504 | 1.7243 | 1380000 | 0.0058747
GEN-2024-124 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 21421.5524 | 1.5523 | 1380000 | 0.046789
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 528184 SENDERO +3 115 528187 SENDERO_345 345 M2 | Current Study |  | (435.00, 435.00) | 20930.4247 | 0.12459 | 16800000 | 0.00023456
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 19622.1649 | 1.1892 | 1650000 | 0.063495
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 13677.0672 | 0.61817 | 2212500 | 0.030569
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 8679.2982 | 0.62893 | 1380000 | 0.030569
GEN-2024-124 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528184 SENDERO +3 115 528193 BLACKRIVER 3 115 1 | Current Study | 0.25 | (598.00, 598.00) | 3146.3614 | 1.2585 | 250000 | 0.0065357
GEN-2024-125 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 4882985.5907 | 0.52035 | 938400000 | 0.039058
GEN-2024-125 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 3889729.5808 | 4.1387 | 93984000 | 0.12841
GEN-2024-125 | 03 CENTRAL | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 3177043.8139 | 1.4552 | 218320000 | 0.022452
GEN-2024-125 | 03 CENTRAL | TBD | ERIS | Rebuild line 645458 S3458 3 345 778170 G24-040-TAP 345 1 | Current Study | 13.15 | (1793.00, 1793.00) | 1215075.2388 | 4.2001 | 28930000 | 0.032564
GEN-2024-125 | 03 CENTRAL | TBD | ERIS | Rebuild line 640139 COOPER 3 345 778170 G24-040-TAP 345 1 | Current Study | 12.59 | (1793.00, 1793.00) | 1163330.5898 | 4.2001 | 27698000 | 0.032564
GEN-2024-125 | 03 CENTRAL | TBD | ERIS | Rebuild line 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 | Current Study | 3.23 | (1793.00, 1793.00) | 618584.3267 | 8.7051 | 7106000 | 0.049062
GEN-2024-125 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 525613.739 | 4.5078 | 11660000 | 0.12841
GEN-2024-125 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 426416.1552 | 0.92873 | 45914000 | 0.023475
GEN-2024-125 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 423831.1731 | 0.21351 | 198511000 | 0.0036084
GEN-2024-125 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 247858.747 | 4.6766 | 5300000 | 0.09943
GEN-2024-125 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 232720.652 | 0.92873 | 25058000 | 0.023475
GEN-2024-125 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 150856.2886 | 0.81106 | 18600000 | 0.071125
GEN-2024-125 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 150856.2886 | 0.81106 | 18600000 | 0.071125
GEN-2024-125 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 75461.2405 | 0.40571 | 18600000 | 0.039058
GEN-2024-125 | 03 CENTRAL | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 61360.5511 | 2.7734 | 2212500 | 0.044575
GEN-2024-125 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 11777.4197 | 0.71378 | 1650000 | 0.021635
GEN-2024-128 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2 | Current Study |  | (478.00, 478.00) | 4745804.4742 | 26.2199 | 18100000 | 0.063593
GEN-2024-128 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2 | Current Study |  | (484.00, 515.00) | 2433776.5094 | 13.4463 | 18100000 | 0.018892
GEN-2024-128 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511425 TUTCONT4 138 514898 CIMARON4 138 1 | Current Study | 14.65 | (395.00, 395.00) | 1450047.7087 | 8.2483 | 17580000 | 0.020889
GEN-2024-128 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 477873.5022 | 2.6402 | 18100000 | 0.011724
GEN-2024-128 | 04 SOUTHEAST | TBD | ERIS | Add 10 MVAR switched shunt at G20-007-TAP 345 kV | Current Study |  |  | 394895.7732 | 7.4509 | 5300000 | 0.04235
GEN-2024-128 | 04 SOUTHEAST | TBD | ERIS | Add 38 MVAR switched shunt at FRNT2WD7 345 kV | Current Study |  |  | 282698.2533 | 5.3339 | 5300000 | 0.045519
GEN-2024-128 | 04 SOUTHEAST | TBD | ERIS | Add 19 MVAR switched shunt at RANCHRD7 345 kV | Current Study |  |  | 258822.6655 | 4.8834 | 5300000 | 0.045519
GEN-2024-128 | 04 SOUTHEAST | TBD | ERIS | Add 0.42 MVAR switched shunt at TWNLKSW4 138 kV | Current Study |  |  | 254896.1548 | 10.4788 | 2432500 | 0.06055
GEN-2024-128 | 04 SOUTHEAST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 111222.1435 | 8.0596 | 1380000 | 0.14787
GEN-2024-128 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 56682.015 | 1.0695 | 5300000 | 0.033345
GEN-2024-128 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 38605.7401 | 0.72841 | 5300000 | 0.036049
GEN-2024-129 | 03 CENTRAL | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 | Current Study | 30.44 | (1793.00, 1793.00) | 66968000 | 100 | 66968000 | 0.33593
GEN-2024-129 | 03 CENTRAL | TBD | ERIS | Add 10 MVAR switched shunt at G20-007-TAP 345 kV | Current Study |  |  | 454386.9883 | 8.5733 | 5300000 | 0.036949
GEN-2024-129 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 449896.5812 | 8.4886 | 5300000 | 0.079331
GEN-2024-132 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 521157 HUGO 7 345 560088 BISON 7 345 1 | Current Study | 74.88 | (1793.00, 1793.00) | 164736000 | 100 | 164736000 | 0.41868
GEN-2024-132 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 13219052.0189 | 11.7196 | 112794000 | 0.15357
GEN-2024-132 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2 | Current Study |  | (478.00, 478.00) | 11464316.4811 | 63.3388 | 18100000 | 0.037258
GEN-2024-132 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 514808 JOHNCO 4 138 514809 JOHNCO 7 345 514810 JOHNCO11 13 M2 | Current Study |  | (478.00, 478.00) | 9075306.0822 | 50.1398 | 18100000 | 0.024475
GEN-2024-132 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2 | Current Study |  | (484.00, 515.00) | 5406268.2149 | 29.8689 | 18100000 | 0.022274
GEN-2024-132 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | Current Study | 13.16 | (395.00, 395.00) | 3966808.6667 | 25.1191 | 15792000 | 0.038167
GEN-2024-132 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 | Current Study | 6.08 | (395.00, 395.00) | 1832689.7184 | 25.1191 | 7296000 | 0.038167
GEN-2024-132 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1 | Current Study | 11.3 | (1793.00, 1793.00) | 1455183.3821 | 5.8535 | 24860000 | 0.027777
GEN-2024-132 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 784986.527 | 4.3369 | 18100000 | 0.010222
GEN-2024-132 | 04 SOUTHEAST | TBD | ERIS | Add 10 MVAR switched shunt at G20-007-TAP 345 kV | Current Study |  |  | 648592.5358 | 12.2376 | 5300000 | 0.036919
GEN-2024-132 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 530568.9708 | 10.0107 | 5300000 | 0.16566
GEN-2024-132 | 04 SOUTHEAST | TBD | ERIS | Add 38 MVAR switched shunt at FRNT2WD7 345 kV | Current Study |  |  | 527425.0261 | 9.9514 | 5300000 | 0.045075
GEN-2024-132 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | Current Study | 0.64 | (717.00, 717.00) | 486441.7159 | 63.3388 | 768000 | 0.074516
GEN-2024-132 | 04 SOUTHEAST | TBD | ERIS | Add 19 MVAR switched shunt at RANCHRD7 345 kV | Current Study |  |  | 482880.773 | 9.111 | 5300000 | 0.045075
GEN-2024-132 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 521049 SCLMNJC4 138 784980 G24-267-TAP 138 1 | Current Study | 6.96 | (472.00, 472.00) | 450633.5381 | 5.3955 | 8352000 | 0.0093597
GEN-2024-132 | 04 SOUTHEAST | TBD | ERIS | Add 0.42 MVAR switched shunt at TWNLKSW4 138 kV | Current Study |  |  | 359115.0188 | 14.7632 | 2432500 | 0.045278
GEN-2024-132 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2 | Current Study |  | (478.00, 478.00) | 332376.953 | 1.8363 | 18100000 | 0.0023639
GEN-2024-132 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 300055.068 | 5.6614 | 5300000 | 0.14871
GEN-2024-132 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 | Current Study | 0.55 | (395.00, 395.00) | 165786.0765 | 25.1191 | 660000 | 0.038167
GEN-2024-132 | 04 SOUTHEAST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 50430.0043 | 3.6543 | 1380000 | 0.035587
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 20304032.6058 | 2.16 | 940000000 | 0.024416
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 532803 BURNS 7 345 1 | Current Study | 50.03 | (1793.00, 1793.00) | 5829689.8867 | 5.2965 | 110066000 | 0.044223
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532803 BURNS 7 345 1 | Current Study | 45.5 | (1793.00, 1793.00) | 5301836.6948 | 5.2965 | 100100000 | 0.044223
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 80 MVAR SVC at AUBURN 6 230 kV | Current Study |  |  | 4300000 | 50 | 8600000 | 0.014919
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 2803585.3945 | 1.866 | 150244000 | 0.03383
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TECHILL6 230 kV | Current Study |  |  | 1912500 | 50 | 3825000 | 0.014919
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1774740.3073 | 0.81291 | 218320000 | 0.020067
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 1623538.7031 | 1.3843 | 117282000 | 0.023304
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1383339.9218 | 0.96202 | 143796000 | 0.038439
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1309902.6475 | 1.3043 | 100427000 | 0.013401
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 982334.3465 | 1.7811 | 55154000 | 0.025127
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 905465.9999 | 0.45763 | 197860000 | 0.018093
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 873347.0489 | 0.65692 | 132946000 | 0.016339
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 785623.2987 | 0.87354 | 89936000 | 0.0081627
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 649990.904 | 0.39379 | 165062000 | 0.019821
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 543625.4397 | 4.5302 | 12000000 | 0.12525
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 479958.1197 | 0.24178 | 198511000 | 0.010339
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 470203.9154 | 1.7811 | 26400000 | 0.025127
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 25 MVAR switched shunt at HIGHPT 3 115 kV | Current Study |  |  | 466717.5801 | 21.0946 | 2212500 | 0.063427
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 407301.7784 | 1.5558 | 26180000 | 0.014063
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 359423.6011 | 0.37644 | 95480000 | 0.012179
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 318843.5171 | 0.37644 | 84700000 | 0.012179
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 314396.2388 | 2.62 | 12000000 | 0.10086
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 138 MVAR switched shunt at GEN-2024-016 345 kV | Current Study |  |  | 311670.8011 | 5.8806 | 5300000 | 0.029453
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at SHARNSP3 115 kV | Current Study |  |  | 295587.4999 | 13.3599 | 2212500 | 0.03169
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 8 MVAR switched shunt at RANSOM 3 115 kV | Current Study |  |  | 295587.4999 | 13.3599 | 2212500 | 0.03169
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at GRANTTP3 115 kV | Current Study |  |  | 285160.2381 | 12.8886 | 2212500 | 0.057497
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at PNTPR-GOAB3 115 kV | Current Study |  |  | 285160.2381 | 12.8886 | 2212500 | 0.057497
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 279580.4262 | 5.2751 | 5300000 | 0.041395
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 276191.6988 | 0.51663 | 53460000 | 0.014919
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 270286.9868 | 5.0998 | 5300000 | 0.05417
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 246975.5776 | 2.0581 | 12000000 | 0.038802
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 245312.1402 | 2.0443 | 12000000 | 0.057497
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 222965.6091 | 0.88129 | 25300000 | 0.014441
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 213075.6442 | 1.7756 | 12000000 | 0.038802
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 206247.1469 | 3.8915 | 5300000 | 0.038802
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 200323.938 | 1.6694 | 12000000 | 0.067949
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 199175.8048 | 0.42385 | 46992000 | 0.013733
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 194334.5488 | 1.291 | 15053000 | 0.01366
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 0.06 MVAR switched shunt at G24-125-TAP 345 kV | Current Study |  |  | 183495.2286 | 3.4622 | 5300000 | 0.019782
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 122 MVAR switched shunt at HOYT 7 345 kV | Current Study |  |  | 174791.4818 | 3.298 | 5300000 | 0.019478
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 173647.2215 | 1.4095 | 12320000 | 0.024195
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 163444.6392 | 1.362 | 12000000 | 0.024195
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 163444.6392 | 1.362 | 12000000 | 0.024195
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 145720.4002 | 1.2143 | 12000000 | 0.024195
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 133906.2518 | 2.5265 | 5300000 | 0.057497
GEN-2024-134 | 04 SOUTHEAST | TBD | NRIS | Add 0.09 MVAR switched shunt at GRAY CO3 115 kV | Current Study |  |  | 132396.0435 | 5.984 | 2212500 | 0.086914
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 128078.5441 | 1.0673 | 12000000 | 0.036144
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 121447.7357 | 1.0121 | 12000000 | 0.028383
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 110725.1576 | 0.92271 | 12000000 | 0.024195
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 110725.1576 | 0.92271 | 12000000 | 0.024195
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 107598.5206 | 0.89665 | 12000000 | 0.024195
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 103795.6375 | 1.9584 | 5300000 | 0.041041
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 100114.4593 | 0.83429 | 12000000 | 0.022586
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 98409.628 | 0.82008 | 12000000 | 0.024195
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 90674.7699 | 0.75562 | 12000000 | 0.0081627
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 74891.193 | 0.62409 | 12000000 | 0.017023
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 73674.7457 | 1.3901 | 5300000 | 0.038802
GEN-2024-134 | 04 SOUTHEAST | TBD | NRIS | Add 16 MVAR switched shunt at UNDERWOOD 2 345 kV | Current Study |  |  | 73359.6798 | 1.3841 | 5300000 | 0.086914
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 69483.403 | 1.311 | 5300000 | 0.038802
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 68385.6129 | 0.56988 | 12000000 | 0.063427
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 64645.2708 | 0.39924 | 16192000 | 0.035812
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 61425.7314 | 1.159 | 5300000 | 0.023304
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at SLKHILLS 4 138 kV | Current Study |  |  | 60170.4339 | 2.4736 | 2432500 | 0.074398
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 48877.6621 | 0.74057 | 6600000 | 0.024195
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 39183.6596 | 1.7811 | 2200000 | 0.025127
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 39069.649 | 0.59196 | 6600000 | 0.018701
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 37644.2455 | 0.71027 | 5300000 | 0.019475
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 0.5 MVAR switched shunt at RKY_RDG4 138 kV | Current Study |  |  | 36487.2983 | 1.5 | 2432500 | 0.074398
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 34790.9256 | 0.2329 | 14938000 | 0.019845
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 33770.4749 | 0.28142 | 12000000 | 0.0099209
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 33679.8731 | 0.2329 | 14460953.1406 | 0.019845
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 29774.4733 | 0.56178 | 5300000 | 0.024195
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 27011.2745 | 0.50965 | 5300000 | 0.035812
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 26219.7502 | 0.49471 | 5300000 | 0.018701
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 21840.5455 | 1.5826 | 1380000 | 0.044223
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 21788.5776 | 0.67042 | 3250000 | 0.024195
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 18872.2671 | 0.35608 | 5300000 | 0.01366
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 18272.8048 | 1.3843 | 1320000 | 0.023304
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 16771.8078 | 0.51606 | 3250000 | 0.018701
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 16208.7606 | 0.30583 | 5300000 | 0.0018187
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 13250.6397 | 0.37644 | 3520000 | 0.012179
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 12681.9735 | 0.015563 | 81488000 | 0.00082669
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 12618.0281 | 0.51873 | 2432500 | 0.018701
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 12588.3584 | 0.42385 | 2970000 | 0.013733
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 12443.1028 | 0.51154 | 2432500 | 0.018701
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 12234.2535 | 0.37644 | 3250000 | 0.012179
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at SEGNTP 3 115 kV | Current Study |  |  | 11902.4305 | 0.53796 | 2212500 | 0.035812
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 9834.1385 | 0.0078784 | 124824000 | 0.00041234
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 9324.71 | 0.42385 | 2200000 | 0.013733
GEN-2024-134 | 04 SOUTHEAST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 8891.6166 | 0.64432 | 1380000 | 0.032628
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 8439.8364 | 0.38146 | 2212500 | 0.03169
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 8226.2339 | 0.5961 | 1380000 | 0.018701
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 6587.4936 | 0.39924 | 1650000 | 0.035812
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 5602.0495 | 0.24357 | 2300000 | 0.013733
GEN-2024-134 | 04 SOUTHEAST | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 1671.5741 | 0.075551 | 2212500 | 0.0019429
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 20304032.6058 | 2.16 | 940000000 | 0.024416
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 532803 BURNS 7 345 1 | Current Study | 50.03 | (1793.00, 1793.00) | 5829689.8867 | 5.2965 | 110066000 | 0.044223
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532803 BURNS 7 345 1 | Current Study | 45.5 | (1793.00, 1793.00) | 5301836.6948 | 5.2965 | 100100000 | 0.044223
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 80 MVAR SVC at AUBURN 6 230 kV | Current Study |  |  | 4300000 | 50 | 8600000 | 0.014919
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 2803585.3945 | 1.866 | 150244000 | 0.03383
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TECHILL6 230 kV | Current Study |  |  | 1912500 | 50 | 3825000 | 0.014919
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1774740.3073 | 0.81291 | 218320000 | 0.020067
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 1623538.7031 | 1.3843 | 117282000 | 0.023304
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1383339.9218 | 0.96202 | 143796000 | 0.038439
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1309902.6475 | 1.3043 | 100427000 | 0.013401
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 982334.3465 | 1.7811 | 55154000 | 0.025127
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 905465.9999 | 0.45763 | 197860000 | 0.018093
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 873347.0489 | 0.65692 | 132946000 | 0.016339
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 785623.2987 | 0.87354 | 89936000 | 0.0081627
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 649990.904 | 0.39379 | 165062000 | 0.019821
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 543625.4397 | 4.5302 | 12000000 | 0.12525
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 479958.1197 | 0.24178 | 198511000 | 0.010339
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 470203.9154 | 1.7811 | 26400000 | 0.025127
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 25 MVAR switched shunt at HIGHPT 3 115 kV | Current Study |  |  | 466717.5801 | 21.0946 | 2212500 | 0.063427
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 407301.7784 | 1.5558 | 26180000 | 0.014063
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 359423.6011 | 0.37644 | 95480000 | 0.012179
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 318843.5171 | 0.37644 | 84700000 | 0.012179
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 314396.2388 | 2.62 | 12000000 | 0.10086
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 138 MVAR switched shunt at GEN-2024-016 345 kV | Current Study |  |  | 311670.8011 | 5.8806 | 5300000 | 0.029453
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at SHARNSP3 115 kV | Current Study |  |  | 295587.4999 | 13.3599 | 2212500 | 0.03169
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 8 MVAR switched shunt at RANSOM 3 115 kV | Current Study |  |  | 295587.4999 | 13.3599 | 2212500 | 0.03169
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at GRANTTP3 115 kV | Current Study |  |  | 285160.2381 | 12.8886 | 2212500 | 0.057497
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at PNTPR-GOAB3 115 kV | Current Study |  |  | 285160.2381 | 12.8886 | 2212500 | 0.057497
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 279580.4262 | 5.2751 | 5300000 | 0.041395
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 276191.6988 | 0.51663 | 53460000 | 0.014919
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 270286.9868 | 5.0998 | 5300000 | 0.05417
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 246975.5776 | 2.0581 | 12000000 | 0.038802
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 245312.1402 | 2.0443 | 12000000 | 0.057497
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 222965.6091 | 0.88129 | 25300000 | 0.014441
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 213075.6442 | 1.7756 | 12000000 | 0.038802
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 206247.1469 | 3.8915 | 5300000 | 0.038802
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 200323.938 | 1.6694 | 12000000 | 0.067949
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 199175.8048 | 0.42385 | 46992000 | 0.013733
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 194334.5488 | 1.291 | 15053000 | 0.01366
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 0.06 MVAR switched shunt at G24-125-TAP 345 kV | Current Study |  |  | 183495.2286 | 3.4622 | 5300000 | 0.019782
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 122 MVAR switched shunt at HOYT 7 345 kV | Current Study |  |  | 174791.4818 | 3.298 | 5300000 | 0.019478
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 173647.2215 | 1.4095 | 12320000 | 0.024195
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 163444.6392 | 1.362 | 12000000 | 0.024195
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 163444.6392 | 1.362 | 12000000 | 0.024195
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 145720.4002 | 1.2143 | 12000000 | 0.024195
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 133906.2518 | 2.5265 | 5300000 | 0.057497
GEN-2024-135 | 04 SOUTHEAST | TBD | NRIS | Add 0.09 MVAR switched shunt at GRAY CO3 115 kV | Current Study |  |  | 132396.0435 | 5.984 | 2212500 | 0.086914
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 128078.5441 | 1.0673 | 12000000 | 0.036144
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 121447.7357 | 1.0121 | 12000000 | 0.028383
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 110725.1576 | 0.92271 | 12000000 | 0.024195
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 110725.1576 | 0.92271 | 12000000 | 0.024195
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 107598.5206 | 0.89665 | 12000000 | 0.024195
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 103795.6375 | 1.9584 | 5300000 | 0.041041
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 100114.4593 | 0.83429 | 12000000 | 0.022586
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 98409.628 | 0.82008 | 12000000 | 0.024195
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 90674.7699 | 0.75562 | 12000000 | 0.0081627
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 74891.193 | 0.62409 | 12000000 | 0.017023
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 73674.7457 | 1.3901 | 5300000 | 0.038802
GEN-2024-135 | 04 SOUTHEAST | TBD | NRIS | Add 16 MVAR switched shunt at UNDERWOOD 2 345 kV | Current Study |  |  | 73359.6798 | 1.3841 | 5300000 | 0.086914
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 69483.403 | 1.311 | 5300000 | 0.038802
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 68385.6129 | 0.56988 | 12000000 | 0.063427
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 64645.2708 | 0.39924 | 16192000 | 0.035812
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 61425.7314 | 1.159 | 5300000 | 0.023304
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at SLKHILLS 4 138 kV | Current Study |  |  | 60170.4339 | 2.4736 | 2432500 | 0.074398
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 48877.6621 | 0.74057 | 6600000 | 0.024195
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 39183.6596 | 1.7811 | 2200000 | 0.025127
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 39069.649 | 0.59196 | 6600000 | 0.018701
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 37644.2455 | 0.71027 | 5300000 | 0.019475
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 0.5 MVAR switched shunt at RKY_RDG4 138 kV | Current Study |  |  | 36487.2983 | 1.5 | 2432500 | 0.074398
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 34790.9256 | 0.2329 | 14938000 | 0.019845
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 33770.4749 | 0.28142 | 12000000 | 0.0099209
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 33679.8731 | 0.2329 | 14460953.1406 | 0.019845
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 29774.4733 | 0.56178 | 5300000 | 0.024195
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 27011.2745 | 0.50965 | 5300000 | 0.035812
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 26219.7502 | 0.49471 | 5300000 | 0.018701
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 21840.5455 | 1.5826 | 1380000 | 0.044223
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 21788.5776 | 0.67042 | 3250000 | 0.024195
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 18872.2671 | 0.35608 | 5300000 | 0.01366
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 18272.8048 | 1.3843 | 1320000 | 0.023304
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 16771.8078 | 0.51606 | 3250000 | 0.018701
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 16208.7606 | 0.30583 | 5300000 | 0.0018187
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 13250.6397 | 0.37644 | 3520000 | 0.012179
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 12681.9735 | 0.015563 | 81488000 | 0.00082669
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 12618.0281 | 0.51873 | 2432500 | 0.018701
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 12588.3584 | 0.42385 | 2970000 | 0.013733
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 12443.1028 | 0.51154 | 2432500 | 0.018701
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 12234.2535 | 0.37644 | 3250000 | 0.012179
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at SEGNTP 3 115 kV | Current Study |  |  | 11902.4305 | 0.53796 | 2212500 | 0.035812
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 9834.1385 | 0.0078784 | 124824000 | 0.00041234
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 9324.71 | 0.42385 | 2200000 | 0.013733
GEN-2024-135 | 04 SOUTHEAST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 8891.6166 | 0.64432 | 1380000 | 0.032628
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 8439.8364 | 0.38146 | 2212500 | 0.03169
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 8226.2339 | 0.5961 | 1380000 | 0.018701
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 6587.4936 | 0.39924 | 1650000 | 0.035812
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 5602.0495 | 0.24357 | 2300000 | 0.013733
GEN-2024-135 | 04 SOUTHEAST | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 1671.5741 | 0.075551 | 2212500 | 0.0019429
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add line 659131 LARAMIE_-MB3 345 800120 UNDERWOOD 2 345 P2 | Current Study | 206.4 | (1792.00, 1792.00) | 125114356.0616 | 19.2531 | 649840000 | 0.027485
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add line 652424 BELFELD3 345 800121 MAURINE 2 345 P2 | Current Study | 154.2 | (1792.00, 1792.00) | 102098704.2718 | 20.921 | 488020000 | 0.021518
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 86068445.4561 | 9.1562 | 940000000 | 0.064686
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Rebuild line 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Current Study | 75.83 | (1793.00, 1793.00) | 40868410.5637 | 24.4976 | 166826000 | 0.13733
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add line 652424 BELFELD3 345 659183 CHARL_CK-BE3 345 P2 | Current Study | 40.74 | (531.00, 531.00) | 31436127.357 | 23.0649 | 136294000 | 0.018911
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 31250833.7858 | 23.5064 | 132946000 | 0.36541
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Rebuild line 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | Current Study | 84.86 | (1793.00, 1793.00) | 20794924.404 | 11.1386 | 186692000 | 0.097128
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Rebuild line 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Current Study | 38.26 | (1793.00, 1793.00) | 12377499.278 | 14.705 | 84172000 | 0.17784
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 12348180.9211 | 6.2204 | 198511000 | 0.10513
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Rebuild line 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Current Study | 37.4 | (1793.00, 1793.00) | 12232931.9974 | 14.8674 | 82280000 | 0.17784
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 10436991.0086 | 5.2749 | 197860000 | 0.13035
GEN-2024-136 | 03 CENTRAL | TBD | NRIS | Rebuild line 640100 CAMBRIG7 115 640269 MCCOOK 7 115 1 | Current Study | 28.11 | (176.00, 176.00) | 8154771.1496 | 29.0102 | 28110000 | 0.017858
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 7153247.0931 | 4.3337 | 165062000 | 0.13633
GEN-2024-136 | 03 CENTRAL | TBD | NRIS | Rebuild line 640194 GOSPER 7 115 640242 JOHN.2 7 115 1 | Current Study | 24.13 | (176.00, 176.00) | 7000164.6332 | 29.0102 | 24130000 | 0.017858
GEN-2024-136 | 03 CENTRAL | TBD | NRIS | Rebuild line 640326 REDWILO7 115 640365 STOCKVL7 115 1 | Current Study | 21.09 | (176.00, 176.00) | 6023339.2038 | 28.5602 | 21090000 | 0.013458
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | Current Study | 21.05 | (1793.00, 1793.00) | 5562248.3742 | 12.0109 | 46310000 | 0.1591
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 531259 SETAB 1 13 531464 SETAB 3 115 531465 SETAB 7 345 M2 | Current Study |  | (280.00, 308.00) | 4417377.4547 | 26.2939 | 16800000 | 0.031937
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Rebuild line 523961 POTTER_CO 7 345 784950 G24-266_TAP 345 1 | Current Study | 18.24 | (1793.00, 1793.00) | 4414138.4879 | 11.0001 | 40128000 | 0.097128
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | Current Study | 19.2 | (2390.00, 2390.00) | 4150861.8156 | 9.8269 | 42240000 | 0.12555
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 3907064.6747 | 1.9682 | 198511000 | 0.052604
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR SVC at GEN-2021-076 345 kV | Current Study |  |  | 3537459.0706 | 29.4788 | 12000000 | 0.17784
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | Current Study | 16.04 | (2390.00, 2390.00) | 3467699.1418 | 9.8269 | 35288000 | 0.12555
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Rebuild line 531419 DOBSON 3 115 531493 GANO 3 115 1 | Current Study | 11.92 | (260.00, 260.00) | 3287979.1204 | 27.5837 | 11920000 | 0.023721
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Rebuild line 531432 PILE 3 115 531433 SCOTCTY3 115 1 | Current Study | 11.88 | (260.00, 260.00) | 3276945.6334 | 27.5837 | 11880000 | 0.023721
GEN-2024-136 | 03 CENTRAL | TBD | NRIS | Rebuild line 640100 CAMBRIG7 115 640194 GOSPER 7 115 1 | Current Study | 8.61 | (176.00, 176.00) | 2497779.4236 | 29.0102 | 8610000 | 0.017858
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Rebuild line 531432 PILE 3 115 531493 GANO 3 115 1 | Current Study | 8.34 | (260.00, 260.00) | 2300482.0356 | 27.5837 | 8340000 | 0.023721
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | Current Study | 13 | (2390.00, 2390.00) | 2260731.2075 | 7.9047 | 28600000 | 0.12497
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 1725097.8986 | 14.3758 | 12000000 | 1
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add 525 MVAR SVC at SD.LS-LR-MB3 345 kV | Current Study |  |  | 1573547.3099 | 13.1129 | 12000000 | 0.25985
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add 0.8 MVAR switched shunt at HARBNGR7 345 kV | Current Study |  |  | 1021376.6353 | 19.2713 | 5300000 | 1
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MINGO 7 345 kV | Current Study |  |  | 999531.7435 | 18.8591 | 5300000 | 0.36265
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Rebuild line 531433 SCOTCTY3 115 531464 SETAB 3 115 1 | Current Study | 2.77 | (394.00, 394.00) | 817152.4473 | 29.5001 | 2770000 | 0.049188
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 750507.6162 | 4.6351 | 16192000 | 0.25985
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add 66 MVAR switched shunt at GEN-2021-021 345 kV | Current Study |  |  | 611270.0502 | 11.5334 | 5300000 | 0.0029892
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 592504.1632 | 0.06314 | 938400000 | 0.0047393
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add 24 MVAR switched shunt at NESSCTY3 115 kV | Current Study |  |  | 584843.5868 | 26.4336 | 2212500 | 1
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 541572.2579 | 1.1795 | 45914000 | 0.029814
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add 248 MVAR switched shunt at GEN-2022-015 345 kV | Current Study |  |  | 537453.076 | 10.1406 | 5300000 | 0.36265
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add 40 MVAR switched shunt at SEGNTP 3 115 kV | Current Study |  |  | 531781.2452 | 24.0353 | 2212500 | 1
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR switched shunt at GEN-2022-075 345 kV | Current Study |  |  | 451196.937 | 8.5131 | 5300000 | 0.13675
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 437650.2355 | 8.2576 | 5300000 | 0.36265
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add 12 MVAR switched shunt at BEELER 3 115 kV | Current Study |  |  | 432355.101 | 19.5415 | 2212500 | 0.36265
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 426116.7896 | 19.2595 | 2212500 | 1
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 369159.0617 | 0.25672 | 143796000 | 0.0064112
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add 7 MVAR switched shunt at G19-030-TAP 345 kV | Current Study |  |  | 369146.302 | 6.965 | 5300000 | 0.13675
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 531448 HOLCOMB3 115 531449 HOLCOMB7 345 531450 HOLCTER1 13 M2 | Current Study |  | (336.00, 358.50) | 320218.8333 | 1.9061 | 16800000 | 0.0052029
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add 0.04 MVAR switched shunt at ELLIS 2 69 kV | Current Study |  |  | 316291.0604 | 22.9196 | 1380000 | 1
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 295568.1848 | 1.1795 | 25058000 | 0.029814
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 295492.175 | 1.9781 | 14938000 | 0.10535
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 286055.5963 | 1.9781 | 14460953.1406 | 0.10535
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Rebuild line 531405 WALKMYR3 115 531481 HUGOTON3 115 1 | Current Study | 12.27 | (598.00, 598.00) | 275343.3463 | 2.244 | 12270000 | 0.016434
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 270408.46 | 19.5948 | 1380000 | 1
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2 | Current Study |  | (350.00, 385.00) | 257667.2009 | 1.5337 | 16800000 | 0.0068272
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at IRS7 115 KV 115 kV | Current Study |  |  | 188353.4383 | 8.5131 | 2212500 | 0.13675
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add 60 MVAR switched shunt at WAYSIDE 4 230 kV | Current Study |  |  | 182746.5256 | 4.7777 | 3825000 | 0.038489
GEN-2024-136 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 180384.8339 | 3.4035 | 5300000 | 0.072362
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MED-LDG3 115 kV | Current Study |  |  | 175699.4924 | 7.9412 | 2212500 | 0.13675
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 171106.5027 | 3.2284 | 5300000 | 0.055324
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 119739.9904 | 5.412 | 2212500 | 0.13675
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 116093.657 | 5.2472 | 2212500 | 0.13675
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 107853.5268 | 4.8747 | 2212500 | 0.25985
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 101209.9491 | 1.9096 | 5300000 | 0.033315
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 94269.1668 | 0.50682 | 18600000 | 0.044446
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 94269.1668 | 0.50682 | 18600000 | 0.044446
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 92124.9796 | 0.4953 | 18600000 | 0.047683
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 531405 WALKMYR3 115 531510 HARBNGR3 115 M2 | Current Study | 1.28 | (598.00, 598.00) | 91901.3017 | 1.5337 | 5992000 | 0.0068272
GEN-2024-136 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 76478.3576 | 4.6351 | 1650000 | 0.25985
GEN-2024-136 | 03 CENTRAL | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 26710.7389 | 1.9356 | 1380000 | 0.061259
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add line 659131 LARAMIE_-MB3 345 800120 UNDERWOOD 2 345 P2 | Current Study | 206.4 | (1792.00, 1792.00) | 82786986.8194 | 12.7396 | 649840000 | 0.024535
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add line 652424 BELFELD3 345 800121 MAURINE 2 345 P2 | Current Study | 154.2 | (1792.00, 1792.00) | 72701264.2959 | 14.8972 | 488020000 | 0.02067
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 63561324.1206 | 6.7618 | 940000000 | 0.064446
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Rebuild line 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Current Study | 75.83 | (1793.00, 1793.00) | 29796232.766 | 17.8607 | 166826000 | 0.13507
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add line 652424 BELFELD3 345 659183 CHARL_CK-BE3 345 P2 | Current Study | 40.74 | (531.00, 531.00) | 24108208.927 | 17.6884 | 136294000 | 0.019565
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 23271598.3019 | 17.5045 | 132946000 | 0.3671
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Rebuild line 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | Current Study | 84.86 | (1793.00, 1793.00) | 14866023.0978 | 7.9629 | 186692000 | 0.093674
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 9287435.1538 | 4.6785 | 198511000 | 0.10667
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Rebuild line 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Current Study | 38.26 | (1793.00, 1793.00) | 8927729.1951 | 10.6065 | 84172000 | 0.17305
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Rebuild line 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Current Study | 37.4 | (1793.00, 1793.00) | 8823454.6965 | 10.7237 | 82280000 | 0.17305
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 7715157.3751 | 3.8993 | 197860000 | 0.12999
GEN-2024-137 | 03 CENTRAL | TBD | NRIS | Rebuild line 640100 CAMBRIG7 115 640269 MCCOOK 7 115 1 | Current Study | 28.11 | (176.00, 176.00) | 5328537.4753 | 18.956 | 28110000 | 0.015742
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 5256910.3319 | 3.1848 | 165062000 | 0.13517
GEN-2024-137 | 03 CENTRAL | TBD | NRIS | Rebuild line 640194 GOSPER 7 115 640242 JOHN.2 7 115 1 | Current Study | 24.13 | (176.00, 176.00) | 4574087.8434 | 18.956 | 24130000 | 0.015742
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | Current Study | 21.05 | (1793.00, 1793.00) | 4102478.3282 | 8.8587 | 46310000 | 0.15831
GEN-2024-137 | 03 CENTRAL | TBD | NRIS | Rebuild line 640326 REDWILO7 115 640365 STOCKVL7 115 1 | Current Study | 21.09 | (176.00, 176.00) | 3958576.1625 | 18.7699 | 21090000 | 0.011932
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 531259 SETAB 1 13 531464 SETAB 3 115 531465 SETAB 7 345 M2 | Current Study |  | (280.00, 308.00) | 3285781.4078 | 19.5582 | 16800000 | 0.032048
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Rebuild line 523961 POTTER_CO 7 345 784950 G24-266_TAP 345 1 | Current Study | 18.24 | (1793.00, 1793.00) | 3155610.6405 | 7.8639 | 40128000 | 0.093674
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | Current Study | 19.2 | (2390.00, 2390.00) | 3001992.9479 | 7.107 | 42240000 | 0.12249
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 2909861.0209 | 1.4658 | 198511000 | 0.052854
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | Current Study | 16.04 | (2390.00, 2390.00) | 2507914.9419 | 7.107 | 35288000 | 0.12249
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Rebuild line 531419 DOBSON 3 115 531493 GANO 3 115 1 | Current Study | 11.92 | (260.00, 260.00) | 2479179.0125 | 20.7985 | 11920000 | 0.02413
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Rebuild line 531432 PILE 3 115 531433 SCOTCTY3 115 1 | Current Study | 11.88 | (260.00, 260.00) | 2470859.6198 | 20.7985 | 11880000 | 0.02413
GEN-2024-137 | 03 CENTRAL | TBD | NRIS | Add 78 MVAR SVC at STEGALL_-MB3 345 kV | Current Study |  |  | 2059962.3173 | 17.1664 | 12000000 | 0.030386
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Rebuild line 531432 PILE 3 115 531493 GANO 3 115 1 | Current Study | 8.34 | (260.00, 260.00) | 1734593.3695 | 20.7985 | 8340000 | 0.02413
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | Current Study | 13 | (2390.00, 2390.00) | 1635009.6542 | 5.7168 | 28600000 | 0.12193
GEN-2024-137 | 03 CENTRAL | TBD | NRIS | Rebuild line 640100 CAMBRIG7 115 640194 GOSPER 7 115 1 | Current Study | 8.61 | (176.00, 176.00) | 1632113.3996 | 18.956 | 8610000 | 0.015742
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 1278728.8173 | 10.6561 | 12000000 | 1
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add 525 MVAR SVC at SD.LS-LR-MB3 345 kV | Current Study |  |  | 1162869.9252 | 9.6906 | 12000000 | 0.25906
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 774179.6976 | 14.6072 | 5300000 | 0.36452
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add 0.8 MVAR switched shunt at HARBNGR7 345 kV | Current Study |  |  | 757095.4309 | 14.2848 | 5300000 | 1
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MINGO 7 345 kV | Current Study |  |  | 744736.1914 | 14.0516 | 5300000 | 0.36452
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 703063.4823 | 1.5313 | 45914000 | 0.052216
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Rebuild line 531433 SCOTCTY3 115 531464 SETAB 3 115 1 | Current Study | 2.77 | (394.00, 394.00) | 607149.2221 | 21.9187 | 2770000 | 0.049305
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 554633.9582 | 3.4254 | 16192000 | 0.25906
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 531337.6816 | 0.36951 | 143796000 | 0.012449
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add 24 MVAR switched shunt at NESSCTY3 115 kV | Current Study |  |  | 433515.3087 | 19.5939 | 2212500 | 1
GEN-2024-137 | 03 CENTRAL | TBD | NRIS | Add 0.7 MVAR switched shunt at STEGALL_-MB4 230 kV | Current Study |  |  | 418382.9586 | 10.9381 | 3825000 | 0.030386
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add 248 MVAR switched shunt at GEN-2022-015 345 kV | Current Study |  |  | 400448.2695 | 7.5556 | 5300000 | 0.36452
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add 40 MVAR switched shunt at SEGNTP 3 115 kV | Current Study |  |  | 394182.848 | 17.8162 | 2212500 | 1
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 531448 HOLCOMB3 115 531449 HOLCOMB7 345 531450 HOLCTER1 13 M2 | Current Study |  | (336.00, 358.50) | 390262.8831 | 2.323 | 16800000 | 0.0085544
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 383703.5488 | 1.5313 | 25058000 | 0.052216
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR switched shunt at GEN-2022-075 345 kV | Current Study |  |  | 331679.1503 | 6.2581 | 5300000 | 0.13562
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 326086.6618 | 6.1526 | 5300000 | 0.36452
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add 12 MVAR switched shunt at BEELER 3 115 kV | Current Study |  |  | 322141.336 | 14.5601 | 2212500 | 0.36452
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 315859.0703 | 14.2761 | 2212500 | 1
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add 7 MVAR switched shunt at G19-030-TAP 345 kV | Current Study |  |  | 271362.9499 | 5.1201 | 5300000 | 0.13562
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add 0.04 MVAR switched shunt at ELLIS 2 69 kV | Current Study |  |  | 234450.7485 | 16.9892 | 1380000 | 1
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 220379.3087 | 1.4753 | 14938000 | 0.10599
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 217279.2716 | 0.023154 | 938400000 | 0.0023446
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 213341.4685 | 1.4753 | 14460953.1406 | 0.10599
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 200440.271 | 14.5247 | 1380000 | 1
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Rebuild line 531405 WALKMYR3 115 531481 HUGOTON3 115 1 | Current Study | 12.27 | (598.00, 598.00) | 200366.9969 | 1.633 | 12270000 | 0.016134
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add 0.9 MVAR switched shunt at GEN-2024-157 138 kV | Current Study |  |  | 191568.0232 | 7.8754 | 2432500 | 0.25906
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2 | Current Study |  | (350.00, 385.00) | 170278.9596 | 1.0136 | 16800000 | 0.0060867
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add 60 MVAR switched shunt at WAYSIDE 4 230 kV | Current Study |  |  | 153544.0874 | 4.0142 | 3825000 | 0.043627
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add 0.5 MVAR switched shunt at RKY_RDG4 138 kV | Current Study |  |  | 150685.1419 | 6.1947 | 2432500 | 0.25906
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at IRS7 115 KV 115 kV | Current Study |  |  | 138460.4 | 6.2581 | 2212500 | 0.13562
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MED-LDG3 115 kV | Current Study |  |  | 129158.3643 | 5.8377 | 2212500 | 0.13562
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add 6 MVAR switched shunt at REDHLSW4 138 kV | Current Study |  |  | 118953.8556 | 4.8902 | 2432500 | 0.035528
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 109019.8163 | 2.057 | 5300000 | 0.047554
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add 5 MVAR switched shunt at SLKHILLS 4 138 kV | Current Study |  |  | 101667.9955 | 4.1796 | 2432500 | 0.10599
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 88022.0033 | 3.9784 | 2212500 | 0.13562
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 85341.549 | 3.8572 | 2212500 | 0.13562
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 79705.0218 | 3.6025 | 2212500 | 0.25906
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 60881.9862 | 0.32732 | 18600000 | 0.038724
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 60881.9862 | 0.32732 | 18600000 | 0.038724
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 531405 WALKMYR3 115 531510 HARBNGR3 115 M2 | Current Study | 1.28 | (598.00, 598.00) | 60732.8289 | 1.0136 | 5992000 | 0.0060867
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 59520.7508 | 0.32 | 18600000 | 0.041561
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 56518.4061 | 3.4254 | 1650000 | 0.25906
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 54451.676 | 1.0274 | 5300000 | 0.02418
GEN-2024-137 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 34185.2638 | 0.645 | 5300000 | 0.018501
GEN-2024-137 | 03 CENTRAL | TBD | NRIS | Add 16 MVAR switched shunt at UNDERWOOD 2 345 kV | Current Study |  |  | 30186.4435 | 0.56956 | 5300000 | 0.030155
GEN-2024-137 | 03 CENTRAL | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 16585.644 | 1.2019 | 1380000 | 0.051316
GEN-2024-137 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR SVC at GEN-2021-076 345 kV | Current Study |  |  | 15770.7813 | 0.13142 | 12000000 | 0.0010696
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add line 659131 LARAMIE_-MB3 345 800120 UNDERWOOD 2 345 P2 | Current Study | 206.4 | (1792.00, 1792.00) | 82786986.8194 | 12.7396 | 649840000 | 0.024535
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add line 652424 BELFELD3 345 800121 MAURINE 2 345 P2 | Current Study | 154.2 | (1792.00, 1792.00) | 72701264.2959 | 14.8972 | 488020000 | 0.02067
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 63561324.1206 | 6.7618 | 940000000 | 0.064446
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Rebuild line 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Current Study | 75.83 | (1793.00, 1793.00) | 29796232.766 | 17.8607 | 166826000 | 0.13507
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add line 652424 BELFELD3 345 659183 CHARL_CK-BE3 345 P2 | Current Study | 40.74 | (531.00, 531.00) | 24108208.927 | 17.6884 | 136294000 | 0.019565
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 23271598.3019 | 17.5045 | 132946000 | 0.3671
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Rebuild line 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | Current Study | 84.86 | (1793.00, 1793.00) | 14866023.0978 | 7.9629 | 186692000 | 0.093674
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 9287435.1538 | 4.6785 | 198511000 | 0.10667
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Rebuild line 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Current Study | 38.26 | (1793.00, 1793.00) | 8927729.1951 | 10.6065 | 84172000 | 0.17305
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Rebuild line 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Current Study | 37.4 | (1793.00, 1793.00) | 8823454.6965 | 10.7237 | 82280000 | 0.17305
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 7715157.3751 | 3.8993 | 197860000 | 0.12999
GEN-2024-138 | 03 CENTRAL | TBD | NRIS | Rebuild line 640100 CAMBRIG7 115 640269 MCCOOK 7 115 1 | Current Study | 28.11 | (176.00, 176.00) | 5328537.4753 | 18.956 | 28110000 | 0.015742
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 5256910.3319 | 3.1848 | 165062000 | 0.13517
GEN-2024-138 | 03 CENTRAL | TBD | NRIS | Rebuild line 640194 GOSPER 7 115 640242 JOHN.2 7 115 1 | Current Study | 24.13 | (176.00, 176.00) | 4574087.8434 | 18.956 | 24130000 | 0.015742
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | Current Study | 21.05 | (1793.00, 1793.00) | 4102478.3282 | 8.8587 | 46310000 | 0.15831
GEN-2024-138 | 03 CENTRAL | TBD | NRIS | Rebuild line 640326 REDWILO7 115 640365 STOCKVL7 115 1 | Current Study | 21.09 | (176.00, 176.00) | 3958576.1625 | 18.7699 | 21090000 | 0.011932
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 531259 SETAB 1 13 531464 SETAB 3 115 531465 SETAB 7 345 M2 | Current Study |  | (280.00, 308.00) | 3285781.4078 | 19.5582 | 16800000 | 0.032048
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Rebuild line 523961 POTTER_CO 7 345 784950 G24-266_TAP 345 1 | Current Study | 18.24 | (1793.00, 1793.00) | 3155610.6405 | 7.8639 | 40128000 | 0.093674
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | Current Study | 19.2 | (2390.00, 2390.00) | 3001992.9479 | 7.107 | 42240000 | 0.12249
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 2909861.0209 | 1.4658 | 198511000 | 0.052854
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | Current Study | 16.04 | (2390.00, 2390.00) | 2507914.9419 | 7.107 | 35288000 | 0.12249
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Rebuild line 531419 DOBSON 3 115 531493 GANO 3 115 1 | Current Study | 11.92 | (260.00, 260.00) | 2479179.0125 | 20.7985 | 11920000 | 0.02413
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Rebuild line 531432 PILE 3 115 531433 SCOTCTY3 115 1 | Current Study | 11.88 | (260.00, 260.00) | 2470859.6198 | 20.7985 | 11880000 | 0.02413
GEN-2024-138 | 03 CENTRAL | TBD | NRIS | Add 78 MVAR SVC at STEGALL_-MB3 345 kV | Current Study |  |  | 2059962.3173 | 17.1664 | 12000000 | 0.030386
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Rebuild line 531432 PILE 3 115 531493 GANO 3 115 1 | Current Study | 8.34 | (260.00, 260.00) | 1734593.3695 | 20.7985 | 8340000 | 0.02413
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | Current Study | 13 | (2390.00, 2390.00) | 1635009.6542 | 5.7168 | 28600000 | 0.12193
GEN-2024-138 | 03 CENTRAL | TBD | NRIS | Rebuild line 640100 CAMBRIG7 115 640194 GOSPER 7 115 1 | Current Study | 8.61 | (176.00, 176.00) | 1632113.3996 | 18.956 | 8610000 | 0.015742
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 1278728.8173 | 10.6561 | 12000000 | 1
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add 525 MVAR SVC at SD.LS-LR-MB3 345 kV | Current Study |  |  | 1162869.9252 | 9.6906 | 12000000 | 0.25906
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 774179.6976 | 14.6072 | 5300000 | 0.36452
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add 0.8 MVAR switched shunt at HARBNGR7 345 kV | Current Study |  |  | 757095.4309 | 14.2848 | 5300000 | 1
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MINGO 7 345 kV | Current Study |  |  | 744736.1914 | 14.0516 | 5300000 | 0.36452
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 703063.4823 | 1.5313 | 45914000 | 0.052216
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Rebuild line 531433 SCOTCTY3 115 531464 SETAB 3 115 1 | Current Study | 2.77 | (394.00, 394.00) | 607149.2221 | 21.9187 | 2770000 | 0.049305
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 554633.9582 | 3.4254 | 16192000 | 0.25906
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 531337.6816 | 0.36951 | 143796000 | 0.012449
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add 24 MVAR switched shunt at NESSCTY3 115 kV | Current Study |  |  | 433515.3087 | 19.5939 | 2212500 | 1
GEN-2024-138 | 03 CENTRAL | TBD | NRIS | Add 0.7 MVAR switched shunt at STEGALL_-MB4 230 kV | Current Study |  |  | 418382.9586 | 10.9381 | 3825000 | 0.030386
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add 248 MVAR switched shunt at GEN-2022-015 345 kV | Current Study |  |  | 400448.2695 | 7.5556 | 5300000 | 0.36452
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add 40 MVAR switched shunt at SEGNTP 3 115 kV | Current Study |  |  | 394182.848 | 17.8162 | 2212500 | 1
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 531448 HOLCOMB3 115 531449 HOLCOMB7 345 531450 HOLCTER1 13 M2 | Current Study |  | (336.00, 358.50) | 390262.8831 | 2.323 | 16800000 | 0.0085544
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 383703.5488 | 1.5313 | 25058000 | 0.052216
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR switched shunt at GEN-2022-075 345 kV | Current Study |  |  | 331679.1503 | 6.2581 | 5300000 | 0.13562
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 326086.6618 | 6.1526 | 5300000 | 0.36452
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add 12 MVAR switched shunt at BEELER 3 115 kV | Current Study |  |  | 322141.336 | 14.5601 | 2212500 | 0.36452
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 315859.0703 | 14.2761 | 2212500 | 1
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add 7 MVAR switched shunt at G19-030-TAP 345 kV | Current Study |  |  | 271362.9499 | 5.1201 | 5300000 | 0.13562
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add 0.04 MVAR switched shunt at ELLIS 2 69 kV | Current Study |  |  | 234450.7485 | 16.9892 | 1380000 | 1
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 220379.3087 | 1.4753 | 14938000 | 0.10599
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 217279.2716 | 0.023154 | 938400000 | 0.0023446
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 213341.4685 | 1.4753 | 14460953.1406 | 0.10599
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 200440.271 | 14.5247 | 1380000 | 1
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Rebuild line 531405 WALKMYR3 115 531481 HUGOTON3 115 1 | Current Study | 12.27 | (598.00, 598.00) | 200366.9969 | 1.633 | 12270000 | 0.016134
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add 0.9 MVAR switched shunt at GEN-2024-157 138 kV | Current Study |  |  | 191568.0232 | 7.8754 | 2432500 | 0.25906
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2 | Current Study |  | (350.00, 385.00) | 170278.9596 | 1.0136 | 16800000 | 0.0060867
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add 60 MVAR switched shunt at WAYSIDE 4 230 kV | Current Study |  |  | 153544.0874 | 4.0142 | 3825000 | 0.043627
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add 0.5 MVAR switched shunt at RKY_RDG4 138 kV | Current Study |  |  | 150685.1419 | 6.1947 | 2432500 | 0.25906
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at IRS7 115 KV 115 kV | Current Study |  |  | 138460.4 | 6.2581 | 2212500 | 0.13562
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MED-LDG3 115 kV | Current Study |  |  | 129158.3643 | 5.8377 | 2212500 | 0.13562
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add 6 MVAR switched shunt at REDHLSW4 138 kV | Current Study |  |  | 118953.8556 | 4.8902 | 2432500 | 0.035528
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 109019.8163 | 2.057 | 5300000 | 0.047554
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add 5 MVAR switched shunt at SLKHILLS 4 138 kV | Current Study |  |  | 101667.9955 | 4.1796 | 2432500 | 0.10599
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 88022.0033 | 3.9784 | 2212500 | 0.13562
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 85341.549 | 3.8572 | 2212500 | 0.13562
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 79705.0218 | 3.6025 | 2212500 | 0.25906
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 60881.9862 | 0.32732 | 18600000 | 0.038724
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 60881.9862 | 0.32732 | 18600000 | 0.038724
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 531405 WALKMYR3 115 531510 HARBNGR3 115 M2 | Current Study | 1.28 | (598.00, 598.00) | 60732.8289 | 1.0136 | 5992000 | 0.0060867
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 59520.7508 | 0.32 | 18600000 | 0.041561
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 56518.4061 | 3.4254 | 1650000 | 0.25906
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 54451.676 | 1.0274 | 5300000 | 0.02418
GEN-2024-138 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 34185.2638 | 0.645 | 5300000 | 0.018501
GEN-2024-138 | 03 CENTRAL | TBD | NRIS | Add 16 MVAR switched shunt at UNDERWOOD 2 345 kV | Current Study |  |  | 30186.4435 | 0.56956 | 5300000 | 0.030155
GEN-2024-138 | 03 CENTRAL | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 16585.644 | 1.2019 | 1380000 | 0.051316
GEN-2024-138 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR SVC at GEN-2021-076 345 kV | Current Study |  |  | 15770.7813 | 0.13142 | 12000000 | 0.0010696
GEN-2024-139 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 2910127.1123 | 0.31012 | 938400000 | 0.037837
GEN-2024-139 | 03 CENTRAL | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1802241.3781 | 0.8255 | 218320000 | 0.020703
GEN-2024-139 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1209502.1703 | 1.2869 | 93984000 | 0.064902
GEN-2024-139 | 03 CENTRAL | TBD | ERIS | Rebuild line 645458 S3458 3 345 778170 G24-040-TAP 345 1 | Current Study | 13.15 | (1793.00, 1793.00) | 952321.0912 | 3.2918 | 28930000 | 0.041486
GEN-2024-139 | 03 CENTRAL | TBD | ERIS | Rebuild line 640139 COOPER 3 345 778170 G24-040-TAP 345 1 | Current Study | 12.59 | (1793.00, 1793.00) | 911765.9725 | 3.2918 | 27698000 | 0.041486
GEN-2024-139 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 815925.1023 | 0.41102 | 198511000 | 0.011292
GEN-2024-139 | 03 CENTRAL | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 522618.4951 | 0.97759 | 53460000 | 0.028679
GEN-2024-139 | 03 CENTRAL | TBD | ERIS | Rebuild line 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 | Current Study | 3.23 | (1793.00, 1793.00) | 479187.6919 | 6.7434 | 7106000 | 0.061779
GEN-2024-139 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 458422.3323 | 8.6495 | 5300000 | 0.29892
GEN-2024-139 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 352796.1145 | 0.76838 | 45914000 | 0.03157
GEN-2024-139 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 192541.8181 | 0.76838 | 25058000 | 0.03157
GEN-2024-139 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 163438.3432 | 1.4017 | 11660000 | 0.064902
GEN-2024-139 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 88552.4445 | 0.47609 | 18600000 | 0.067865
GEN-2024-139 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 88552.4445 | 0.47609 | 18600000 | 0.067865
GEN-2024-139 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 44972.8548 | 0.24179 | 18600000 | 0.037837
GEN-2024-139 | 03 CENTRAL | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 34774.0983 | 1.5717 | 2212500 | 0.041062
GEN-2024-139 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 9470.0737 | 0.57394 | 1650000 | 0.028278
GEN-2024-140 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | Current Study | 23.61 | (386.00, 386.00) | 8170743.4951 | 18.2143 | 44859000 | 0.068985
GEN-2024-140 | 02 NEBRASKA | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 6152.8601 | 0.44586 | 1380000 | 0.056927
GEN-2024-141 | 01 NORTH | TBD | ERIS | Rebuild line 640404 WAYSIDE 4 230 652484 NUNDRWD4 230 1 | Current Study | 80.12 | (519.00, 519.00) | 18078112.1084 | 11.8757 | 152228000 | 0.032147
GEN-2024-141 | 01 NORTH | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659202 LO.KVA2_-BE9 13 M2 | Current Study |  | (500.00, 617.00) | 15732942.2043 | 62.9318 | 25000000 | 0.16338
GEN-2024-141 | 01 NORTH | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659201 LO.KU1A_-BE9 13 M2 | Current Study |  | (600.00, 637.40) | 15516721.4357 | 62.0669 | 25000000 | 0.18523
GEN-2024-141 | 01 NORTH | TBD | ERIS | Rebuild line 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Current Study | 36.8 | (1793.00, 1793.00) | 10373849.8051 | 12.8135 | 80960000 | 0.084619
GEN-2024-141 | 01 NORTH | TBD | ERIS | Rebuild line 652529 WATERTN3 345 659165 CROCKER_-BE3 345 1 | Current Study | 44.23 | (1793.00, 1793.00) | 7675079.3781 | 7.8876 | 97306000 | 0.089207
GEN-2024-141 | 01 NORTH | TBD | ERIS | Rebuild line 652884 NUNDRWD-LNX3 230 785430 G24-282-TAP 230 1 | Current Study | 35.21 | (519.00, 519.00) | 3658222.1477 | 5.4683 | 66899000 | 0.037645
GEN-2024-141 | 01 NORTH | TBD | NRIS | Add 25 MVAR switched shunt at BELFELD3 345 kV | Current Study |  |  | 3350249.9003 | 63.2123 | 5300000 | 0.059267
GEN-2024-141 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 659120 BROADLND-BE3 345 659204 BD.KU2A_-BE9 13 659205 BROADLND-BE4 230 M2 | Current Study |  | (471.00, 478.00) | 2863144.8578 | 11.4526 | 25000000 | 0.045777
GEN-2024-141 | 01 NORTH | TBD | ERIS | Add 34 MVAR switched shunt at OUTLAW_WF7 345 kV | Current Study |  |  | 2475300.9607 | 46.7038 | 5300000 | 0.028348
GEN-2024-141 | 01 NORTH | TBD | ERIS | Rebuild line 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | Current Study | 4.2 | (519.00, 519.00) | 1989494.7785 | 24.931 | 7980000 | 0.047245
GEN-2024-141 | 01 NORTH | TBD | ERIS | Rebuild line 659106 LELAND_O-BE4 230 659199 BASIN___-BE4 230 1 | Current Study | 1 | (637.00, 637.00) | 1900000 | 100 | 1900000 | 1
GEN-2024-141 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 659160 GROTON__-BE3 345 659161 GRT.KU2A-BE9 13 659187 GROTON__-BE7 115 M2 | Current Study |  | (400.00, 400.00) | 867844.0014 | 5.1657 | 16800000 | 0.0077683
GEN-2024-141 | 01 NORTH | TBD | ERIS | Add 525 MVAR SVC at SD.LS-LR-MB3 345 kV | Current Study |  |  | 378535.3769 | 3.1545 | 12000000 | 0.058971
GEN-2024-141 | 01 NORTH | TBD | ERIS | Add 60 MVAR switched shunt at WAYSIDE 4 230 kV | Current Study |  |  | 319131.5638 | 8.3433 | 3825000 | 0.063409
GEN-2024-141 | 01 NORTH | TBD | ERIS | Add 0.4 MVAR switched shunt at SHINDLER-ER7 115 kV | Current Study |  |  | 313163.777 | 14.1543 | 2212500 | 0.1028
GEN-2024-141 | 01 NORTH | TBD | ERIS | Add 24 MVAR switched shunt at DAYTON__-ER7 115 kV | Current Study |  |  | 283499.3154 | 12.8135 | 2212500 | 0.084618
GEN-2024-141 | 01 NORTH | TBD | ERIS | Add line and rebuild line 652568 GROTONSOUTH7 115 659187 GROTON__-BE7 115 M2 | Current Study | 0.1 | (598.00, 598.00) | 217770.305 | 5.0177 | 4340000 | 0.0077683
GEN-2024-141 | 01 NORTH | TBD | ERIS | Add 0.5 MVAR switched shunt at ORLAND-ER8 69 kV | Current Study |  |  | 176826.6916 | 12.8135 | 1380000 | 0.084618
GEN-2024-141 | 01 NORTH | TBD | ERIS | Add 14.4 MVAR switched shunt at SW145-ER8 69 kV | Current Study |  |  | 176826.6916 | 12.8135 | 1380000 | 0.084618
GEN-2024-141 | 01 NORTH | TBD | ERIS | Add 10 MVAR switched shunt at REDFIELD 115 kV | Current Study |  |  | 174512.3457 | 7.8876 | 2212500 | 0.089207
GEN-2024-141 | 01 NORTH | TBD | ERIS | Add 54 MVAR switched shunt at REDFELD-ER7 115 kV | Current Study |  |  | 174512.3457 | 7.8876 | 2212500 | 0.089207
GEN-2024-141 | 01 NORTH | TBD | NRIS | Add 16 MVAR switched shunt at UNDERWOOD 2 345 kV | Current Study |  |  | 150809.6171 | 2.8455 | 5300000 | 0.10535
GEN-2024-141 | 01 NORTH | TBD | ERIS | Add 4.4 MVAR switched shunt at DESMET-ER7 115 kV | Current Study |  |  | 145912.4947 | 6.5949 | 2212500 | 0.089207
GEN-2024-141 | 01 NORTH | TBD | ERIS | Add 4 MVAR switched shunt at MOS-RDFL-ER8 69 kV | Current Study |  |  | 108848.3783 | 7.8876 | 1380000 | 0.089207
GEN-2024-141 | 01 NORTH | TBD | ERIS | Add 5.5 MVAR switched shunt at LOOMIS-ER8 69 kV | Current Study |  |  | 102590.1204 | 7.4341 | 1380000 | 0.1028
GEN-2024-141 | 01 NORTH | TBD | ERIS | Add 0.9 MVAR switched shunt at GEN-2024-157 138 kV | Current Study |  |  | 62358.8867 | 2.5636 | 2432500 | 0.058971
GEN-2024-141 | 01 NORTH | TBD | ERIS | Rebuild line 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Current Study | 0 | (880.00, 880.00) | 28189.8093 | 12.8135 | 220000 | 0.084619
GEN-2024-141 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 652237 WATERT19 13 652529 WATERTN3 345 652530 WATERTN4 230 M2 | Current Study |  | (400.00, 478.00) | 28018.2141 | 0.11207 | 25000000 | 0.00018971
GEN-2024-141 | 01 NORTH | TBD | ERIS | Rebuild line 652484 NUNDRWD4 230 652884 NUNDRWD-LNX3 230 Z | Current Study | 0.14514 | (519.00, 519.00) | 15079.6269 | 5.4683 | 275765.6361 | 0.037645
GEN-2024-141 | 01 NORTH | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 11826.8256 | 0.85702 | 1380000 | 0.063409
GEN-2024-142 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 11668710.0957 | 8.1148 | 143796000 | 0.27383
GEN-2024-142 | 03 CENTRAL | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 6744907.9517 | 3.0895 | 218320000 | 0.064406
GEN-2024-142 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 5791843.8099 | 0.6172 | 938400000 | 0.035371
GEN-2024-142 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 4415433.6722 | 0.47053 | 938400000 | 0.047722
GEN-2024-142 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 3081617.165 | 1.5524 | 198511000 | 0.035451
GEN-2024-142 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Current Study | 26.47 | (1793.00, 1793.00) | 2649608.5139 | 4.5499 | 58234000 | 0.052633
GEN-2024-142 | 03 CENTRAL | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 1591357.3299 | 2.9767 | 53460000 | 0.072592
GEN-2024-142 | 03 CENTRAL | TBD | ERIS | Add 66 MVAR switched shunt at GEN-2021-021 345 kV | Current Study |  |  | 1528228.128 | 28.8345 | 5300000 | 0.010098
GEN-2024-142 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 1220111.1397 | 2.6574 | 45914000 | 0.09076
GEN-2024-142 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | Current Study | 19.87 | (1793.00, 1793.00) | 1057799.3027 | 2.4198 | 43714000 | 0.027919
GEN-2024-142 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1012345.9888 | 0.50997 | 198511000 | 0.018417
GEN-2024-142 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 665887.2008 | 2.6574 | 25058000 | 0.09076
GEN-2024-142 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | Current Study | 16.71 | (1793.00, 1793.00) | 638039.672 | 1.7356 | 36762000 | 0.03282
GEN-2024-142 | 03 CENTRAL | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 323296.4583 | 1.7382 | 18600000 | 0.11768
GEN-2024-142 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 145435.1222 | 0.78191 | 18600000 | 0.092652
GEN-2024-142 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 145435.1222 | 0.78191 | 18600000 | 0.092652
GEN-2024-142 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 73913.6623 | 0.4948 | 14938000 | 0.035606
GEN-2024-142 | 03 CENTRAL | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 73296.5507 | 0.39407 | 18600000 | 0.035371
GEN-2024-142 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 71553.2204 | 0.4948 | 14460953.1406 | 0.035606
GEN-2024-142 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 68235.7333 | 0.36686 | 18600000 | 0.047722
GEN-2024-142 | 03 CENTRAL | TBD | ERIS | Add 5 MVAR switched shunt at SLKHILLS 4 138 kV | Current Study |  |  | 64105.1168 | 2.6354 | 2432500 | 0.066939
GEN-2024-142 | 03 CENTRAL | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 55821.8661 | 1.0532 | 5300000 | 0.024388
GEN-2024-142 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 50177.7282 | 0.94675 | 5300000 | 0.027199
GEN-2024-142 | 03 CENTRAL | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 44317.923 | 0.36932 | 12000000 | 0.034713
GEN-2024-142 | 03 CENTRAL | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 40643.7429 | 0.76686 | 5300000 | 0.018077
GEN-2024-142 | 03 CENTRAL | TBD | ERIS | Add 248 MVAR switched shunt at GEN-2022-015 345 kV | Current Study |  |  | 36840.5413 | 0.6951 | 5300000 | 0.033589
GEN-2024-142 | 03 CENTRAL | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 29999.4033 | 0.56603 | 5300000 | 0.033589
GEN-2024-142 | 03 CENTRAL | TBD | ERIS | Add 0.5 MVAR switched shunt at RKY_RDG4 138 kV | Current Study |  |  | 20835.1563 | 0.85653 | 2432500 | 0.035878
GEN-2024-142 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 13839.129 | 0.83874 | 1650000 | 0.034351
GEN-2024-142 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MED-LDG3 115 kV | Current Study |  |  | 9601.5875 | 0.43397 | 2212500 | 0.010098
GEN-2024-142 | 03 CENTRAL | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 4939.4351 | 0.22325 | 2212500 | 0.0048485
GEN-2024-142 | 03 CENTRAL | TBD | ERIS | Add 0.8 MVAR switched shunt at HARBNGR7 345 kV | Current Study |  |  | 2242.0077 | 0.042302 | 5300000 | 0.002966
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add line 523869 CHAN+TASCOS6 230 523959 POTTER_CO 6 230 P2 | Current Study | 41.65 | (496.00, 546.00) | 37867141.1808 | 34.0149 | 111325000 | 0.26205
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add line 523221 XIT_INTG 6 230 523869 CHAN+TASCOS6 230 P2 | Current Study | 32.28 | (495.00, 545.00) | 29902705.6045 | 34.019 | 87900000 | 0.26217
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 20756897.0172 | 2.2119 | 938400000 | 0.1501
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 17945970.7613 | 1.9124 | 938400000 | 0.22967
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 16802711.8729 | 1.1094 | 1514620000 | 0.027292
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 14964815.1719 | 1.1768 | 1271630000 | 0.096945
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 14946883.7529 | 1.1631 | 1285130000 | 0.14661
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 11828420.167 | 1.632 | 724760000 | 0.15486
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 9468788.652 | 0.88183 | 1073760000 | 0.060422
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523095 HITCHLAND 6 230 778320 G24-045-TAP 230 1 | Current Study | 37.8 | (772.00, 772.00) | 5831597.3811 | 8.1197 | 71820000 | 0.16802
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 5824923.888 | 1.2064 | 482840000 | 0.12263
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523216 RB-HOGUE 3 115 523246 DALHART 3 115 1 | Current Study | 11.44 | (115.00, 115.00) | 5792991.6954 | 50.638 | 11440000 | 0.032512
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 5608901.1652 | 1.1951 | 469340000 | 0.081641
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 2547799.8435 | 1.2877 | 197860000 | 0.050911
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 46 MVAR switched shunt at STLN-DEMARC6 230 kV | Current Study |  |  | 1936905.003 | 50.638 | 3825000 | 0.041383
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 1807497.6374 | 1.095 | 165062000 | 0.055119
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523091 HITCHLD_TR01 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2 | Current Study |  | (560.00, 644.00) | 1696017.7936 | 6.7841 | 25000000 | 0.052355
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523094 HITCHLD_TR21 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2 | Current Study |  | (560.00, 644.00) | 1696017.7936 | 6.7841 | 25000000 | 0.060185
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | Current Study | 13.92 | (519.00, 519.00) | 1666348.3806 | 6.3005 | 26448000 | 0.041383
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1579741.4424 | 0.7958 | 198511000 | 0.034031
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 1451964.6339 | 1.7183 | 84500000 | 0.087383
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-161-TAP 138 kV | Current Study |  |  | 1422821.3586 | 58.4921 | 2432500 | 1
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1379079.2871 | 1.632 | 84500000 | 0.15486
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | Current Study | 11.15 | (519.00, 519.00) | 1309474.4356 | 6.1811 | 21185000 | 0.04003
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 1178653.929 | 3.3085 | 35625000 | 0.027605
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1163118.3792 | 0.93181 | 124824000 | 0.048769
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 824901.7325 | 0.97622 | 84500000 | 0.023978
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 807131.7829 | 0.99049 | 81488000 | 0.052614
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523093 HITCHLAND 3 115 523095 HITCHLAND 6 230 523098 HITCHLD_TR41 13 M2 | Current Study |  | (250.00, 288.00) | 753091.6936 | 5.4572 | 13800000 | 0.012742
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523092 HITCHLD_TR11 13 523093 HITCHLAND 3 115 523095 HITCHLAND 6 230 M2 | Current Study |  | (250.00, 288.00) | 752687.4092 | 5.4543 | 13800000 | 0.013263
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 746924.0171 | 1.7182 | 43472000 | 0.041892
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 476170.5028 | 3.4012 | 14000000 | 0.013802
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 0.3 MVAR switched shunt at ROSVTAP2 69 kV | Current Study |  |  | 460000 | 33.3333 | 1380000 | 1
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 393320.6729 | 0.71228 | 55220000 | 0.027794
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 7 MVAR switched shunt at CL-AFTP4 138 kV | Current Study |  |  | 392212.1896 | 16.1238 | 2432500 | 1
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 373478.6514 | 2.0079 | 18600000 | 0.16098
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 304460.8034 | 1.6369 | 18600000 | 0.22967
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 304460.8034 | 1.6369 | 18600000 | 0.22967
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 303560.6478 | 1.632 | 18600000 | 0.15486
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 294180.4709 | 1.1767 | 25000000 | 0.015968
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 294180.4709 | 1.1767 | 25000000 | 0.013915
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 277335.4929 | 1.4911 | 18600000 | 0.22967
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 262681.2815 | 1.4123 | 18600000 | 0.1501
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 222281.42 | 1.1951 | 18600000 | 0.081641
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 218791.8903 | 1.1763 | 18600000 | 0.096945
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 216193.2162 | 1.1623 | 18600000 | 0.14661
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 215754.8296 | 1.16 | 18600000 | 0.096945
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 206342.4759 | 1.1094 | 18600000 | 0.027292
GEN-2024-143 | 05 SOUTHWEST | TBD | NRIS | Add 0.09 MVAR switched shunt at GRAY CO3 115 kV | Current Study |  |  | 191620.4574 | 8.6608 | 2212500 | 0.12579
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 185944.3682 | 1.1484 | 16192000 | 0.10301
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 18 MVAR switched shunt at FALCNRD4 138 kV | Current Study |  |  | 171259.4849 | 7.0405 | 2432500 | 0.042168
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 0.7 MVAR switched shunt at GEN-2024-161 138 kV | Current Study |  |  | 133857.2835 | 5.5029 | 2432500 | 0.020894
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 115509.8474 | 0.77326 | 14938000 | 0.065889
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 111821.0262 | 0.77326 | 14460953.1406 | 0.065889
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 111061.2808 | 0.92551 | 12000000 | 0.10301
GEN-2024-143 | 05 SOUTHWEST | TBD | NRIS | Add 16 MVAR switched shunt at UNDERWOOD 2 345 kV | Current Study |  |  | 108307.6106 | 2.0435 | 5300000 | 0.12832
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 0.7 MVAR switched shunt at ROSEVLT2 69 kV | Current Study |  |  | 97158.5156 | 7.0405 | 1380000 | 0.042168
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 78389.2342 | 5.6804 | 1380000 | 0.032512
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 69279.4098 | 3.1313 | 2212500 | 0.10301
GEN-2024-143 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 63028.4575 | 0.34822 | 18100000 | 0.0042679
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 0.5 MVAR switched shunt at RKY_RDG4 138 kV | Current Study |  |  | 50518.1068 | 2.0768 | 2432500 | 0.10301
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 32980.9154 | 0.50306 | 6556000 | 0.027794
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 26721.5915 | 1.2078 | 2212500 | 0.10301
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 18948.1353 | 1.1484 | 1650000 | 0.10301
GEN-2024-143 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 17943.509 | 1.3003 | 1380000 | 0.065843
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 11328.1728 | 0.82088 | 1380000 | 0.10301
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 10351.9671 | 0.46789 | 2212500 | 0.03887
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 9094.4704 | 0.17159 | 5300000 | 0.019659
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 8057.0648 | 0.58385 | 1380000 | 0.041383
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 6569.2307 | 0.47603 | 1380000 | 0.03887
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 255.6918 | 0.018528 | 1380000 | 0.0015461
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add line 659131 LARAMIE_-MB3 345 800120 UNDERWOOD 2 345 P2 | Current Study | 206.4 | (1792.00, 1792.00) | 82898672.4678 | 12.7568 | 649840000 | 0.024535
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add line 652424 BELFELD3 345 800121 MAURINE 2 345 P2 | Current Study | 154.2 | (1792.00, 1792.00) | 72799343.5732 | 14.9173 | 488020000 | 0.02067
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 63647072.9558 | 6.771 | 940000000 | 0.064446
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Rebuild line 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Current Study | 75.83 | (1793.00, 1793.00) | 29836430.0446 | 17.8848 | 166826000 | 0.13507
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add line 652424 BELFELD3 345 659183 CHARL_CK-BE3 345 P2 | Current Study | 40.74 | (531.00, 531.00) | 24140732.649 | 17.7122 | 136294000 | 0.019565
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 23302993.3755 | 17.5282 | 132946000 | 0.3671
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Rebuild line 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | Current Study | 84.86 | (1793.00, 1793.00) | 14886078.4409 | 7.9736 | 186692000 | 0.093674
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 9299964.5773 | 4.6849 | 198511000 | 0.10667
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Rebuild line 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Current Study | 38.26 | (1793.00, 1793.00) | 8939773.3491 | 10.6208 | 84172000 | 0.17305
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Rebuild line 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Current Study | 37.4 | (1793.00, 1793.00) | 8835358.1767 | 10.7382 | 82280000 | 0.17305
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 7725565.6818 | 3.9046 | 197860000 | 0.12999
GEN-2024-144 | 03 CENTRAL | TBD | NRIS | Rebuild line 640100 CAMBRIG7 115 640269 MCCOOK 7 115 1 | Current Study | 28.11 | (176.00, 176.00) | 5335726.0587 | 18.9816 | 28110000 | 0.015742
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 5264002.2851 | 3.1891 | 165062000 | 0.13517
GEN-2024-144 | 03 CENTRAL | TBD | NRIS | Rebuild line 640194 GOSPER 7 115 640242 JOHN.2 7 115 1 | Current Study | 24.13 | (176.00, 176.00) | 4580258.6196 | 18.9816 | 24130000 | 0.015742
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | Current Study | 21.05 | (1793.00, 1793.00) | 4108012.8689 | 8.8707 | 46310000 | 0.15831
GEN-2024-144 | 03 CENTRAL | TBD | NRIS | Rebuild line 640326 REDWILO7 115 640365 STOCKVL7 115 1 | Current Study | 21.09 | (176.00, 176.00) | 3963916.5688 | 18.7952 | 21090000 | 0.011932
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 531259 SETAB 1 13 531464 SETAB 3 115 531465 SETAB 7 345 M2 | Current Study |  | (280.00, 308.00) | 3290214.1652 | 19.5846 | 16800000 | 0.032048
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Rebuild line 523961 POTTER_CO 7 345 784950 G24-266_TAP 345 1 | Current Study | 18.24 | (1793.00, 1793.00) | 3159867.7881 | 7.8745 | 40128000 | 0.093674
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | Current Study | 19.2 | (2390.00, 2390.00) | 3006042.854 | 7.1166 | 42240000 | 0.12249
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 2913786.6344 | 1.4678 | 198511000 | 0.052854
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | Current Study | 16.04 | (2390.00, 2390.00) | 2511298.301 | 7.1166 | 35288000 | 0.12249
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Rebuild line 531419 DOBSON 3 115 531493 GANO 3 115 1 | Current Study | 11.92 | (260.00, 260.00) | 2482523.6047 | 20.8265 | 11920000 | 0.02413
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Rebuild line 531432 PILE 3 115 531433 SCOTCTY3 115 1 | Current Study | 11.88 | (260.00, 260.00) | 2474192.9886 | 20.8265 | 11880000 | 0.02413
GEN-2024-144 | 03 CENTRAL | TBD | NRIS | Add 78 MVAR SVC at STEGALL_-MB3 345 kV | Current Study |  |  | 2062741.3558 | 17.1895 | 12000000 | 0.030386
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Rebuild line 531432 PILE 3 115 531493 GANO 3 115 1 | Current Study | 8.34 | (260.00, 260.00) | 1736933.4617 | 20.8265 | 8340000 | 0.02413
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | Current Study | 13 | (2390.00, 2390.00) | 1637215.4008 | 5.7245 | 28600000 | 0.12193
GEN-2024-144 | 03 CENTRAL | TBD | NRIS | Rebuild line 640100 CAMBRIG7 115 640194 GOSPER 7 115 1 | Current Study | 8.61 | (176.00, 176.00) | 1634315.2389 | 18.9816 | 8610000 | 0.015742
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 1280453.9152 | 10.6704 | 12000000 | 1
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add 525 MVAR SVC at SD.LS-LR-MB3 345 kV | Current Study |  |  | 1164438.721 | 9.7037 | 12000000 | 0.25906
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 775224.1222 | 14.6269 | 5300000 | 0.36452
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add 0.8 MVAR switched shunt at HARBNGR7 345 kV | Current Study |  |  | 758116.8076 | 14.3041 | 5300000 | 1
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MINGO 7 345 kV | Current Study |  |  | 745740.8946 | 14.0706 | 5300000 | 0.36452
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 704011.9659 | 1.5333 | 45914000 | 0.052216
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Rebuild line 531433 SCOTCTY3 115 531464 SETAB 3 115 1 | Current Study | 2.77 | (394.00, 394.00) | 607968.3104 | 21.9483 | 2770000 | 0.049305
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add 0.5 MVAR switched shunt at RKY_RDG4 138 kV | Current Study |  |  | 582436.1762 | 23.9439 | 2432500 | 1
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 555382.1996 | 3.43 | 16192000 | 0.25906
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 532054.4947 | 0.37001 | 143796000 | 0.012449
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add 24 MVAR switched shunt at NESSCTY3 115 kV | Current Study |  |  | 434100.1523 | 19.6203 | 2212500 | 1
GEN-2024-144 | 03 CENTRAL | TBD | NRIS | Add 0.7 MVAR switched shunt at STEGALL_-MB4 230 kV | Current Study |  |  | 418947.3875 | 10.9529 | 3825000 | 0.030386
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add 248 MVAR switched shunt at GEN-2022-015 345 kV | Current Study |  |  | 400988.5032 | 7.5658 | 5300000 | 0.36452
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add 40 MVAR switched shunt at SEGNTP 3 115 kV | Current Study |  |  | 394714.6293 | 17.8402 | 2212500 | 1
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 531448 HOLCOMB3 115 531449 HOLCOMB7 345 531450 HOLCTER1 13 M2 | Current Study |  | (336.00, 358.50) | 390789.376 | 2.3261 | 16800000 | 0.0085544
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 384221.1927 | 1.5333 | 25058000 | 0.052216
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR switched shunt at GEN-2022-075 345 kV | Current Study |  |  | 332126.6096 | 6.2665 | 5300000 | 0.13562
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 326526.5763 | 6.1609 | 5300000 | 0.36452
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add 12 MVAR switched shunt at BEELER 3 115 kV | Current Study |  |  | 322575.9281 | 14.5797 | 2212500 | 0.36452
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 316285.1871 | 14.2954 | 2212500 | 1
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add 7 MVAR switched shunt at G19-030-TAP 345 kV | Current Study |  |  | 271729.0382 | 5.127 | 5300000 | 0.13562
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add 0.04 MVAR switched shunt at ELLIS 2 69 kV | Current Study |  |  | 234767.0395 | 17.0121 | 1380000 | 1
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 220676.6164 | 1.4773 | 14938000 | 0.10599
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 217572.3971 | 0.023185 | 938400000 | 0.0023446
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 213629.2816 | 1.4773 | 14460953.1406 | 0.10599
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 200710.6795 | 14.5443 | 1380000 | 1
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Rebuild line 531405 WALKMYR3 115 531481 HUGOTON3 115 1 | Current Study | 12.27 | (598.00, 598.00) | 200637.3065 | 1.6352 | 12270000 | 0.016134
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add 0.9 MVAR switched shunt at GEN-2024-157 138 kV | Current Study |  |  | 191826.4623 | 7.886 | 2432500 | 0.25906
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2 | Current Study |  | (350.00, 385.00) | 170508.6782 | 1.0149 | 16800000 | 0.0060867
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add 60 MVAR switched shunt at WAYSIDE 4 230 kV | Current Study |  |  | 153751.2295 | 4.0196 | 3825000 | 0.043627
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at IRS7 115 KV 115 kV | Current Study |  |  | 138647.1931 | 6.2665 | 2212500 | 0.13562
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MED-LDG3 115 kV | Current Study |  |  | 129332.6083 | 5.8455 | 2212500 | 0.13562
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add 6 MVAR switched shunt at REDHLSW4 138 kV | Current Study |  |  | 119114.333 | 4.8968 | 2432500 | 0.035528
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 109166.8919 | 2.0598 | 5300000 | 0.047554
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add 5 MVAR switched shunt at SLKHILLS 4 138 kV | Current Study |  |  | 101805.153 | 4.1852 | 2432500 | 0.10599
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 88140.7514 | 3.9838 | 2212500 | 0.13562
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 85456.6809 | 3.8624 | 2212500 | 0.13562
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 79812.5497 | 3.6073 | 2212500 | 0.25906
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 60964.1204 | 0.32776 | 18600000 | 0.038724
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 60964.1204 | 0.32776 | 18600000 | 0.038724
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 531405 WALKMYR3 115 531510 HARBNGR3 115 M2 | Current Study | 1.28 | (598.00, 598.00) | 60814.7619 | 1.0149 | 5992000 | 0.0060867
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 59601.0486 | 0.32044 | 18600000 | 0.041561
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 56594.6535 | 3.43 | 1650000 | 0.25906
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 54525.1352 | 1.0288 | 5300000 | 0.02418
GEN-2024-144 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 34231.3822 | 0.64588 | 5300000 | 0.018501
GEN-2024-144 | 03 CENTRAL | TBD | NRIS | Add 16 MVAR switched shunt at UNDERWOOD 2 345 kV | Current Study |  |  | 30227.1672 | 0.57032 | 5300000 | 0.030155
GEN-2024-144 | 03 CENTRAL | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 16608.0192 | 1.2035 | 1380000 | 0.051316
GEN-2024-144 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR SVC at GEN-2021-076 345 kV | Current Study |  |  | 15792.0573 | 0.1316 | 12000000 | 0.0010696
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add line 523869 CHAN+TASCOS6 230 523959 POTTER_CO 6 230 P2 | Current Study | 41.65 | (496.00, 546.00) | 36912889.223 | 33.1578 | 111325000 | 0.26205
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add line 523221 XIT_INTG 6 230 523869 CHAN+TASCOS6 230 P2 | Current Study | 32.28 | (495.00, 545.00) | 29149157.4233 | 33.1617 | 87900000 | 0.26217
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 20233823.2123 | 2.1562 | 938400000 | 0.1501
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 17493732.2981 | 1.8642 | 938400000 | 0.22967
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 16379283.5337 | 1.0814 | 1514620000 | 0.027292
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 14587701.8296 | 1.1472 | 1271630000 | 0.096945
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 14570222.2823 | 1.1338 | 1285130000 | 0.14661
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 11530343.9788 | 1.5909 | 724760000 | 0.15486
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 9230175.178 | 0.85961 | 1073760000 | 0.060422
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523095 HITCHLAND 6 230 778320 G24-045-TAP 230 1 | Current Study | 37.8 | (772.00, 772.00) | 5684641.1271 | 7.9151 | 71820000 | 0.16802
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 5678135.8061 | 1.176 | 482840000 | 0.12263
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523216 RB-HOGUE 3 115 523246 DALHART 3 115 1 | Current Study | 11.44 | (115.00, 115.00) | 5647008.3046 | 49.362 | 11440000 | 0.032512
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 5467556.8559 | 1.1649 | 469340000 | 0.081641
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 2483595.2875 | 1.2552 | 197860000 | 0.050911
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 1.2 MVAR switched shunt at LAKEP4WT 138 kV | Current Study |  |  | 2432500 | 100 | 2432500 | 1
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 46 MVAR switched shunt at STLN-DEMARC6 230 kV | Current Study |  |  | 1888094.997 | 49.362 | 3825000 | 0.041383
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 1761948.6969 | 1.0674 | 165062000 | 0.055119
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523091 HITCHLD_TR01 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2 | Current Study |  | (560.00, 644.00) | 1653278.1452 | 6.6131 | 25000000 | 0.052355
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523094 HITCHLD_TR21 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2 | Current Study |  | (560.00, 644.00) | 1653278.1452 | 6.6131 | 25000000 | 0.060185
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | Current Study | 13.92 | (519.00, 519.00) | 1624356.4014 | 6.1417 | 26448000 | 0.041383
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1539931.958 | 0.77574 | 198511000 | 0.034031
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 1415375.1251 | 1.675 | 84500000 | 0.087383
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1344326.4891 | 1.5909 | 84500000 | 0.15486
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | Current Study | 11.15 | (519.00, 519.00) | 1276475.6798 | 6.0254 | 21185000 | 0.04003
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 1148951.85 | 3.2251 | 35625000 | 0.027605
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1133807.796 | 0.90833 | 124824000 | 0.048769
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 804114.2088 | 0.95161 | 84500000 | 0.023978
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 786792.062 | 0.96553 | 81488000 | 0.052614
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523093 HITCHLAND 3 115 523095 HITCHLAND 6 230 523098 HITCHLD_TR41 13 M2 | Current Study |  | (250.00, 288.00) | 734113.7829 | 5.3197 | 13800000 | 0.012742
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523092 HITCHLD_TR11 13 523093 HITCHLAND 3 115 523095 HITCHLAND 6 230 M2 | Current Study |  | (250.00, 288.00) | 733719.6865 | 5.3168 | 13800000 | 0.013263
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 728101.5318 | 1.6749 | 43472000 | 0.041892
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 464171.0061 | 3.3155 | 14000000 | 0.013802
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 383408.9919 | 0.69433 | 55220000 | 0.027794
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 364066.9894 | 1.9573 | 18600000 | 0.16098
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 296788.3911 | 1.5956 | 18600000 | 0.22967
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 296788.3911 | 1.5956 | 18600000 | 0.22967
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 295910.9195 | 1.5909 | 18600000 | 0.15486
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 286767.123 | 1.1471 | 25000000 | 0.015968
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 286767.123 | 1.1471 | 25000000 | 0.013915
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 270346.6385 | 1.4535 | 18600000 | 0.22967
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 256061.7132 | 1.3767 | 18600000 | 0.1501
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 216679.9282 | 1.1649 | 18600000 | 0.081641
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 213278.3347 | 1.1467 | 18600000 | 0.096945
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 210745.1471 | 1.133 | 18600000 | 0.14661
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 210317.8079 | 1.1307 | 18600000 | 0.096945
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 201142.6455 | 1.0814 | 18600000 | 0.027292
GEN-2024-145 | 05 SOUTHWEST | TBD | NRIS | Add 0.09 MVAR switched shunt at GRAY CO3 115 kV | Current Study |  |  | 186791.6218 | 8.4426 | 2212500 | 0.12579
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 181258.5701 | 1.1194 | 16192000 | 0.10301
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 18 MVAR switched shunt at FALCNRD4 138 kV | Current Study |  |  | 166943.7459 | 6.8631 | 2432500 | 0.042168
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 0.7 MVAR switched shunt at GEN-2024-161 138 kV | Current Study |  |  | 130484.0799 | 5.3642 | 2432500 | 0.020894
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 112598.9992 | 0.75378 | 14938000 | 0.065889
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 109003.1364 | 0.75378 | 14460953.1406 | 0.065889
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 108262.5365 | 0.90219 | 12000000 | 0.10301
GEN-2024-145 | 05 SOUTHWEST | TBD | NRIS | Add 16 MVAR switched shunt at UNDERWOOD 2 345 kV | Current Study |  |  | 105578.2588 | 1.992 | 5300000 | 0.12832
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 0.7 MVAR switched shunt at ROSEVLT2 69 kV | Current Study |  |  | 94710.121 | 6.8631 | 1380000 | 0.042168
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 76413.8255 | 5.5372 | 1380000 | 0.032512
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 67533.5686 | 3.0524 | 2212500 | 0.10301
GEN-2024-145 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 61440.1404 | 0.33945 | 18100000 | 0.0042679
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-161-TAP 138 kV | Current Study |  |  | 57315.1224 | 2.3562 | 2432500 | 0.020894
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 0.5 MVAR switched shunt at RKY_RDG4 138 kV | Current Study |  |  | 49245.0506 | 2.0245 | 2432500 | 0.10301
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 32149.7963 | 0.49039 | 6556000 | 0.027794
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 26048.2074 | 1.1773 | 2212500 | 0.10301
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 18470.6423 | 1.1194 | 1650000 | 0.10301
GEN-2024-145 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 17491.3326 | 1.2675 | 1380000 | 0.065843
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 11042.7028 | 0.8002 | 1380000 | 0.10301
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 10091.0975 | 0.45609 | 2212500 | 0.03887
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 8865.2897 | 0.16727 | 5300000 | 0.019659
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 7854.0268 | 0.56913 | 1380000 | 0.041383
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 6403.6861 | 0.46404 | 1380000 | 0.03887
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 249.2484 | 0.018061 | 1380000 | 0.0015461
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 28865080.691 | 1.9058 | 1514620000 | 0.046884
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 23679957.9848 | 2.5234 | 938400000 | 0.17124
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 21302061.1232 | 2.27 | 938400000 | 0.27262
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 20775741.7098 | 1.6166 | 1285130000 | 0.20379
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 20435278.0335 | 1.607 | 1271630000 | 0.13238
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 14170450.2302 | 1.9552 | 724760000 | 0.18553
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 12311719.9454 | 1.1466 | 1073760000 | 0.078564
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1 | Current Study | 18.95 | (901.00, 901.00) | 9900627.5965 | 27.4979 | 36005000 | 0.64251
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 8495798.3816 | 1.7595 | 482840000 | 0.17887
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Rebuild 3-winding transformer and add 3-winding transformer 524263 BSHLND_TR1 1 13 524266 BUSHLAND 3 115 524267 BUSHLAND 6 230 1 | Current Study |  | (323.00, 323.00) | 8312415.111 | 37.9562 | 21900000 | 0.077177
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 8100461.9058 | 1.7259 | 469340000 | 0.11791
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 524243 OUTPOST 3 115 524266 BUSHLAND 3 115 M2 | Current Study | 1.93 | (598.00, 598.00) | 2619739.2281 | 37.9562 | 6902000 | 0.077177
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 1983875.7779 | 1.0027 | 197860000 | 0.039643
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | Current Study | 13.92 | (519.00, 519.00) | 1839349.0346 | 6.9546 | 26448000 | 0.04568
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523095 HITCHLAND 6 230 778320 G24-045-TAP 230 1 | Current Study | 37.8 | (772.00, 772.00) | 1754246.9523 | 2.4426 | 71820000 | 0.050542
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 1715038.8689 | 2.0296 | 84500000 | 0.10322
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1652137.3206 | 1.9552 | 84500000 | 0.18553
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1577908.5009 | 1.2641 | 124824000 | 0.066161
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1552382.0541 | 0.78201 | 198511000 | 0.033442
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | Current Study | 11.15 | (519.00, 519.00) | 1456074.7581 | 6.8731 | 21185000 | 0.044511
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 1413725.5752 | 0.85648 | 165062000 | 0.043111
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524243 OUTPOST 3 115 524560 ARNOT 3 115 1 | Current Study | 3.43 | (598.00, 598.00) | 1301898.8051 | 37.9562 | 3430000 | 0.15435
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 1209522.8003 | 3.3952 | 35625000 | 0.028328
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524300 HILLSIDE 3 115 524560 ARNOT 3 115 1 | Current Study | 3.17 | (598.00, 598.00) | 1203212.5983 | 37.9562 | 3170000 | 0.15435
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 1091809.382 | 1.3398 | 81488000 | 0.071171
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 941946.0417 | 2.1668 | 43472000 | 0.05283
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 926037.2046 | 1.677 | 55220000 | 0.065438
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 857368.6971 | 1.0146 | 84500000 | 0.024922
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524300 HILLSIDE 3 115 524306 COULTER 3 115 1 | Current Study | 2.11 | (598.00, 598.00) | 800876.5244 | 37.9562 | 2110000 | 0.15435
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523094 HITCHLD_TR21 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2 | Current Study |  | (560.00, 644.00) | 664186.3372 | 2.6567 | 25000000 | 0.023569
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523091 HITCHLD_TR01 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2 | Current Study |  | (560.00, 644.00) | 664186.3372 | 2.6567 | 25000000 | 0.020503
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 610780.3829 | 2.4431 | 25000000 | 0.028891
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 610780.3829 | 2.4431 | 25000000 | 0.033153
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 488641.3779 | 3.4903 | 14000000 | 0.014164
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524281 34TH_ST_TP 3 115 524325 WESTERN 3 115 1 | Current Study | 1.11 | (217.00, 217.00) | 437337.6122 | 39.3998 | 1110000 | 0.076597
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 397292.1779 | 2.136 | 18600000 | 0.17124
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524281 34TH_ST_TP 3 115 524306 COULTER 3 115 1 | Current Study | 0.96 | (217.00, 217.00) | 378237.9349 | 39.3998 | 960000 | 0.076597
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 363665.7297 | 1.9552 | 18600000 | 0.18553
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 361398.262 | 1.943 | 18600000 | 0.27262
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 361398.262 | 1.943 | 18600000 | 0.27262
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 354472.0794 | 1.9058 | 18600000 | 0.046884
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 329200.2255 | 1.7699 | 18600000 | 0.27262
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 321022.2684 | 1.7259 | 18600000 | 0.11791
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 300502.3986 | 1.6156 | 18600000 | 0.20379
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 299673.0053 | 1.6111 | 18600000 | 0.17124
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 298772.3576 | 1.6063 | 18600000 | 0.13238
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 294625.0841 | 1.584 | 18600000 | 0.13238
GEN-2024-153 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 142255.1702 | 0.78594 | 18100000 | 0.0096327
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 142199.9984 | 0.87821 | 16192000 | 0.078774
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 112562.6643 | 0.75353 | 14938000 | 0.064208
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 108967.9619 | 0.75353 | 14460953.1406 | 0.064208
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 95498.5731 | 1.8019 | 5300000 | 0.20643
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 77650.5197 | 1.1844 | 6556000 | 0.065438
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 52981.1193 | 2.3946 | 2212500 | 0.078775
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 37336.6757 | 0.31114 | 12000000 | 0.034629
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 34140.2758 | 2.4739 | 1380000 | 0.20643
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 33071.2758 | 2.3965 | 1380000 | 0.013717
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 25104.9725 | 1.8192 | 1380000 | 0.12895
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 22702.1045 | 1.6451 | 1380000 | 0.20643
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 20435.2178 | 0.92363 | 2212500 | 0.078775
GEN-2024-153 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 16991.9218 | 1.2313 | 1380000 | 0.062352
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 14490.489 | 0.87821 | 1650000 | 0.078774
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 9222.54 | 0.41684 | 2212500 | 0.034629
GEN-2024-153 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 5852.5102 | 0.42409 | 1380000 | 0.034629
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 15233717.5651 | 1.6206 | 940000000 | 0.022898
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 532803 BURNS 7 345 1 | Current Study | 50.03 | (1793.00, 1793.00) | 5416487.5047 | 4.9211 | 110066000 | 0.051361
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532803 BURNS 7 345 1 | Current Study | 45.5 | (1793.00, 1793.00) | 4926048.0004 | 4.9211 | 100100000 | 0.051361
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 2514762.9065 | 2.1442 | 117282000 | 0.045121
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 2466639.3899 | 1.6418 | 150244000 | 0.037205
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1486169.8645 | 0.74866 | 198511000 | 0.040019
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1441253.8014 | 0.66016 | 218320000 | 0.02037
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1309757.1938 | 1.3042 | 100427000 | 0.01675
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 1256677.0148 | 2.2785 | 55154000 | 0.04018
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 1230385.7222 | 0.62185 | 197860000 | 0.030733
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1174790.107 | 0.81698 | 143796000 | 0.040805
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1137969.8956 | 0.91166 | 124824000 | 0.059643
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1000763.3876 | 1.0481 | 95480000 | 0.042387
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 984525.6059 | 1.0947 | 89936000 | 0.012787
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 901836.6414 | 1.3664 | 66000000 | 0.031407
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 887773.9729 | 1.0481 | 84700000 | 0.042387
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 882506.338 | 0.53465 | 165062000 | 0.03364
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 777612.5385 | 0.95427 | 81488000 | 0.063362
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 753713.8951 | 0.56693 | 132946000 | 0.017626
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 6.3 MVAR switched shunt at HOLLIS 4 138 kV | Current Study |  |  | 656430.4445 | 26.9858 | 2432500 | 0.048163
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 633417.6667 | 1.3479 | 46992000 | 0.054593
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 601520.7091 | 2.2785 | 26400000 | 0.04018
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 467088.103 | 0.49699 | 93984000 | 0.030839
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 411909.3938 | 1.5734 | 26180000 | 0.017778
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 400385.9106 | 0.74894 | 53460000 | 0.027034
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 315390.3227 | 1.2466 | 25300000 | 0.025534
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 138 MVAR switched shunt at GEN-2024-016 345 kV | Current Study |  |  | 309960.2584 | 5.8483 | 5300000 | 0.036614
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 122 MVAR switched shunt at HOYT 7 345 kV | Current Study |  |  | 304131.7057 | 5.7383 | 5300000 | 0.042364
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 262500.912 | 2.1307 | 12320000 | 0.045719
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at SHARNSP3 115 kV | Current Study |  |  | 258990.4815 | 11.7058 | 2212500 | 0.034708
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 8 MVAR switched shunt at RANSOM 3 115 kV | Current Study |  |  | 258990.4815 | 11.7058 | 2212500 | 0.034708
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 247077.9517 | 2.059 | 12000000 | 0.045719
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 247077.9517 | 2.059 | 12000000 | 0.045719
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 240236.5091 | 2.002 | 12000000 | 0.027033
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at GRANTTP3 115 kV | Current Study |  |  | 239735.6534 | 10.8355 | 2212500 | 0.060423
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at PNTPR-GOAB3 115 kV | Current Study |  |  | 239735.6534 | 10.8355 | 2212500 | 0.060423
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 0.06 MVAR switched shunt at G24-125-TAP 345 kV | Current Study |  |  | 236400.5002 | 4.4604 | 5300000 | 0.031857
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 220284.3616 | 1.8357 | 12000000 | 0.045719
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 219555.947 | 0.85517 | 25674000 | 0.030021
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 25 MVAR switched shunt at HIGHPT 3 115 kV | Current Study |  |  | 204317.838 | 9.2347 | 2212500 | 0.034708
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 200462.8864 | 1.6705 | 12000000 | 0.039368
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 194861.0228 | 1.2945 | 15053000 | 0.017121
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 177663.97 | 1.4805 | 12000000 | 0.075328
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 174787.3166 | 3.2979 | 5300000 | 0.043788
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 172947.2974 | 1.4412 | 12000000 | 0.039368
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 167404.8049 | 3.1586 | 5300000 | 0.039368
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 167382.3338 | 1.3949 | 12000000 | 0.045719
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 167382.3338 | 1.3949 | 12000000 | 0.045719
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 160528.0593 | 1.3377 | 12000000 | 0.045121
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 158742.6078 | 1.3229 | 12000000 | 0.045719
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 158008.5554 | 1.3167 | 12000000 | 0.063363
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 156501.1672 | 1.3042 | 12000000 | 0.045719
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 156046.5935 | 1.3004 | 12000000 | 0.045719
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 156035.4917 | 0.87132 | 17908000 | 0.031094
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 148765.0463 | 1.2397 | 12000000 | 0.045719
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 126484.8054 | 2.3865 | 5300000 | 0.073413
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 124499.6703 | 1.0375 | 12000000 | 0.045719
GEN-2024-154 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 118003.2039 | 0.65195 | 18100000 | 0.0099881
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 109415.314 | 0.73246 | 14938000 | 0.078016
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 105921.1225 | 0.73246 | 14460953.1406 | 0.078016
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 95144.8037 | 1.7952 | 5300000 | 0.045121
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 94882.7609 | 0.79069 | 12000000 | 0.026757
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 91290.6475 | 1.7225 | 5300000 | 0.045121
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 87258.0685 | 0.5389 | 16192000 | 0.060423
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 83257.119 | 1.5709 | 5300000 | 0.075328
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 82341.7826 | 1.5536 | 5300000 | 0.073413
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 77385.5461 | 3.1813 | 2432500 | 0.14429
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 75851.0603 | 0.63209 | 12000000 | 0.026757
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 75479.642 | 0.629 | 12000000 | 0.021446
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 73887.9702 | 1.1195 | 6600000 | 0.045719
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CHILD4WT 138 kV | Current Study |  |  | 68043.6503 | 2.7973 | 2432500 | 0.14429
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 63116.9646 | 0.54131 | 11660000 | 0.030839
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 60878.1658 | 1.1486 | 5300000 | 0.039368
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 59799.6463 | 1.1283 | 5300000 | 0.039368
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 59352.8882 | 1.1199 | 5300000 | 0.031857
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 56397.6554 | 1.0641 | 5300000 | 0.039368
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 50126.7258 | 2.2785 | 2200000 | 0.04018
GEN-2024-154 | 04 SOUTHEAST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 45428.9384 | 3.292 | 1380000 | 0.20838
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 45009.8328 | 0.84924 | 5300000 | 0.045719
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 40033.4199 | 1.3479 | 2970000 | 0.054593
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 39076.9269 | 1.6065 | 2432500 | 0.073413
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 36894.5028 | 1.0481 | 3520000 | 0.042387
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 36459.8568 | 0.68792 | 5300000 | 0.060423
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 34064.5557 | 1.0481 | 3250000 | 0.042387
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 32937.6182 | 1.0135 | 3250000 | 0.045719
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 29937.5922 | 0.24948 | 12000000 | 0.034708
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 29654.3851 | 1.3479 | 2200000 | 0.054593
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 28356.5573 | 1.2817 | 2212500 | 0.041199
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 28303.4655 | 2.1442 | 1320000 | 0.045121
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 25590.7299 | 0.48284 | 5300000 | 0.0047362
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 22723.7882 | 0.42875 | 5300000 | 0.0031871
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 22125.694 | 0.68079 | 3250000 | 0.030839
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 20292.7843 | 1.4705 | 1380000 | 0.051362
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 17815.6588 | 0.77459 | 2300000 | 0.054593
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 16645.9472 | 0.68431 | 2432500 | 0.030839
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at SEGNTP 3 115 kV | Current Study |  |  | 16065.9176 | 0.72614 | 2212500 | 0.060423
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 8891.7869 | 0.5389 | 1650000 | 0.060423
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 7394.8908 | 0.33423 | 2212500 | 0.034708
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 9427369.8291 | 1.0029 | 940000000 | 0.020244
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511564 MARTHA 4 138 781800 G24-161-TAP 138 1 | Current Study | 20.7 | (395.00, 395.00) | 9330640.4016 | 37.563 | 24840000 | 0.20466
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512110 LAKEP4WT 138 521043 RUSSELL4 138 1 | Current Study | 37.45 | (134.00, 134.00) | 7525549.5542 | 16.7458 | 44940000 | 0.031885
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512101 CHILD4WT 138 512110 LAKEP4WT 138 1 | Current Study | 35.14 | (134.00, 134.00) | 7296769.7612 | 17.304 | 42168000 | 0.031316
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 6105503.2972 | 17.1383 | 35625000 | 0.25535
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511446 CL-AFTP4 138 511458 ELKCTY-4 138 1 | Current Study | 13.67 | (395.00, 395.00) | 6027039.8883 | 36.7413 | 16404000 | 0.35742
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 532803 BURNS 7 345 1 | Current Study | 50.03 | (1793.00, 1793.00) | 3412355.1469 | 3.1003 | 110066000 | 0.046225
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532803 BURNS 7 345 1 | Current Study | 45.5 | (1793.00, 1793.00) | 3103381.155 | 3.1003 | 100100000 | 0.046225
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511564 MARTHA 4 138 529302 OMALTUS4 138 1 | Current Study | 6.37 | (395.00, 395.00) | 2871313.0125 | 37.563 | 7644000 | 0.20466
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 2466593.8857 | 17.6185 | 14000000 | 0.12767
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511440 ALTUSJT4 138 521043 RUSSELL4 138 1 | Current Study | 12.25 | (211.00, 211.00) | 2299213.7405 | 15.6409 | 14700000 | 0.057665
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 521042 RUSSELL2 69 529342 OMMANGM2 69 1 | Current Study | 18.66 | (69.00, 69.00) | 2076444.585 | 13.0915 | 15861000 | 0.015195
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511477 S.W.S.-4 138 520814 ANADARK4 138 1 | Current Study | 7.37 | (395.00, 395.00) | 1987445.5039 | 22.4722 | 8844000 | 0.095575
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 529298 OMPVET-4 138 529345 OMPARK-4 138 1 | Current Study | 3.79 | (395.00, 395.00) | 1708363.6291 | 37.563 | 4548000 | 0.20466
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 1689233.9008 | 1.4403 | 117282000 | 0.043298
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 1643412.3715 | 1.0938 | 150244000 | 0.035411
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2 | Current Study |  | (478.00, 478.00) | 1570549.9339 | 8.6771 | 18100000 | 0.10372
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515802 GRACMNT4 138 521089 WASHITA4 138 1 | Current Study | 5.87 | (265.00, 265.00) | 1563493.1128 | 22.1961 | 7044000 | 0.088849
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | Current Study | 11.1 | (395.00, 395.00) | 1554687.3034 | 11.6718 | 13320000 | 0.04712
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511440 ALTUSJT4 138 529345 OMPARK-4 138 1 | Current Study | 2.86 | (281.00, 281.00) | 1289160.9444 | 37.563 | 3432000 | 0.20466
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511435 SNYDER-4 138 765230 G20-012-TAP 138 1 | Current Study | 7.51 | (395.00, 395.00) | 1160975.8241 | 12.8826 | 9012000 | 0.12769
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 972221.9252 | 0.44532 | 218320000 | 0.01963
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 529298 OMPVET-4 138 529302 OMALTUS4 138 1 | Current Study | 2.13 | (395.00, 395.00) | 960109.3747 | 37.563 | 2556000 | 0.20466
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 932071.7698 | 0.92811 | 100427000 | 0.017028
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 830242.7835 | 0.41824 | 198511000 | 0.031938
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 820729.4879 | 1.4881 | 55154000 | 0.037488
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 796766.0472 | 0.55409 | 143796000 | 0.039536
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild 3-winding transformer 521042 RUSSELL2 69 521043 RUSSELL4 138 521175 RSLTERT 13 1 | Current Study |  | (81.00, 81.00) | 780884.4251 | 14.4608 | 5400000 | 0.025779
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 776900.8612 | 0.86384 | 89936000 | 0.014414
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 764314.6997 | 0.8005 | 95480000 | 0.046247
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 710105.6937 | 0.35889 | 197860000 | 0.025339
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 699383.4383 | 1.0597 | 66000000 | 0.034795
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 694033.8948 | 0.55601 | 124824000 | 0.051965
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 678021.1045 | 0.8005 | 84700000 | 0.046247
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511425 TUTCONT4 138 514898 CIMARON4 138 1 | Current Study | 14.65 | (395.00, 395.00) | 525688.5523 | 2.9903 | 17580000 | 0.037324
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 509855.5623 | 0.30889 | 165062000 | 0.027764
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | Current Study | 13.6 | (1793.00, 1793.00) | 496798.3463 | 1.6604 | 29920000 | 0.04479
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 485043.3169 | 1.0322 | 46992000 | 0.059721
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 471349.7566 | 0.57843 | 81488000 | 0.054867
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | Current Study | 1 | (395.00, 395.00) | 464017.9531 | 38.6682 | 1200000 | 0.79534
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 457127.6176 | 0.34384 | 132946000 | 0.015272
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511477 S.W.S.-4 138 521089 WASHITA4 138 1 | Current Study | 2.05 | (717.00, 717.00) | 406529.6531 | 16.5256 | 2460000 | 0.15031
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 764550 G20-087-TAP 345 1 | Current Study | 14.38 | (1793.00, 1793.00) | 401517.7292 | 1.2692 | 31636000 | 0.061831
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 392850.1737 | 1.4881 | 26400000 | 0.037488
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR SVC at ELDORDO2 69 kV | Current Study |  |  | 385152.7302 | 16.7458 | 2300000 | 0.031885
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 376602.0317 | 0.40071 | 93984000 | 0.035521
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 6.3 MVAR switched shunt at HOLLIS 4 138 kV | Current Study |  |  | 348204.694 | 14.3147 | 2432500 | 0.036497
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 294365.6542 | 1.1244 | 26180000 | 0.01815
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CHILD4WT 138 kV | Current Study |  |  | 262548.1987 | 10.7933 | 2432500 | 0.79534
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 260364.2683 | 0.77503 | 33594000 | 0.045177
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 248668.4609 | 0.46515 | 53460000 | 0.023986
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | Current Study | 8.91 | (2390.00, 2390.00) | 245530.8624 | 1.2526 | 19602000 | 0.061831
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 230638.8293 | 0.91162 | 25300000 | 0.026675
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 122 MVAR switched shunt at HOYT 7 345 kV | Current Study |  |  | 203537.801 | 3.8403 | 5300000 | 0.040502
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 200562.0724 | 0.43682 | 45914000 | 0.031547
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 196592.3878 | 0.76573 | 25674000 | 0.038402
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 138 MVAR switched shunt at GEN-2024-016 345 kV | Current Study |  |  | 192813.7728 | 3.638 | 5300000 | 0.032537
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 176426.0112 | 1.432 | 12320000 | 0.043896
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 166060.4071 | 1.3838 | 12000000 | 0.043896
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 166060.4071 | 1.3838 | 12000000 | 0.043896
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | Current Study | 5.97 | (2390.00, 2390.00) | 164513.9448 | 1.2526 | 13134000 | 0.061831
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at SHARNSP3 115 kV | Current Study |  |  | 158830.0212 | 7.1788 | 2212500 | 0.030408
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 8 MVAR switched shunt at RANSOM 3 115 kV | Current Study |  |  | 158830.0212 | 7.1788 | 2212500 | 0.030408
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 0.06 MVAR switched shunt at G24-125-TAP 345 kV | Current Study |  |  | 158205.2876 | 2.985 | 5300000 | 0.030456
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 148052.5094 | 1.2338 | 12000000 | 0.043896
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at GRANTTP3 115 kV | Current Study |  |  | 140793.7125 | 6.3636 | 2212500 | 0.050694
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at PNTPR-GOAB3 115 kV | Current Study |  |  | 140793.7125 | 6.3636 | 2212500 | 0.050694
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 139689.4205 | 0.78004 | 17908000 | 0.039767
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 138031.8026 | 0.91697 | 15053000 | 0.017326
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 126667.8462 | 1.0556 | 12000000 | 0.035536
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 25 MVAR switched shunt at HIGHPT 3 115 kV | Current Study |  |  | 125301.1553 | 5.6633 | 2212500 | 0.030408
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 119315.3002 | 2.2512 | 5300000 | 0.031546
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 117973.0715 | 0.98311 | 12000000 | 0.071457
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 112497.203 | 0.93748 | 12000000 | 0.043896
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 112497.203 | 0.93748 | 12000000 | 0.043896
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 110815.6697 | 0.92346 | 12000000 | 0.046247
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 109458.649 | 0.43682 | 25058000 | 0.031547
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 109281.3839 | 0.91068 | 12000000 | 0.035536
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 107831.0936 | 0.89859 | 12000000 | 0.043298
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 106690.4671 | 0.88909 | 12000000 | 0.043896
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 105899.7373 | 1.9981 | 5300000 | 0.0379
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 105779.2116 | 1.9958 | 5300000 | 0.035536
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 104878.4833 | 0.87399 | 12000000 | 0.043896
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 99984.5756 | 0.8332 | 12000000 | 0.043896
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 99167.9966 | 0.8264 | 12000000 | 0.03995
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 95776.8062 | 0.79814 | 12000000 | 0.054867
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 94535.3735 | 3.8863 | 2432500 | 0.25181
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 89668.9494 | 0.74724 | 12000000 | 0.014415
GEN-2024-157 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 87249.8642 | 0.48204 | 18100000 | 0.01055
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511501 TUTTLE4 138 511575 LEONARD4 138 1 | Current Study | 2.12 | (395.00, 395.00) | 82911.0746 | 3.2591 | 2544000 | 0.037324
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 79276.7581 | 0.66064 | 12000000 | 0.03995
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 68472.9243 | 0.57061 | 12000000 | 0.027793
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 63911.3703 | 1.2059 | 5300000 | 0.043298
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 62200.1405 | 0.41639 | 14938000 | 0.063357
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 61322.428 | 1.157 | 5300000 | 0.043298
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 60213.7714 | 0.41639 | 14460953.1406 | 0.063357
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 59111.3139 | 1.1153 | 5300000 | 0.049013
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 55284.693 | 1.0431 | 5300000 | 0.071457
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 52979.4683 | 0.4415 | 12000000 | 0.027793
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 52318.7465 | 0.79271 | 6600000 | 0.046247
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 51245.5366 | 0.31649 | 16192000 | 0.050694
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 51221.01 | 0.96643 | 5300000 | 0.03995
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 50889.7078 | 0.43645 | 11660000 | 0.035521
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 41556.5292 | 0.62964 | 6600000 | 0.035521
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | Current Study | 1.06 | (395.00, 395.00) | 41455.5373 | 3.2591 | 1272000 | 0.037324
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 39720.4775 | 0.74944 | 5300000 | 0.030456
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 38973.8962 | 0.59051 | 6600000 | 0.027793
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 38973.8962 | 0.59051 | 6600000 | 0.027793
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 38481.5468 | 0.72607 | 5300000 | 0.049013
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 38467.5003 | 0.7258 | 5300000 | 0.035536
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 37786.0088 | 0.71294 | 5300000 | 0.035536
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 37036.7237 | 0.56116 | 6600000 | 0.027793
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 35705.7495 | 1.4679 | 2432500 | 0.043298
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 35636.3697 | 0.67238 | 5300000 | 0.035536
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 32737.5145 | 1.4881 | 2200000 | 0.037488
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 32555.9688 | 0.61426 | 5300000 | 0.027793
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 30655.8276 | 1.0322 | 2970000 | 0.059721
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 30250.9839 | 0.57077 | 5300000 | 0.043896
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 28177.5004 | 0.8005 | 3520000 | 0.046247
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 26016.1759 | 0.8005 | 3250000 | 0.046247
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 25395.0205 | 0.47915 | 5300000 | 0.098025
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 24148.4515 | 0.74303 | 3250000 | 0.027793
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 23322.5367 | 0.71762 | 3250000 | 0.046247
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 22708.0205 | 1.0322 | 2200000 | 0.059721
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 21412.4121 | 0.40401 | 5300000 | 0.050694
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 20681.3946 | 0.63635 | 3250000 | 0.027793
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 20498.9602 | 0.63074 | 3250000 | 0.027793
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 20497.6908 | 0.6307 | 3250000 | 0.027793
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 19963.5658 | 0.61426 | 3250000 | 0.027793
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 19060.7266 | 0.8615 | 2212500 | 0.039562
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 19035.5244 | 0.35916 | 5300000 | 0.003814
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 19012.1992 | 1.4403 | 1320000 | 0.043298
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 18717.2666 | 0.57592 | 3250000 | 0.027793
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 18359.7033 | 0.153 | 12000000 | 0.030408
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 17839.3751 | 0.5489 | 3250000 | 0.035521
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 17173.6483 | 0.52842 | 3250000 | 0.027793
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 13642.4371 | 0.59315 | 2300000 | 0.059721
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 13421.1969 | 0.55174 | 2432500 | 0.035521
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 13235.1372 | 0.5441 | 2432500 | 0.035521
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 12784.3377 | 0.9264 | 1380000 | 0.046225
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at SEGNTP 3 115 kV | Current Study |  |  | 9435.3099 | 0.42645 | 2212500 | 0.050694
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 8749.8541 | 0.63405 | 1380000 | 0.035521
GEN-2024-157 | 04 SOUTHEAST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 8542.878 | 0.61905 | 1380000 | 0.055979
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 7234.8821 | 0.52427 | 1380000 | 0.036486
GEN-2024-157 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 7184.0918 | 0.13555 | 5300000 | 0.033063
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 5222.0316 | 0.31649 | 1650000 | 0.050694
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 4535.0341 | 0.20497 | 2212500 | 0.030408
GEN-2024-157 | 04 SOUTHEAST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 3979.2232 | 0.28835 | 1380000 | 0.036497
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512110 LAKEP4WT 138 521043 RUSSELL4 138 1 | Current Study | 37.45 | (134.00, 134.00) | 25858381.7784 | 57.5398 | 44940000 | 0.080729
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512101 CHILD4WT 138 512110 LAKEP4WT 138 1 | Current Study | 35.14 | (134.00, 134.00) | 23888803.9447 | 56.6515 | 42168000 | 0.075546
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 12591496.2315 | 1.3395 | 940000000 | 0.019923
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 521042 RUSSELL2 69 529342 OMMANGM2 69 1 | Current Study | 18.66 | (69.00, 69.00) | 10186237.5494 | 64.2219 | 15861000 | 0.054925
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 511419 SNYDRTER 13 511435 SNYDER-4 138 511475 SNYDER-2 69 M2 | Current Study |  | (75.00, 75.00) | 9000000 | 100 | 9000000 | 0.022558
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511440 ALTUSJT4 138 521043 RUSSELL4 138 1 | Current Study | 12.25 | (211.00, 211.00) | 8716773.4592 | 59.2978 | 14700000 | 0.16109
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511435 SNYDER-4 138 765230 G20-012-TAP 138 1 | Current Study | 7.51 | (395.00, 395.00) | 5927194.1744 | 65.77 | 9012000 | 0.48034
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 532803 BURNS 7 345 1 | Current Study | 50.03 | (1793.00, 1793.00) | 4537404.3615 | 4.1224 | 110066000 | 0.04529
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 4443794.6919 | 12.4738 | 35625000 | 0.13694
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532803 BURNS 7 345 1 | Current Study | 45.5 | (1793.00, 1793.00) | 4126562.0318 | 4.1224 | 100100000 | 0.04529
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511440 ALTUSJT4 138 781710 G24-158-TAP 138 1 | Current Study | 3.23 | (395.00, 395.00) | 3876000 | 100 | 3876000 | 0.51966
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511446 CL-AFTP4 138 511458 ELKCTY-4 138 1 | Current Study | 13.67 | (395.00, 395.00) | 3659214.0793 | 22.3068 | 16404000 | 0.15989
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild 3-winding transformer 521042 RUSSELL2 69 521043 RUSSELL4 138 521175 RSLTERT 13 1 | Current Study |  | (81.00, 81.00) | 3303474.9262 | 61.1755 | 5400000 | 0.080358
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 781680 GEN-2024-157 138 781800 G24-161-TAP 138 1 | Current Study | 6.36 | (211.00, 211.00) | 2343708.1533 | 30.709 | 7632000 | 0.28545
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 2267894.8084 | 1.9337 | 117282000 | 0.042833
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 2205603.0663 | 1.468 | 150244000 | 0.035018
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | Current Study | 11.1 | (395.00, 395.00) | 2182722.0294 | 16.3868 | 13320000 | 0.048745
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 1795271.6235 | 12.8234 | 14000000 | 0.068471
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2 | Current Study |  | (478.00, 478.00) | 1689379.0922 | 9.3336 | 18100000 | 0.082209
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at WELL 4WT 138 kV | Current Study |  |  | 1666402.8067 | 68.5058 | 2432500 | 0.051802
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 764550 G20-087-TAP 345 1 | Current Study | 14.38 | (1793.00, 1793.00) | 1384281.4839 | 4.3757 | 31636000 | 0.15707
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR SVC at ELDORDO2 69 kV | Current Study |  |  | 1323415.1887 | 57.5398 | 2300000 | 0.080729
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1305900.0033 | 0.59816 | 218320000 | 0.019429
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1258491.3423 | 1.2531 | 100427000 | 0.016941
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515802 GRACMNT4 138 521089 WASHITA4 138 1 | Current Study | 5.87 | (265.00, 265.00) | 1189745.4327 | 16.8902 | 7044000 | 0.049818
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511477 S.W.S.-4 138 520814 ANADARK4 138 1 | Current Study | 7.37 | (395.00, 395.00) | 1106182.034 | 12.5077 | 8844000 | 0.039197
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 1096655.7956 | 1.9884 | 55154000 | 0.036909
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1085339.0213 | 0.54674 | 198511000 | 0.030764
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1072280.7896 | 0.7457 | 143796000 | 0.039205
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 1069890.7508 | 1.1896 | 89936000 | 0.014627
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1048737.1935 | 1.0984 | 95480000 | 0.046757
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | Current Study | 13.6 | (1793.00, 1793.00) | 1004620.4929 | 3.3577 | 29920000 | 0.066738
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 6.3 MVAR switched shunt at HOLLIS 4 138 kV | Current Study |  |  | 978169.7895 | 40.2125 | 2432500 | 0.075546
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 960782.5591 | 1.4557 | 66000000 | 0.035221
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 956829.8229 | 0.48359 | 197860000 | 0.025158
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 934748.4211 | 0.74885 | 124824000 | 0.05157
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 930331.3813 | 1.0984 | 84700000 | 0.046757
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | Current Study | 8.91 | (2390.00, 2390.00) | 846497.6808 | 4.3184 | 19602000 | 0.15707
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511425 TUTCONT4 138 514898 CIMARON4 138 1 | Current Study | 14.65 | (395.00, 395.00) | 696150.1935 | 3.9599 | 17580000 | 0.03642
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 686708.3784 | 0.41603 | 165062000 | 0.027554
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 668720.8521 | 1.4231 | 46992000 | 0.060669
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 632364.0318 | 0.77602 | 81488000 | 0.054239
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 609759.8301 | 0.45865 | 132946000 | 0.01501
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | Current Study | 5.97 | (2390.00, 2390.00) | 567181.9478 | 4.3184 | 13134000 | 0.15707
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 524924.9919 | 1.9884 | 26400000 | 0.036909
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 520235.2581 | 0.55354 | 93984000 | 0.036155
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 460118.7537 | 0.72746 | 63250000 | 0.04158
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 398957.385 | 1.5239 | 26180000 | 0.018125
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 368184.9777 | 1.096 | 33594000 | 0.047074
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 328623.5289 | 0.61471 | 53460000 | 0.023356
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 314496.1187 | 1.2431 | 25300000 | 0.026801
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511477 S.W.S.-4 138 521089 WASHITA4 138 1 | Current Study | 2.05 | (717.00, 717.00) | 311360.7413 | 12.6569 | 2460000 | 0.084828
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 286299.1981 | 1.1151 | 25674000 | 0.041208
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 283221.1994 | 0.61685 | 45914000 | 0.032825
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 122 MVAR switched shunt at HOYT 7 345 kV | Current Study |  |  | 273169.5102 | 5.1541 | 5300000 | 0.040054
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 138 MVAR switched shunt at GEN-2024-016 345 kV | Current Study |  |  | 257002.9752 | 4.8491 | 5300000 | 0.031956
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 236897.2436 | 1.9229 | 12320000 | 0.043431
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | Current Study | 1 | (395.00, 395.00) | 226012.4638 | 18.8344 | 1200000 | 0.28545
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 222978.7751 | 1.8582 | 12000000 | 0.043431
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 222978.7751 | 1.8582 | 12000000 | 0.043431
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 0.06 MVAR switched shunt at G24-125-TAP 345 kV | Current Study |  |  | 211623.199 | 3.9929 | 5300000 | 0.030019
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at SHARNSP3 115 kV | Current Study |  |  | 211451.3602 | 9.5571 | 2212500 | 0.029829
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 8 MVAR switched shunt at RANSOM 3 115 kV | Current Study |  |  | 211451.3602 | 9.5571 | 2212500 | 0.029829
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 203451.485 | 1.1361 | 17908000 | 0.042677
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 198798.5443 | 1.6567 | 12000000 | 0.043431
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at GRANTTP3 115 kV | Current Study |  |  | 188991.0993 | 8.542 | 2212500 | 0.05014
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at PNTPR-GOAB3 115 kV | Current Study |  |  | 188991.0993 | 8.542 | 2212500 | 0.05014
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 186426.4064 | 1.2385 | 15053000 | 0.017242
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 168489.6964 | 3.1791 | 5300000 | 0.032825
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 168331.7961 | 1.4028 | 12000000 | 0.034798
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 25 MVAR switched shunt at HIGHPT 3 115 kV | Current Study |  |  | 166814.1798 | 7.5396 | 2212500 | 0.029829
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 158240.2612 | 1.3187 | 12000000 | 0.070624
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 154570.6498 | 0.61685 | 25058000 | 0.032825
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 152053.2168 | 1.2671 | 12000000 | 0.046757
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 151056.4075 | 1.2588 | 12000000 | 0.043431
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 151056.4075 | 1.2588 | 12000000 | 0.043431
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 145438.3357 | 5.979 | 2432500 | 0.28545
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 145226.5291 | 1.2102 | 12000000 | 0.034798
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 144769.5297 | 1.2064 | 12000000 | 0.042833
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 143259.3722 | 1.1938 | 12000000 | 0.043431
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 140826.3183 | 1.1736 | 12000000 | 0.043431
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 140572.4122 | 2.6523 | 5300000 | 0.034798
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 139643.1019 | 2.6348 | 5300000 | 0.036825
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 138517.7488 | 1.1543 | 12000000 | 0.041117
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 134254.9895 | 1.1188 | 12000000 | 0.043431
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 128494.3903 | 1.0708 | 12000000 | 0.054239
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CHILD4WT 138 kV | Current Study |  |  | 127881.1839 | 5.2572 | 2432500 | 0.28545
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 123485.4743 | 1.029 | 12000000 | 0.014627
GEN-2024-158 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 120741.5181 | 0.66708 | 18100000 | 0.010758
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 110733.6887 | 0.92278 | 12000000 | 0.041117
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511501 TUTTLE4 138 511575 LEONARD4 138 1 | Current Study | 2.12 | (395.00, 395.00) | 109796.1147 | 4.3159 | 2544000 | 0.03642
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 96511.6105 | 0.80426 | 12000000 | 0.028865
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 85804.7406 | 1.619 | 5300000 | 0.042833
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 82328.9347 | 1.5534 | 5300000 | 0.042833
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 81002.9653 | 0.54226 | 14938000 | 0.060797
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 78416.1257 | 0.54226 | 14460953.1406 | 0.060797
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 77941.61 | 1.4706 | 5300000 | 0.047619
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 74673.8053 | 0.62228 | 12000000 | 0.028865
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 74154.7554 | 1.3991 | 5300000 | 0.070624
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 71787.9857 | 1.0877 | 6600000 | 0.046757
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 71545.4506 | 1.3499 | 5300000 | 0.041117
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 70298.6656 | 0.6029 | 11660000 | 0.036155
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 68788.2287 | 0.42483 | 16192000 | 0.05014
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 57405.8636 | 0.86979 | 6600000 | 0.036156
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 54933.151 | 0.83232 | 6600000 | 0.028865
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 54933.151 | 0.83232 | 6600000 | 0.028865
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | Current Study | 1.06 | (395.00, 395.00) | 54898.0574 | 4.3159 | 1272000 | 0.03642
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 53132.0706 | 1.0025 | 5300000 | 0.030019
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 52202.734 | 0.79095 | 6600000 | 0.028865
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 51120.3404 | 0.96453 | 5300000 | 0.034798
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 50740.0956 | 0.95736 | 5300000 | 0.047619
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 50214.6908 | 0.94745 | 5300000 | 0.034798
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 47937.0504 | 1.9707 | 2432500 | 0.042833
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 47357.9863 | 0.89355 | 5300000 | 0.034798
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 45887.1738 | 0.8658 | 5300000 | 0.028865
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 43743.7493 | 1.9884 | 2200000 | 0.036909
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 42264.6606 | 1.4231 | 2970000 | 0.060669
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 40619.7206 | 0.76641 | 5300000 | 0.043431
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 38663.1223 | 1.0984 | 3520000 | 0.046757
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 35697.5078 | 1.0984 | 3250000 | 0.046757
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 34036.8981 | 1.0473 | 3250000 | 0.028865
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 33484.7706 | 0.63179 | 5300000 | 0.095238
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 32001.4916 | 0.98466 | 3250000 | 0.046757
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 31307.156 | 1.4231 | 2200000 | 0.060669
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 29150.1308 | 0.89693 | 3250000 | 0.028865
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 28892.9921 | 0.88902 | 3250000 | 0.028865
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 28891.2029 | 0.88896 | 3250000 | 0.028865
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 28742.4433 | 0.54231 | 5300000 | 0.05014
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 28138.3613 | 0.8658 | 3250000 | 0.028865
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 26381.7205 | 0.81175 | 3250000 | 0.028865
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 26305.5749 | 0.49633 | 5300000 | 0.0038836
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 25524.9838 | 1.9337 | 1320000 | 0.042833
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 24643.1728 | 0.75825 | 3250000 | 0.036156
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 24442.3832 | 0.20369 | 12000000 | 0.029829
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 24206.0124 | 0.7448 | 3250000 | 0.028865
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 18808.5906 | 0.81776 | 2300000 | 0.060669
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 18539.9362 | 0.76218 | 2432500 | 0.036156
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 18282.9147 | 0.75161 | 2432500 | 0.036156
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 16999.3187 | 1.2318 | 1380000 | 0.045291
GEN-2024-158 | 04 SOUTHEAST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 14060.3152 | 1.0189 | 1380000 | 0.067887
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at SEGNTP 3 115 kV | Current Study |  |  | 12665.2644 | 0.57244 | 2212500 | 0.05014
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 12086.9799 | 0.87587 | 1380000 | 0.036156
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 11375.3994 | 0.8243 | 1380000 | 0.04227
GEN-2024-158 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 10430.942 | 0.19681 | 5300000 | 0.035372
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 7665.0249 | 0.55544 | 1380000 | 0.051802
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 7009.67 | 0.42483 | 1650000 | 0.05014
GEN-2024-158 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 6037.5181 | 0.27288 | 2212500 | 0.029829
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 36372566.8271 | 2.4014 | 1514620000 | 0.049232
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 30248510.198 | 2.3537 | 1285130000 | 0.24725
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 29467775.9227 | 2.3173 | 1271630000 | 0.15908
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3 | Current Study | 39.39 | (478.00, 544.00) | 23484922.9245 | 22.2237 | 105675000 | 0.25317
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 22511570.0745 | 2.3989 | 938400000 | 0.13566
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 20862792.526 | 1.943 | 1073760000 | 0.11094
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 20413472.63 | 5.5698 | 366500000 | 0.12203
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 19249553.5916 | 2.0513 | 938400000 | 0.2053
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 16798393.7329 | 2.3178 | 724760000 | 0.18328
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Current Study | 54.58 | (637.00, 637.00) | 14664041.197 | 14.1406 | 103702000 | 0.10945
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 11400122.852 | 2.3611 | 482840000 | 0.20001
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 10971365.8094 | 2.3376 | 469340000 | 0.13308
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1 | Current Study | 52.45 | (1046.00, 1046.00) | 5656019.4988 | 5.6756 | 99655000 | 0.12486
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1 | Current Study | 9.6 | (901.00, 901.00) | 5026774.3118 | 27.5591 | 18240000 | 0.61538
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 524872 OASIS_TR1 1 13 524874 OASIS 3 115 524875 OASIS 6 230 M2 | Current Study |  | (239.00, 239.00) | 4534357.2087 | 32.8577 | 13800000 | 0.056641
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524863 FE-CHZPLT 3 115 524874 OASIS 3 115 1 | Current Study | 7.8 | (176.00, 176.00) | 2564263.0451 | 32.8752 | 7800000 | 0.053266
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524764 NORRIS_TP 3 115 524863 FE-CHZPLT 3 115 1 | Current Study | 7.62 | (176.00, 176.00) | 2505087.744 | 32.8752 | 7620000 | 0.053266
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 2059795.7698 | 1.041 | 197860000 | 0.0343
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 1984038.9088 | 2.348 | 84500000 | 0.099504
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 1970897.4474 | 3.5692 | 55220000 | 0.11606
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1958530.0933 | 2.3178 | 84500000 | 0.18328
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1950382.3026 | 2.3081 | 84500000 | 0.047245
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1873947.1865 | 1.5013 | 124824000 | 0.065478
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1787560.8656 | 0.90048 | 198511000 | 0.03209
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527597 TWEEDY 3 115 527798 EDDY_NTH 3 115 1 | Current Study | 44.83 | (394.00, 394.00) | 1559246.5398 | 3.4781 | 44830000 | 0.022295
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 1476563.0569 | 0.89455 | 165062000 | 0.037523
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 1295903.1884 | 1.5903 | 81488000 | 0.070396
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524623 DEAFSMITH 6 230 525520 OLSON 6 230 1 | Current Study | 11 | (519.00, 519.00) | 1264337.5214 | 6.0495 | 20900000 | 0.040992
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add line 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 P2 | Current Study | 2.51 | (478.00, 478.00) | 1226561.984 | 9.1025 | 13475000 | 0.069512
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 1181895.9585 | 4.7276 | 25000000 | 0.05346
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 1181895.9585 | 4.7276 | 25000000 | 0.046589
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1 | Current Study | 18.95 | (901.00, 901.00) | 1150229.2039 | 3.1946 | 36005000 | 0.062204
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 1036527.2326 | 2.3844 | 43472000 | 0.048446
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 446666.3209 | 2.4014 | 18600000 | 0.049232
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 437517.466 | 2.3522 | 18600000 | 0.24725
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 435434.2324 | 1.6431 | 26500000 | 0.017216
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 434796.5314 | 2.3376 | 18600000 | 0.13308
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 431108.3992 | 2.3178 | 18600000 | 0.18328
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 430831.2748 | 2.3163 | 18600000 | 0.15908
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 424850.8852 | 2.2841 | 18600000 | 0.15908
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 377689.4667 | 2.0306 | 18600000 | 0.13566
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 326576.6243 | 1.7558 | 18600000 | 0.2053
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 326576.6243 | 1.7558 | 18600000 | 0.2053
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 297480.9501 | 1.5994 | 18600000 | 0.2053
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 284886.9015 | 1.5317 | 18600000 | 0.13566
GEN-2024-159 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 186216.9507 | 1.0288 | 18100000 | 0.010508
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 165264.6463 | 2.5208 | 6556000 | 0.11606
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 145795.3075 | 0.90042 | 16192000 | 0.067305
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 129237.3842 | 0.86516 | 14938000 | 0.061433
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 125110.1725 | 0.86516 | 14460953.1406 | 0.061433
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 110477.3 | 2.0845 | 5300000 | 0.19901
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | Current Study | 0.78 | (598.00, 598.00) | 90356.5225 | 1.7074 | 5292000 | 0.016079
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1 | Current Study | 2.49 | (394.00, 394.00) | 86605.4848 | 3.4781 | 2490000 | 0.022295
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | Current Study | 0.2 | (598.00, 598.00) | 76492.2942 | 1.7074 | 4480000 | 0.016079
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 54320.677 | 2.4552 | 2212500 | 0.067305
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 40894.3374 | 0.34079 | 12000000 | 0.031607
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 39495.0978 | 2.862 | 1380000 | 0.19901
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 36647.5401 | 2.6556 | 1380000 | 0.15686
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 26262.8762 | 1.9031 | 1380000 | 0.19901
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 21744.4735 | 1.5757 | 1380000 | 0.0075156
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 20951.8953 | 0.94698 | 2212500 | 0.067305
GEN-2024-159 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 16989.7347 | 1.2311 | 1380000 | 0.051953
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 14856.8588 | 0.90042 | 1650000 | 0.067305
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 10101.3188 | 0.45656 | 2212500 | 0.031607
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 6410.1723 | 0.46451 | 1380000 | 0.031607
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511564 MARTHA 4 138 781800 G24-161-TAP 138 1 | Current Study | 20.7 | (395.00, 395.00) | 15509359.5984 | 62.437 | 24840000 | 0.28015
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512110 LAKEP4WT 138 521043 RUSSELL4 138 1 | Current Study | 37.45 | (134.00, 134.00) | 11556068.6674 | 25.7144 | 44940000 | 0.040322
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 11425035.6203 | 1.2154 | 940000000 | 0.020204
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512101 CHILD4WT 138 512110 LAKEP4WT 138 1 | Current Study | 35.14 | (134.00, 134.00) | 10982426.2941 | 26.0445 | 42168000 | 0.038817
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 6908428.5722 | 19.3921 | 35625000 | 0.23794
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511446 CL-AFTP4 138 511458 ELKCTY-4 138 1 | Current Study | 13.67 | (395.00, 395.00) | 6717746.0324 | 40.9519 | 16404000 | 0.32807
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 781680 GEN-2024-157 138 781800 G24-161-TAP 138 1 | Current Study | 6.36 | (211.00, 211.00) | 5288291.8467 | 69.291 | 7632000 | 0.71985
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511564 MARTHA 4 138 529302 OMALTUS4 138 1 | Current Study | 6.37 | (395.00, 395.00) | 4772686.9875 | 62.437 | 7644000 | 0.28015
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 532803 BURNS 7 345 1 | Current Study | 50.03 | (1793.00, 1793.00) | 4132349.4821 | 3.7544 | 110066000 | 0.046099
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532803 BURNS 7 345 1 | Current Study | 45.5 | (1793.00, 1793.00) | 3758183.1189 | 3.7544 | 100100000 | 0.046099
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511440 ALTUSJT4 138 521043 RUSSELL4 138 1 | Current Study | 12.25 | (211.00, 211.00) | 3684012.8002 | 25.0613 | 14700000 | 0.076091
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 521042 RUSSELL2 69 529342 OMMANGM2 69 1 | Current Study | 18.66 | (69.00, 69.00) | 3598317.8656 | 22.6866 | 15861000 | 0.021685
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 529298 OMPVET-4 138 529345 OMPARK-4 138 1 | Current Study | 3.79 | (395.00, 395.00) | 2839636.3709 | 62.437 | 4548000 | 0.28015
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 2790971.8244 | 19.9355 | 14000000 | 0.11897
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511477 S.W.S.-4 138 520814 ANADARK4 138 1 | Current Study | 7.37 | (395.00, 395.00) | 2202890.1478 | 24.9083 | 8844000 | 0.087241
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511440 ALTUSJT4 138 529345 OMPARK-4 138 1 | Current Study | 2.86 | (281.00, 281.00) | 2142839.0556 | 62.437 | 3432000 | 0.28015
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 2048191.5794 | 1.7464 | 117282000 | 0.043234
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 1992562.7945 | 1.3262 | 150244000 | 0.035358
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511435 SNYDER-4 138 765230 G20-012-TAP 138 1 | Current Study | 7.51 | (395.00, 395.00) | 1923830.0016 | 21.3474 | 9012000 | 0.17425
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | Current Study | 11.1 | (395.00, 395.00) | 1894976.5966 | 14.2266 | 13320000 | 0.047298
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2 | Current Study |  | (478.00, 478.00) | 1847528.4638 | 10.2073 | 18100000 | 0.10048
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515802 GRACMNT4 138 521089 WASHITA4 138 1 | Current Study | 5.87 | (265.00, 265.00) | 1775283.4206 | 25.2028 | 7044000 | 0.083081
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 529298 OMPVET-4 138 529302 OMALTUS4 138 1 | Current Study | 2.13 | (395.00, 395.00) | 1595890.6253 | 62.437 | 2556000 | 0.28015
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild 3-winding transformer 521042 RUSSELL2 69 521043 RUSSELL4 138 521175 RSLTERT 13 1 | Current Study |  | (81.00, 81.00) | 1315640.6487 | 24.3637 | 5400000 | 0.035769
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1178877.207 | 0.53998 | 218320000 | 0.019602
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1130924.5966 | 1.1261 | 100427000 | 0.017015
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1003080.2366 | 0.5053 | 198511000 | 0.031777
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 994513.6928 | 1.8032 | 55154000 | 0.037409
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 966387.6445 | 0.67205 | 143796000 | 0.03949
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 945165.0128 | 1.0509 | 89936000 | 0.014442
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 929417.1013 | 0.97342 | 95480000 | 0.046312
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 862039.1807 | 0.43568 | 197860000 | 0.025332
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 850585.3021 | 1.2888 | 66000000 | 0.034849
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 842155.666 | 0.67467 | 124824000 | 0.051928
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 824482.9124 | 0.97342 | 84700000 | 0.046312
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at WELL 4WT 138 kV | Current Study |  |  | 766097.1933 | 31.4942 | 2432500 | 0.026617
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | Current Study | 13.6 | (1793.00, 1793.00) | 644624.0929 | 2.1545 | 29920000 | 0.047861
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511425 TUTCONT4 138 514898 CIMARON4 138 1 | Current Study | 14.65 | (395.00, 395.00) | 635231.4258 | 3.6134 | 17580000 | 0.037143
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 618889.8127 | 0.37494 | 165062000 | 0.027754
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 764550 G20-087-TAP 345 1 | Current Study | 14.38 | (1793.00, 1793.00) | 594753.7076 | 1.88 | 31636000 | 0.075425
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR SVC at ELDORDO2 69 kV | Current Study |  |  | 591432.0811 | 25.7144 | 2300000 | 0.040322
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 590212.7696 | 1.256 | 46992000 | 0.059846
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 571630.5809 | 0.70149 | 81488000 | 0.054798
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 553928.0107 | 0.41666 | 132946000 | 0.01524
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | Current Study | 1 | (395.00, 395.00) | 509969.5831 | 42.4975 | 1200000 | 0.71985
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 476033.6782 | 1.8032 | 26400000 | 0.037409
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511477 S.W.S.-4 138 521089 WASHITA4 138 1 | Current Study | 2.05 | (717.00, 717.00) | 461379.5341 | 18.7553 | 2460000 | 0.14049
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 458359.7937 | 0.4877 | 93984000 | 0.035603
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 6.3 MVAR switched shunt at HOLLIS 4 138 kV | Current Study |  |  | 449695.072 | 18.487 | 2432500 | 0.038817
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | Current Study | 8.91 | (2390.00, 2390.00) | 363695.9968 | 1.8554 | 19602000 | 0.075425
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 357355.7315 | 1.365 | 26180000 | 0.018145
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 328163.8822 | 13.4908 | 2432500 | 0.71985
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 317894.4134 | 0.94628 | 33594000 | 0.045426
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 300882.2591 | 0.56282 | 53460000 | 0.0239
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CHILD4WT 138 kV | Current Study |  |  | 288548.3084 | 11.8622 | 2432500 | 0.71985
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 280227.2425 | 1.1076 | 25300000 | 0.02669
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 122 MVAR switched shunt at HOYT 7 345 kV | Current Study |  |  | 246775.5514 | 4.6561 | 5300000 | 0.040441
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 244564.4911 | 0.53266 | 45914000 | 0.031679
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | Current Study | 5.97 | (2390.00, 2390.00) | 243688.5635 | 1.8554 | 13134000 | 0.075425
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 241133.1892 | 0.93921 | 25674000 | 0.03879
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 138 MVAR switched shunt at GEN-2024-016 345 kV | Current Study |  |  | 233600.4762 | 4.4076 | 5300000 | 0.032463
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 213920.3647 | 1.7364 | 12320000 | 0.043832
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 201351.8469 | 1.6779 | 12000000 | 0.043833
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 201351.8469 | 1.6779 | 12000000 | 0.043833
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at SHARNSP3 115 kV | Current Study |  |  | 192405.6509 | 8.6963 | 2212500 | 0.030335
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 8 MVAR switched shunt at RANSOM 3 115 kV | Current Study |  |  | 192405.6509 | 8.6963 | 2212500 | 0.030335
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 0.06 MVAR switched shunt at G24-125-TAP 345 kV | Current Study |  |  | 191725.5525 | 3.6175 | 5300000 | 0.030396
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 179516.8802 | 1.496 | 12000000 | 0.043833
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 171340.6968 | 0.95678 | 17908000 | 0.04017
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at GRANTTP3 115 kV | Current Study |  |  | 170819.6231 | 7.7207 | 2212500 | 0.050651
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at PNTPR-GOAB3 115 kV | Current Study |  |  | 170819.6231 | 7.7207 | 2212500 | 0.050651
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 167487.9567 | 1.1127 | 15053000 | 0.017313
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 153377.6706 | 1.2781 | 12000000 | 0.035436
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 25 MVAR switched shunt at HIGHPT 3 115 kV | Current Study |  |  | 151789.0016 | 6.8605 | 2212500 | 0.030335
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 145492.5522 | 2.7451 | 5300000 | 0.031679
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 143025.4867 | 1.1919 | 12000000 | 0.071343
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 136405.2997 | 1.1367 | 12000000 | 0.043833
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 136405.2997 | 1.1367 | 12000000 | 0.043833
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 134753.3652 | 1.1229 | 12000000 | 0.046312
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 133473.3854 | 0.53266 | 25058000 | 0.031679
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 132325.0108 | 1.1027 | 12000000 | 0.035436
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 130744.9134 | 1.0895 | 12000000 | 0.043234
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 129364.5064 | 1.078 | 12000000 | 0.043833
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 128100.7623 | 2.417 | 5300000 | 0.037755
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 128084.3526 | 2.4167 | 5300000 | 0.035436
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 127167.4368 | 1.0597 | 12000000 | 0.043833
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 121233.4675 | 1.0103 | 12000000 | 0.043833
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 120850.0266 | 1.0071 | 12000000 | 0.040093
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 116153.5562 | 0.96795 | 12000000 | 0.054798
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 109089.7911 | 0.90908 | 12000000 | 0.014442
GEN-2024-161 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 106230.2742 | 0.58691 | 18100000 | 0.010578
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511501 TUTTLE4 138 511575 LEONARD4 138 1 | Current Study | 2.12 | (395.00, 395.00) | 100188.0674 | 3.9382 | 2544000 | 0.037143
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 96609.7799 | 0.80508 | 12000000 | 0.040093
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 83569.7758 | 0.69641 | 12000000 | 0.027935
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 77492.366 | 1.4621 | 5300000 | 0.043234
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 75105.6185 | 0.50278 | 14938000 | 0.063002
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 74353.2804 | 1.4029 | 5300000 | 0.043234
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 72707.1114 | 0.50278 | 14460953.1406 | 0.063002
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 71561.7184 | 1.3502 | 5300000 | 0.048865
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 67024.7882 | 1.2646 | 5300000 | 0.071343
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 64660.336 | 0.53884 | 12000000 | 0.027935
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 63620.3091 | 0.96394 | 6600000 | 0.046312
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 62419.9403 | 1.1777 | 5300000 | 0.040093
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 62174.2483 | 0.38398 | 16192000 | 0.050651
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 61937.5203 | 0.5312 | 11660000 | 0.035603
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 50578.1694 | 0.76634 | 6600000 | 0.035603
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | Current Study | 1.06 | (395.00, 395.00) | 50094.0337 | 3.9382 | 1272000 | 0.037143
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 48136.3841 | 0.90823 | 5300000 | 0.030396
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 47566.8273 | 0.72071 | 6600000 | 0.027935
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 47566.8273 | 0.72071 | 6600000 | 0.027935
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 46586.7773 | 0.879 | 5300000 | 0.048865
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 46578.9525 | 0.87885 | 5300000 | 0.035436
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 45753.7583 | 0.86328 | 5300000 | 0.035436
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 45202.5487 | 0.68489 | 6600000 | 0.027935
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 43293.1261 | 1.7798 | 2432500 | 0.043234
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 43150.8354 | 0.81417 | 5300000 | 0.035436
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 39733.8808 | 0.7497 | 5300000 | 0.027935
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 39669.4732 | 1.8032 | 2200000 | 0.037409
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 37302.7734 | 1.256 | 2970000 | 0.059846
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 36679.9745 | 0.69207 | 5300000 | 0.043833
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 34264.2249 | 0.97342 | 3520000 | 0.046312
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 31636.0246 | 0.97342 | 3250000 | 0.046312
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 30743.8828 | 0.58007 | 5300000 | 0.09773
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 29472.6813 | 0.90685 | 3250000 | 0.027935
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 28360.5226 | 0.87263 | 3250000 | 0.046312
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 27631.684 | 1.256 | 2200000 | 0.059846
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 25978.8601 | 0.49017 | 5300000 | 0.050651
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 25241.2107 | 0.77665 | 3250000 | 0.027935
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 25018.5533 | 0.7698 | 3250000 | 0.027935
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 25017.0041 | 0.76975 | 3250000 | 0.027935
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 24365.1156 | 0.7497 | 3250000 | 0.027935
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 23168.0733 | 0.43713 | 5300000 | 0.0038228
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 23052.2406 | 1.7464 | 1320000 | 0.043234
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 22844.0335 | 0.70289 | 3250000 | 0.027935
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 22240.8247 | 0.18534 | 12000000 | 0.030335
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 21712.1822 | 0.66807 | 3250000 | 0.035603
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 20960.0795 | 0.64493 | 3250000 | 0.027935
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 16600.4565 | 0.72176 | 2300000 | 0.059846
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 16334.8476 | 0.67153 | 2432500 | 0.035603
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 16108.3956 | 0.66222 | 2432500 | 0.035603
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 15481.7859 | 1.1219 | 1380000 | 0.0461
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at SEGNTP 3 115 kV | Current Study |  |  | 11447.5004 | 0.5174 | 2212500 | 0.050651
GEN-2024-161 | 04 SOUTHEAST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 10679.0673 | 0.77385 | 1380000 | 0.057628
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 10649.388 | 0.77169 | 1380000 | 0.035603
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 8980.4833 | 0.65076 | 1380000 | 0.037297
GEN-2024-161 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 8807.7873 | 0.16618 | 5300000 | 0.033382
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 6335.6911 | 0.38398 | 1650000 | 0.050651
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 5493.7107 | 0.2483 | 2212500 | 0.030335
GEN-2024-161 | 04 SOUTHEAST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 4247.3762 | 0.30778 | 1380000 | 0.032082
GEN-2024-162 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | Current Study | 23.61 | (386.00, 386.00) | 32307568.7723 | 72.0203 | 44859000 | 0.60927
GEN-2024-162 | 02 NEBRASKA | TBD | NRIS | Rebuild line 640080 BELDEN 7 115 640212 HARTGTN7 115 1 | Current Study | 12.27 | (176.00, 176.00) | 12270000 | 100 | 12270000 | 0.033362
GEN-2024-162 | 02 NEBRASKA | TBD | NRIS | Add 5 MVAR switched shunt at MOORHED7 115 kV | Current Study |  |  | 2212500 | 100 | 2212500 | 0.030817
GEN-2024-162 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659202 LO.KVA2_-BE9 13 M2 | Current Study |  | (500.00, 617.00) | 200014.3046 | 0.80006 | 25000000 | 0.008006
GEN-2024-162 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659201 LO.KU1A_-BE9 13 M2 | Current Study |  | (600.00, 637.40) | 197265.4706 | 0.78906 | 25000000 | 0.0090769
GEN-2024-162 | 02 NEBRASKA | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 2261.572 | 0.16388 | 1380000 | 0.046738
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515117 ARBUCKL4 138 515531 VANOSTP4 138 1 | Current Study | 18.2 | (472.00, 472.00) | 5258576.6009 | 24.0777 | 21840000 | 0.23861
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515044 SEMINOL4 138 515531 VANOSTP4 138 1 | Current Study | 21.55 | (395.00, 395.00) | 5219260.1152 | 20.1828 | 25860000 | 0.16812
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515097 WLNUTCK4 138 515100 PAOLI- 4 138 1 | Current Study | 15.55 | (265.00, 265.00) | 4020879.5249 | 21.5481 | 18660000 | 0.08072
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515133 BLUERIV4 138 515178 PARKLN 4 138 1 | Current Study | 12.7 | (395.00, 395.00) | 3988656.3174 | 26.1723 | 15240000 | 0.17513
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 1 | Current Study |  | (1868.00, 1868.00) | 3296851.0303 | 5.3607 | 61500000 | 0.13122
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 2 | Current Study |  | (1868.00, 1868.00) | 3296851.0303 | 5.3607 | 61500000 | 0.13122
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515117 ARBUCKL4 138 515133 BLUERIV4 138 1 | Current Study | 10.35 | (395.00, 395.00) | 3250597.865 | 26.1723 | 12420000 | 0.17513
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515178 PARKLN 4 138 515977 LKKONWA4 138 1 | Current Study | 13.56 | (472.00, 472.00) | 2461247.9286 | 15.1257 | 16272000 | 0.18388
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 2170692.6725 | 1.8508 | 117282000 | 0.039143
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 2103297.5989 | 1.3999 | 150244000 | 0.031884
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1270354.6619 | 1.265 | 100427000 | 0.016327
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1262207.056 | 0.57815 | 218320000 | 0.017929
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 1245056.1166 | 1.3844 | 89936000 | 0.016252
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 1194539.5933 | 2.147 | 55638000 | 0.048666
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1193138.7842 | 1.2496 | 95480000 | 0.050789
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 1094891.2631 | 1.6589 | 66000000 | 0.038322
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 1058429.5666 | 1.2496 | 84700000 | 0.050789
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1043430.2775 | 0.72563 | 143796000 | 0.036425
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 1023093.4844 | 1.6175 | 63250000 | 0.088273
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 1008603.9268 | 1.8287 | 55154000 | 0.03241
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 885643.0263 | 0.44614 | 198511000 | 0.023968
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 882197.1892 | 1.9676 | 44836000 | 0.046425
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 799016.8297 | 0.70839 | 112794000 | 0.06064
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 785785.7365 | 0.62951 | 124824000 | 0.041391
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 784930.3332 | 0.39671 | 197860000 | 0.019705
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 742382.1877 | 1.5798 | 46992000 | 0.064305
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 764550 G20-087-TAP 345 1 | Current Study | 14.38 | (1793.00, 1793.00) | 708050.9714 | 2.2381 | 31636000 | 0.076708
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 626428.8538 | 0.66653 | 93984000 | 0.041567
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 776060 G23-204-TAP 345 1 | Current Study | 17.82 | (1793.00, 1793.00) | 568620.0306 | 1.4504 | 39204000 | 0.054911
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 566135.0354 | 0.34298 | 165062000 | 0.021688
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | Current Study | 13.6 | (1793.00, 1793.00) | 560473.1319 | 1.8732 | 29920000 | 0.035549
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520400 NOBLE4 138 520975 LIDDELL4 138 1 | Current Study | 5.73 | (265.00, 265.00) | 549794.5046 | 7.9958 | 6876000 | 0.025772
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 531359.745 | 0.39968 | 132946000 | 0.012489
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 521907.1061 | 0.64047 | 81488000 | 0.04274
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 508502.8679 | 1.5137 | 33594000 | 0.062074
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 496928.0929 | 1.9355 | 25674000 | 0.068289
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 482778.1062 | 1.8287 | 26400000 | 0.03241
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | Current Study | 8.91 | (2390.00, 2390.00) | 432978.0555 | 2.2088 | 19602000 | 0.076708
GEN-2024-164 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 515055 MAUD 4 138 787770 G24-360-TAP 138 1 | Current Study | 5.11 | (395.00, 395.00) | 431928.5678 | 7.0438 | 6132000 | 0.030204
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 413691.2862 | 1.5802 | 26180000 | 0.017945
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 412535.8892 | 0.8985 | 45914000 | 0.04565
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 352832.9727 | 1.9703 | 17908000 | 0.070665
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 341219.1528 | 1.3487 | 25300000 | 0.027764
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | Current Study | 7.74 | (1793.00, 1793.00) | 331891.7602 | 1.9491 | 17028000 | 0.054911
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | Current Study | 5.97 | (2390.00, 2390.00) | 290109.8756 | 2.2088 | 13134000 | 0.076708
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 273999.2979 | 0.51253 | 53460000 | 0.018593
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 245420.5827 | 4.6306 | 5300000 | 0.04565
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR SVC at JAY 4 138 kV | Current Study |  |  | 242582.6261 | 4.577 | 5300000 | 0.025592
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 227038.1524 | 1.8428 | 12320000 | 0.039741
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 225145.3655 | 0.8985 | 25058000 | 0.04565
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | Current Study | 6.93 | (1793.00, 1793.00) | 221130.0119 | 1.4504 | 15246000 | 0.054911
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 213699.0604 | 1.7808 | 12000000 | 0.039741
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 213699.0604 | 1.7808 | 12000000 | 0.039741
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514948 CEDARLN4 138 766111 G21-088-TAP 138 1 | Current Study | 2.86 | (395.00, 395.00) | 196813.1434 | 5.7346 | 3432000 | 0.049397
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 190525.139 | 1.5877 | 12000000 | 0.039741
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 187994.6122 | 1.2489 | 15053000 | 0.016601
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 172989.4897 | 1.4416 | 12000000 | 0.050789
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 171712.2448 | 1.4309 | 12000000 | 0.048666
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 152139.6286 | 1.2678 | 12000000 | 0.030028
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 150267.7275 | 1.2522 | 12000000 | 0.064033
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 144769.8882 | 1.2064 | 12000000 | 0.039741
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 144769.8882 | 1.2064 | 12000000 | 0.039741
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 143702.7342 | 1.1975 | 12000000 | 0.016252
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 138564.7787 | 1.1547 | 12000000 | 0.039143
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 137297.3424 | 1.1441 | 12000000 | 0.039741
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 137269.992 | 1.1439 | 12000000 | 0.048666
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at CENTRTN5 161 kV | Current Study |  |  | 136336.3057 | 4.195 | 3250000 | 0.026975
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 134965.545 | 1.1247 | 12000000 | 0.039741
GEN-2024-164 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 132099.8471 | 0.72983 | 18100000 | 0.011237
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 131256.9027 | 1.0938 | 12000000 | 0.030028
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 129438.3117 | 1.0787 | 12000000 | 0.036962
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 128667.6953 | 1.0722 | 12000000 | 0.039741
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 127050.4745 | 2.3972 | 5300000 | 0.030028
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 126021.454 | 1.0502 | 12000000 | 0.050789
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 119468.0956 | 2.2541 | 5300000 | 0.03008
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 104632.9691 | 1.5853 | 6600000 | 0.033127
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 100150.1398 | 0.83458 | 12000000 | 0.036962
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 88690.6554 | 1.6734 | 5300000 | 0.048666
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 84648.4583 | 0.72597 | 11660000 | 0.041567
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 82127.1915 | 1.5496 | 5300000 | 0.039143
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 81672.5043 | 1.2375 | 6600000 | 0.050789
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 78800.3569 | 1.4868 | 5300000 | 0.039143
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 73674.6002 | 1.1163 | 6600000 | 0.036962
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 73674.6002 | 1.1163 | 6600000 | 0.036962
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 71258.1275 | 1.3445 | 5300000 | 0.041567
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 70418.6564 | 1.3287 | 5300000 | 0.064033
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 70012.6515 | 1.0608 | 6600000 | 0.036962
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 69123.7471 | 1.0473 | 6600000 | 0.041567
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 65993.2573 | 0.44178 | 14938000 | 0.047291
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 63885.7545 | 0.44178 | 14460953.1406 | 0.047291
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 62803.9883 | 1.9324 | 3250000 | 0.036962
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 62803.9883 | 1.9324 | 3250000 | 0.036962
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 61542.4225 | 1.1612 | 5300000 | 0.036962
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 56214.398 | 0.34717 | 16192000 | 0.039122
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 52395.8444 | 1.6122 | 3250000 | 0.033127
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 52395.8444 | 1.6122 | 3250000 | 0.033127
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 51048.4852 | 1.5707 | 3250000 | 0.036962
GEN-2024-164 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 50343.0138 | 0.94987 | 5300000 | 0.163
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 48921.0358 | 0.92304 | 5300000 | 0.026389
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 46920.2225 | 1.5798 | 2970000 | 0.064305
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 46389.1392 | 0.87527 | 5300000 | 0.041567
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 46202.974 | 0.87175 | 5300000 | 0.030028
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 45882.4919 | 1.8862 | 2432500 | 0.039143
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 45649.2084 | 1.4046 | 3250000 | 0.036962
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 45384.4407 | 0.85631 | 5300000 | 0.030028
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 43986.6833 | 1.2496 | 3520000 | 0.050789
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 42802.5282 | 0.80759 | 5300000 | 0.030028
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 40717.7673 | 0.76826 | 5300000 | 0.041567
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 40612.713 | 1.2496 | 3250000 | 0.050789
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 40231.5088 | 1.8287 | 2200000 | 0.03241
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 39095.2312 | 1.2029 | 3250000 | 0.036962
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 38750.3648 | 1.1923 | 3250000 | 0.036962
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 38747.9653 | 1.1922 | 3250000 | 0.036962
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 37738.278 | 1.1612 | 3250000 | 0.036962
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 36407.7908 | 1.1202 | 3250000 | 0.050789
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CHILD4WT 138 kV | Current Study |  |  | 35993.0392 | 1.4797 | 2432500 | 0.076708
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 35382.3269 | 1.0887 | 3250000 | 0.036962
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 34755.7204 | 1.5798 | 2200000 | 0.064305
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 34462.315 | 1.0604 | 3250000 | 0.036962
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 32464.3363 | 0.9989 | 3250000 | 0.036962
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 31568.3998 | 0.59563 | 5300000 | 0.0044498
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 29673.4225 | 0.91303 | 3250000 | 0.041567
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 25806.4278 | 1.0609 | 2432500 | 0.048359
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 24430.9811 | 1.8508 | 1320000 | 0.039143
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 24270.4232 | 1.7587 | 1380000 | 0.086109
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 23488.6113 | 0.44318 | 5300000 | 0.039122
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 22324.3721 | 0.91775 | 2432500 | 0.041567
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 22014.8865 | 0.90503 | 2432500 | 0.041567
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 21419.0669 | 1.5521 | 1380000 | 0.036962
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 21272.0971 | 0.17727 | 12000000 | 0.024786
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 20880.3911 | 0.90784 | 2300000 | 0.064306
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514947 CANADN-4 138 766111 G21-088-TAP 138 1 | Current Study | 0.3 | (395.00, 395.00) | 20644.7353 | 5.7346 | 360000 | 0.049397
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 19883.9734 | 1.4409 | 1380000 | 0.033127
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 17621.6351 | 1.2769 | 1380000 | 0.036962
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520400 NOBLE4 138 520842 CANADNS4 138 1 | Current Study | 0.18 | (265.00, 265.00) | 17271.0316 | 7.9958 | 216000 | 0.025772
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 15065.2287 | 1.0917 | 1380000 | 0.038322
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 14634.3834 | 0.27612 | 5300000 | 0.039741
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 14554.216 | 1.0547 | 1380000 | 0.041567
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 9307.8736 | 0.42069 | 2212500 | 0.021367
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 9024.4294 | 0.40788 | 2212500 | 0.021367
GEN-2024-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 5728.3694 | 0.34717 | 1650000 | 0.039122
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 8676759.8707 | 7.6926 | 112794000 | 0.26209
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1 | Current Study | 56.1 | (1793.00, 1793.00) | 7230218.2787 | 5.8582 | 123420000 | 0.033609
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 1 | Current Study |  | (1868.00, 1868.00) | 6637292.4118 | 10.7923 | 61500000 | 0.10514
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 2 | Current Study |  | (1868.00, 1868.00) | 6637292.4118 | 10.7923 | 61500000 | 0.10514
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 5264653.1627 | 4.4889 | 117282000 | 0.037784
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505600 TUPELO 4 138 505602 S BROWN4 138 1 | Current Study | 36.9 | (281.00, 281.00) | 5219724.8454 | 11.788 | 44280000 | 0.030478
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 5205566.883 | 8.2301 | 63250000 | 0.17876
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 5117627.6465 | 3.4062 | 150244000 | 0.030876
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1 | Current Study | 30.63 | (1793.00, 1793.00) | 3459239.1029 | 5.1335 | 67386000 | 0.033621
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 3124941.8735 | 3.4746 | 89936000 | 0.016234
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 3068607.9653 | 1.4056 | 218320000 | 0.017348
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 3052559.2419 | 3.0396 | 100427000 | 0.015615
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 2995604.1173 | 3.1374 | 95480000 | 0.050752
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 2884838.5957 | 5.185 | 55638000 | 0.046777
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | Current Study | 13.16 | (395.00, 395.00) | 2837447.821 | 17.9676 | 15792000 | 0.070981
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 2744558.3057 | 4.1584 | 66000000 | 0.038232
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515044 SEMINOL4 138 515531 VANOSTP4 138 1 | Current Study | 21.55 | (395.00, 395.00) | 2742754.646 | 10.6062 | 25860000 | 0.035163
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 2657390.7492 | 3.1374 | 84700000 | 0.050752
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 2547311.9684 | 1.7715 | 143796000 | 0.035392
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515117 ARBUCKL4 138 515531 VANOSTP4 138 1 | Current Study | 18.2 | (472.00, 472.00) | 2535575.3387 | 11.6098 | 21840000 | 0.045792
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 2428812.0967 | 4.4037 | 55154000 | 0.031063
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 764550 G20-087-TAP 345 1 | Current Study | 14.38 | (1793.00, 1793.00) | 2379798.0973 | 7.5224 | 31636000 | 0.10261
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 2125105.3301 | 1.0705 | 198511000 | 0.02289
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 2081410.7663 | 4.6423 | 44836000 | 0.043594
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 776060 G23-204-TAP 345 1 | Current Study | 17.82 | (1793.00, 1793.00) | 2076583.5537 | 5.2969 | 39204000 | 0.079812
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 1909321.3208 | 0.96499 | 197860000 | 0.019077
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1864856.6869 | 1.494 | 124824000 | 0.039096
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515133 BLUERIV4 138 515178 PARKLN 4 138 1 | Current Study | 12.7 | (395.00, 395.00) | 1837163.6806 | 12.0549 | 15240000 | 0.032104
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 1816763.7471 | 7.0763 | 25674000 | 0.099367
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 1684740.5472 | 3.5852 | 46992000 | 0.058081
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | Current Study | 13.6 | (1793.00, 1793.00) | 1608083.6885 | 5.3746 | 29920000 | 0.040594
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1594806.3159 | 1.6969 | 93984000 | 0.042118
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515117 ARBUCKL4 138 515133 BLUERIV4 138 1 | Current Study | 10.35 | (395.00, 395.00) | 1497216.0704 | 12.0549 | 12420000 | 0.032104
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515178 PARKLN 4 138 515977 LKKONWA4 138 1 | Current Study | 13.56 | (472.00, 472.00) | 1464358.1591 | 8.9993 | 16272000 | 0.043543
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | Current Study | 8.91 | (2390.00, 2390.00) | 1455262.9603 | 7.4241 | 19602000 | 0.10261
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 1378052.9266 | 0.83487 | 165062000 | 0.021012
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 | Current Study | 6.08 | (395.00, 395.00) | 1310918.1422 | 17.9676 | 7296000 | 0.070981
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 1309862.6173 | 3.8991 | 33594000 | 0.063639
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 1294145.4888 | 7.2266 | 17908000 | 0.10316
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 1291674.7411 | 0.97158 | 132946000 | 0.012083
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 1240596.5839 | 1.5224 | 81488000 | 0.040435
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | Current Study | 7.74 | (1793.00, 1793.00) | 1212058.9034 | 7.118 | 17028000 | 0.079812
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 1162574.5975 | 4.4037 | 26400000 | 0.031063
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 1013731.1674 | 3.8722 | 26180000 | 0.017501
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | Current Study | 5.97 | (2390.00, 2390.00) | 975075.1822 | 7.4241 | 13134000 | 0.10261
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 971588.2029 | 2.1161 | 45914000 | 0.04279
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 853424.6135 | 3.3732 | 25300000 | 0.027637
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | Current Study | 6.93 | (1793.00, 1793.00) | 807560.2709 | 5.2969 | 15246000 | 0.079812
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1 | Current Study | 11.3 | (1793.00, 1793.00) | 686631.7716 | 2.762 | 24860000 | 0.034077
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 673174.6421 | 5.6098 | 12000000 | 0.033376
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 638722.1445 | 1.1948 | 53460000 | 0.01725
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 578004.8107 | 10.9058 | 5300000 | 0.04279
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 550941.2228 | 4.4719 | 12320000 | 0.038382
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 530253.4562 | 2.1161 | 25058000 | 0.04279
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 518571.9501 | 4.3214 | 12000000 | 0.038382
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 518571.9501 | 4.3214 | 12000000 | 0.038382
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 462337.0486 | 3.8528 | 12000000 | 0.038382
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 452724.1523 | 3.0075 | 15053000 | 0.015911
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 434323.2917 | 3.6194 | 12000000 | 0.050752
GEN-2024-165 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 429545.7618 | 8.1046 | 5300000 | 0.55352
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 414688.4973 | 3.4557 | 12000000 | 0.046776
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 369794.8362 | 3.0816 | 12000000 | 0.029049
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 366023.74 | 3.0502 | 12000000 | 0.062077
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 360676.5447 | 3.0056 | 12000000 | 0.016234
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 351305.2566 | 2.9275 | 12000000 | 0.038382
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 351305.2566 | 2.9275 | 12000000 | 0.038382
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 336065.7562 | 2.8005 | 12000000 | 0.037784
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 333172.0339 | 2.7764 | 12000000 | 0.038382
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 331509.7696 | 2.7626 | 12000000 | 0.046776
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 327513.5873 | 2.7293 | 12000000 | 0.038382
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 325859.5482 | 2.7155 | 12000000 | 0.037034
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 319036.6987 | 2.6586 | 12000000 | 0.029049
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 316401.03 | 2.6367 | 12000000 | 0.050752
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 312230.9362 | 2.6019 | 12000000 | 0.038382
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 308812.4366 | 5.8266 | 5300000 | 0.029049
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 288796.4655 | 5.449 | 5300000 | 0.02894
GEN-2024-165 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 286623.699 | 1.5836 | 18100000 | 0.0097042
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 284986.3657 | 4.318 | 6600000 | 0.035911
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 271193.4608 | 5.1169 | 5300000 | 0.033376
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 252126.8925 | 2.1011 | 12000000 | 0.037034
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 215503.9555 | 1.8482 | 11660000 | 0.042118
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 214189.7024 | 4.0413 | 5300000 | 0.046776
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 205054.4861 | 3.1069 | 6600000 | 0.050752
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 199185.8032 | 3.7582 | 5300000 | 0.037784
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 191117.1208 | 3.606 | 5300000 | 0.037784
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 185606.5881 | 13.4498 | 1380000 | 0.26209
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 185475.0083 | 2.8102 | 6600000 | 0.037034
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 185475.0083 | 2.8102 | 6600000 | 0.037034
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 181413.8647 | 3.4229 | 5300000 | 0.042118
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 176256.0922 | 2.6705 | 6600000 | 0.037034
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 175980.0116 | 2.6664 | 6600000 | 0.042118
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 171526.5175 | 3.2363 | 5300000 | 0.062077
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 158516.2432 | 1.0612 | 14938000 | 0.04521
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 158108.3604 | 4.8649 | 3250000 | 0.037034
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 158108.3604 | 4.8649 | 3250000 | 0.037034
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 154932.3823 | 2.9233 | 5300000 | 0.037034
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 153454.0075 | 1.0612 | 14460953.1406 | 0.04521
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 142709.3333 | 4.3911 | 3250000 | 0.035911
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 142709.3333 | 4.3911 | 3250000 | 0.035911
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 136833.1485 | 0.84507 | 16192000 | 0.037901
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 128514.0087 | 3.9543 | 3250000 | 0.037034
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CHILD4WT 138 kV | Current Study |  |  | 120974.5787 | 4.9733 | 2432500 | 0.10261
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 | Current Study | 0.55 | (395.00, 395.00) | 118586.3451 | 17.9676 | 660000 | 0.070981
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 118100.6759 | 2.2283 | 5300000 | 0.042118
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 116843.3536 | 2.2046 | 5300000 | 0.025085
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 114921.3878 | 3.536 | 3250000 | 0.037034
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 112302.2409 | 2.1189 | 5300000 | 0.029049
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 111280.3303 | 4.5747 | 2432500 | 0.037784
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 110437.0182 | 3.1374 | 3520000 | 0.050752
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 110312.6908 | 2.0814 | 5300000 | 0.029049
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 106479.3885 | 3.5852 | 2970000 | 0.058081
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 104037.022 | 1.963 | 5300000 | 0.029049
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 103662.1054 | 1.9559 | 5300000 | 0.042118
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 101966.0052 | 3.1374 | 3250000 | 0.050752
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 98421.8211 | 3.0284 | 3250000 | 0.037034
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 97553.6239 | 3.0016 | 3250000 | 0.037034
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 97547.583 | 3.0015 | 3250000 | 0.037034
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 96881.2165 | 4.4037 | 2200000 | 0.031063
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 95005.7061 | 2.9233 | 3250000 | 0.037034
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 91408.7415 | 2.8126 | 3250000 | 0.050752
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 89074.6249 | 2.7408 | 3250000 | 0.037034
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 86758.5048 | 2.6695 | 3250000 | 0.037034
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 81728.6152 | 2.5147 | 3250000 | 0.037034
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 79718.3732 | 3.2772 | 2432500 | 0.059455
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 78873.6211 | 3.5852 | 2200000 | 0.058081
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 78124.0491 | 1.474 | 5300000 | 0.0043829
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 77415.0838 | 5.6098 | 1380000 | 0.033376
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 75544.6493 | 2.3245 | 3250000 | 0.042118
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 74985.9319 | 3.2603 | 2300000 | 0.091912
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 59253.2714 | 4.4889 | 1320000 | 0.037784
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 57174.3306 | 1.0788 | 5300000 | 0.037901
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 56834.929 | 2.3365 | 2432500 | 0.042118
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 56047.0193 | 2.3041 | 2432500 | 0.042118
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 54157.5122 | 3.9245 | 1380000 | 0.035911
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 53922.269 | 3.9074 | 1380000 | 0.037034
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 51728.1449 | 0.43107 | 12000000 | 0.023989
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 44362.2755 | 3.2147 | 1380000 | 0.037034
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 37763.9213 | 2.7365 | 1380000 | 0.038233
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 37053.1288 | 2.685 | 1380000 | 0.042118
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 35512.4666 | 0.67005 | 5300000 | 0.038382
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 25171.6587 | 1.1377 | 2212500 | 0.022998
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 24405.129 | 1.1031 | 2212500 | 0.022998
GEN-2024-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 13943.5953 | 0.84507 | 1650000 | 0.037901
GEN-2024-166 | 03 CENTRAL | TBD | NRIS | Rebuild line 533044 GILL E 4 138 533051 INTERST4 138 1 | Current Study | 6.25 | (211.00, 211.00) | 7500000 | 100 | 7500000 | 0.1819
GEN-2024-166 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 6553458.6589 | 0.69837 | 938400000 | 0.043083
GEN-2024-166 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 5547412.8076 | 0.59116 | 938400000 | 0.064542
GEN-2024-166 | 03 CENTRAL | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 3044110.9578 | 1.3943 | 218320000 | 0.031291
GEN-2024-166 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Current Study | 26.47 | (1793.00, 1793.00) | 1427392.4401 | 2.4511 | 58234000 | 0.030522
GEN-2024-166 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 1074327.3711 | 2.3399 | 45914000 | 0.086027
GEN-2024-166 | 03 CENTRAL | TBD | ERIS | Rebuild line 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 | Current Study | 9.08 | (395.00, 395.00) | 995090.4487 | 9.1326 | 10896000 | 0.035876
GEN-2024-166 | 03 CENTRAL | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 899148.9694 | 1.6819 | 53460000 | 0.044153
GEN-2024-166 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 586324.3295 | 2.3399 | 25058000 | 0.086027
GEN-2024-166 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 473751.9552 | 0.23865 | 198511000 | 0.0058668
GEN-2024-166 | 03 CENTRAL | TBD | ERIS | Rebuild line 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Current Study | 3.89 | (395.00, 395.00) | 426310.7759 | 9.1326 | 4668000 | 0.035876
GEN-2024-166 | 03 CENTRAL | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 408604.8271 | 2.1968 | 18600000 | 0.16011
GEN-2024-166 | 03 CENTRAL | TBD | ERIS | Rebuild line 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 | Current Study | 3.49 | (395.00, 395.00) | 382474.1923 | 9.1326 | 4188000 | 0.035876
GEN-2024-166 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 227739.6872 | 1.2244 | 18600000 | 0.15618
GEN-2024-166 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 227739.6872 | 1.2244 | 18600000 | 0.15618
GEN-2024-166 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 193057.5299 | 3.6426 | 5300000 | 0.11265
GEN-2024-166 | 03 CENTRAL | TBD | ERIS | Rebuild line 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Current Study | 1.46 | (395.00, 395.00) | 160003.5303 | 9.1326 | 1752000 | 0.035876
GEN-2024-166 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 85729.2417 | 0.46091 | 18600000 | 0.064542
GEN-2024-166 | 03 CENTRAL | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 82934.8875 | 0.44589 | 18600000 | 0.043083
GEN-2024-166 | 03 CENTRAL | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 64865.5224 | 1.2239 | 5300000 | 0.031056
GEN-2024-166 | 03 CENTRAL | TBD | ERIS | Rebuild line 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Current Study | 0.58 | (395.00, 395.00) | 63563.0463 | 9.1326 | 696000 | 0.035876
GEN-2024-166 | 03 CENTRAL | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 58633.8663 | 2.6501 | 2212500 | 0.061956
GEN-2024-166 | 03 CENTRAL | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 37640.4807 | 0.7102 | 5300000 | 0.017702
GEN-2024-166 | 03 CENTRAL | TBD | ERIS | Add 248 MVAR switched shunt at GEN-2022-015 345 kV | Current Study |  |  | 35082.2396 | 0.66193 | 5300000 | 0.034432
GEN-2024-166 | 03 CENTRAL | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 28567.611 | 0.53901 | 5300000 | 0.034432
GEN-2024-166 | 03 CENTRAL | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 22002.6832 | 0.18336 | 12000000 | 0.018552
GEN-2024-166 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 7231.132 | 0.43825 | 1650000 | 0.019322
GEN-2024-167 | 03 CENTRAL | TBD | ERIS | Rebuild line 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | Current Study | 17.54 | (1793.00, 1793.00) | 1918658.2996 | 4.9722 | 38588000 | 0.024011
GEN-2024-167 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 1879976.8875 | 0.20034 | 938400000 | 0.030226
GEN-2024-167 | 03 CENTRAL | TBD | ERIS | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | Current Study | 6.07 | (364.00, 364.00) | 1512088.3929 | 16.6072 | 9105000 | 0.13409
GEN-2024-167 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 1141891.3373 | 0.57523 | 198511000 | 0.019541
GEN-2024-167 | 03 CENTRAL | TBD | ERIS | Rebuild line 645458 S3458 3 345 778170 G24-040-TAP 345 1 | Current Study | 13.15 | (1793.00, 1793.00) | 963808.6139 | 3.3315 | 28930000 | 0.05192
GEN-2024-167 | 03 CENTRAL | TBD | ERIS | Rebuild line 640139 COOPER 3 345 778170 G24-040-TAP 345 1 | Current Study | 12.59 | (1793.00, 1793.00) | 922764.2927 | 3.3315 | 27698000 | 0.05192
GEN-2024-167 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 783954.5841 | 0.83414 | 93984000 | 0.052019
GEN-2024-167 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 588741.675 | 0.40943 | 143796000 | 0.020552
GEN-2024-167 | 03 CENTRAL | TBD | ERIS | Rebuild line 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 | Current Study | 3.23 | (1793.00, 1793.00) | 236075.5345 | 3.3222 | 7106000 | 0.037636
GEN-2024-167 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 221240.0095 | 0.48186 | 45914000 | 0.024482
GEN-2024-167 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 120743.8289 | 0.48186 | 25058000 | 0.024482
GEN-2024-167 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 105934.6907 | 0.90853 | 11660000 | 0.052019
GEN-2024-167 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 49568.4276 | 0.2665 | 18600000 | 0.046975
GEN-2024-167 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 49568.4276 | 0.2665 | 18600000 | 0.046975
GEN-2024-167 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 29221.6508 | 0.19562 | 14938000 | 0.02094
GEN-2024-167 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 29053.0016 | 0.1562 | 18600000 | 0.030226
GEN-2024-167 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 28288.4538 | 0.19562 | 14460953.1406 | 0.02094
GEN-2024-167 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 9381.7635 | 0.56859 | 1650000 | 0.034642
GEN-2024-168 | 02 NEBRASKA | TBD | NRIS | Add 13 MVAR switched shunt at HASTING4 230 kV | Current Study |  |  | 3825000 | 100 | 3825000 | 0.049345
GEN-2024-168 | 02 NEBRASKA | TBD | NRIS | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | Current Study | 17.69 | (160.00, 160.00) | 1518336.5981 | 5.722 | 26535000 | 0.024601
GEN-2024-168 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2 | Current Study |  | (110.00, 120.00) | 686641.7629 | 5.722 | 12000000 | 0.0123
GEN-2024-168 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1 | Current Study | 5.46 | (217.00, 217.00) | 224009.8774 | 4.1027 | 5460000 | 0.034262
GEN-2024-168 | 02 NEBRASKA | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 4795.2732 | 0.34748 | 1380000 | 0.055509
GEN-2024-170 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 2700095.2601 | 0.28773 | 938400000 | 0.030854
GEN-2024-170 | 03 CENTRAL | TBD | ERIS | Rebuild line 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | Current Study | 17.54 | (1793.00, 1793.00) | 2404864.8239 | 6.2322 | 38588000 | 0.021389
GEN-2024-170 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 1494759.5147 | 0.75299 | 198511000 | 0.01818
GEN-2024-170 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1248671.1472 | 1.3286 | 93984000 | 0.058887
GEN-2024-170 | 03 CENTRAL | TBD | ERIS | Rebuild line 645458 S3458 3 345 778170 G24-040-TAP 345 1 | Current Study | 13.15 | (1793.00, 1793.00) | 1157199.9539 | 4 | 28930000 | 0.044304
GEN-2024-170 | 03 CENTRAL | TBD | ERIS | Rebuild line 640139 COOPER 3 345 778170 G24-040-TAP 345 1 | Current Study | 12.59 | (1793.00, 1793.00) | 1107919.9559 | 4 | 27698000 | 0.044304
GEN-2024-170 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 668661.8125 | 0.46501 | 143796000 | 0.01659
GEN-2024-170 | 03 CENTRAL | TBD | ERIS | Rebuild line 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 | Current Study | 3.23 | (1793.00, 1793.00) | 356133.0932 | 5.0117 | 7106000 | 0.040352
GEN-2024-170 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 312074.9194 | 0.67969 | 45914000 | 0.024543
GEN-2024-170 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 170317.8406 | 0.67969 | 25058000 | 0.024543
GEN-2024-170 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 168731.1924 | 1.4471 | 11660000 | 0.058887
GEN-2024-170 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 72172.1464 | 0.38802 | 18600000 | 0.048611
GEN-2024-170 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 72172.1464 | 0.38802 | 18600000 | 0.048611
GEN-2024-170 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 41727.0406 | 0.22434 | 18600000 | 0.030854
GEN-2024-170 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 12397.3177 | 0.75135 | 1650000 | 0.032534
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 2759775.3364 | 2.3531 | 117282000 | 0.039613
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 2569919.2271 | 1.7105 | 150244000 | 0.03101
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 2209460.7846 | 2.2001 | 100427000 | 0.022604
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 2158030.7115 | 2.3995 | 89936000 | 0.022422
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 2058957.658 | 3.7006 | 55638000 | 0.066771
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 2043323.7599 | 2.1401 | 95480000 | 0.069236
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 1812625.9161 | 2.1401 | 84700000 | 0.069236
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 1703112.9709 | 2.5805 | 66000000 | 0.047449
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1645400.1897 | 0.75366 | 218320000 | 0.018605
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1512628.7028 | 1.6095 | 93984000 | 0.079895
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 1510965.3192 | 4.4977 | 33594000 | 0.14682
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1304943.7694 | 0.9075 | 143796000 | 0.036261
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 1268029.0559 | 2.6984 | 46992000 | 0.08743
GEN-2024-171 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 509817 T.NO.--4 138 509900 46ST-TP-4 138 1 | Current Study | 5.18 | (211.00, 211.00) | 1247936.4743 | 20.0762 | 6216000 | 0.019726
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 1228957.7319 | 2.2282 | 55154000 | 0.031435
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 1175832.2438 | 2.6225 | 44836000 | 0.049255
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 68 MVAR SVC at TONTITN7 345 kV | Current Study |  |  | 887264.2953 | 7.3939 | 12000000 | 0.040352
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 38 MVAR SVC at WROGERS 5 161 kV | Current Study |  |  | 754159.2738 | 11.4267 | 6600000 | 0.040352
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 715077.8149 | 0.36022 | 198511000 | 0.015404
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 654077.4544 | 2.4984 | 26180000 | 0.022584
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 588252.604 | 2.2282 | 26400000 | 0.031435
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 37 MVAR switched shunt at CHAMSPR7 345 kV | Current Study |  |  | 586517.2457 | 11.0664 | 5300000 | 0.040352
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 576632.0312 | 1.2559 | 45914000 | 0.050791
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 568893.3993 | 0.45576 | 124824000 | 0.023853
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 544289.8248 | 0.32975 | 165062000 | 0.016598
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 499422.5279 | 1.974 | 25300000 | 0.032346
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR SVC at JAY 4 138 kV | Current Study |  |  | 476826.4206 | 8.9967 | 5300000 | 0.040042
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 326843.5253 | 2.1713 | 15053000 | 0.022974
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 325318.9978 | 0.60853 | 53460000 | 0.017572
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 314702.3879 | 1.2559 | 25058000 | 0.050791
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 296255.0307 | 2.4688 | 12000000 | 0.069236
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 295968.9873 | 2.4664 | 12000000 | 0.06677
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 288600.1876 | 2.3425 | 12320000 | 0.040211
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 271644.544 | 2.2637 | 12000000 | 0.040212
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 271644.544 | 2.2637 | 12000000 | 0.040212
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at CENTRTN5 161 kV | Current Study |  |  | 256212.6601 | 7.8835 | 3250000 | 0.040352
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 255950.0501 | 2.1329 | 12000000 | 0.040212
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 249076.9199 | 2.0756 | 12000000 | 0.022422
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 242186.9072 | 2.0182 | 12000000 | 0.040212
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 236603.1646 | 1.9717 | 12000000 | 0.06677
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 224894.5545 | 1.8741 | 12000000 | 0.051119
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 215819.4107 | 1.7985 | 12000000 | 0.069236
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 204399.4092 | 1.753 | 11660000 | 0.079895
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 204118.8667 | 1.701 | 12000000 | 0.069236
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Current Study | 11.41 | (395.00, 395.00) | 202011.9859 | 1.4754 | 13692000 | 0.0018017
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 184024.9096 | 1.5335 | 12000000 | 0.040212
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 184024.9096 | 1.5335 | 12000000 | 0.040212
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 176168.7445 | 1.4681 | 12000000 | 0.039614
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 174526.1486 | 1.4544 | 12000000 | 0.040212
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 174007.3767 | 1.4501 | 12000000 | 0.051119
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 172065.5001 | 3.2465 | 5300000 | 0.079895
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 171562.0736 | 1.4297 | 12000000 | 0.040212
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 166911.6567 | 2.529 | 6600000 | 0.079895
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 163556.5331 | 1.363 | 12000000 | 0.040212
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 152870.1899 | 2.8843 | 5300000 | 0.06677
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 4.8 MVAR switched shunt at COWSKIN2 69 kV | Current Study |  |  | 148763.5907 | 10.78 | 1380000 | 0.040042
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 147119.4369 | 1.226 | 12000000 | 0.026791
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 139869.1349 | 2.1192 | 6600000 | 0.069236
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 128007.0496 | 1.9395 | 6600000 | 0.051119
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 128007.0496 | 1.9395 | 6600000 | 0.051119
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 121644.5414 | 1.8431 | 6600000 | 0.051119
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 112014.8777 | 2.1135 | 5300000 | 0.079895
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 109119.7403 | 3.3575 | 3250000 | 0.051119
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 109119.7403 | 3.3575 | 3250000 | 0.051119
GEN-2024-171 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 107285.827 | 0.59274 | 18100000 | 0.0072648
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 106927.8138 | 2.0175 | 5300000 | 0.051119
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 104415.0206 | 1.9701 | 5300000 | 0.039614
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 100185.3435 | 1.8903 | 5300000 | 0.039614
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 98320.3353 | 1.8551 | 5300000 | 0.079895
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 95654.4468 | 1.8048 | 5300000 | 0.069236
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 88694.9635 | 2.7291 | 3250000 | 0.051119
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 80142.2858 | 2.6984 | 2970000 | 0.08743
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 79313.9083 | 2.4404 | 3250000 | 0.051119
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 77768.733 | 1.4673 | 5300000 | 0.0087258
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 75329.9082 | 2.1401 | 3520000 | 0.069236
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 71651.7885 | 2.2047 | 3250000 | 0.079895
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 69551.7431 | 2.1401 | 3250000 | 0.069236
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 67926.6013 | 2.09 | 3250000 | 0.051119
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 67327.4081 | 2.0716 | 3250000 | 0.051119
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 67323.2389 | 2.0715 | 3250000 | 0.051119
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 65568.9424 | 2.0175 | 3250000 | 0.051119
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 62350.5578 | 1.9185 | 3250000 | 0.069236
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 61475.5596 | 1.8916 | 3250000 | 0.051119
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 59877.0709 | 1.8424 | 3250000 | 0.051119
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 59364.6562 | 2.6984 | 2200000 | 0.08743
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 58334.1674 | 2.3981 | 2432500 | 0.039614
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 57644.0062 | 1.0876 | 5300000 | 0.024752
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 56405.6527 | 1.7356 | 3250000 | 0.051119
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 54314.9164 | 0.33544 | 16192000 | 0.030089
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 53992.8226 | 0.36145 | 14938000 | 0.030799
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 53906.1913 | 2.2161 | 2432500 | 0.079895
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 53158.883 | 2.1854 | 2432500 | 0.079895
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 52268.5552 | 0.36145 | 14460953.1406 | 0.030799
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 49021.0503 | 2.2282 | 2200000 | 0.031435
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 37214.8821 | 2.6967 | 1380000 | 0.051119
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 35664.8396 | 1.5506 | 2300000 | 0.087431
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 35143.759 | 2.5466 | 1380000 | 0.079895
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 31061.0617 | 2.3531 | 1320000 | 0.039613
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 30616.9767 | 2.2186 | 1380000 | 0.051119
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509752 INOLATP4 138 510442 GUAVA 4 138 1 | Current Study | 1.63 | (395.00, 395.00) | 28858.8551 | 1.4754 | 1956000 | 0.0018017
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 23434.1079 | 1.6981 | 1380000 | 0.04745
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 22188.709 | 1.6079 | 1380000 | 0.029426
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 18602.5638 | 0.35099 | 5300000 | 0.040212
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 5534.8081 | 0.33544 | 1650000 | 0.030089
GEN-2024-173 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640316 PAWNEEL7 115 640340 SEWARD 7 115 1 | Current Study | 11.21 | (217.00, 217.00) | 11210000 | 100 | 11210000 | 0.21365
GEN-2024-173 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1 | Current Study | 5.46 | (217.00, 217.00) | 5235990.1226 | 95.8973 | 5460000 | 0.78635
GEN-2024-173 | 02 NEBRASKA | TBD | NRIS | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | Current Study | 17.69 | (160.00, 160.00) | 4484239.5841 | 16.8993 | 26535000 | 0.071341
GEN-2024-173 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2 | Current Study |  | (110.00, 120.00) | 2027920.6711 | 16.8993 | 12000000 | 0.035671
GEN-2024-173 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659201 LO.KU1A_-BE9 13 M2 | Current Study |  | (600.00, 637.40) | 343579.6779 | 1.3743 | 25000000 | 0.0086951
GEN-2024-173 | 02 NEBRASKA | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 3997.8458 | 0.2897 | 1380000 | 0.045441
GEN-2024-175 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 1552842.3363 | 0.16548 | 938400000 | 0.024842
GEN-2024-175 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 85561.2526 | 0.043102 | 198511000 | 0.0014569
GEN-2024-175 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 67900.356 | 1.2811 | 5300000 | 0.054477
GEN-2024-175 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 32261.8863 | 0.17345 | 18600000 | 0.030421
GEN-2024-175 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 32261.8863 | 0.17345 | 18600000 | 0.030421
GEN-2024-175 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 23997.4923 | 0.12902 | 18600000 | 0.024842
GEN-2024-176 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 8072107.7925 | 5.6136 | 143796000 | 0.2243
GEN-2024-176 | 03 CENTRAL | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 4832276.8486 | 2.2134 | 218320000 | 0.054639
GEN-2024-176 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 4588013.332 | 0.48892 | 938400000 | 0.033178
GEN-2024-176 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 3457469.0674 | 0.36844 | 938400000 | 0.044249
GEN-2024-176 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 2979803.7233 | 1.5011 | 198511000 | 0.040591
GEN-2024-176 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Current Study | 26.47 | (1793.00, 1793.00) | 2260571.1545 | 3.8819 | 58234000 | 0.053173
GEN-2024-176 | 03 CENTRAL | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 1411185.083 | 2.6397 | 53460000 | 0.076226
GEN-2024-176 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1041231.3057 | 0.52452 | 198511000 | 0.02243
GEN-2024-176 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | Current Study | 19.87 | (1793.00, 1793.00) | 864034.5307 | 1.9766 | 43714000 | 0.027003
GEN-2024-176 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 767643.9211 | 1.6719 | 45914000 | 0.067616
GEN-2024-176 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | Current Study | 16.71 | (1793.00, 1793.00) | 597326.4824 | 1.6248 | 36762000 | 0.036383
GEN-2024-176 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 418948.9344 | 1.6719 | 25058000 | 0.067616
GEN-2024-176 | 03 CENTRAL | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 250051.8953 | 1.3444 | 18600000 | 0.10778
GEN-2024-176 | 03 CENTRAL | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 231911.3674 | 4.3757 | 5300000 | 0.057082
GEN-2024-176 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 142431.6274 | 2.6874 | 5300000 | 0.091419
GEN-2024-176 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 111747.9828 | 0.6008 | 18600000 | 0.084298
GEN-2024-176 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 111747.9828 | 0.6008 | 18600000 | 0.084298
GEN-2024-176 | 03 CENTRAL | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 93537.3553 | 4.2277 | 2212500 | 0.10872
GEN-2024-176 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 76489.7825 | 0.51205 | 14938000 | 0.043631
GEN-2024-176 | 03 CENTRAL | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 74856.4128 | 1.4124 | 5300000 | 0.039424
GEN-2024-176 | 03 CENTRAL | TBD | ERIS | Add 0.8 MVAR switched shunt at HARBNGR7 345 kV | Current Study |  |  | 74168.9356 | 1.3994 | 5300000 | 0.11619
GEN-2024-176 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 74047.0719 | 0.51205 | 14460953.1406 | 0.043631
GEN-2024-176 | 03 CENTRAL | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 62774.3626 | 0.52312 | 12000000 | 0.058222
GEN-2024-176 | 03 CENTRAL | TBD | ERIS | Add 66 MVAR switched shunt at GEN-2021-021 345 kV | Current Study |  |  | 59297.37 | 1.1188 | 5300000 | 0.00046395
GEN-2024-176 | 03 CENTRAL | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 58061.9165 | 0.31216 | 18600000 | 0.033178
GEN-2024-176 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 53431.4304 | 0.28727 | 18600000 | 0.044249
GEN-2024-176 | 03 CENTRAL | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 49205.264 | 0.9284 | 5300000 | 0.025455
GEN-2024-176 | 03 CENTRAL | TBD | ERIS | Add 248 MVAR switched shunt at GEN-2022-015 345 kV | Current Study |  |  | 36517.0839 | 0.689 | 5300000 | 0.039424
GEN-2024-176 | 03 CENTRAL | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 29736.0106 | 0.56106 | 5300000 | 0.039424
GEN-2024-176 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 8091.6752 | 0.4904 | 1650000 | 0.023783
GEN-2024-176 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MED-LDG3 115 kV | Current Study |  |  | 2432.9639 | 0.10996 | 2212500 | 0.0030298
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 1670277.5928 | 1.1117 | 150244000 | 0.02532
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1021621.4648 | 1.07 | 95480000 | 0.043488
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 960058.893 | 0.43975 | 218320000 | 0.013637
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 906277.1059 | 1.07 | 84700000 | 0.043488
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 846849.2166 | 0.58892 | 143796000 | 0.029562
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 717824.2375 | 0.71477 | 100427000 | 0.0092259
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 693926.7931 | 1.4767 | 46992000 | 0.060108
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 681652.5905 | 0.34338 | 198511000 | 0.018448
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 588546.1733 | 0.4715 | 124824000 | 0.031002
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 501759.4718 | 0.53388 | 93984000 | 0.033294
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 497449.9775 | 0.78648 | 63250000 | 0.04292
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 456077.6854 | 0.27631 | 165062000 | 0.017472
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 435434.6428 | 3.6286 | 12000000 | 0.054243
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 401773.7398 | 1.196 | 33594000 | 0.049045
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 390279.795 | 0.47894 | 81488000 | 0.031961
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 345296.53 | 0.30613 | 112794000 | 0.026206
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at PHILL 7 345 kV | Current Study |  |  | 332297.9075 | 6.2698 | 5300000 | 0.028101
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 308352.5242 | 1.2188 | 25300000 | 0.025089
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 238441.8752 | 0.92873 | 25674000 | 0.032767
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 216061.7243 | 1.8005 | 12000000 | 0.066734
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 210780.307 | 3.1936 | 6600000 | 0.066734
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 180819.4472 | 1.5068 | 12000000 | 0.066734
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 175418.1164 | 3.3098 | 5300000 | 0.054243
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 170600.2894 | 0.95265 | 17908000 | 0.034167
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 165584.3492 | 1.3799 | 12000000 | 0.066734
GEN-2024-177 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 148973.7727 | 0.82306 | 18100000 | 0.012673
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 148121.7147 | 1.2343 | 12000000 | 0.043488
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 133525.9869 | 1.1127 | 12000000 | 0.015101
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 133007.6279 | 1.1084 | 12000000 | 0.037696
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 127293.1405 | 1.0608 | 12000000 | 0.054243
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 126406.7027 | 1.9153 | 6600000 | 0.066734
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 119753.9541 | 0.99795 | 12000000 | 0.023636
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 110373.3472 | 0.91978 | 12000000 | 0.031518
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 109799.5749 | 0.915 | 12000000 | 0.030141
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 109799.5749 | 0.915 | 12000000 | 0.030141
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 106328.7947 | 0.88607 | 12000000 | 0.037696
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 105964.1559 | 0.70394 | 15053000 | 0.0093572
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 105550.0217 | 3.2477 | 3250000 | 0.066734
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 105550.0217 | 3.2477 | 3250000 | 0.066734
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 104581.9508 | 0.87152 | 12000000 | 0.029543
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 103316.4945 | 0.86097 | 12000000 | 0.023636
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 102363.5485 | 0.85303 | 12000000 | 0.030141
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 100555.5649 | 1.8973 | 5300000 | 0.054243
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 69931.8288 | 1.0596 | 6600000 | 0.043488
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 67802.0584 | 0.58149 | 11660000 | 0.033294
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 65370.8806 | 1.2334 | 5300000 | 0.066734
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 63882.2153 | 1.9656 | 3250000 | 0.066734
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 62823.0709 | 0.95186 | 6600000 | 0.031518
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 62823.0709 | 0.95186 | 6600000 | 0.031518
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 62221.1487 | 1.9145 | 3250000 | 0.066734
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 58613.8308 | 1.8035 | 3250000 | 0.066734
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 57076.5268 | 1.0769 | 5300000 | 0.033294
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 55862.5727 | 1.054 | 5300000 | 0.050797
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 52477.8412 | 0.99015 | 5300000 | 0.031518
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 50731.3821 | 0.33961 | 14938000 | 0.036354
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 50074.9839 | 3.6286 | 1380000 | 0.054243
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 49111.2692 | 0.33961 | 14460953.1406 | 0.036354
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 47837.5717 | 1.4719 | 3250000 | 0.066734
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 45015.0052 | 0.27801 | 16192000 | 0.031328
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 43857.7327 | 1.4767 | 2970000 | 0.060108
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 40055.7305 | 2.9026 | 1380000 | 0.066734
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 38925.538 | 1.1977 | 3250000 | 0.031518
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 37663.4641 | 1.07 | 3520000 | 0.043488
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 37156.8976 | 0.70107 | 5300000 | 0.033294
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 34774.5097 | 1.07 | 3250000 | 0.043488
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 33336.8959 | 1.0258 | 3250000 | 0.031518
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 33042.8249 | 1.0167 | 3250000 | 0.031518
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 33040.7788 | 1.0166 | 3250000 | 0.031518
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 32487.2094 | 1.4767 | 2200000 | 0.060108
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 32179.8083 | 0.99015 | 3250000 | 0.031518
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV | Current Study |  |  | 31504.9996 | 2.283 | 1380000 | 0.030253
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 25790.8557 | 1.1657 | 2212500 | 0.059206
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 25005.4701 | 1.1302 | 2212500 | 0.059206
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 23767.8978 | 0.73132 | 3250000 | 0.033294
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 23568.1079 | 0.44468 | 5300000 | 0.0033221
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 21323.8096 | 1.5452 | 1380000 | 0.054243
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 19517.4929 | 0.84859 | 2300000 | 0.060108
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 17881.4357 | 0.73511 | 2432500 | 0.033294
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 17633.5431 | 0.72491 | 2432500 | 0.033294
GEN-2024-177 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 17005.884 | 0.32087 | 5300000 | 0.05506
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 15613.6599 | 0.64188 | 2432500 | 0.029259
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 15026.145 | 1.0889 | 1380000 | 0.031518
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 12369.6688 | 0.89635 | 1380000 | 0.043886
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 8524.3201 | 0.38528 | 2212500 | 0.041281
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 4587.1269 | 0.27801 | 1650000 | 0.031328
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 1649076.3433 | 1.0976 | 150244000 | 0.024998
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1013425.3278 | 1.0614 | 95480000 | 0.043139
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 944943.2512 | 0.43282 | 218320000 | 0.013423
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 899006.3392 | 1.0614 | 84700000 | 0.043139
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 837217.7322 | 0.58223 | 143796000 | 0.029226
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 700471.2883 | 0.62102 | 112794000 | 0.053161
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 690381.5191 | 0.68745 | 100427000 | 0.0088732
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 671945.1563 | 0.33849 | 198511000 | 0.018185
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 648902.1645 | 1.3809 | 46992000 | 0.056208
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 647622.1771 | 1.0239 | 63250000 | 0.055877
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 576720.9813 | 0.46203 | 124824000 | 0.030379
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 499674.0884 | 0.53166 | 93984000 | 0.033156
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 449398.9356 | 0.27226 | 165062000 | 0.017216
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | Current Study | 7.6 | (211.00, 211.00) | 448046.9953 | 4.9128 | 9120000 | 0.04717
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 434061.757 | 3.6172 | 12000000 | 0.054072
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | Current Study | 10.42 | (395.00, 395.00) | 433483.0935 | 3.4668 | 12504000 | 0.014071
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 400590.0807 | 1.1924 | 33594000 | 0.048901
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 382543.6881 | 0.46945 | 81488000 | 0.031328
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at PHILL 7 345 kV | Current Study |  |  | 337411.5262 | 6.3663 | 5300000 | 0.028533
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 306690.7841 | 1.2122 | 25300000 | 0.024954
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 268989.5738 | 1.0477 | 25674000 | 0.036965
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 214515.0799 | 1.7876 | 12000000 | 0.066256
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 209271.4688 | 3.1708 | 6600000 | 0.066256
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 192345.5538 | 1.0741 | 17908000 | 0.038523
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 179525.0791 | 1.496 | 12000000 | 0.066256
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 174865.0391 | 3.2993 | 5300000 | 0.054072
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 164399.0393 | 1.37 | 12000000 | 0.066256
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 146933.3828 | 1.2244 | 12000000 | 0.043139
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 136242.0631 | 1.1354 | 12000000 | 0.015408
GEN-2024-178 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 136226.4494 | 0.75263 | 18100000 | 0.011588
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 132204.7268 | 1.1017 | 12000000 | 0.037469
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 126891.7968 | 1.0574 | 12000000 | 0.054072
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 125501.8399 | 1.9015 | 6600000 | 0.066256
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 118242.1548 | 0.98535 | 12000000 | 0.023338
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 108156.7377 | 0.90131 | 12000000 | 0.02969
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 108156.7377 | 0.90131 | 12000000 | 0.02969
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 107785.3683 | 0.89821 | 12000000 | 0.030779
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 105686.9405 | 0.88072 | 12000000 | 0.037469
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 104794.4582 | 3.2244 | 3250000 | 0.066256
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 104794.4582 | 3.2244 | 3250000 | 0.066256
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 102985.5037 | 0.85821 | 12000000 | 0.029092
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 102117.4059 | 0.67839 | 15053000 | 0.0090175
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 102012.2052 | 0.8501 | 12000000 | 0.023338
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 100831.9702 | 0.84027 | 12000000 | 0.02969
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 100238.5224 | 1.8913 | 5300000 | 0.054072
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV | Current Study |  |  | 92384.8534 | 6.6946 | 1380000 | 0.088713
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | Current Study | 1.8 | (395.00, 395.00) | 74881.9163 | 3.4668 | 2160000 | 0.014071
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 69370.7887 | 1.0511 | 6600000 | 0.043139
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 67520.2634 | 0.57908 | 11660000 | 0.033156
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 64902.9333 | 1.2246 | 5300000 | 0.066256
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 63424.9244 | 1.9515 | 3250000 | 0.066256
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 61775.7483 | 1.9008 | 3250000 | 0.066256
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 61350.027 | 0.92955 | 6600000 | 0.030779
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 61350.027 | 0.92955 | 6600000 | 0.030779
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 58194.2528 | 1.7906 | 3250000 | 0.066256
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 56839.3023 | 1.0724 | 5300000 | 0.033156
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 55182.8261 | 1.0412 | 5300000 | 0.050179
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 51247.3671 | 0.96693 | 5300000 | 0.030779
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 50067.9675 | 0.33517 | 14938000 | 0.035879
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 49917.1021 | 3.6172 | 1380000 | 0.054072
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 48469.0408 | 0.33517 | 14460953.1406 | 0.035879
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 47495.1339 | 1.4614 | 3250000 | 0.066256
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 44377.6685 | 0.27407 | 16192000 | 0.030884
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 41012.075 | 1.3809 | 2970000 | 0.056208
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 39768.9977 | 2.8818 | 1380000 | 0.066256
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 38012.8315 | 1.1696 | 3250000 | 0.030779
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 37361.3024 | 1.0614 | 3520000 | 0.043139
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 37002.4642 | 0.69816 | 5300000 | 0.033156
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 34495.5253 | 1.0614 | 3250000 | 0.043139
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 32555.2291 | 1.0017 | 3250000 | 0.030779
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 32268.0533 | 0.99286 | 3250000 | 0.030779
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 32266.0552 | 0.9928 | 3250000 | 0.030779
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 31425.2723 | 0.96693 | 3250000 | 0.030779
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 31411.0204 | 1.4197 | 2212500 | 0.072108
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 30454.489 | 1.3765 | 2212500 | 0.072108
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 30379.3148 | 1.3809 | 2200000 | 0.056208
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 23669.1124 | 0.72828 | 3250000 | 0.033156
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 23263.0309 | 0.43893 | 5300000 | 0.0032791
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 21256.5776 | 1.5403 | 1380000 | 0.054072
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 18251.1218 | 0.79353 | 2300000 | 0.056208
GEN-2024-178 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 18162.9717 | 0.3427 | 5300000 | 0.058807
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 17807.1159 | 0.73205 | 2432500 | 0.033156
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 17560.2536 | 0.7219 | 2432500 | 0.033156
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 16270.7628 | 0.66889 | 2432500 | 0.03049
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 15863.3182 | 1.1495 | 1380000 | 0.056281
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 14673.8195 | 1.0633 | 1380000 | 0.030779
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 8630.3662 | 0.39007 | 2212500 | 0.041795
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 4522.1809 | 0.27407 | 1650000 | 0.030884
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512631 MIAMI 5 161 512632 AFTON 5 161 1 | Current Study | 13.5 | (309.00, 309.00) | 20250000 | 100 | 20250000 | 0.052807
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512632 AFTON 5 161 512669 KETCHUM5 161 1 | Current Study | 12.8 | (309.00, 309.00) | 19200000 | 100 | 19200000 | 0.05704
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512631 MIAMI 5 161 547487 HOC404 5 161 1 | Current Study | 9.9 | (246.00, 246.00) | 14850000 | 100 | 14850000 | 0.054846
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512654 PENSA 5 161 512669 KETCHUM5 161 1 | Current Study | 4.8 | (364.00, 364.00) | 7200000 | 100 | 7200000 | 0.05704
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 547469 RIV4525 161 547729 BAX488 5 161 1 | Current Study | 5.19 | (364.00, 364.00) | 3826950.032 | 49.158 | 7785000 | 0.05586
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 547487 HOC404 5 161 547729 BAX488 5 161 1 | Current Study | 2.6 | (364.00, 364.00) | 1917161.8658 | 49.158 | 3900000 | 0.05586
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 8 MVAR switched shunt at KANSAS 2 69 kV | Current Study |  |  | 1380000 | 100 | 1380000 | 0.11182
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 1005948.5529 | 0.85772 | 117282000 | 0.036098
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 949171.7114 | 1.0554 | 89936000 | 0.024655
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 68 MVAR SVC at TONTITN7 345 kV | Current Study |  |  | 914604.0158 | 7.6217 | 12000000 | 0.10399
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 870672.8813 | 0.91189 | 95480000 | 0.073755
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 865085.49 | 0.57579 | 150244000 | 0.026097
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 860280.83 | 0.85662 | 100427000 | 0.022003
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 38 MVAR SVC at WROGERS 5 161 kV | Current Study |  |  | 777397.5624 | 11.7788 | 6600000 | 0.10399
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 772371.1044 | 0.91189 | 84700000 | 0.073755
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 744893.2636 | 1.1286 | 66000000 | 0.051882
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 37 MVAR switched shunt at CHAMSPR7 345 kV | Current Study |  |  | 604589.8963 | 11.4074 | 5300000 | 0.10399
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 590702.0478 | 0.27057 | 218320000 | 0.016698
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 446357.0891 | 0.31041 | 143796000 | 0.031008
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR SVC at JAY 4 138 kV | Current Study |  |  | 409244.411 | 7.7216 | 5300000 | 0.085917
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 398660.5246 | 0.72281 | 55154000 | 0.025493
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 269083.2264 | 1.0278 | 26180000 | 0.023227
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at CENTRTN5 161 kV | Current Study |  |  | 264107.4695 | 8.1264 | 3250000 | 0.10399
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 219105.5502 | 1.8259 | 12000000 | 0.12451
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 212034.7819 | 0.22561 | 93984000 | 0.027999
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 209803.6239 | 0.82926 | 25300000 | 0.033971
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 190822.7481 | 0.72281 | 26400000 | 0.025493
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 185085.0413 | 0.55095 | 33594000 | 0.044961
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 169528.2578 | 1.4127 | 12000000 | 0.12451
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 162006.5321 | 1.3501 | 12000000 | 0.073755
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 135012.5437 | 1.1251 | 12000000 | 0.073755
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 135012.5437 | 1.1251 | 12000000 | 0.073755
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 4.8 MVAR switched shunt at COWSKIN2 69 kV | Current Study |  |  | 127678.8899 | 9.2521 | 1380000 | 0.085917
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 127239.371 | 0.84528 | 15053000 | 0.02236
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 125869.0033 | 1.0489 | 12000000 | 0.073755
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 124712.0239 | 1.8896 | 6600000 | 0.12451
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 124712.0239 | 1.8896 | 6600000 | 0.12451
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 118513.2928 | 1.7957 | 6600000 | 0.12451
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 109551.6485 | 0.91293 | 12000000 | 0.024655
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 106310.8922 | 3.2711 | 3250000 | 0.12451
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 106310.8922 | 3.2711 | 3250000 | 0.12451
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 105348.2224 | 0.8551 | 12320000 | 0.036696
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 104541.3472 | 0.87118 | 12000000 | 0.073755
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 104450.8328 | 0.87042 | 12000000 | 0.060165
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 104175.388 | 1.9656 | 5300000 | 0.12451
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 99158.63 | 0.82632 | 12000000 | 0.036696
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 99158.63 | 0.82632 | 12000000 | 0.036696
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 93429.656 | 0.77858 | 12000000 | 0.036696
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 91961.6702 | 0.76635 | 12000000 | 0.073755
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 88405.6848 | 0.73671 | 12000000 | 0.036696
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 86976.0131 | 0.7248 | 12000000 | 0.073755
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 86411.869 | 2.6588 | 3250000 | 0.12451
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 77762.145 | 1.4672 | 5300000 | 0.073755
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 77272.2912 | 2.3776 | 3250000 | 0.12451
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 66178.1046 | 2.0362 | 3250000 | 0.12451
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 65594.3352 | 2.0183 | 3250000 | 0.12451
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 65590.2734 | 2.0182 | 3250000 | 0.12451
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 65471.6244 | 0.5456 | 12000000 | 0.038252
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 64214.0132 | 0.53512 | 12000000 | 0.036098
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 63881.1342 | 1.9656 | 3250000 | 0.12451
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 62733.7181 | 0.52278 | 12000000 | 0.035381
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 61288.8253 | 1.1564 | 5300000 | 0.12451
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 59893.119 | 1.8429 | 3250000 | 0.12451
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 59703.175 | 0.49753 | 12000000 | 0.036696
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 59598.899 | 0.90301 | 6600000 | 0.073755
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 58335.777 | 1.7949 | 3250000 | 0.12451
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 56047.2749 | 1.0575 | 5300000 | 0.060165
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 54953.7164 | 1.6909 | 3250000 | 0.12451
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 45832.4107 | 0.69443 | 6600000 | 0.054846
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 44664.7576 | 1.3743 | 3250000 | 0.12451
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 40758.8116 | 0.76903 | 5300000 | 0.073755
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 36517.8454 | 0.68902 | 5300000 | 0.036098
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 36256.9349 | 2.6273 | 1380000 | 0.12451
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 32098.5394 | 0.91189 | 3520000 | 0.073755
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 29828.866 | 2.1615 | 1380000 | 0.12451
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 29636.3262 | 0.91189 | 3250000 | 0.073755
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 28651.9647 | 0.24573 | 11660000 | 0.027999
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 26567.8672 | 0.81747 | 3250000 | 0.073755
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 15901.8957 | 0.72281 | 2200000 | 0.025493
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 15701.9748 | 0.29626 | 5300000 | 0.027999
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 15642.9618 | 0.29515 | 5300000 | 0.0043879
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 11321.8745 | 0.85772 | 1320000 | 0.036098
GEN-2024-180 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 10249.3664 | 0.74271 | 1380000 | 0.051883
GEN-2024-181 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 1546727.0424 | 0.16483 | 938400000 | 0.024868
GEN-2024-181 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 118451.7009 | 0.05967 | 198511000 | 0.0020271
GEN-2024-181 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 70639.4332 | 1.3328 | 5300000 | 0.056959
GEN-2024-181 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 32089.4912 | 0.17252 | 18600000 | 0.030411
GEN-2024-181 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 32089.4912 | 0.17252 | 18600000 | 0.030411
GEN-2024-181 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 23902.987 | 0.12851 | 18600000 | 0.024868
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510880 COALGTP4 138 510881 ALLENGT4 138 1 | Current Study | 11.48 | (211.00, 211.00) | 13776000 | 100 | 13776000 | 0.3919
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505598 ALLEN 4 138 505600 TUPELO 4 138 1 | Current Study | 19.4 | (211.00, 211.00) | 9671071.788 | 41.5424 | 23280000 | 0.11365
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510895 LEHIGH-4 138 782490 G24-184-TAP 138 1 | Current Study | 7.71 | (211.00, 211.00) | 9252000 | 100 | 9252000 | 0.3919
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505592 WELEETK4 138 505595 GREASYC4 138 1 | Current Study | 16.28 | (211.00, 211.00) | 9028558.5682 | 46.215 | 19536000 | 0.11344
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505596 EXPLOR 4 138 505598 ALLEN 4 138 1 | Current Study | 14.8 | (211.00, 211.00) | 7388630.0669 | 41.6026 | 17760000 | 0.11344
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510880 COALGTP4 138 510895 LEHIGH-4 138 1 | Current Study | 4.81 | (211.00, 211.00) | 5772000 | 100 | 5772000 | 0.3919
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505595 GREASYC4 138 505596 EXPLOR 4 138 1 | Current Study | 6.91 | (211.00, 211.00) | 3832146.1736 | 46.215 | 8292000 | 0.11344
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1 | Current Study | 56.1 | (1793.00, 1793.00) | 3524651.371 | 2.8558 | 123420000 | 0.041166
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 1 | Current Study |  | (1868.00, 1868.00) | 2234757.8736 | 3.6338 | 61500000 | 0.088948
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 2 | Current Study |  | (1868.00, 1868.00) | 2234757.8736 | 3.6338 | 61500000 | 0.088948
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 2064300.4956 | 1.7601 | 117282000 | 0.037224
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 2007960.1176 | 1.3365 | 150244000 | 0.030439
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515178 PARKLN 4 138 515977 LKKONWA4 138 1 | Current Study | 13.56 | (472.00, 472.00) | 1802869.5425 | 11.0796 | 16272000 | 0.1347
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520854 CIVIT 4 138 521023 PAOLI 4 138 1 | Current Study | 11.15 | (211.00, 211.00) | 1773397.3294 | 13.2541 | 13380000 | 0.11332
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1 | Current Study | 30.63 | (1793.00, 1793.00) | 1674079.1743 | 2.4843 | 67386000 | 0.040881
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515044 SEMINOL4 138 515531 VANOSTP4 138 1 | Current Study | 21.55 | (395.00, 395.00) | 1512648.2094 | 5.8494 | 25860000 | 0.048725
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515150 CANEYCK4 138 515151 LTLCITY4 138 1 | Current Study | 11.79 | (265.00, 265.00) | 1477595.3278 | 10.4438 | 14148000 | 0.056619
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520888 PAYNESW4 138 521023 PAOLI 4 138 1 | Current Study | 12 | (265.00, 265.00) | 1375876.8871 | 9.5547 | 14400000 | 0.057836
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 1251377.7119 | 1.3914 | 89936000 | 0.016334
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 1248265.243 | 1.9735 | 63250000 | 0.1077
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1205213.7754 | 0.55204 | 218320000 | 0.01712
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1200301.075 | 1.1952 | 100427000 | 0.015427
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1197009.6115 | 1.2537 | 95480000 | 0.050954
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 1177783.1228 | 2.1169 | 55638000 | 0.047983
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 1156384.6146 | 1.0252 | 112794000 | 0.087762
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 1099444.8555 | 1.6658 | 66000000 | 0.038481
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 1061863.3651 | 1.2537 | 84700000 | 0.050954
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1002062.5051 | 0.69686 | 143796000 | 0.034981
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 776060 G23-204-TAP 345 1 | Current Study | 17.82 | (1793.00, 1793.00) | 948260.9954 | 2.4188 | 39204000 | 0.091572
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 946747.8896 | 1.7166 | 55154000 | 0.030423
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 856737.3834 | 1.9108 | 44836000 | 0.045086
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 815371.4343 | 0.41074 | 198511000 | 0.022067
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515151 LTLCITY4 138 515157 BROWN 4 138 1 | Current Study | 6.37 | (265.00, 265.00) | 798327.5859 | 10.4438 | 7644000 | 0.056619
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 733211.8345 | 0.37057 | 197860000 | 0.018406
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 712712.2861 | 0.57097 | 124824000 | 0.037542
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 639782.7698 | 0.68074 | 93984000 | 0.042453
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520842 CANADNS4 138 520976 LIL AXE4 138 1 | Current Study | 11.08 | (265.00, 265.00) | 628228.2337 | 4.7249 | 13296000 | 0.037488
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 622099.7049 | 1.3238 | 46992000 | 0.053887
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | Current Study | 7.74 | (1793.00, 1793.00) | 553480.3453 | 3.2504 | 17028000 | 0.091572
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 531531.2687 | 1.5822 | 33594000 | 0.064885
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 529546.0571 | 0.32082 | 165062000 | 0.020287
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520973 LEXNGTN4 138 520976 LIL AXE4 138 1 | Current Study | 9.71 | (265.00, 265.00) | 522709.6409 | 4.486 | 11652000 | 0.037488
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 500968.9606 | 0.37682 | 132946000 | 0.011774
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 472668.6741 | 0.58005 | 81488000 | 0.038708
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 470928.825 | 1.8343 | 25674000 | 0.064716
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 764550 G20-087-TAP 345 1 | Current Study | 14.38 | (1793.00, 1793.00) | 462048.7881 | 1.4605 | 31636000 | 0.050057
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505600 TUPELO 4 138 510881 ALLENGT4 138 1 | Current Study | 0.38 | (211.00, 211.00) | 456000 | 100 | 456000 | 0.3919
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 453170.1107 | 1.7166 | 26400000 | 0.030423
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | Current Study | 13.6 | (1793.00, 1793.00) | 448417.3126 | 1.4987 | 29920000 | 0.028442
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 403382.5637 | 0.87856 | 45914000 | 0.044637
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 400315.5431 | 1.5291 | 26180000 | 0.017364
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | Current Study | 6.93 | (1793.00, 1793.00) | 368768.1649 | 2.4188 | 15246000 | 0.091572
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 340025.204 | 1.344 | 25300000 | 0.027666
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510887 ATOKA--4 138 782490 G24-184-TAP 138 1 | Current Study | 0.28 | (211.00, 211.00) | 336000 | 100 | 336000 | 0.6081
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 330800.57 | 1.8472 | 17908000 | 0.066252
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | Current Study | 8.91 | (2390.00, 2390.00) | 282546.0227 | 1.4414 | 19602000 | 0.050057
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 278800.9547 | 2.3233 | 12000000 | 0.034731
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 244186.695 | 0.45677 | 53460000 | 0.01657
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 220149.8515 | 0.87856 | 25058000 | 0.044637
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 216077.7927 | 1.7539 | 12320000 | 0.037822
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 203382.664 | 1.6949 | 12000000 | 0.037823
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 203382.664 | 1.6949 | 12000000 | 0.037823
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | Current Study | 5.97 | (2390.00, 2390.00) | 189315.3485 | 1.4414 | 13134000 | 0.050057
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 181327.4717 | 1.5111 | 12000000 | 0.037823
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 177597.4483 | 1.1798 | 15053000 | 0.015683
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 173550.6855 | 1.4463 | 12000000 | 0.050954
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 169303.3759 | 1.4109 | 12000000 | 0.047983
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514948 CEDARLN4 138 766111 G21-088-TAP 138 1 | Current Study | 2.86 | (395.00, 395.00) | 158557.8248 | 4.62 | 3432000 | 0.039796
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 144432.308 | 1.2036 | 12000000 | 0.016334
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 144112.3322 | 1.2009 | 12000000 | 0.028444
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 143410.6277 | 1.1951 | 12000000 | 0.061111
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 137781.0715 | 1.1482 | 12000000 | 0.037823
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 137781.0715 | 1.1482 | 12000000 | 0.037823
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 135344.297 | 1.1279 | 12000000 | 0.047983
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 131773.3109 | 1.0981 | 12000000 | 0.037225
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 130848.7343 | 1.0904 | 12000000 | 0.037365
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 130669.2655 | 1.0889 | 12000000 | 0.037823
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 128450.0364 | 1.0704 | 12000000 | 0.037823
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 126430.2806 | 1.0536 | 12000000 | 0.050954
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 124331.4351 | 1.0361 | 12000000 | 0.028444
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 122456.2176 | 1.0205 | 12000000 | 0.037823
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 120346.9494 | 2.2707 | 5300000 | 0.028444
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 116222.7742 | 1.761 | 6600000 | 0.036797
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 112317.0587 | 2.1192 | 5300000 | 0.034731
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 111767.3409 | 2.1088 | 5300000 | 0.028141
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 101241.4242 | 0.84368 | 12000000 | 0.037365
GEN-2024-184 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 96580.0115 | 0.53359 | 18100000 | 0.0082159
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 87446.4567 | 1.6499 | 5300000 | 0.047983
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 86452.9543 | 0.74145 | 11660000 | 0.042453
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 81937.4584 | 1.2415 | 6600000 | 0.050954
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 78101.8961 | 1.4736 | 5300000 | 0.037225
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 74938.1195 | 1.4139 | 5300000 | 0.037225
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 74477.3943 | 1.1284 | 6600000 | 0.037365
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 74477.3943 | 1.1284 | 6600000 | 0.037365
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 72777.135 | 1.3732 | 5300000 | 0.042453
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 70775.5433 | 1.0724 | 6600000 | 0.037365
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 70597.2561 | 1.0697 | 6600000 | 0.042453
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 67205.2735 | 1.268 | 5300000 | 0.061111
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 63488.3309 | 1.9535 | 3250000 | 0.037365
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 63488.3309 | 1.9535 | 3250000 | 0.037365
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 62213.0185 | 1.1738 | 5300000 | 0.037365
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 60895.0873 | 0.40765 | 14938000 | 0.043638
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 58950.3952 | 0.40765 | 14460953.1406 | 0.043638
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 58199.5373 | 1.7908 | 3250000 | 0.036797
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 58199.5373 | 1.7908 | 3250000 | 0.036797
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 52599.9937 | 0.32485 | 16192000 | 0.036607
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 51604.7342 | 1.5878 | 3250000 | 0.037365
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 47378.0152 | 0.89392 | 5300000 | 0.042453
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 46146.6243 | 1.4199 | 3250000 | 0.037365
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 45745.4594 | 0.86312 | 5300000 | 0.024676
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 44129.3866 | 1.2537 | 3520000 | 0.050954
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 43765.1807 | 0.82576 | 5300000 | 0.028444
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 43633.6559 | 1.7938 | 2432500 | 0.037225
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 42989.8354 | 0.81113 | 5300000 | 0.028444
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 41585.7468 | 0.78464 | 5300000 | 0.042453
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 40744.4649 | 1.2537 | 3250000 | 0.050954
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 40544.1515 | 0.76498 | 5300000 | 0.028444
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 39521.2317 | 1.216 | 3250000 | 0.037365
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 39318.0993 | 1.3238 | 2970000 | 0.053887
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 39172.6076 | 1.2053 | 3250000 | 0.037365
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 39170.1819 | 1.2052 | 3250000 | 0.037365
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 38149.4925 | 1.1738 | 3250000 | 0.037365
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 37764.1759 | 1.7166 | 2200000 | 0.030423
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 36525.9014 | 1.1239 | 3250000 | 0.050954
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 35767.8699 | 1.1005 | 3250000 | 0.037365
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 34837.8331 | 1.0719 | 3250000 | 0.037365
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 32818.0835 | 1.0098 | 3250000 | 0.037365
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 32788.3552 | 1.4256 | 2300000 | 0.10098
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 32062.1098 | 2.3233 | 1380000 | 0.034731
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 31863.8331 | 0.6012 | 5300000 | 0.0044915
GEN-2024-184 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 30641.3657 | 0.57814 | 5300000 | 0.099208
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 30305.97 | 0.93249 | 3250000 | 0.042453
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 29124.518 | 1.3238 | 2200000 | 0.053887
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 24736.4875 | 1.7925 | 1380000 | 0.087762
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CHILD4WT 138 kV | Current Study |  |  | 23487.7707 | 0.96558 | 2432500 | 0.050057
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 23233.5453 | 1.7601 | 1320000 | 0.037224
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 23006.0701 | 0.94578 | 2432500 | 0.043111
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 22800.2601 | 0.93732 | 2432500 | 0.042453
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 22484.1773 | 0.92432 | 2432500 | 0.042453
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 22086.4472 | 1.6005 | 1380000 | 0.036797
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 21978.3706 | 0.41469 | 5300000 | 0.036607
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 21652.4594 | 1.569 | 1380000 | 0.037365
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 20064.9274 | 0.16721 | 12000000 | 0.023379
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520854 CIVIT 4 138 782580 G24-187-TAP 138 1 | Current Study | 0.12 | (265.00, 265.00) | 19085.8905 | 13.2541 | 144000 | 0.11332
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 17813.649 | 1.2908 | 1380000 | 0.037365
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514947 CANADN-4 138 766111 G21-088-TAP 138 1 | Current Study | 0.3 | (395.00, 395.00) | 16631.9397 | 4.62 | 360000 | 0.039796
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 15127.8805 | 1.0962 | 1380000 | 0.038482
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 14864.4679 | 1.0771 | 1380000 | 0.042453
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 13927.9035 | 0.26279 | 5300000 | 0.037823
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 10386.7833 | 0.46946 | 2212500 | 0.023844
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 10070.484 | 0.45516 | 2212500 | 0.023844
GEN-2024-184 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 5360.0537 | 0.32485 | 1650000 | 0.036607
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 24632949.5152 | 1.6263 | 1514620000 | 0.050264
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 21580874.8911 | 2.0098 | 1073760000 | 0.17301
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 21255503.2125 | 1.654 | 1285130000 | 0.26193
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 21042268.9899 | 1.6547 | 1271630000 | 0.17125
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1 | Current Study | 52.45 | (1046.00, 1046.00) | 15129611.0047 | 15.182 | 99655000 | 0.50353
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 12930844.0885 | 1.378 | 938400000 | 0.11747
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 11415011.2009 | 1.2164 | 938400000 | 0.18353
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527597 TWEEDY 3 115 527798 EDDY_NTH 3 115 1 | Current Study | 44.83 | (394.00, 394.00) | 11299555.8538 | 25.2053 | 44830000 | 0.24357
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 11105772.6678 | 1.5323 | 724760000 | 0.18267
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 7821702.5209 | 1.6199 | 482840000 | 0.20688
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 7726690.1492 | 2.1082 | 366500000 | 0.069633
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 7648160.3733 | 1.6296 | 469340000 | 0.13985
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3 | Current Study | 39.39 | (478.00, 544.00) | 5198610.4111 | 4.9194 | 105675000 | 0.084486
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528095 7-RIVERS 6 230 528179 PECOS 6 230 1 | Current Study | 20.61 | (386.00, 386.00) | 4926707.4357 | 12.5813 | 39159000 | 0.097694
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527799 EDDY_NORTH 6 230 528095 7-RIVERS 6 230 1 | Current Study | 24.1 | (386.00, 386.00) | 4715417.0239 | 10.2979 | 45790000 | 0.080666
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524875 OASIS 6 230 787680 G24-357-TAP 230 1 | Current Study | 26.02 | (901.00, 901.00) | 4533374.6354 | 9.1698 | 49438000 | 0.25182
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Current Study | 54.58 | (637.00, 637.00) | 3838741.8384 | 3.7017 | 103702000 | 0.043195
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524885 SN_JUAN_SS 6 230 787680 G24-357-TAP 230 1 | Current Study | 20.18 | (901.00, 901.00) | 3515891.6273 | 9.1698 | 38342000 | 0.25182
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 527796 EDDY_TR 1 13 527799 EDDY_NORTH 6 230 527802 EDDY_CNTY 7 345 M2 | Current Study |  | (516.00, 558.00) | 3231687.7201 | 12.9268 | 25000000 | 0.21545
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527482 CHAVES_CNTY3 115 527546 SAMSON 3 115 1 | Current Study | 7.78 | (217.00, 217.00) | 2539839.0021 | 32.6457 | 7780000 | 0.29986
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1507499.6892 | 1.784 | 84500000 | 0.05505
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527522 ROSWELL_CTY3 115 527534 SW4J795_W 3 115 1 | Current Study | 3.33 | (217.00, 217.00) | 1473013.375 | 44.2346 | 3330000 | 0.31551
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 1298565.7153 | 0.65631 | 197860000 | 0.032599
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1294825.5842 | 1.5323 | 84500000 | 0.18267
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 1287862.3198 | 1.5241 | 84500000 | 0.097371
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1229588.1402 | 0.98506 | 124824000 | 0.064769
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1164568.7481 | 0.58665 | 198511000 | 0.031517
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1 | Current Study | 9.6 | (901.00, 901.00) | 980436.5626 | 5.3752 | 18240000 | 0.18094
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 932133.4083 | 0.56472 | 165062000 | 0.03571
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 524872 OASIS_TR1 1 13 524874 OASIS 3 115 524875 OASIS 6 230 M2 | Current Study |  | (239.00, 239.00) | 911573.1902 | 6.6056 | 13800000 | 0.017166
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 858339.235 | 1.5544 | 55220000 | 0.076199
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 850556.3186 | 1.0438 | 81488000 | 0.069654
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 699137.5762 | 2.6383 | 26500000 | 0.041672
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528013 PHANTOM 3 115 528228 WOOD_DRAW 3 115 1 | Current Study | 7.71 | (260.00, 260.00) | 661648.8074 | 8.5817 | 7710000 | 0.012601
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 661587.4438 | 1.5219 | 43472000 | 0.046615
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1 | Current Study | 2.49 | (394.00, 394.00) | 627613.0733 | 25.2053 | 2490000 | 0.24357
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528016 SAND_DUNES 3 115 528018 RED_BLUFF 3 115 1 | Current Study | 7.69 | (394.00, 394.00) | 530500.593 | 6.8986 | 7690000 | 0.03695
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 356627.537 | 1.4265 | 25000000 | 0.021193
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 356627.537 | 1.4265 | 25000000 | 0.024319
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1 | Current Study | 18.95 | (901.00, 901.00) | 341668.452 | 0.94895 | 36005000 | 0.027855
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 307646.8206 | 1.654 | 18600000 | 0.17125
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 307441.7168 | 1.6529 | 18600000 | 0.26193
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 303376.3603 | 1.6311 | 18600000 | 0.17125
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 303097.5049 | 1.6296 | 18600000 | 0.13985
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 302500.2053 | 1.6263 | 18600000 | 0.050264
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 285014.8623 | 1.5323 | 18600000 | 0.18267
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528018 RED_BLUFF 3 115 528235 WOLFCAMP_TP3 115 1 | Current Study | 7.81 | (598.00, 598.00) | 257899.7299 | 3.3022 | 7810000 | 0.044495
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 528184 SENDERO +3 115 528187 SENDERO_345 345 M2 | Current Study |  | (435.00, 435.00) | 233334.5044 | 1.3889 | 16800000 | 0.0055188
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 231167.2966 | 1.2428 | 18600000 | 0.2405
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 216948.1556 | 1.1664 | 18600000 | 0.11747
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 193660.378 | 1.0412 | 18600000 | 0.18353
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 193660.378 | 1.0412 | 18600000 | 0.18353
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 163641.545 | 0.87979 | 18600000 | 0.11747
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | Current Study | 0.78 | (598.00, 598.00) | 133085.9519 | 2.5149 | 5292000 | 0.035702
GEN-2024-186 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 127779.0551 | 0.70596 | 18100000 | 0.01087
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | Current Study | 0.2 | (598.00, 598.00) | 112665.3561 | 2.5149 | 4480000 | 0.035702
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 91754.342 | 0.56666 | 16192000 | 0.063856
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 84200.5508 | 0.56367 | 14938000 | 0.060339
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 81511.5959 | 0.56367 | 14460953.1406 | 0.060339
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 71973.8768 | 1.0978 | 6556000 | 0.076199
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 71712.0739 | 1.3531 | 5300000 | 0.19474
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1 | Current Study | 2.13 | (598.00, 598.00) | 45112.5149 | 2.118 | 2130000 | 0.023213
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 26305.878 | 0.21922 | 12000000 | 0.030651
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 26207.5834 | 1.8991 | 1380000 | 0.16911
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 25636.7179 | 1.8577 | 1380000 | 0.19474
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 17460.7678 | 0.78919 | 2212500 | 0.032615
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 17047.5321 | 1.2353 | 1380000 | 0.19474
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 13185.7982 | 0.59597 | 2212500 | 0.063856
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 11916.0818 | 0.86348 | 1380000 | 0.0062089
GEN-2024-186 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 10204.6532 | 0.73947 | 1380000 | 0.047043
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 9349.9669 | 0.56666 | 1650000 | 0.063856
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 6497.8204 | 0.29369 | 2212500 | 0.030651
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528184 SENDERO +3 115 528193 BLACKRIVER 3 115 1 | Current Study | 0.25 | (598.00, 598.00) | 5294.8961 | 2.118 | 250000 | 0.023213
GEN-2024-186 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 4123.4367 | 0.2988 | 1380000 | 0.030651
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 521056 STRATFD4 138 782580 G24-187-TAP 138 1 | Current Study | 12.99 | (211.00, 211.00) | 15588000 | 100 | 15588000 | 0.31918
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520854 CIVIT 4 138 521023 PAOLI 4 138 1 | Current Study | 11.15 | (211.00, 211.00) | 10654336.8156 | 79.6288 | 13380000 | 0.68082
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 521014 OILCRTP4 138 521056 STRATFD4 138 1 | Current Study | 7.3 | (211.00, 211.00) | 8760000 | 100 | 8760000 | 0.31918
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520969 LASALLE4 138 520971 LATTAJT4 138 1 | Current Study | 7.1 | (211.00, 211.00) | 8520000 | 100 | 8520000 | 0.31918
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520888 PAYNESW4 138 521023 PAOLI 4 138 1 | Current Study | 12 | (265.00, 265.00) | 7586254.4981 | 52.6823 | 14400000 | 0.3189
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520861 COLE 4 138 520868 CRINER 4 138 1 | Current Study | 10.06 | (211.00, 211.00) | 5559231.1168 | 46.0506 | 12072000 | 0.15378
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520971 LATTAJT4 138 521014 OILCRTP4 138 1 | Current Study | 4.55 | (211.00, 211.00) | 5460000 | 100 | 5460000 | 0.31918
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505598 ALLEN 4 138 505600 TUPELO 4 138 1 | Current Study | 19.4 | (211.00, 211.00) | 4815143.5632 | 20.6836 | 23280000 | 0.056584
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505592 WELEETK4 138 505595 GREASYC4 138 1 | Current Study | 16.28 | (211.00, 211.00) | 4486877.9732 | 22.9672 | 19536000 | 0.056375
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 532803 BURNS 7 345 1 | Current Study | 50.03 | (1793.00, 1793.00) | 4186252.5304 | 3.8034 | 110066000 | 0.039895
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532803 BURNS 7 345 1 | Current Study | 45.5 | (1793.00, 1793.00) | 3807205.4794 | 3.8034 | 100100000 | 0.039895
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505596 EXPLOR 4 138 505598 ALLEN 4 138 1 | Current Study | 14.8 | (211.00, 211.00) | 3671890.8394 | 20.6751 | 17760000 | 0.056375
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520868 CRINER 4 138 520888 PAYNESW4 138 1 | Current Study | 6.54 | (211.00, 211.00) | 3614052.8334 | 46.0506 | 7848000 | 0.15378
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520842 CANADNS4 138 520976 LIL AXE4 138 1 | Current Study | 11.08 | (265.00, 265.00) | 3606356.2681 | 27.1236 | 13296000 | 0.2152
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520973 LEXNGTN4 138 520976 LIL AXE4 138 1 | Current Study | 9.71 | (265.00, 265.00) | 3000624.7552 | 25.752 | 11652000 | 0.2152
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 2243759.3584 | 1.9131 | 117282000 | 0.040461
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 1 | Current Study |  | (1868.00, 1868.00) | 2171507.6965 | 3.5309 | 61500000 | 0.086431
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 2 | Current Study |  | (1868.00, 1868.00) | 2171507.6965 | 3.5309 | 61500000 | 0.086431
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 2168772.6605 | 1.4435 | 150244000 | 0.032876
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505595 GREASYC4 138 505596 EXPLOR 4 138 1 | Current Study | 6.91 | (211.00, 211.00) | 1904442.6778 | 22.9672 | 8292000 | 0.056375
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520400 NOBLE4 138 520975 LIDDELL4 138 1 | Current Study | 5.73 | (265.00, 265.00) | 1604531.657 | 23.3352 | 6876000 | 0.075212
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1310090.9501 | 1.3045 | 100427000 | 0.016838
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1300310.98 | 0.5956 | 218320000 | 0.018471
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 1236311.4916 | 2.2221 | 55638000 | 0.050368
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 1233207.4021 | 1.3712 | 89936000 | 0.016097
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2 | Current Study |  | (478.00, 478.00) | 1208078.1294 | 6.6745 | 18100000 | 0.056129
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1183398.3993 | 1.2394 | 95480000 | 0.050375
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 1088807.7681 | 1.6497 | 66000000 | 0.038109
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1071609.0093 | 0.74523 | 143796000 | 0.037409
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 1051889.1606 | 1.9072 | 55154000 | 0.033801
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 1049788.9026 | 1.2394 | 84700000 | 0.050375
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515178 PARKLN 4 138 515977 LKKONWA4 138 1 | Current Study | 13.56 | (472.00, 472.00) | 956892.4121 | 5.8806 | 16272000 | 0.071491
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 941056.6861 | 2.0989 | 44836000 | 0.049523
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 936665.1447 | 0.47185 | 198511000 | 0.025349
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515044 SEMINOL4 138 515531 VANOSTP4 138 1 | Current Study | 21.55 | (395.00, 395.00) | 875799.4279 | 3.3867 | 25860000 | 0.028211
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 826794.3033 | 0.66237 | 124824000 | 0.043552
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 811357.3436 | 0.41007 | 197860000 | 0.020368
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511425 TUTCONT4 138 514898 CIMARON4 138 1 | Current Study | 14.65 | (395.00, 395.00) | 761362.0366 | 4.3308 | 17580000 | 0.03803
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 710757.955 | 1.1237 | 63250000 | 0.061324
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 697978.9186 | 1.4853 | 46992000 | 0.060459
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514948 CEDARLN4 138 766111 G21-088-TAP 138 1 | Current Study | 2.86 | (395.00, 395.00) | 628872.3636 | 18.3238 | 3432000 | 0.15784
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 617766.3588 | 0.65731 | 93984000 | 0.040992
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 584805.2686 | 0.35429 | 165062000 | 0.022404
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 550796.122 | 0.4143 | 132946000 | 0.012945
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 550028.4307 | 0.67498 | 81488000 | 0.045043
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | Current Study | 13.6 | (1793.00, 1793.00) | 540699.8101 | 1.8072 | 29920000 | 0.034295
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 503497.0055 | 1.9072 | 26400000 | 0.033801
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 492480.2238 | 1.466 | 33594000 | 0.060118
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 776060 G23-204-TAP 345 1 | Current Study | 17.82 | (1793.00, 1793.00) | 444194.1889 | 1.133 | 39204000 | 0.042895
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 443816.2437 | 0.96663 | 45914000 | 0.049111
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 421077.5712 | 1.6084 | 26180000 | 0.018265
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 369807.721 | 1.4404 | 25674000 | 0.05082
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 341165.5648 | 1.3485 | 25300000 | 0.027759
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 294663.6368 | 0.55119 | 53460000 | 0.019996
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 764550 G20-087-TAP 345 1 | Current Study | 14.38 | (1793.00, 1793.00) | 294562.8105 | 0.9311 | 31636000 | 0.031912
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 264029.5073 | 4.9817 | 5300000 | 0.049111
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 260966.9083 | 1.4573 | 17908000 | 0.052266
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 242216.915 | 0.96663 | 25058000 | 0.049111
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 234565.3708 | 1.9039 | 12320000 | 0.041059
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 220784.0383 | 1.8399 | 12000000 | 0.041059
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 220784.0383 | 1.8399 | 12000000 | 0.041059
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 196841.8088 | 1.6403 | 12000000 | 0.041059
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 193982.9353 | 1.2887 | 15053000 | 0.01713
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | Current Study | 8.91 | (2390.00, 2390.00) | 180127.1915 | 0.91892 | 19602000 | 0.031912
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 177716.9764 | 1.481 | 12000000 | 0.050368
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | Current Study | 6.93 | (1793.00, 1793.00) | 172742.1846 | 1.133 | 15246000 | 0.042895
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 171577.2903 | 1.4298 | 12000000 | 0.050375
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 157936.1788 | 1.3161 | 12000000 | 0.031172
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 155040.7984 | 1.292 | 12000000 | 0.066067
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 149569.5886 | 1.2464 | 12000000 | 0.041059
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 149569.5886 | 1.2464 | 12000000 | 0.041059
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 143228.9459 | 1.1936 | 12000000 | 0.040461
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 142335.2273 | 1.1861 | 12000000 | 0.016097
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 142070.2872 | 1.1839 | 12000000 | 0.050368
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 141849.298 | 1.1821 | 12000000 | 0.041059
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 139440.1922 | 1.162 | 12000000 | 0.041059
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 136257.8169 | 1.1355 | 12000000 | 0.031172
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at CENTRTN5 161 kV | Current Study |  |  | 134619.0297 | 4.1421 | 3250000 | 0.026636
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 132933.5436 | 1.1078 | 12000000 | 0.041059
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 131891.1229 | 2.4885 | 5300000 | 0.031172
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 125165.1367 | 2.3616 | 5300000 | 0.031514
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 124992.6781 | 1.0416 | 12000000 | 0.050375
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 122583.9997 | 1.0215 | 12000000 | 0.035005
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | Current Study | 5.97 | (2390.00, 2390.00) | 120691.2832 | 0.91892 | 13134000 | 0.031912
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511501 TUTTLE4 138 511575 LEONARD4 138 1 | Current Study | 2.12 | (395.00, 395.00) | 120081.2616 | 4.7202 | 2544000 | 0.03803
GEN-2024-187 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 116025.9951 | 0.64103 | 18100000 | 0.0098701
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520854 CIVIT 4 138 782580 G24-187-TAP 138 1 | Current Study | 0.12 | (265.00, 265.00) | 114665.5083 | 79.6288 | 144000 | 0.68082
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 94846.7617 | 0.79039 | 12000000 | 0.035005
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 91792.1441 | 1.7319 | 5300000 | 0.050368
GEN-2024-187 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 514959 FOSTER 4 138 515387 NEWDOMI4 138 1 | Current Study | 1.44 | (281.00, 281.00) | 86884.7644 | 5.0281 | 1728000 | 0.024804
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 84891.6383 | 1.6017 | 5300000 | 0.040461
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 83477.9074 | 0.71593 | 11660000 | 0.040992
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 81452.8207 | 1.5368 | 5300000 | 0.040461
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 81005.771 | 1.2274 | 6600000 | 0.050375
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 72655.4191 | 1.3709 | 5300000 | 0.066067
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 70272.7657 | 1.3259 | 5300000 | 0.040992
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 69968.2671 | 0.46839 | 14938000 | 0.05014
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 69773.2151 | 1.0572 | 6600000 | 0.035005
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 69773.2151 | 1.0572 | 6600000 | 0.035005
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 68167.8997 | 1.0328 | 6600000 | 0.040992
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 67733.8219 | 0.46839 | 14460953.1406 | 0.05014
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 66305.1823 | 1.0046 | 6600000 | 0.035005
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514947 CANADN-4 138 766111 G21-088-TAP 138 1 | Current Study | 0.3 | (395.00, 395.00) | 65965.6326 | 18.3238 | 360000 | 0.15784
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | Current Study | 1.06 | (395.00, 395.00) | 60040.6308 | 4.7202 | 1272000 | 0.03803
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 59478.2486 | 1.8301 | 3250000 | 0.035005
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 59478.2486 | 1.8301 | 3250000 | 0.035005
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 58283.4881 | 1.0997 | 5300000 | 0.035005
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 58202.7176 | 0.35945 | 16192000 | 0.040506
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 51618.5176 | 0.97393 | 5300000 | 0.027845
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520400 NOBLE4 138 520842 CANADNS4 138 1 | Current Study | 0.18 | (265.00, 265.00) | 50404.1358 | 23.3352 | 216000 | 0.075212
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 48345.2496 | 1.4875 | 3250000 | 0.035005
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 47963.3166 | 0.90497 | 5300000 | 0.031172
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 47426.922 | 1.9497 | 2432500 | 0.040461
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 47113.5969 | 0.88894 | 5300000 | 0.031172
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 46238.8406 | 1.9009 | 2432500 | 0.086647
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 45747.6673 | 0.86316 | 5300000 | 0.040992
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 44433.313 | 0.83836 | 5300000 | 0.031172
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 44113.8361 | 1.4853 | 2970000 | 0.060459
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 43627.5908 | 1.2394 | 3520000 | 0.050375
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 43231.8876 | 1.3302 | 3250000 | 0.035005
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 41958.0838 | 1.9072 | 2200000 | 0.033801
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CHILD4WT 138 kV | Current Study |  |  | 40656.9399 | 1.6714 | 2432500 | 0.086647
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 40281.1712 | 1.2394 | 3250000 | 0.050375
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 40219.9086 | 0.75887 | 5300000 | 0.041059
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 37024.9715 | 1.1392 | 3250000 | 0.035005
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 36698.3673 | 1.1292 | 3250000 | 0.035005
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 36696.0948 | 1.1291 | 3250000 | 0.035005
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 36110.5759 | 1.1111 | 3250000 | 0.050375
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 35739.8748 | 1.0997 | 3250000 | 0.035005
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 33508.6814 | 1.031 | 3250000 | 0.035005
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 32676.9157 | 1.4853 | 2200000 | 0.060459
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 32637.3881 | 1.0042 | 3250000 | 0.035005
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 31603.7735 | 0.5963 | 5300000 | 0.0044548
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 30745.2109 | 0.94601 | 3250000 | 0.035005
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 29263.0966 | 0.9004 | 3250000 | 0.040992
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 25253.3411 | 1.9131 | 1320000 | 0.040461
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 24319.4104 | 0.45886 | 5300000 | 0.040506
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 22083.0527 | 0.18403 | 12000000 | 0.025731
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 22015.6693 | 0.90506 | 2432500 | 0.040992
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 21710.4633 | 0.89252 | 2432500 | 0.040992
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 20284.8357 | 1.4699 | 1380000 | 0.035005
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 19631.5015 | 0.85354 | 2300000 | 0.060459
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 19119.6552 | 1.3855 | 1380000 | 0.031854
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 16688.4942 | 1.2093 | 1380000 | 0.035005
GEN-2024-187 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 16305.9718 | 0.30766 | 5300000 | 0.052794
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 15683.7371 | 1.1365 | 1380000 | 0.039896
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 15119.5717 | 0.28527 | 5300000 | 0.041059
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 14352.9594 | 1.0401 | 1380000 | 0.040992
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 10274.823 | 0.74455 | 1380000 | 0.036454
GEN-2024-187 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 5930.9835 | 0.35945 | 1650000 | 0.040506
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 22587338.862 | 2.4029 | 940000000 | 0.034123
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 14330394.158 | 7.2189 | 198511000 | 0.24524
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 5772882.2149 | 2.9081 | 198511000 | 0.15623
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | Current Study | 13 | (2390.00, 2390.00) | 5643423.9821 | 19.7323 | 28600000 | 0.62708
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Rebuild line 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | Current Study | 84.86 | (1793.00, 1793.00) | 5608062.9966 | 3.0039 | 186692000 | 0.052651
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Rebuild line 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Current Study | 38.26 | (1793.00, 1793.00) | 1886095.4785 | 2.2408 | 84172000 | 0.054471
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Rebuild line 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Current Study | 37.4 | (1793.00, 1793.00) | 1864066.1745 | 2.2655 | 82280000 | 0.054471
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Current Study | 26.47 | (1793.00, 1793.00) | 1289087.6338 | 2.2136 | 58234000 | 0.038092
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 1238649.2978 | 0.132 | 938400000 | 0.019915
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Rebuild line 523961 POTTER_CO 7 345 784950 G24-266_TAP 345 1 | Current Study | 18.24 | (1793.00, 1793.00) | 1190423.5012 | 2.9666 | 40128000 | 0.052651
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1111426.7627 | 0.50908 | 218320000 | 0.015788
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 876180.6709 | 0.44283 | 197860000 | 0.021995
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 642348.4639 | 0.38916 | 165062000 | 0.024608
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR SVC at GEN-2021-076 345 kV | Current Study |  |  | 539044.3667 | 4.492 | 12000000 | 0.054471
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Add 525 MVAR SVC at SD.LS-LR-MB3 345 kV | Current Study |  |  | 529696.2927 | 4.4141 | 12000000 | 0.17582
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 436355.2661 | 2.9211 | 14938000 | 0.3127
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 433392.8054 | 0.81069 | 53460000 | 0.029409
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 422420.2073 | 2.9211 | 14460953.1406 | 0.3127
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 283262.4402 | 0.61694 | 45914000 | 0.031345
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 154593.1574 | 0.61694 | 25058000 | 0.031345
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 150897.4277 | 1.2575 | 12000000 | 0.17582
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Add 66 MVAR switched shunt at GEN-2021-021 345 kV | Current Study |  |  | 148572.8588 | 2.8033 | 5300000 | 0.0014604
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 132551.773 | 2.501 | 5300000 | 0.086147
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 130203.4815 | 2.4567 | 5300000 | 0.086147
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Add 248 MVAR switched shunt at GEN-2022-015 345 kV | Current Study |  |  | 129635.4908 | 2.446 | 5300000 | 0.17582
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 105562.7097 | 1.9917 | 5300000 | 0.17582
GEN-2024-189 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 104563.2539 | 1.9729 | 5300000 | 0.084314
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | Current Study | 19.2 | (2390.00, 2390.00) | 90108.6315 | 0.21333 | 42240000 | 0.0054782
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | Current Study | 16.04 | (2390.00, 2390.00) | 75278.2525 | 0.21333 | 35288000 | 0.0054782
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MINGO 7 345 kV | Current Study |  |  | 74692.0322 | 1.4093 | 5300000 | 0.054471
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 62996.0164 | 0.38906 | 16192000 | 0.043842
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 58508.7175 | 0.31456 | 18600000 | 0.055448
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 58508.7175 | 0.31456 | 18600000 | 0.055448
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR switched shunt at GEN-2022-075 345 kV | Current Study |  |  | 41108.6983 | 0.77564 | 5300000 | 0.025044
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 40487.8339 | 0.21768 | 18600000 | 0.042123
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Add 7 MVAR switched shunt at G19-030-TAP 345 kV | Current Study |  |  | 33633.0385 | 0.63459 | 5300000 | 0.025044
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Add 0.04 MVAR switched shunt at ELLIS 2 69 kV | Current Study |  |  | 27666.5501 | 2.0048 | 1380000 | 0.17582
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Add 12 MVAR switched shunt at BEELER 3 115 kV | Current Study |  |  | 26003.7335 | 1.1753 | 2212500 | 0.043842
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Add 0.8 MVAR switched shunt at HARBNGR7 345 kV | Current Study |  |  | 25981.1959 | 0.49021 | 5300000 | 0.051131
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at IRS7 115 KV 115 kV | Current Study |  |  | 17160.9425 | 0.77564 | 2212500 | 0.025044
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MED-LDG3 115 kV | Current Study |  |  | 16008.0374 | 0.72353 | 2212500 | 0.025044
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Add 24 MVAR switched shunt at NESSCTY3 115 kV | Current Study |  |  | 14876.9174 | 0.6724 | 2212500 | 0.051131
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Add 40 MVAR switched shunt at SEGNTP 3 115 kV | Current Study |  |  | 13527.1478 | 0.6114 | 2212500 | 0.051131
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 10909.5491 | 0.49309 | 2212500 | 0.025044
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 10839.3157 | 0.48991 | 2212500 | 0.051131
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 10577.3305 | 0.47807 | 2212500 | 0.025044
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 9053.0149 | 0.40918 | 2212500 | 0.043842
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 6878.4961 | 0.49844 | 1380000 | 0.051131
GEN-2024-189 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 6419.431 | 0.38906 | 1650000 | 0.043842
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 36451755.9535 | 3.8778 | 940000000 | 0.043904
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 14327587.5809 | 7.2175 | 198511000 | 0.19548
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Rebuild line 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | Current Study | 84.86 | (1793.00, 1793.00) | 8331372.9247 | 4.4626 | 186692000 | 0.062362
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | Current Study | 21.05 | (1793.00, 1793.00) | 7498967.3919 | 16.193 | 46310000 | 0.34374
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 5492233.0791 | 2.7667 | 198511000 | 0.1185
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | Current Study | 19.2 | (2390.00, 2390.00) | 4904794.9391 | 11.6117 | 42240000 | 0.23774
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | Current Study | 16.04 | (2390.00, 2390.00) | 4097547.4387 | 11.6117 | 35288000 | 0.23774
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Rebuild line 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Current Study | 38.26 | (1793.00, 1793.00) | 2855402.9155 | 3.3923 | 84172000 | 0.065747
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Rebuild line 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Current Study | 37.4 | (1793.00, 1793.00) | 2822052.2503 | 3.4298 | 82280000 | 0.065747
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 2756363.6164 | 1.3931 | 197860000 | 0.055167
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | Current Study | 13 | (2390.00, 2390.00) | 2671354.4025 | 9.3404 | 28600000 | 0.23666
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 1919506.7786 | 1.1629 | 165062000 | 0.058628
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Rebuild line 523961 POTTER_CO 7 345 784950 G24-266_TAP 345 1 | Current Study | 18.24 | (1793.00, 1793.00) | 1768500.4845 | 4.4071 | 40128000 | 0.062362
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Current Study | 26.47 | (1793.00, 1793.00) | 1312213.6283 | 2.2533 | 58234000 | 0.030915
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add 525 MVAR SVC at SD.LS-LR-MB3 345 kV | Current Study |  |  | 1115697.2378 | 9.2975 | 12000000 | 0.29526
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 1108238.5449 | 0.1181 | 938400000 | 0.014206
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 613199.1172 | 1.3355 | 45914000 | 0.054099
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add 66 MVAR switched shunt at GEN-2021-021 345 kV | Current Study |  |  | 611098.5715 | 11.5302 | 5300000 | 0.004789
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 415160.3677 | 2.7792 | 14938000 | 0.23719
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 401902.1705 | 2.7792 | 14460953.1406 | 0.23719
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add 7 MVAR switched shunt at G19-030-TAP 345 kV | Current Study |  |  | 400453.9498 | 7.5557 | 5300000 | 0.23774
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 334659.2211 | 1.3355 | 25058000 | 0.054099
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 317834.6641 | 2.6486 | 12000000 | 0.29526
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add 248 MVAR switched shunt at GEN-2022-015 345 kV | Current Study |  |  | 273050.7292 | 5.1519 | 5300000 | 0.29526
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 222346.3243 | 4.1952 | 5300000 | 0.29526
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 197575.623 | 1.2202 | 16192000 | 0.10963
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 192816.5839 | 0.36067 | 53460000 | 0.010432
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add 5 MVAR switched shunt at SLKHILLS 4 138 kV | Current Study |  |  | 191526.709 | 7.8737 | 2432500 | 0.23719
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MINGO 7 345 kV | Current Study |  |  | 188543.3321 | 3.5574 | 5300000 | 0.10963
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 154193.9722 | 2.9093 | 5300000 | 0.081338
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add 0.5 MVAR switched shunt at RKY_RDG4 138 kV | Current Study |  |  | 144572.4865 | 5.9434 | 2432500 | 0.29526
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR switched shunt at GEN-2022-075 345 kV | Current Study |  |  | 121653.3289 | 2.2953 | 5300000 | 0.059089
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add 6 MVAR switched shunt at REDHLSW4 138 kV | Current Study |  |  | 106647.8163 | 4.3843 | 2432500 | 0.037838
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 81991.3957 | 1.547 | 5300000 | 0.042485
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add 12 MVAR switched shunt at BEELER 3 115 kV | Current Study |  |  | 81555.8605 | 3.6861 | 2212500 | 0.10963
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add 0.9 MVAR switched shunt at GEN-2024-157 138 kV | Current Study |  |  | 68241.7312 | 2.8054 | 2432500 | 0.10963
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 63214.3082 | 2.8571 | 2212500 | 0.23774
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 61004.078 | 0.32798 | 18600000 | 0.046093
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 61004.078 | 0.32798 | 18600000 | 0.046093
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add 0.04 MVAR switched shunt at ELLIS 2 69 kV | Current Study |  |  | 58273.9467 | 4.2227 | 1380000 | 0.29526
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at IRS7 115 KV 115 kV | Current Study |  |  | 50784.5264 | 2.2953 | 2212500 | 0.059089
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MED-LDG3 115 kV | Current Study |  |  | 47372.7244 | 2.1411 | 2212500 | 0.059089
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 45589.3316 | 0.2451 | 18600000 | 0.037815
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add 0.8 MVAR switched shunt at HARBNGR7 345 kV | Current Study |  |  | 42552.5854 | 0.80288 | 5300000 | 0.066766
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 40115.0204 | 2.9069 | 1380000 | 0.23774
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add 40 MVAR switched shunt at SEGNTP 3 115 kV | Current Study |  |  | 36377.4566 | 1.6442 | 2212500 | 0.10963
GEN-2024-193 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 34056.82 | 0.64258 | 5300000 | 0.021894
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 32284.7237 | 1.4592 | 2212500 | 0.059089
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 31301.5862 | 1.4148 | 2212500 | 0.059089
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 28393.0929 | 1.2833 | 2212500 | 0.10963
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add 24 MVAR switched shunt at NESSCTY3 115 kV | Current Study |  |  | 24365.749 | 1.1013 | 2212500 | 0.066766
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 20133.3855 | 1.2202 | 1650000 | 0.10963
GEN-2024-193 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR SVC at GEN-2021-076 345 kV | Current Study |  |  | 832.4842 | 0.0069374 | 12000000 | 6.707e-05
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 36451755.9535 | 3.8778 | 940000000 | 0.043904
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 14327587.5809 | 7.2175 | 198511000 | 0.19548
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Rebuild line 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | Current Study | 84.86 | (1793.00, 1793.00) | 8331372.9247 | 4.4626 | 186692000 | 0.062362
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | Current Study | 21.05 | (1793.00, 1793.00) | 7498967.3919 | 16.193 | 46310000 | 0.34374
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 5492233.0791 | 2.7667 | 198511000 | 0.1185
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | Current Study | 19.2 | (2390.00, 2390.00) | 4904794.9391 | 11.6117 | 42240000 | 0.23774
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | Current Study | 16.04 | (2390.00, 2390.00) | 4097547.4387 | 11.6117 | 35288000 | 0.23774
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Rebuild line 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Current Study | 38.26 | (1793.00, 1793.00) | 2855402.9155 | 3.3923 | 84172000 | 0.065747
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Rebuild line 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Current Study | 37.4 | (1793.00, 1793.00) | 2822052.2503 | 3.4298 | 82280000 | 0.065747
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 2756363.6164 | 1.3931 | 197860000 | 0.055167
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | Current Study | 13 | (2390.00, 2390.00) | 2671354.4025 | 9.3404 | 28600000 | 0.23666
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 1919506.7786 | 1.1629 | 165062000 | 0.058628
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Rebuild line 523961 POTTER_CO 7 345 784950 G24-266_TAP 345 1 | Current Study | 18.24 | (1793.00, 1793.00) | 1768500.4845 | 4.4071 | 40128000 | 0.062362
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Current Study | 26.47 | (1793.00, 1793.00) | 1312213.6283 | 2.2533 | 58234000 | 0.030915
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add 525 MVAR SVC at SD.LS-LR-MB3 345 kV | Current Study |  |  | 1115697.2378 | 9.2975 | 12000000 | 0.29526
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 1108238.5449 | 0.1181 | 938400000 | 0.014206
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 613199.1172 | 1.3355 | 45914000 | 0.054099
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add 66 MVAR switched shunt at GEN-2021-021 345 kV | Current Study |  |  | 611098.5715 | 11.5302 | 5300000 | 0.004789
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 415160.3677 | 2.7792 | 14938000 | 0.23719
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 401902.1705 | 2.7792 | 14460953.1406 | 0.23719
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add 7 MVAR switched shunt at G19-030-TAP 345 kV | Current Study |  |  | 400453.9498 | 7.5557 | 5300000 | 0.23774
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 334659.2211 | 1.3355 | 25058000 | 0.054099
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 317834.6641 | 2.6486 | 12000000 | 0.29526
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add 248 MVAR switched shunt at GEN-2022-015 345 kV | Current Study |  |  | 273050.7292 | 5.1519 | 5300000 | 0.29526
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 222346.3243 | 4.1952 | 5300000 | 0.29526
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 197575.623 | 1.2202 | 16192000 | 0.10963
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 192816.5839 | 0.36067 | 53460000 | 0.010432
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add 5 MVAR switched shunt at SLKHILLS 4 138 kV | Current Study |  |  | 191526.709 | 7.8737 | 2432500 | 0.23719
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MINGO 7 345 kV | Current Study |  |  | 188543.3321 | 3.5574 | 5300000 | 0.10963
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 154193.9722 | 2.9093 | 5300000 | 0.081338
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add 0.5 MVAR switched shunt at RKY_RDG4 138 kV | Current Study |  |  | 144572.4865 | 5.9434 | 2432500 | 0.29526
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR switched shunt at GEN-2022-075 345 kV | Current Study |  |  | 121653.3289 | 2.2953 | 5300000 | 0.059089
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add 6 MVAR switched shunt at REDHLSW4 138 kV | Current Study |  |  | 106647.8163 | 4.3843 | 2432500 | 0.037838
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 81991.3957 | 1.547 | 5300000 | 0.042485
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add 12 MVAR switched shunt at BEELER 3 115 kV | Current Study |  |  | 81555.8605 | 3.6861 | 2212500 | 0.10963
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add 0.9 MVAR switched shunt at GEN-2024-157 138 kV | Current Study |  |  | 68241.7312 | 2.8054 | 2432500 | 0.10963
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 63214.3082 | 2.8571 | 2212500 | 0.23774
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 61004.078 | 0.32798 | 18600000 | 0.046093
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 61004.078 | 0.32798 | 18600000 | 0.046093
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add 0.04 MVAR switched shunt at ELLIS 2 69 kV | Current Study |  |  | 58273.9467 | 4.2227 | 1380000 | 0.29526
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at IRS7 115 KV 115 kV | Current Study |  |  | 50784.5264 | 2.2953 | 2212500 | 0.059089
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MED-LDG3 115 kV | Current Study |  |  | 47372.7244 | 2.1411 | 2212500 | 0.059089
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 45589.3316 | 0.2451 | 18600000 | 0.037815
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add 0.8 MVAR switched shunt at HARBNGR7 345 kV | Current Study |  |  | 42552.5854 | 0.80288 | 5300000 | 0.066766
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 40115.0204 | 2.9069 | 1380000 | 0.23774
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add 40 MVAR switched shunt at SEGNTP 3 115 kV | Current Study |  |  | 36377.4566 | 1.6442 | 2212500 | 0.10963
GEN-2024-194 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 34056.82 | 0.64258 | 5300000 | 0.021894
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 32284.7237 | 1.4592 | 2212500 | 0.059089
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 31301.5862 | 1.4148 | 2212500 | 0.059089
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 28393.0929 | 1.2833 | 2212500 | 0.10963
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add 24 MVAR switched shunt at NESSCTY3 115 kV | Current Study |  |  | 24365.749 | 1.1013 | 2212500 | 0.066766
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 20133.3855 | 1.2202 | 1650000 | 0.10963
GEN-2024-194 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR SVC at GEN-2021-076 345 kV | Current Study |  |  | 832.4842 | 0.0069374 | 12000000 | 6.707e-05
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505600 TUPELO 4 138 505602 S BROWN4 138 1 | Current Study | 36.9 | (281.00, 281.00) | 8282975.2843 | 18.7059 | 44280000 | 0.24182
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515150 CANEYCK4 138 515151 LTLCITY4 138 1 | Current Study | 11.79 | (265.00, 265.00) | 3816127.2963 | 26.9729 | 14148000 | 0.29099
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520939 HLDTNTP4 138 520981 LOCO 4 138 1 | Current Study | 12.85 | (211.00, 211.00) | 2815752.4746 | 18.2604 | 15420000 | 0.050109
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505598 ALLEN 4 138 505600 TUPELO 4 138 1 | Current Study | 19.4 | (211.00, 211.00) | 2321967.3997 | 9.9741 | 23280000 | 0.054299
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505592 WELEETK4 138 505595 GREASYC4 138 1 | Current Study | 16.28 | (211.00, 211.00) | 2163332.5733 | 11.0736 | 19536000 | 0.05409
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515151 LTLCITY4 138 515157 BROWN 4 138 1 | Current Study | 6.37 | (265.00, 265.00) | 2061809.2347 | 26.9729 | 7644000 | 0.29099
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505596 EXPLOR 4 138 505598 ALLEN 4 138 1 | Current Study | 14.8 | (211.00, 211.00) | 1770389.3679 | 9.9684 | 17760000 | 0.05409
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1 | Current Study | 56.1 | (1793.00, 1793.00) | 1599897.0693 | 1.2963 | 123420000 | 0.037185
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 1 | Current Study |  | (1868.00, 1868.00) | 1171363.5043 | 1.9047 | 61500000 | 0.09278
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 2 | Current Study |  | (1868.00, 1868.00) | 1171363.5043 | 1.9047 | 61500000 | 0.09278
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 1057068.0038 | 0.9013 | 117282000 | 0.037932
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 1029053.9776 | 0.68492 | 150244000 | 0.031043
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515044 SEMINOL4 138 515531 VANOSTP4 138 1 | Current Study | 21.55 | (395.00, 395.00) | 938945.3738 | 3.6309 | 25860000 | 0.060188
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505595 GREASYC4 138 505596 EXPLOR 4 138 1 | Current Study | 6.91 | (211.00, 211.00) | 918220.3981 | 11.0736 | 8292000 | 0.05409
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 840257.1641 | 0.74495 | 112794000 | 0.1269
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1 | Current Study | 30.63 | (1793.00, 1793.00) | 766378.1652 | 1.1373 | 67386000 | 0.037243
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 678306.8239 | 1.0724 | 63250000 | 0.11646
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515178 PARKLN 4 138 515977 LKKONWA4 138 1 | Current Study | 13.56 | (472.00, 472.00) | 664072.2262 | 4.0811 | 16272000 | 0.098732
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520918 FROGVIL4 138 520948 HUGO PP4 138 1 | Current Study | 6.55 | (717.00, 717.00) | 657382.0099 | 8.3636 | 7860000 | 0.14407
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515117 ARBUCKL4 138 515531 VANOSTP4 138 1 | Current Study | 18.2 | (472.00, 472.00) | 651092.1326 | 2.9812 | 21840000 | 0.058793
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520918 FROGVIL4 138 773820 G23-092-TAP 138 1 | Current Study | 6.3 | (717.00, 717.00) | 632291.0935 | 8.3636 | 7560000 | 0.14407
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 618991.2166 | 0.68826 | 89936000 | 0.016078
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 615934.613 | 0.28212 | 218320000 | 0.017411
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 608414.8452 | 0.60583 | 100427000 | 0.015561
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 593600.6668 | 0.6217 | 95480000 | 0.050284
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 581340.9367 | 1.0449 | 55638000 | 0.047131
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | Current Study | 13.16 | (395.00, 395.00) | 560156.3375 | 3.5471 | 15792000 | 0.070064
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 545970.5685 | 0.82723 | 66000000 | 0.038027
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 526581.2367 | 0.6217 | 84700000 | 0.050284
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 511727.2858 | 0.35587 | 143796000 | 0.035549
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 488605.0528 | 0.88589 | 55154000 | 0.031245
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 764550 G20-087-TAP 345 1 | Current Study | 14.38 | (1793.00, 1793.00) | 449266.615 | 1.4201 | 31636000 | 0.096857
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 776060 G23-204-TAP 345 1 | Current Study | 17.82 | (1793.00, 1793.00) | 446358.5589 | 1.1386 | 39204000 | 0.085777
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 430791.4057 | 0.21701 | 198511000 | 0.023201
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 422231.6496 | 0.94172 | 44836000 | 0.044218
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 384547.7865 | 0.19435 | 197860000 | 0.019211
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515133 BLUERIV4 138 515178 PARKLN 4 138 1 | Current Study | 12.7 | (395.00, 395.00) | 382427.4411 | 2.5094 | 15240000 | 0.033414
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 378773.3792 | 0.30345 | 124824000 | 0.039704
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520854 CIVIT 4 138 521023 PAOLI 4 138 1 | Current Study | 11.15 | (211.00, 211.00) | 340322.0848 | 2.5435 | 13380000 | 0.043276
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 337866.5685 | 0.71899 | 46992000 | 0.05824
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | Current Study | 13.6 | (1793.00, 1793.00) | 323230.4258 | 1.0803 | 29920000 | 0.040798
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 313193.9588 | 0.33324 | 93984000 | 0.041356
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515117 ARBUCKL4 138 515133 BLUERIV4 138 1 | Current Study | 10.35 | (395.00, 395.00) | 311663.3083 | 2.5094 | 12420000 | 0.033414
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 277515.3792 | 0.16813 | 165062000 | 0.021157
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | Current Study | 8.91 | (2390.00, 2390.00) | 274729.6356 | 1.4015 | 19602000 | 0.096857
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 265331.2393 | 1.0335 | 25674000 | 0.072561
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | Current Study | 7.74 | (1793.00, 1793.00) | 260530.2659 | 1.53 | 17028000 | 0.085777
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 260232.8958 | 0.19574 | 132946000 | 0.012171
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 | Current Study | 6.08 | (395.00, 395.00) | 258795.6331 | 3.5471 | 7296000 | 0.070064
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 255379.1148 | 0.76019 | 33594000 | 0.062037
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 251570.6402 | 0.30872 | 81488000 | 0.040998
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 233875.5737 | 0.88589 | 26400000 | 0.031245
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 201862.0699 | 0.77105 | 26180000 | 0.017425
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 197603.7297 | 0.43038 | 45914000 | 0.043514
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 188029.4068 | 1.05 | 17908000 | 0.07494
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | Current Study | 5.97 | (2390.00, 2390.00) | 184078.106 | 1.4015 | 13134000 | 0.096857
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | Current Study | 6.93 | (1793.00, 1793.00) | 173583.884 | 1.1386 | 15246000 | 0.085777
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 170022.0168 | 0.67202 | 25300000 | 0.02753
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 135048.2774 | 1.1254 | 12000000 | 0.033478
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 128993.6207 | 0.24129 | 53460000 | 0.017419
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 117555.8808 | 2.218 | 5300000 | 0.043513
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 110614.4702 | 0.89784 | 12320000 | 0.038531
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 107844.1055 | 0.43038 | 25058000 | 0.043514
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 104115.5749 | 0.86763 | 12000000 | 0.038531
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 104115.5749 | 0.86763 | 12000000 | 0.038531
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 92825.0894 | 0.77354 | 12000000 | 0.038531
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 90080.0004 | 0.59842 | 15053000 | 0.01583
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 86064.314 | 0.7172 | 12000000 | 0.050284
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 83566.3551 | 0.69639 | 12000000 | 0.047131
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514948 CEDARLN4 138 766111 G21-088-TAP 138 1 | Current Study | 2.86 | (395.00, 395.00) | 75328.1663 | 2.1949 | 3432000 | 0.037623
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 74389.7259 | 0.61991 | 12000000 | 0.029218
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 73520.4077 | 0.61267 | 12000000 | 0.062344
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 71443.1329 | 0.59536 | 12000000 | 0.016079
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 70532.833 | 0.58777 | 12000000 | 0.038531
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 70532.833 | 0.58777 | 12000000 | 0.038531
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 67477.2584 | 0.56231 | 12000000 | 0.037933
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 66892.16 | 0.55743 | 12000000 | 0.038531
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 66804.5131 | 0.5567 | 12000000 | 0.047131
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 65756.0931 | 0.54797 | 12000000 | 0.038531
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 64178.9724 | 0.53482 | 12000000 | 0.029218
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 63946.0663 | 0.53288 | 12000000 | 0.036338
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 62697.1616 | 0.52248 | 12000000 | 0.050284
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 62687.7397 | 0.5224 | 12000000 | 0.038531
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 62122.2101 | 1.1721 | 5300000 | 0.029218
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 58260.9578 | 1.0993 | 5300000 | 0.029191
GEN-2024-204 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 57264.9563 | 0.31638 | 18100000 | 0.0096941
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 55112.719 | 0.83504 | 6600000 | 0.034723
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 54405.2129 | 1.0265 | 5300000 | 0.033478
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 49476.9083 | 0.41231 | 12000000 | 0.036338
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 43162.6458 | 0.81439 | 5300000 | 0.047131
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 42321.4633 | 0.36296 | 11660000 | 0.041356
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 40633.0354 | 0.61565 | 6600000 | 0.050284
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 39993.6967 | 0.7546 | 5300000 | 0.037933
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 38373.6192 | 0.72403 | 5300000 | 0.037933
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 36397.2676 | 0.55147 | 6600000 | 0.036338
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 36397.2676 | 0.55147 | 6600000 | 0.036338
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 35626.7277 | 0.6722 | 5300000 | 0.041356
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 34588.1648 | 0.52406 | 6600000 | 0.036338
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 34559.6075 | 0.52363 | 6600000 | 0.041356
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 34453.2283 | 0.65006 | 5300000 | 0.062344
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 32100.4104 | 0.21489 | 14938000 | 0.045777
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 31075.2798 | 0.21489 | 14460953.1406 | 0.045777
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 31026.888 | 0.95467 | 3250000 | 0.036338
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 31026.888 | 0.95467 | 3250000 | 0.036338
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 30403.64 | 0.57365 | 5300000 | 0.036338
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 27598.1602 | 0.84917 | 3250000 | 0.034723
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 27598.1602 | 0.84917 | 3250000 | 0.034723
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 27546.7272 | 0.17013 | 16192000 | 0.03815
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 25219.3479 | 0.77598 | 3250000 | 0.036338
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 23635.9227 | 0.44596 | 5300000 | 0.025372
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 | Current Study | 0.55 | (395.00, 395.00) | 23410.7892 | 3.5471 | 660000 | 0.070064
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 23193.0488 | 0.4376 | 5300000 | 0.041356
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CHILD4WT 138 kV | Current Study |  |  | 22838.0043 | 0.93887 | 2432500 | 0.096857
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 22591.2644 | 0.42625 | 5300000 | 0.029218
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 22551.9575 | 0.69391 | 3250000 | 0.036338
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 22343.519 | 0.91854 | 2432500 | 0.037933
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 22191.0368 | 0.4187 | 5300000 | 0.029218
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 21883.8956 | 0.6217 | 3520000 | 0.050284
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 21353.9264 | 0.71899 | 2970000 | 0.05824
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 20928.5928 | 0.39488 | 5300000 | 0.029218
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 20357.5488 | 0.3841 | 5300000 | 0.041356
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 20205.3044 | 0.6217 | 3250000 | 0.050284
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 19489.6311 | 0.88589 | 2200000 | 0.031245
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 19314.1135 | 0.59428 | 3250000 | 0.036338
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 19143.7401 | 0.58904 | 3250000 | 0.036338
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 19142.5546 | 0.589 | 3250000 | 0.036338
GEN-2024-204 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 19141.9624 | 0.36117 | 5300000 | 0.12333
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 18643.7415 | 0.57365 | 3250000 | 0.036338
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 18113.3059 | 0.55733 | 3250000 | 0.050284
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 18104.1955 | 0.74426 | 2432500 | 0.067512
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 17974.1346 | 1.3025 | 1380000 | 0.1269
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 17479.8372 | 0.53784 | 3250000 | 0.036338
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 17025.3262 | 0.52386 | 3250000 | 0.036338
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 16038.2701 | 0.49349 | 3250000 | 0.036338
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 15819.7712 | 0.68782 | 2300000 | 0.096953
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 15817.7232 | 0.71899 | 2200000 | 0.05824
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 15559.8291 | 0.29358 | 5300000 | 0.0043646
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 15530.5519 | 1.1254 | 1380000 | 0.033478
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 14835.7385 | 0.45648 | 3250000 | 0.041356
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 11897.2201 | 0.9013 | 1320000 | 0.037932
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 11510.118 | 0.21717 | 5300000 | 0.03815
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 11161.4542 | 0.45885 | 2432500 | 0.041356
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 11006.7216 | 0.45249 | 2432500 | 0.041356
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 10581.6049 | 0.76678 | 1380000 | 0.036338
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 10473.3703 | 0.75894 | 1380000 | 0.034723
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 10412.6199 | 0.086772 | 12000000 | 0.024144
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 8705.5697 | 0.63084 | 1380000 | 0.036338
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514947 CANADN-4 138 766111 G21-088-TAP 138 1 | Current Study | 0.3 | (395.00, 395.00) | 7901.5559 | 2.1949 | 360000 | 0.037623
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 7512.3167 | 0.54437 | 1380000 | 0.038028
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 7276.6309 | 0.52729 | 1380000 | 0.041356
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 7129.967 | 0.13453 | 5300000 | 0.038531
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 5182.3121 | 0.23423 | 2212500 | 0.023674
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 5024.4999 | 0.2271 | 2212500 | 0.023674
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520854 CIVIT 4 138 782580 G24-187-TAP 138 1 | Current Study | 0.12 | (265.00, 265.00) | 3662.6592 | 2.5435 | 144000 | 0.043276
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 2807.0714 | 0.17013 | 1650000 | 0.03815
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 530582 S HAYS6 230 539679 GRTBEND6 230 1 | Current Study | 39.2 | (386.00, 386.00) | 12276458.1973 | 16.4829 | 74480000 | 0.14262
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 530618 HUNTSVL3 115 530624 ST JOHN3 115 1 | Current Study | 26.5 | (297.00, 297.00) | 8322439.888 | 31.4054 | 26500000 | 0.28469
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | Current Study | 14.69 | (260.00, 260.00) | 5570671.3313 | 37.9215 | 14690000 | 0.43073
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 539642 ELLSWTP3 115 539678 GRTBEND3 115 1 | Current Study | 30.21 | (115.00, 115.00) | 5326905.6443 | 17.6329 | 30210000 | 0.046472
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 | Current Study | 21.74 | (386.00, 386.00) | 5109551.6064 | 12.37 | 41306000 | 0.087381
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 530618 HUNTSVL3 115 530724 CENTENNIAL3 115 1 | Current Study | 12.45 | (297.00, 297.00) | 3909976.4757 | 31.4054 | 12450000 | 0.28469
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | Current Study | 13.1 | (297.00, 297.00) | 3877929.0924 | 29.6025 | 13100000 | 0.3455
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 3788901.9366 | 1.9087 | 198511000 | 0.083246
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 530724 CENTENNIAL3 115 533412 ARKVALJ3 115 1 | Current Study | 10.96 | (297.00, 297.00) | 3442035.5159 | 31.4054 | 10960000 | 0.28469
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 539649 SAWYER 3 115 539760 BARBER 3 115 1 | Current Study | 19 | (598.00, 598.00) | 2730233.9147 | 14.3697 | 19000000 | 0.28457
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 539666 GBENDTP3 115 539678 GRTBEND3 115 1 | Current Study | 7.21 | (176.00, 176.00) | 2134344.8944 | 29.6026 | 7210000 | 0.22346
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 530565 SEWARD 2 69 530569 GB STH 2 69 1 | Current Study | 8.56 | (69.00, 69.00) | 2005169.593 | 27.5587 | 7276000 | 0.048929
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1901512.9058 | 0.87098 | 218320000 | 0.034678
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1732833.2284 | 1.2051 | 143796000 | 0.077663
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 1665040.0029 | 0.17743 | 938400000 | 0.03437
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 533412 ARKVALJ3 115 533413 CIRCLE 3 115 1 | Current Study | 5.2 | (297.00, 297.00) | 1633082.5441 | 31.4054 | 5200000 | 0.28469
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 539638 FLATRDG4 138 539674 BARBER 4 138 1 | Current Study | 8.92 | (472.00, 472.00) | 1544777.2709 | 14.4318 | 10704000 | 0.25731
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 539674 BARBER 4 138 539760 BARBER 3 115 539917 BARBER-1 13 M2 | Current Study |  | (324.00, 324.00) | 1500904.6728 | 14.4318 | 10400000 | 0.12866
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1455715.5499 | 0.73332 | 198511000 | 0.05058
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild 3-winding transformer 530565 SEWARD 2 69 530631 SWRD1 1 12 530679 SEWRDMW3 115 1 | Current Study |  | (87.00, 87.00) | 1305431.4472 | 27.6282 | 4725000 | 0.085229
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Current Study | 26.47 | (1793.00, 1793.00) | 1300848.848 | 2.2338 | 58234000 | 0.049352
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Current Study | 38.26 | (1793.00, 1793.00) | 1086595.8431 | 1.2909 | 84172000 | 0.04029
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Current Study | 37.4 | (1793.00, 1793.00) | 1073904.5714 | 1.3052 | 82280000 | 0.04029
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 533413 CIRCLE 3 115 533416 RENO 3 115 2 | Current Study | 5.95 | (217.00, 217.00) | 1018351.4061 | 17.1151 | 5950000 | 0.12613
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 539668 HARPER 4 138 539881 SPRVLSTR 138 1 | Current Study | 12.1 | (281.00, 281.00) | 750059.6191 | 5.1657 | 14520000 | 0.030821
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 539009 CONWAY 4 138 539881 SPRVLSTR 138 1 | Current Study | 10.66 | (281.00, 281.00) | 660796.3256 | 5.1657 | 12792000 | 0.030821
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | Current Study | 19.2 | (2390.00, 2390.00) | 638929.9894 | 1.5126 | 42240000 | 0.049871
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 602131.7219 | 1.1263 | 53460000 | 0.052459
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | Current Study | 16.04 | (2390.00, 2390.00) | 533772.762 | 1.5126 | 35288000 | 0.049871
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 523961 POTTER_CO 7 345 784950 G24-266_TAP 345 1 | Current Study | 18.24 | (1793.00, 1793.00) | 498890.1953 | 1.2432 | 40128000 | 0.028329
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 463749.1433 | 0.23438 | 197860000 | 0.014947
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | Current Study | 16.71 | (1793.00, 1793.00) | 385509.5985 | 1.0487 | 36762000 | 0.037873
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 376940.4818 | 0.22836 | 165062000 | 0.01854
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 367601.6734 | 0.80063 | 45914000 | 0.052225
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 533075 VIOLA 4 138 539009 CONWAY 4 138 1 | Current Study | 5.62 | (281.00, 281.00) | 348374.7983 | 5.1657 | 6744000 | 0.030821
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | Current Study | 13 | (2390.00, 2390.00) | 347987.7266 | 1.2167 | 28600000 | 0.049644
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Add 45 MVAR switched shunt at HUNTSVL3 115 kV | Current Study |  |  | 318046.8924 | 14.375 | 2212500 | 0.28469
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Add 63 MVAR switched shunt at SADLHRN3 115 kV | Current Study |  |  | 317936.5024 | 14.37 | 2212500 | 0.28458
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Add 21 MVAR switched shunt at LARNED3 115 kV | Current Study |  |  | 317929.2773 | 14.3697 | 2212500 | 0.28457
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR SVC at GEN-2021-076 345 kV | Current Study |  |  | 310546.5239 | 2.5879 | 12000000 | 0.04029
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 200622.092 | 0.80063 | 25058000 | 0.052225
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 107673.3243 | 0.7208 | 14938000 | 0.099063
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 104234.7635 | 0.7208 | 14460953.1406 | 0.099063
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 94724.8822 | 1.7873 | 5300000 | 0.079039
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 93046.7331 | 1.7556 | 5300000 | 0.079039
GEN-2024-205 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 82759.1261 | 1.5615 | 5300000 | 0.085675
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 73526.1075 | 0.61272 | 12000000 | 0.10999
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 73267.7347 | 1.3824 | 5300000 | 0.029087
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Add 66 MVAR switched shunt at GEN-2021-021 345 kV | Current Study |  |  | 70531.7247 | 1.3308 | 5300000 | 0.00089008
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Add 7 MVAR switched shunt at G19-030-TAP 345 kV | Current Study |  |  | 52167.125 | 0.98429 | 5300000 | 0.049872
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Add 248 MVAR switched shunt at GEN-2022-015 345 kV | Current Study |  |  | 45390.8387 | 0.85643 | 5300000 | 0.079039
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 44081.4616 | 0.237 | 18600000 | 0.053634
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 44081.4616 | 0.237 | 18600000 | 0.053634
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 37439.1672 | 1.6922 | 2212500 | 0.070187
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 36961.9454 | 0.6974 | 5300000 | 0.079039
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 32947.9254 | 0.20348 | 16192000 | 0.029439
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 530624 ST JOHN3 115 539696 ST-JOHN3 115 Z1 | Current Study | 0.1 | (326.00, 326.00) | 31405.4335 | 31.4054 | 100000 | 0.28469
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 25731.3854 | 0.13834 | 18600000 | 0.03437
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Add 0.8 MVAR switched shunt at HARBNGR7 345 kV | Current Study |  |  | 24982.0064 | 0.47136 | 5300000 | 0.06312
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR switched shunt at GEN-2022-075 345 kV | Current Study |  |  | 23423.8189 | 0.44196 | 5300000 | 0.018321
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MED-LDG3 115 kV | Current Study |  |  | 13568.559 | 0.61327 | 2212500 | 0.027254
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at IRS7 115 KV 115 kV | Current Study |  |  | 9778.3395 | 0.44196 | 2212500 | 0.018321
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 6216.283 | 0.28096 | 2212500 | 0.018321
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 6026.9842 | 0.27241 | 2212500 | 0.018321
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 3357.4652 | 0.20348 | 1650000 | 0.029439
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 1770.76 | 0.10732 | 1650000 | 0.0083946
GEN-2024-206 | 03 CENTRAL | TBD | ERIS | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1 | Current Study | 6.85 | (837.00, 837.00) | 2333777.3429 | 22.7132 | 10275000 | 0.514
GEN-2024-206 | 03 CENTRAL | TBD | ERIS | Rebuild line 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | Current Study | 6.5 | (837.00, 837.00) | 2166546.198 | 22.221 | 9750000 | 0.3931
GEN-2024-206 | 03 CENTRAL | TBD | ERIS | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | Current Study | 4.5 | (837.00, 837.00) | 1499916.5986 | 22.221 | 6750000 | 0.3931
GEN-2024-206 | 03 CENTRAL | TBD | ERIS | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | Current Study | 4.34 | (837.00, 837.00) | 1478732.0116 | 22.7148 | 6510000 | 0.52526
GEN-2024-206 | 03 CENTRAL | TBD | ERIS | Rebuild 2-winding transformer 548814 SUB M-161 161 548815 SUB M 69 1 | Current Study |  | (139.00, 139.00) | 1384417.2552 | 22.7888 | 6075000 | 0.011264
GEN-2024-206 | 03 CENTRAL | TBD | ERIS | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | Current Study |  | (180.00, 180.00) | 1381120.7402 | 22.7345 | 6075000 | 0.040266
GEN-2024-206 | 03 CENTRAL | TBD | ERIS | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | Current Study |  | (185.00, 185.00) | 1381120.7402 | 22.7345 | 6075000 | 0.041369
GEN-2024-206 | 03 CENTRAL | TBD | ERIS | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | Current Study | 6.07 | (364.00, 364.00) | 1288642.1005 | 14.1531 | 9105000 | 0.10049
GEN-2024-206 | 03 CENTRAL | TBD | ERIS | Rebuild line 548802 SUB H 69 548806 BLUVLY 69 1 | Current Study | 3.8 | (106.00, 106.00) | 734164.7837 | 22.7296 | 3230000 | 0.022414
GEN-2024-206 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 9253.1328 | 0.5608 | 1650000 | 0.030045
GEN-2024-207 | 03 CENTRAL | TBD | ERIS | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1 | Current Study | 6.85 | (837.00, 837.00) | 7941222.6571 | 77.2868 | 10275000 | 0.50835
GEN-2024-207 | 03 CENTRAL | TBD | ERIS | Rebuild line 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | Current Study | 6.5 | (837.00, 837.00) | 7583453.802 | 77.779 | 9750000 | 0.39992
GEN-2024-207 | 03 CENTRAL | TBD | ERIS | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | Current Study | 4.5 | (837.00, 837.00) | 5250083.4014 | 77.779 | 6750000 | 0.39992
GEN-2024-207 | 03 CENTRAL | TBD | ERIS | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | Current Study | 4.34 | (837.00, 837.00) | 5031267.9884 | 77.2852 | 6510000 | 0.51944
GEN-2024-207 | 03 CENTRAL | TBD | ERIS | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | Current Study |  | (180.00, 180.00) | 4693879.2598 | 77.2655 | 6075000 | 0.039775
GEN-2024-207 | 03 CENTRAL | TBD | ERIS | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | Current Study |  | (185.00, 185.00) | 4693879.2598 | 77.2655 | 6075000 | 0.040865
GEN-2024-207 | 03 CENTRAL | TBD | ERIS | Rebuild 2-winding transformer 548814 SUB M-161 161 548815 SUB M 69 1 | Current Study |  | (139.00, 139.00) | 4690582.7448 | 77.2112 | 6075000 | 0.011092
GEN-2024-207 | 03 CENTRAL | TBD | ERIS | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | Current Study | 6.07 | (364.00, 364.00) | 4534724.0435 | 49.8048 | 9105000 | 0.10278
GEN-2024-207 | 03 CENTRAL | TBD | ERIS | Rebuild line 548802 SUB H 69 548806 BLUVLY 69 1 | Current Study | 3.8 | (106.00, 106.00) | 2495835.2163 | 77.2704 | 3230000 | 0.022147
GEN-2024-207 | 03 CENTRAL | TBD | ERIS | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | Current Study | 0.2 | (837.00, 837.00) | 300000 | 100 | 300000 | 0.60008
GEN-2024-207 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 31806.7851 | 1.9277 | 1650000 | 0.030018
GEN-2024-209 | 03 CENTRAL | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 9543235.9572 | 4.3712 | 218320000 | 0.13556
GEN-2024-209 | 03 CENTRAL | TBD | ERIS | Rebuild line 539656 CLIFTON3 115 539657 CONCORD3 115 1 | Current Study | 23.19 | (176.00, 176.00) | 4613267.4409 | 19.8933 | 23190000 | 0.022206
GEN-2024-209 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Current Study | 26.47 | (1793.00, 1793.00) | 3782692.1696 | 6.4957 | 58234000 | 0.11178
GEN-2024-209 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 2717784.3725 | 1.89 | 143796000 | 0.094875
GEN-2024-209 | 03 CENTRAL | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 2263369.4141 | 4.2338 | 53460000 | 0.15359
GEN-2024-209 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 2172629.1739 | 1.0945 | 198511000 | 0.03718
GEN-2024-209 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 2127264.9434 | 0.22669 | 938400000 | 0.034202
GEN-2024-209 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | Current Study | 19.87 | (1793.00, 1793.00) | 1327323.6086 | 3.0364 | 43714000 | 0.052114
GEN-2024-209 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | Current Study | 16.71 | (1793.00, 1793.00) | 926184.732 | 2.5194 | 36762000 | 0.070871
GEN-2024-209 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 765480.6431 | 0.38561 | 198511000 | 0.020716
GEN-2024-209 | 03 CENTRAL | TBD | ERIS | Rebuild line 645458 S3458 3 345 778170 G24-040-TAP 345 1 | Current Study | 13.15 | (1793.00, 1793.00) | 537756.5191 | 1.8588 | 28930000 | 0.028969
GEN-2024-209 | 03 CENTRAL | TBD | ERIS | Rebuild line 640139 COOPER 3 345 778170 G24-040-TAP 345 1 | Current Study | 12.59 | (1793.00, 1793.00) | 514855.8612 | 1.8588 | 27698000 | 0.028969
GEN-2024-209 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 436886.1264 | 0.46485 | 93984000 | 0.02899
GEN-2024-209 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 388527.552 | 0.84621 | 45914000 | 0.042993
GEN-2024-209 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 212042.5883 | 0.84621 | 25058000 | 0.042993
GEN-2024-209 | 03 CENTRAL | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 185248.2583 | 8.3728 | 2212500 | 0.2705
GEN-2024-209 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 65647.2698 | 1.2386 | 5300000 | 0.052934
GEN-2024-209 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 61032.0277 | 0.32813 | 18600000 | 0.057839
GEN-2024-209 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 61032.0277 | 0.32813 | 18600000 | 0.057839
GEN-2024-209 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 59035.8136 | 0.50631 | 11660000 | 0.02899
GEN-2024-209 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 56549.4387 | 0.37856 | 14938000 | 0.040524
GEN-2024-209 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 54743.5254 | 0.37856 | 14460953.1406 | 0.040524
GEN-2024-209 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 32874.57 | 0.17674 | 18600000 | 0.034202
GEN-2024-209 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 13944.184 | 0.8451 | 1650000 | 0.051489
GEN-2024-209 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MED-LDG3 115 kV | Current Study |  |  | 6965.6118 | 0.31483 | 2212500 | 0.010898
GEN-2024-209 | 03 CENTRAL | TBD | ERIS | Add 0.8 MVAR switched shunt at HARBNGR7 345 kV | Current Study |  |  | 3700.0204 | 0.069812 | 5300000 | 0.0072816
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add line 659131 LARAMIE_-MB3 345 800120 UNDERWOOD 2 345 P2 | Current Study | 206.4 | (1792.00, 1792.00) | 41499686.4664 | 6.3861 | 649840000 | 0.024311
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add line 652424 BELFELD3 345 800121 MAURINE 2 345 P2 | Current Study | 154.2 | (1792.00, 1792.00) | 34790013.1365 | 7.1288 | 488020000 | 0.019552
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Rebuild line 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Current Study | 75.83 | (1793.00, 1793.00) | 21737345.0644 | 13.03 | 166826000 | 0.19478
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 16855419.9663 | 1.7931 | 940000000 | 0.033781
GEN-2024-210 | 03 CENTRAL | TBD | NRIS | Rebuild line 640082 BEVERLY7 115 640326 REDWILO7 115 1 | Current Study | 16.08 | (176.00, 176.00) | 16080000 | 100 | 16080000 | 0.013591
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Rebuild line 531357 RULETON3 115 531368 LAWNRID3 115 1 | Current Study | 14.78 | (176.00, 176.00) | 14780000 | 100 | 14780000 | 0.48999
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Rebuild line 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Current Study | 38.26 | (1793.00, 1793.00) | 6558081.8946 | 7.7913 | 84172000 | 0.25127
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Rebuild line 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Current Study | 37.4 | (1793.00, 1793.00) | 6481484.5106 | 7.8774 | 82280000 | 0.25127
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Rebuild line 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | Current Study | 84.86 | (1793.00, 1793.00) | 6288268.445 | 3.3683 | 186692000 | 0.078323
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 6283057.0607 | 4.726 | 132946000 | 0.19591
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 4283697.43 | 2.1579 | 198511000 | 0.097254
GEN-2024-210 | 03 CENTRAL | TBD | NRIS | Rebuild line 640100 CAMBRIG7 115 640269 MCCOOK 7 115 1 | Current Study | 28.11 | (176.00, 176.00) | 3962427.8411 | 14.0962 | 28110000 | 0.023139
GEN-2024-210 | 03 CENTRAL | TBD | NRIS | Rebuild line 640194 GOSPER 7 115 640242 JOHN.2 7 115 1 | Current Study | 24.13 | (176.00, 176.00) | 3401401.0604 | 14.0962 | 24130000 | 0.023139
GEN-2024-210 | 03 CENTRAL | TBD | NRIS | Rebuild line 640326 REDWILO7 115 640365 STOCKVL7 115 1 | Current Study | 21.09 | (176.00, 176.00) | 3185591.9024 | 15.1048 | 21090000 | 0.018981
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 2665902.9853 | 1.3474 | 197860000 | 0.088786
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 531259 SETAB 1 13 531464 SETAB 3 115 531465 SETAB 7 345 M2 | Current Study |  | (280.00, 308.00) | 2520845.5645 | 15.005 | 16800000 | 0.048601
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 2052121.083 | 1.2432 | 165062000 | 0.1043
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR SVC at GEN-2021-076 345 kV | Current Study |  |  | 1874274.3934 | 15.619 | 12000000 | 0.25127
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1431858.4506 | 0.7213 | 198511000 | 0.051409
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | Current Study | 19.2 | (2390.00, 2390.00) | 1401428.107 | 3.3178 | 42240000 | 0.11303
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Rebuild line 523961 POTTER_CO 7 345 784950 G24-266_TAP 345 1 | Current Study | 18.24 | (1793.00, 1793.00) | 1334810.7079 | 3.3264 | 40128000 | 0.078323
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | Current Study | 21.05 | (1793.00, 1793.00) | 1311822.9648 | 2.8327 | 46310000 | 0.10006
GEN-2024-210 | 03 CENTRAL | TBD | NRIS | Rebuild line 640100 CAMBRIG7 115 640194 GOSPER 7 115 1 | Current Study | 8.61 | (176.00, 176.00) | 1213678.5383 | 14.0962 | 8610000 | 0.023139
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Rebuild line 531419 DOBSON 3 115 531493 GANO 3 115 1 | Current Study | 11.92 | (260.00, 260.00) | 1191139.2499 | 9.9928 | 11920000 | 0.022916
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Rebuild line 531432 PILE 3 115 531433 SCOTCTY3 115 1 | Current Study | 11.88 | (260.00, 260.00) | 1187142.1383 | 9.9928 | 11880000 | 0.022916
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | Current Study | 16.04 | (2390.00, 2390.00) | 1170776.3977 | 3.3178 | 35288000 | 0.11303
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Current Study | 26.47 | (1793.00, 1793.00) | 1054357.0696 | 1.8106 | 58234000 | 0.041334
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Rebuild line 531432 PILE 3 115 531493 GANO 3 115 1 | Current Study | 8.34 | (260.00, 260.00) | 833397.7638 | 9.9928 | 8340000 | 0.022916
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | Current Study | 13 | (2390.00, 2390.00) | 763275.7719 | 2.6688 | 28600000 | 0.11252
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 531448 HOLCOMB3 115 531449 HOLCOMB7 345 531450 HOLCTER1 13 M2 | Current Study |  | (336.00, 358.50) | 637293.9586 | 3.7934 | 16800000 | 0.027612
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 526580.8068 | 0.3662 | 143796000 | 0.024387
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add 525 MVAR SVC at SD.LS-LR-MB3 345 kV | Current Study |  |  | 407873.6849 | 3.3989 | 12000000 | 0.17961
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MINGO 7 345 kV | Current Study |  |  | 324235.3918 | 6.1176 | 5300000 | 0.3137
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 219938.9884 | 0.47902 | 45914000 | 0.032288
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2 | Current Study |  | (350.00, 385.00) | 216437.2533 | 1.2883 | 16800000 | 0.015293
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Rebuild line 530605 REDLIN 3 115 786630 G24-322-TAP 115 1 | Current Study | 0.86 | (115.00, 115.00) | 199796.5165 | 23.2322 | 860000 | 0.092549
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 194536.9713 | 1.2014 | 16192000 | 0.17961
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Rebuild line 531405 WALKMYR3 115 531481 HUGOTON3 115 1 | Current Study | 12.27 | (598.00, 598.00) | 187613.5913 | 1.529 | 12270000 | 0.029861
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add 66 MVAR switched shunt at GEN-2021-021 345 kV | Current Study |  |  | 162242.6974 | 3.0612 | 5300000 | 0.0021157
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 159879.2881 | 0.017037 | 938400000 | 0.0034102
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Rebuild line 531433 SCOTCTY3 115 531464 SETAB 3 115 1 | Current Study | 2.77 | (394.00, 394.00) | 130580.7982 | 4.7141 | 2770000 | 0.020961
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR switched shunt at GEN-2022-075 345 kV | Current Study |  |  | 130035.601 | 2.4535 | 5300000 | 0.1051
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 128557.2726 | 1.0713 | 12000000 | 0.19872
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 120033.7843 | 0.47902 | 25058000 | 0.032288
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add 7 MVAR switched shunt at G19-030-TAP 345 kV | Current Study |  |  | 114421.1332 | 2.1589 | 5300000 | 0.11303
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add 248 MVAR switched shunt at GEN-2022-015 345 kV | Current Study |  |  | 110443.136 | 2.0838 | 5300000 | 0.19872
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 108053.7727 | 0.72335 | 14938000 | 0.10273
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 104603.0622 | 0.72335 | 14460953.1406 | 0.10273
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 89934.2969 | 1.6969 | 5300000 | 0.19872
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add 12 MVAR switched shunt at BEELER 3 115 kV | Current Study |  |  | 88846.1809 | 4.0156 | 2212500 | 0.19872
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 531405 WALKMYR3 115 531510 HARBNGR3 115 M2 | Current Study | 1.28 | (598.00, 598.00) | 77195.9537 | 1.2883 | 5992000 | 0.015293
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add 0.8 MVAR switched shunt at HARBNGR7 345 kV | Current Study |  |  | 76114.7496 | 1.4361 | 5300000 | 0.19872
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 70946.0179 | 1.3386 | 5300000 | 0.061171
GEN-2024-210 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 63990.7404 | 1.2074 | 5300000 | 0.068454
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add 60 MVAR switched shunt at WAYSIDE 4 230 kV | Current Study |  |  | 61502.961 | 1.6079 | 3825000 | 0.034542
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at IRS7 115 KV 115 kV | Current Study |  |  | 54283.7297 | 2.4535 | 2212500 | 0.1051
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MED-LDG3 115 kV | Current Study |  |  | 50636.8444 | 2.2887 | 2212500 | 0.1051
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add 24 MVAR switched shunt at NESSCTY3 115 kV | Current Study |  |  | 43583.5534 | 1.9699 | 2212500 | 0.19872
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 43571.5119 | 0.8221 | 5300000 | 0.038246
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add 40 MVAR switched shunt at SEGNTP 3 115 kV | Current Study |  |  | 39629.2562 | 1.7912 | 2212500 | 0.19872
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add 2.3 MVAR switched shunt at GRANT 3 115 kV | Current Study |  |  | 37187.0911 | 1.6808 | 2212500 | 0.029861
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 34697.0493 | 0.18654 | 18600000 | 0.043623
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 34697.0493 | 0.18654 | 18600000 | 0.043623
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 34509.2361 | 1.5597 | 2212500 | 0.1051
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 33458.3576 | 1.5122 | 2212500 | 0.1051
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 31754.9586 | 1.4353 | 2212500 | 0.19872
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 30945.7817 | 0.16638 | 18600000 | 0.042713
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 27956.3348 | 1.2636 | 2212500 | 0.17961
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add 0.04 MVAR switched shunt at ELLIS 2 69 kV | Current Study |  |  | 23570.5557 | 1.708 | 1380000 | 0.19872
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 20151.3051 | 1.4602 | 1380000 | 0.19872
GEN-2024-210 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 19823.7403 | 1.2014 | 1650000 | 0.17961
GEN-2024-210 | 03 CENTRAL | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 7355.7619 | 0.53303 | 1380000 | 0.044986
GEN-2024-211 | 02 NEBRASKA | TBD | ERIS | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1 | Current Study | 20.15 | (1793.00, 1793.00) | 13904751.5528 | 31.3665 | 44330000 | 0.28528
GEN-2024-211 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659202 LO.KVA2_-BE9 13 M2 | Current Study |  | (500.00, 617.00) | 583837.922 | 2.3354 | 25000000 | 0.008484
GEN-2024-211 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659201 LO.KU1A_-BE9 13 M2 | Current Study |  | (600.00, 637.40) | 575814.1282 | 2.3033 | 25000000 | 0.0096187
GEN-2024-212 | 02 NEBRASKA | TBD | ERIS | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1 | Current Study | 20.15 | (1793.00, 1793.00) | 13904751.5528 | 31.3665 | 44330000 | 0.28528
GEN-2024-212 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659202 LO.KVA2_-BE9 13 M2 | Current Study |  | (500.00, 617.00) | 583837.922 | 2.3354 | 25000000 | 0.008484
GEN-2024-212 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659201 LO.KU1A_-BE9 13 M2 | Current Study |  | (600.00, 637.40) | 575814.1282 | 2.3033 | 25000000 | 0.0096187
GEN-2024-213 | 02 NEBRASKA | TBD | ERIS | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1 | Current Study | 20.15 | (1793.00, 1793.00) | 16520496.8944 | 37.2671 | 44330000 | 0.28528
GEN-2024-213 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659202 LO.KVA2_-BE9 13 M2 | Current Study |  | (500.00, 617.00) | 693668.8182 | 2.7747 | 25000000 | 0.008484
GEN-2024-213 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659201 LO.KU1A_-BE9 13 M2 | Current Study |  | (600.00, 637.40) | 684135.5978 | 2.7365 | 25000000 | 0.0096187
GEN-2024-215 | 03 CENTRAL | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 23651831.6901 | 10.8336 | 218320000 | 0.22286
GEN-2024-215 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Current Study | 26.47 | (1793.00, 1793.00) | 9627976.7767 | 16.5333 | 58234000 | 0.18872
GEN-2024-215 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 5036725.5072 | 3.5027 | 143796000 | 0.11663
GEN-2024-215 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 3690059.0703 | 1.8589 | 198511000 | 0.041888
GEN-2024-215 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 3156284.6106 | 0.33635 | 938400000 | 0.033662
GEN-2024-215 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | Current Study | 19.87 | (1793.00, 1793.00) | 2896576.6417 | 6.6262 | 43714000 | 0.075438
GEN-2024-215 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | Current Study | 16.71 | (1793.00, 1793.00) | 2236887.9266 | 6.0848 | 36762000 | 0.11354
GEN-2024-215 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1299809.5157 | 0.65478 | 198511000 | 0.023334
GEN-2024-215 | 03 CENTRAL | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 1220091.8 | 2.2823 | 53460000 | 0.05492
GEN-2024-215 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | Current Study | 19.2 | (2390.00, 2390.00) | 609349.2792 | 1.4426 | 42240000 | 0.024574
GEN-2024-215 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 605118.718 | 1.3179 | 45914000 | 0.044417
GEN-2024-215 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | Current Study | 16.04 | (2390.00, 2390.00) | 509060.5437 | 1.4426 | 35288000 | 0.024574
GEN-2024-215 | 03 CENTRAL | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 459643.7816 | 20.7749 | 2212500 | 0.44521
GEN-2024-215 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | Current Study | 13 | (2390.00, 2390.00) | 331876.847 | 1.1604 | 28600000 | 0.024462
GEN-2024-215 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 330249.2668 | 1.3179 | 25058000 | 0.044417
GEN-2024-215 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 101360.4589 | 1.9125 | 5300000 | 0.054215
GEN-2024-215 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 96290.7343 | 0.6446 | 14938000 | 0.045772
GEN-2024-215 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 93215.6779 | 0.6446 | 14460953.1406 | 0.045772
GEN-2024-215 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 89760.2211 | 0.48258 | 18600000 | 0.056426
GEN-2024-215 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 89760.2211 | 0.48258 | 18600000 | 0.056426
GEN-2024-215 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 56577.4503 | 0.34942 | 16192000 | 0.026118
GEN-2024-215 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 48776.9517 | 0.26224 | 18600000 | 0.033662
GEN-2024-215 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 20778.4678 | 1.2593 | 1650000 | 0.050894
GEN-2024-215 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MED-LDG3 115 kV | Current Study |  |  | 13564.7982 | 0.6131 | 2212500 | 0.014077
GEN-2024-215 | 03 CENTRAL | TBD | ERIS | Add 0.8 MVAR switched shunt at HARBNGR7 345 kV | Current Study |  |  | 7369.2335 | 0.13904 | 5300000 | 0.00962
GEN-2024-215 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 5765.3652 | 0.34942 | 1650000 | 0.026118
GEN-2024-216 | 01 NORTH | TBD | ERIS | Rebuild line 652403 DAWSONC4 230 652411 MI CTYE4 230 1 | Current Study | 70.4 | (386.00, 386.00) | 93303376.6992 | 69.7543 | 133760000 | 0.51939
GEN-2024-216 | 01 NORTH | TBD | ERIS | Rebuild line 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1 | Current Study | 40.93 | (519.00, 519.00) | 55270143.7705 | 71.0715 | 77767000 | 0.19011
GEN-2024-216 | 01 NORTH | TBD | ERIS | Rebuild line 652403 DAWSONC4 230 652616 MINGUSVILLE4 230 1 | Current Study | 30.68 | (386.00, 386.00) | 41428976.5668 | 71.0715 | 58292000 | 0.19011
GEN-2024-216 | 01 NORTH | TBD | ERIS | Rebuild line 652404 DAWSONC7 115 661056 LEWIS 7 115 1 | Current Study | 51.58 | (176.00, 176.00) | 30617972.7718 | 59.3602 | 51580000 | 0.061146
GEN-2024-216 | 01 NORTH | TBD | ERIS | Rebuild line 652425 BELFELD4 230 659247 MEDORA__-UM4 230 1 | Current Study | 22.59 | (519.00, 519.00) | 30504582.1592 | 71.0715 | 42921000 | 0.19011
GEN-2024-216 | 01 NORTH | TBD | ERIS | Rebuild line 652497 MAURINE4 230 659351 BISON___-GE4 230 1 | Current Study | 38.56 | (386.00, 386.00) | 25939547.6844 | 35.4056 | 73264000 | 0.13375
GEN-2024-216 | 01 NORTH | TBD | ERIS | Rebuild line 659265 LITTL_MS-BE4 230 659266 RHAME___-BE4 230 1 | Current Study | 24.19 | (519.00, 519.00) | 14786660.8086 | 32.1722 | 45961000 | 0.35146
GEN-2024-216 | 01 NORTH | TBD | ERIS | Rebuild line 640404 WAYSIDE 4 230 652484 NUNDRWD4 230 1 | Current Study | 80.12 | (519.00, 519.00) | 13617674.7171 | 8.9456 | 152228000 | 0.045633
GEN-2024-216 | 01 NORTH | TBD | NRIS | Rebuild line 652424 BELFELD3 345 659183 CHARL_CK-BE3 345 1 | Current Study | 40.74 | (1793.00, 1793.00) | 8354933.164 | 9.3218 | 89628000 | 0.084246
GEN-2024-216 | 01 NORTH | TBD | NRIS | Add 256 MVAR switched shunt at SD.LS-KS-MB3 345 kV | Current Study |  |  | 5300000 | 100 | 5300000 | 0.045428
GEN-2024-216 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 652221 BELFELD9 13 652424 BELFELD3 345 652425 BELFELD4 230 M2 | Current Study |  | (312.00, 390.00) | 5119641.2446 | 20.4786 | 25000000 | 0.064311
GEN-2024-216 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 652220 BELFELD29 13 652424 BELFELD3 345 652425 BELFELD4 230 M2 | Current Study |  | (250.00, 312.00) | 5119641.2446 | 20.4786 | 25000000 | 0.081116
GEN-2024-216 | 01 NORTH | TBD | ERIS | Rebuild line 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Current Study | 36.8 | (1793.00, 1793.00) | 4855310.1404 | 5.9972 | 80960000 | 0.074632
GEN-2024-216 | 01 NORTH | TBD | ERIS | Rebuild line 652884 NUNDRWD-LNX3 230 785430 G24-282-TAP 230 1 | Current Study | 35.21 | (519.00, 519.00) | 4033173.9721 | 6.0288 | 66899000 | 0.07821
GEN-2024-216 | 01 NORTH | TBD | NRIS | Add 18 MVAR switched shunt at CHARL_CK-BE4 230 kV | Current Study |  |  | 3825000 | 100 | 3825000 | 0.11305
GEN-2024-216 | 01 NORTH | TBD | NRIS | Rebuild line 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 | Current Study | 13.41 | (217.00, 217.00) | 3122076.5534 | 23.2817 | 13410000 | 0.0084216
GEN-2024-216 | 01 NORTH | TBD | ERIS | Rebuild line 652529 WATERTN3 345 659165 CROCKER_-BE3 345 1 | Current Study | 44.23 | (1793.00, 1793.00) | 3022982.3871 | 3.1067 | 97306000 | 0.066212
GEN-2024-216 | 01 NORTH | TBD | ERIS | Add 314 MVAR SVC at MAURINE4 230 kV | Current Study |  |  | 2510124.9484 | 29.1875 | 8600000 | 1
GEN-2024-216 | 01 NORTH | TBD | NRIS | Add 78 MVAR SVC at STEGALL_-MB3 345 kV | Current Study |  |  | 2465383.9446 | 20.5449 | 12000000 | 0.047923
GEN-2024-216 | 01 NORTH | TBD | NRIS | Add 0.7 MVAR switched shunt at SCOTBLF 7 115 kV | Current Study |  |  | 2212500 | 100 | 2212500 | 0.036211
GEN-2024-216 | 01 NORTH | TBD | NRIS | Add 25 MVAR switched shunt at BELFELD3 345 kV | Current Study |  |  | 1949750.0997 | 36.7877 | 5300000 | 0.064998
GEN-2024-216 | 01 NORTH | TBD | NRIS | Rebuild line 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 | Current Study | 7.43 | (217.00, 217.00) | 1729830.6332 | 23.2817 | 7430000 | 0.0084216
GEN-2024-216 | 01 NORTH | TBD | NRIS | Add 0.7 MVAR switched shunt at STEGALL_-MB4 230 kV | Current Study |  |  | 1709924.8862 | 44.7039 | 3825000 | 0.16365
GEN-2024-216 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 659120 BROADLND-BE3 345 659204 BD.KU2A_-BE9 13 659205 BROADLND-BE4 230 M2 | Current Study |  | (471.00, 478.00) | 1419926.7462 | 5.6797 | 25000000 | 0.042781
GEN-2024-216 | 01 NORTH | TBD | ERIS | Add 34 MVAR switched shunt at OUTLAW_WF7 345 kV | Current Study |  |  | 1263870.8304 | 23.8466 | 5300000 | 0.027276
GEN-2024-216 | 01 NORTH | TBD | NRIS | Rebuild line 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 | Current Study | 5 | (217.00, 217.00) | 1164085.2175 | 23.2817 | 5000000 | 0.0084216
GEN-2024-216 | 01 NORTH | TBD | ERIS | Rebuild line 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | Current Study | 4.2 | (519.00, 519.00) | 772072.8804 | 9.6751 | 7980000 | 0.03455
GEN-2024-216 | 01 NORTH | TBD | ERIS | Rebuild line 652200 GLENDIVE7 115 661032 GLENDCT7 115 1 | Current Study | 3.8 | (176.00, 176.00) | 689662.8888 | 18.149 | 3800000 | 0.023048
GEN-2024-216 | 01 NORTH | TBD | ERIS | Rebuild line 652200 GLENDIVE7 115 652404 DAWSONC7 115 1 | Current Study | 2.73 | (176.00, 176.00) | 495468.3385 | 18.149 | 2730000 | 0.023048
GEN-2024-216 | 01 NORTH | TBD | ERIS | Add 24 MVAR switched shunt at DH_CS_EA-TS4 230 kV | Current Study |  |  | 487745.9729 | 12.7515 | 3825000 | 0.032211
GEN-2024-216 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 652237 WATERT19 13 652529 WATERTN3 345 652530 WATERTN4 230 M2 | Current Study |  | (400.00, 478.00) | 307446.3868 | 1.2298 | 25000000 | 0.0039229
GEN-2024-216 | 01 NORTH | TBD | ERIS | Add 525 MVAR SVC at SD.LS-LR-MB3 345 kV | Current Study |  |  | 287701.3367 | 2.3975 | 12000000 | 0.084462
GEN-2024-216 | 01 NORTH | TBD | ERIS | Add 60 MVAR switched shunt at WAYSIDE 4 230 kV | Current Study |  |  | 237133.209 | 6.1996 | 3825000 | 0.088789
GEN-2024-216 | 01 NORTH | TBD | ERIS | Add 0.4 MVAR switched shunt at SHINDLER-ER7 115 kV | Current Study |  |  | 150040.3003 | 6.7815 | 2212500 | 0.092817
GEN-2024-216 | 01 NORTH | TBD | ERIS | Add 24 MVAR switched shunt at DAYTON__-ER7 115 kV | Current Study |  |  | 132686.969 | 5.9972 | 2212500 | 0.074632
GEN-2024-216 | 01 NORTH | TBD | NRIS | Add 16 MVAR switched shunt at UNDERWOOD 2 345 kV | Current Study |  |  | 124318.0924 | 2.3456 | 5300000 | 0.16365
GEN-2024-216 | 01 NORTH | TBD | ERIS | Add 14.4 MVAR switched shunt at SW145-ER8 69 kV | Current Study |  |  | 82760.6858 | 5.9972 | 1380000 | 0.074632
GEN-2024-216 | 01 NORTH | TBD | ERIS | Add 0.5 MVAR switched shunt at ORLAND-ER8 69 kV | Current Study |  |  | 82760.6858 | 5.9972 | 1380000 | 0.074632
GEN-2024-216 | 01 NORTH | TBD | ERIS | Add 4.4 MVAR switched shunt at DESMET-ER7 115 kV | Current Study |  |  | 77066.8234 | 3.4832 | 2212500 | 0.088789
GEN-2024-216 | 01 NORTH | TBD | ERIS | Add 10 MVAR switched shunt at REDFIELD 115 kV | Current Study |  |  | 68735.0684 | 3.1067 | 2212500 | 0.066212
GEN-2024-216 | 01 NORTH | TBD | ERIS | Add 54 MVAR switched shunt at REDFELD-ER7 115 kV | Current Study |  |  | 68735.0684 | 3.1067 | 2212500 | 0.066212
GEN-2024-216 | 01 NORTH | TBD | NRIS | Add 0.09 MVAR switched shunt at GRAY CO3 115 kV | Current Study |  |  | 62280.01 | 2.8149 | 2212500 | 0.045428
GEN-2024-216 | 01 NORTH | TBD | ERIS | Add line and rebuild line 652568 GROTONSOUTH7 115 659187 GROTON__-BE7 115 M2 | Current Study | 0.1 | (598.00, 598.00) | 61527.3462 | 1.4177 | 4340000 | 0.004136
GEN-2024-216 | 01 NORTH | TBD | ERIS | Add 5.5 MVAR switched shunt at LOOMIS-ER8 69 kV | Current Study |  |  | 49152.0847 | 3.5617 | 1380000 | 0.092817
GEN-2024-216 | 01 NORTH | TBD | ERIS | Add 4 MVAR switched shunt at MOS-RDFL-ER8 69 kV | Current Study |  |  | 42872.0427 | 3.1067 | 1380000 | 0.066212
GEN-2024-216 | 01 NORTH | TBD | ERIS | Add 0.9 MVAR switched shunt at GEN-2024-157 138 kV | Current Study |  |  | 38629.0821 | 1.588 | 2432500 | 0.06884
GEN-2024-216 | 01 NORTH | TBD | ERIS | Rebuild line 652484 NUNDRWD4 230 652884 NUNDRWD-LNX3 230 Z | Current Study | 0.14514 | (519.00, 519.00) | 16625.2229 | 6.0288 | 275765.6361 | 0.07821
GEN-2024-216 | 01 NORTH | TBD | ERIS | Rebuild line 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Current Study | 0 | (880.00, 880.00) | 13193.7776 | 5.9972 | 220000 | 0.074632
GEN-2024-216 | 01 NORTH | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 8788.0155 | 0.63681 | 1380000 | 0.088789
GEN-2024-217 | 03 CENTRAL | TBD | ERIS | Rebuild line 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | Current Study | 17.54 | (1793.00, 1793.00) | 2545772.7877 | 6.5973 | 38588000 | 0.02536
GEN-2024-217 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 2361648.2616 | 0.25167 | 938400000 | 0.030224
GEN-2024-217 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 1494484.9277 | 0.75285 | 198511000 | 0.020358
GEN-2024-217 | 03 CENTRAL | TBD | ERIS | Rebuild line 645458 S3458 3 345 778170 G24-040-TAP 345 1 | Current Study | 13.15 | (1793.00, 1793.00) | 980086.6457 | 3.3878 | 28930000 | 0.042026
GEN-2024-217 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 973540.3842 | 1.0359 | 93984000 | 0.051421
GEN-2024-217 | 03 CENTRAL | TBD | ERIS | Rebuild line 640139 COOPER 3 345 778170 G24-040-TAP 345 1 | Current Study | 12.59 | (1793.00, 1793.00) | 938349.1155 | 3.3878 | 27698000 | 0.042026
GEN-2024-217 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 790272.0843 | 0.54958 | 143796000 | 0.02196
GEN-2024-217 | 03 CENTRAL | TBD | ERIS | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | Current Study | 6.07 | (364.00, 364.00) | 358004.8658 | 3.932 | 9105000 | 0.025271
GEN-2024-217 | 03 CENTRAL | TBD | ERIS | Rebuild line 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 | Current Study | 3.23 | (1793.00, 1793.00) | 292089.9235 | 4.1105 | 7106000 | 0.037067
GEN-2024-217 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 283494.4616 | 0.61745 | 45914000 | 0.024971
GEN-2024-217 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 154719.7852 | 0.61745 | 25058000 | 0.024971
GEN-2024-217 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 131553.1557 | 1.1282 | 11660000 | 0.051421
GEN-2024-217 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 62337.6103 | 0.33515 | 18600000 | 0.047025
GEN-2024-217 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 62337.6103 | 0.33515 | 18600000 | 0.047025
GEN-2024-217 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 38275.7106 | 0.25623 | 14938000 | 0.021833
GEN-2024-217 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 37053.3711 | 0.25623 | 14460953.1406 | 0.021833
GEN-2024-217 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 36496.7097 | 0.19622 | 18600000 | 0.030224
GEN-2024-217 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 11302.4408 | 0.685 | 1650000 | 0.03322
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 33592888.4715 | 3.5737 | 940000000 | 0.050749
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Rebuild line 523106 TXPHSF 3 115 539672 E-LIBER3 115 1 | Current Study | 47.28 | (260.00, 260.00) | 32202627.9541 | 68.1105 | 47280000 | 0.19288
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Rebuild line 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Current Study | 27.23 | (297.00, 297.00) | 24090399.859 | 88.4701 | 27230000 | 0.38345
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Rebuild line 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | Current Study | 84.86 | (1793.00, 1793.00) | 14124494.6275 | 7.5657 | 186692000 | 0.13261
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Rebuild line 539652 CMRIVTP3 115 539672 E-LIBER3 115 1 | Current Study | 11.74 | (176.00, 176.00) | 10634279.0665 | 90.5816 | 11740000 | 0.19697
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Rebuild line 539652 CMRIVTP3 115 539654 CIM-PLT3 115 1 | Current Study | 4.08 | (217.00, 217.00) | 3979773.4396 | 97.5435 | 4080000 | 0.59288
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2 | Current Study |  | (350.00, 385.00) | 3649270.0335 | 21.7218 | 16800000 | 0.19436
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 3378283.3205 | 2.0467 | 165062000 | 0.12942
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 3121732.6165 | 1.5726 | 198511000 | 0.053422
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Rebuild line 523961 POTTER_CO 7 345 784950 G24-266_TAP 345 1 | Current Study | 18.24 | (1793.00, 1793.00) | 2998206.3963 | 7.4716 | 40128000 | 0.13261
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Add phase shifting xfmr 523084 SOONER 3 115 523106 TXPHSF 3 115 M2 | Current Study |  | (120.00, 120.00) | 2928750.0043 | 68.1105 | 4300000 | 0.096442
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Rebuild line 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Current Study | 38.26 | (1793.00, 1793.00) | 2923579.7747 | 3.4733 | 84172000 | 0.084434
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Rebuild line 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Current Study | 37.4 | (1793.00, 1793.00) | 2889432.8143 | 3.5117 | 82280000 | 0.084434
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 2829780.0437 | 0.30155 | 938400000 | 0.045497
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 531448 HOLCOMB3 115 531449 HOLCOMB7 345 531450 HOLCTER1 13 M2 | Current Study |  | (336.00, 358.50) | 2555789.8807 | 15.213 | 16800000 | 0.08347
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | Current Study | 19.2 | (2390.00, 2390.00) | 1474089.9015 | 3.4898 | 42240000 | 0.089618
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 531405 WALKMYR3 115 531510 HARBNGR3 115 M2 | Current Study | 1.28 | (598.00, 598.00) | 1301572.9786 | 21.7218 | 5992000 | 0.19436
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | Current Study | 16.04 | (2390.00, 2390.00) | 1231479.2719 | 3.4898 | 35288000 | 0.089618
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1113076.5786 | 0.56071 | 198511000 | 0.030123
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | Current Study | 21.05 | (1793.00, 1793.00) | 989423.2704 | 2.1365 | 46310000 | 0.056886
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR SVC at GEN-2021-076 345 kV | Current Study |  |  | 835552.9079 | 6.9629 | 12000000 | 0.084434
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | Current Study | 13 | (2390.00, 2390.00) | 802850.3938 | 2.8072 | 28600000 | 0.08921
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR switched shunt at GEN-2022-075 345 kV | Current Study |  |  | 638048.4317 | 12.0386 | 5300000 | 0.38871
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Add 7 MVAR switched shunt at G19-030-TAP 345 kV | Current Study |  |  | 522018.6569 | 9.8494 | 5300000 | 0.38871
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Add 248 MVAR switched shunt at GEN-2022-015 345 kV | Current Study |  |  | 286599.8852 | 5.4075 | 5300000 | 0.38871
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at IRS7 115 KV 115 kV | Current Study |  |  | 266355.1236 | 12.0386 | 2212500 | 0.38871
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 257105.4083 | 0.55997 | 45914000 | 0.02845
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MED-LDG3 115 kV | Current Study |  |  | 248460.8745 | 11.2299 | 2212500 | 0.38871
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 233379.4574 | 4.4034 | 5300000 | 0.38871
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Add 66 MVAR switched shunt at GEN-2021-021 345 kV | Current Study |  |  | 218775.1687 | 4.1278 | 5300000 | 0.0021504
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Add 0.8 MVAR switched shunt at HARBNGR7 345 kV | Current Study |  |  | 197517.7388 | 3.7267 | 5300000 | 0.38871
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 178293.1066 | 1.1011 | 16192000 | 0.12408
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 169327.198 | 7.6532 | 2212500 | 0.38871
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 164170.8302 | 7.4202 | 2212500 | 0.38871
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 140317.7097 | 0.55997 | 25058000 | 0.02845
GEN-2024-218 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 99862.9477 | 1.8842 | 5300000 | 0.080523
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Add 525 MVAR SVC at SD.LS-LR-MB3 345 kV | Current Study |  |  | 86224.7999 | 0.71854 | 12000000 | 0.028621
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 81257.3814 | 1.5332 | 5300000 | 0.053763
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 74846.6424 | 0.62372 | 12000000 | 0.08721
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 72814.7812 | 0.48745 | 14938000 | 0.05218
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 70489.4322 | 0.48745 | 14460953.1406 | 0.05218
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 64663.9366 | 0.34766 | 18600000 | 0.067275
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 63239.3052 | 0.34 | 18600000 | 0.059931
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 63239.3052 | 0.34 | 18600000 | 0.059931
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 61564.3271 | 1.1616 | 5300000 | 0.040011
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Add 24 MVAR switched shunt at NESSCTY3 115 kV | Current Study |  |  | 25374.5476 | 1.1469 | 2212500 | 0.08721
GEN-2024-218 | 03 CENTRAL | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 22664.1706 | 1.6423 | 1380000 | 0.10448
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 18168.4552 | 1.1011 | 1650000 | 0.12408
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Add 0.04 MVAR switched shunt at ELLIS 2 69 kV | Current Study |  |  | 13722.8872 | 0.99441 | 1380000 | 0.08721
GEN-2024-218 | 03 CENTRAL | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 11732.1836 | 0.85016 | 1380000 | 0.08721
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild 3-winding transformer 515113 CHIGLEY2 69 515114 CHIGLEY4 138 515712 CHIGLEY1 13 3 | Current Study |  | (71.00, 71.00) | 5400000 | 100 | 5400000 | 0.043082
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515097 WLNUTCK4 138 515100 PAOLI- 4 138 1 | Current Study | 15.55 | (265.00, 265.00) | 5116154.6548 | 27.4178 | 18660000 | 0.12774
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515117 ARBUCKL4 138 515531 VANOSTP4 138 1 | Current Study | 18.2 | (472.00, 472.00) | 3601287.3887 | 16.4894 | 21840000 | 0.20324
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515044 SEMINOL4 138 515531 VANOSTP4 138 1 | Current Study | 21.55 | (395.00, 395.00) | 3563995.1999 | 13.7819 | 25860000 | 0.14279
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515133 BLUERIV4 138 515178 PARKLN 4 138 1 | Current Study | 12.7 | (395.00, 395.00) | 2735540.506 | 17.9497 | 15240000 | 0.14939
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 1 | Current Study |  | (1868.00, 1868.00) | 2646203.64 | 4.3028 | 61500000 | 0.131
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 2 | Current Study |  | (1868.00, 1868.00) | 2646203.64 | 4.3028 | 61500000 | 0.131
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515117 ARBUCKL4 138 515133 BLUERIV4 138 1 | Current Study | 10.35 | (395.00, 395.00) | 2229357.8139 | 17.9497 | 12420000 | 0.14939
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 1754604.3877 | 1.4961 | 117282000 | 0.039352
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 1698943.9791 | 1.1308 | 150244000 | 0.032032
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515178 PARKLN 4 138 515977 LKKONWA4 138 1 | Current Study | 13.56 | (472.00, 472.00) | 1672837.1359 | 10.2805 | 16272000 | 0.15545
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515105 WYNWOD 2 69 515113 CHIGLEY2 69 1 | Current Study | 1.87 | (106.00, 106.00) | 1589500 | 100 | 1589500 | 0.034466
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1027737.4288 | 1.0234 | 100427000 | 0.016429
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1019663.8778 | 0.46705 | 218320000 | 0.018015
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 1001234.9445 | 1.1133 | 89936000 | 0.016255
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 968928.3001 | 1.7415 | 55638000 | 0.049096
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 959369.1114 | 1.0048 | 95480000 | 0.050793
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 880767.9327 | 1.3345 | 66000000 | 0.038341
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 851053.244 | 1.0048 | 84700000 | 0.050793
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 842463.9155 | 0.58587 | 143796000 | 0.036578
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 816110.0947 | 1.4797 | 55154000 | 0.032617
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 772480.9515 | 1.2213 | 63250000 | 0.082896
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 720931.7547 | 1.6079 | 44836000 | 0.047187
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 716592.6832 | 0.36098 | 198511000 | 0.02412
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520400 NOBLE4 138 520975 LIDDELL4 138 1 | Current Study | 5.73 | (265.00, 265.00) | 646912.3847 | 9.4083 | 6876000 | 0.037715
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 636374.8883 | 0.50982 | 124824000 | 0.041692
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 633120.0437 | 0.31998 | 197860000 | 0.019768
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 599487.5907 | 1.2757 | 46992000 | 0.064585
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 533815.8929 | 0.47327 | 112794000 | 0.050388
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 764550 G20-087-TAP 345 1 | Current Study | 14.38 | (1793.00, 1793.00) | 518752.4544 | 1.6398 | 31636000 | 0.069898
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 503172.7011 | 0.53538 | 93984000 | 0.041526
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 456608.9017 | 0.27663 | 165062000 | 0.021756
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | Current Study | 13.6 | (1793.00, 1793.00) | 434112.5966 | 1.4509 | 29920000 | 0.034246
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 776060 G23-204-TAP 345 1 | Current Study | 17.82 | (1793.00, 1793.00) | 432411.6953 | 1.103 | 39204000 | 0.051935
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 429016.4508 | 0.3227 | 132946000 | 0.012541
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 422629.8433 | 0.51864 | 81488000 | 0.043047
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 407791.6839 | 1.2139 | 33594000 | 0.061914
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 390639.0561 | 1.4797 | 26400000 | 0.032617
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 387419.3166 | 1.509 | 25674000 | 0.066218
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 337358.6968 | 0.73476 | 45914000 | 0.04643
GEN-2024-219 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 515055 MAUD 4 138 787770 G24-360-TAP 138 1 | Current Study | 5.11 | (395.00, 395.00) | 334581.9165 | 5.4563 | 6132000 | 0.029099
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 333872.9893 | 1.2753 | 26180000 | 0.018012
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | Current Study | 8.91 | (2390.00, 2390.00) | 317220.706 | 1.6183 | 19602000 | 0.069898
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 275076.8727 | 1.5361 | 17908000 | 0.06852
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 274549.153 | 1.0852 | 25300000 | 0.027784
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | Current Study | 7.74 | (1793.00, 1793.00) | 252389.7699 | 1.4822 | 17028000 | 0.051935
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514948 CEDARLN4 138 766111 G21-088-TAP 138 1 | Current Study | 2.86 | (395.00, 395.00) | 227401.7881 | 6.6259 | 3432000 | 0.070986
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 222722.3445 | 0.41661 | 53460000 | 0.018798
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | Current Study | 5.97 | (2390.00, 2390.00) | 212548.5538 | 1.6183 | 13134000 | 0.069898
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 200697.1366 | 3.7867 | 5300000 | 0.04643
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR SVC at JAY 4 138 kV | Current Study |  |  | 196431.9417 | 3.7063 | 5300000 | 0.025774
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 184116.7013 | 0.73476 | 25058000 | 0.04643
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 183503.7666 | 1.4895 | 12320000 | 0.03995
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 172722.4369 | 1.4394 | 12000000 | 0.03995
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 172722.4369 | 1.4394 | 12000000 | 0.03995
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | Current Study | 6.93 | (1793.00, 1793.00) | 168160.1037 | 1.103 | 15246000 | 0.051935
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 153992.0964 | 1.2833 | 12000000 | 0.03995
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 152104.6124 | 1.0105 | 15053000 | 0.016706
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 139281.1652 | 1.1607 | 12000000 | 0.049096
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 139095.9535 | 1.1591 | 12000000 | 0.050793
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 122920.7796 | 1.0243 | 12000000 | 0.030175
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 121385.9278 | 1.0115 | 12000000 | 0.064334
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 117010.3782 | 0.97509 | 12000000 | 0.03995
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 117010.3782 | 0.97509 | 12000000 | 0.03995
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 115561.2233 | 0.96301 | 12000000 | 0.016255
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 112004.0504 | 0.93337 | 12000000 | 0.039352
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 111343.9781 | 0.92787 | 12000000 | 0.049096
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 110970.6871 | 0.92476 | 12000000 | 0.03995
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at CENTRTN5 161 kV | Current Study |  |  | 110187.7429 | 3.3904 | 3250000 | 0.027116
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 109086.01 | 0.90905 | 12000000 | 0.03995
GEN-2024-219 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 106544.144 | 0.58864 | 18100000 | 0.011273
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 106048.6407 | 0.88374 | 12000000 | 0.030175
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 103995.7679 | 0.86663 | 12000000 | 0.03995
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 103703.7798 | 0.8642 | 12000000 | 0.036831
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 102650.069 | 1.9368 | 5300000 | 0.030175
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 101330.2851 | 0.84442 | 12000000 | 0.050793
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 96590.948 | 1.8225 | 5300000 | 0.030248
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 83380.2069 | 1.2633 | 6600000 | 0.032833
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 80238.5932 | 0.66865 | 12000000 | 0.036831
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 71939.7608 | 1.3574 | 5300000 | 0.049096
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 67993.0261 | 0.58313 | 11660000 | 0.041526
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 66384.6772 | 1.2525 | 5300000 | 0.039352
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 65670.5496 | 0.99501 | 6600000 | 0.050793
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 63695.5454 | 1.2018 | 5300000 | 0.039352
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 59026.84 | 0.89435 | 6600000 | 0.036831
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 59026.84 | 0.89435 | 6600000 | 0.036831
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 57237.3791 | 1.08 | 5300000 | 0.041527
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 56884.0302 | 1.0733 | 5300000 | 0.064334
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 56092.9488 | 0.84989 | 6600000 | 0.036831
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 55522.9593 | 0.84126 | 6600000 | 0.041527
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 53412.0916 | 0.35756 | 14938000 | 0.047605
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 51706.3699 | 0.35756 | 14460953.1406 | 0.047605
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 50317.4901 | 1.5482 | 3250000 | 0.036831
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 50317.4901 | 1.5482 | 3250000 | 0.036831
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 49306.745 | 0.93032 | 5300000 | 0.036831
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 45347.0239 | 0.28006 | 16192000 | 0.039251
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 41753.3439 | 1.2847 | 3250000 | 0.032833
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 41753.3439 | 1.2847 | 3250000 | 0.032833
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 40899.1804 | 1.2584 | 3250000 | 0.036831
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 39663.3188 | 0.74836 | 5300000 | 0.026611
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 37888.9629 | 1.2757 | 2970000 | 0.064585
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 37329.5613 | 0.70433 | 5300000 | 0.030175
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 37261.6127 | 0.70305 | 5300000 | 0.041527
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 37087.5267 | 1.5247 | 2432500 | 0.039352
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 36668.2296 | 0.69185 | 5300000 | 0.030175
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 36573.3714 | 1.1253 | 3250000 | 0.036831
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 35368.4465 | 1.0048 | 3520000 | 0.050793
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 34582.1807 | 0.65249 | 5300000 | 0.030175
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 32706.1398 | 0.6171 | 5300000 | 0.041527
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 32655.5333 | 1.0048 | 3250000 | 0.050793
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 32553.2547 | 1.4797 | 2200000 | 0.032617
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 31322.4361 | 0.96377 | 3250000 | 0.036831
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 31046.135 | 0.95527 | 3250000 | 0.036831
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 31044.2125 | 0.95521 | 3250000 | 0.036831
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 30235.2682 | 0.93032 | 3250000 | 0.036831
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 29274.4743 | 0.90075 | 3250000 | 0.050793
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 28347.7202 | 0.87224 | 3250000 | 0.036831
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 28065.8984 | 1.2757 | 2200000 | 0.064585
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 27610.6222 | 0.84956 | 3250000 | 0.036831
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CHILD4WT 138 kV | Current Study |  |  | 26370.2446 | 1.0841 | 2432500 | 0.069898
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 26009.8756 | 0.8003 | 3250000 | 0.036831
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 25433.1621 | 0.47987 | 5300000 | 0.0044588
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514947 CANADN-4 138 766111 G21-088-TAP 138 1 | Current Study | 0.3 | (395.00, 395.00) | 23853.3344 | 6.6259 | 360000 | 0.070986
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 23834.8802 | 0.73338 | 3250000 | 0.041527
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 20605.129 | 0.84708 | 2432500 | 0.048024
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520400 NOBLE4 138 520842 CANADNS4 138 1 | Current Study | 0.18 | (265.00, 265.00) | 20321.855 | 9.4083 | 216000 | 0.037715
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 19747.9391 | 1.4961 | 1320000 | 0.039352
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 18947.7903 | 0.35751 | 5300000 | 0.039251
GEN-2024-219 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 18473.7716 | 0.34856 | 5300000 | 0.074392
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 18319.5819 | 1.3275 | 1380000 | 0.080838
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 17931.8289 | 0.73718 | 2432500 | 0.041527
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 17683.2377 | 0.72696 | 2432500 | 0.041527
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 17178.5612 | 0.14315 | 12000000 | 0.024895
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 17160.5931 | 1.2435 | 1380000 | 0.036831
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 16861.3092 | 0.7331 | 2300000 | 0.064585
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 15845.1951 | 1.1482 | 1380000 | 0.032833
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 14118.1551 | 1.0231 | 1380000 | 0.036831
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 12118.9853 | 0.87819 | 1380000 | 0.038342
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 11828.2521 | 0.22317 | 5300000 | 0.03995
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 11690.5286 | 0.84714 | 1380000 | 0.041527
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 7374.5583 | 0.33331 | 2212500 | 0.021056
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 7149.9876 | 0.32316 | 2212500 | 0.021056
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 4620.9603 | 0.28006 | 1650000 | 0.039251
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | Current Study | 10.34 | (69.00, 69.00) | 5809982.0928 | 66.1052 | 8789000 | 0.30505
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | Current Study | 8.6 | (69.00, 69.00) | 4832286.847 | 66.1052 | 7310000 | 0.30505
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508803 GILLIAM2 69 508815 SUPEROR2 69 1 | Current Study | 6 | (69.00, 69.00) | 1724167.3994 | 33.8072 | 5100000 | 0.10452
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1 | Current Study | 56.1 | (1793.00, 1793.00) | 1655776.1521 | 1.3416 | 123420000 | 0.06997
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508813 PLAINDL2 69 778290 G24-044-TAP 69 1 | Current Study | 9.39 | (69.00, 69.00) | 1629539.8482 | 20.4165 | 7981500 | 0.096165
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508055 BLOOMBG2 69 783570 G24-220-TAP 69 1 | Current Study | 1.23 | (69.00, 69.00) | 1045500 | 100 | 1045500 | 0.69495
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508812 OILCITY2 69 508815 SUPEROR2 69 1 | Current Study | 4.66 | (106.00, 106.00) | 707840.9515 | 17.8703 | 3961000 | 0.1472
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | Current Study | 14.95 | (329.00, 329.00) | 518541.0986 | 3.4685 | 14950000 | 0.027965
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508805 LIEBERM2 69 508812 OILCITY2 69 1 | Current Study | 3.4 | (106.00, 106.00) | 516450.4796 | 17.8703 | 2890000 | 0.1472
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 466589.1521 | 0.31055 | 150244000 | 0.025591
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508089 WATLANT2 69 779100 G24-071-TAP 69 1 | Current Study | 1.78 | (106.00, 106.00) | 343717.0219 | 22.7176 | 1513000 | 0.3395
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507452 HOPESWI3 115 507453 HOPE 3 115 1 | Current Study | 6.38 | (260.00, 260.00) | 321006.9816 | 5.0315 | 6380000 | 0.03144
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 337505 3EMMET 115 507448 NHOPE 3 115 1 | Current Study | 12 | (329.00, 329.00) | 303529.0801 | 2.5294 | 12000000 | 0.03144
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 285983.35 | 0.29952 | 95480000 | 0.044047
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 274739.0082 | 0.24358 | 112794000 | 0.075442
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 269325.6376 | 0.12336 | 218320000 | 0.013842
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 507454 TURK 4 138 507456 TURK 3 115 507458 TURK1 1 13 M2 | Current Study |  | (257.00, 257.00) | 254979.7615 | 2.4517 | 10400000 | 0.032731
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 253694.9073 | 0.29952 | 84700000 | 0.044047
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507449 NWHOPE 3 115 507452 HOPESWI3 115 1 | Current Study | 9.8 | (329.00, 329.00) | 247882.0821 | 2.5294 | 9800000 | 0.03144
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 236371.3975 | 0.16438 | 143796000 | 0.029855
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 221440.674 | 0.3501 | 63250000 | 0.069129
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 206516.1118 | 0.20564 | 100427000 | 0.0096036
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 189919.0655 | 0.095672 | 198511000 | 0.018597
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 176754.5231 | 0.37614 | 46992000 | 0.055396
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 163183.0549 | 0.13073 | 124824000 | 0.031101
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1 | Current Study | 0.28 | (69.00, 69.00) | 157330.2694 | 66.1052 | 238000 | 0.30505
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 142502.7999 | 0.15162 | 93984000 | 0.034213
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 126665.7791 | 0.076738 | 165062000 | 0.017557
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | Current Study | 10.42 | (395.00, 395.00) | 121849.219 | 0.97448 | 12504000 | 0.014311
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 121787.4044 | 1.0149 | 12000000 | 0.054892
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 114721.4149 | 0.34149 | 33594000 | 0.05067
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 108138.1623 | 0.1327 | 81488000 | 0.032042
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 504122 MCNAB 3 115 507453 HOPE 3 115 1 | Current Study | 3.32 | (394.00, 394.00) | 106473.3036 | 3.207 | 3320000 | 0.065461
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at PHILL 7 345 kV | Current Study |  |  | 90557.3087 | 1.7086 | 5300000 | 0.027708
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 85994.9863 | 0.33495 | 25674000 | 0.042759
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 85871.6642 | 0.33941 | 25300000 | 0.02528
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 764550 G20-087-TAP 345 1 | Current Study | 14.38 | (1793.00, 1793.00) | 69039.0917 | 0.21823 | 31636000 | 0.027062
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 504122 MCNAB 3 115 507456 TURK 3 115 1 | Current Study | 2.65 | (394.00, 394.00) | 64970.8046 | 2.4517 | 2650000 | 0.065461
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 61401.6604 | 0.34287 | 17908000 | 0.044494
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 59397.4682 | 0.49498 | 12000000 | 0.066379
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 57945.5553 | 0.87796 | 6600000 | 0.066379
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1 | Current Study | 11.3 | (1793.00, 1793.00) | 55233.2509 | 0.22218 | 24860000 | 0.02492
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 49709.0237 | 0.41424 | 12000000 | 0.066379
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 49062.9706 | 0.92572 | 5300000 | 0.054892
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 45520.7472 | 0.37934 | 12000000 | 0.066379
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | Current Study | 8.91 | (2390.00, 2390.00) | 42217.881 | 0.21538 | 19602000 | 0.027062
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 41463.8351 | 0.34553 | 12000000 | 0.044047
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 37514.3665 | 0.31262 | 12000000 | 0.038469
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 36374.1607 | 0.30312 | 12000000 | 0.014884
GEN-2024-220 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 36116.6233 | 0.19954 | 18100000 | 0.011116
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 35608.4968 | 1.6094 | 2212500 | 0.30505
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 35602.8199 | 0.29669 | 12000000 | 0.054892
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 34750.4313 | 0.52652 | 6600000 | 0.066379
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 33441.7609 | 0.27868 | 12000000 | 0.023882
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 30738.9144 | 0.25616 | 12000000 | 0.030531
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 30738.9144 | 0.25616 | 12000000 | 0.030531
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 30472.1533 | 0.20243 | 15053000 | 0.009736
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 30469.3165 | 0.25391 | 12000000 | 0.031481
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507448 NHOPE 3 115 507449 NWHOPE 3 115 1 | Current Study | 1.2 | (329.00, 329.00) | 30352.908 | 2.5294 | 1200000 | 0.03144
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 29989.6888 | 0.24991 | 12000000 | 0.038469
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 29285.7798 | 0.24405 | 12000000 | 0.029933
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 29016.727 | 0.89282 | 3250000 | 0.066379
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 29016.727 | 0.89282 | 3250000 | 0.066379
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 28851.5359 | 0.24043 | 12000000 | 0.023882
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 28657.1634 | 0.23881 | 12000000 | 0.030531
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | Current Study | 5.97 | (2390.00, 2390.00) | 28287.4018 | 0.21538 | 13134000 | 0.027062
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 28124.5451 | 0.53065 | 5300000 | 0.054892
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | Current Study | 1.8 | (395.00, 395.00) | 21048.8094 | 0.97448 | 2160000 | 0.014311
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 19576.0752 | 0.29661 | 6600000 | 0.044047
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 19376.4502 | 0.36559 | 5300000 | 0.038469
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 19256.2048 | 0.16515 | 11660000 | 0.034213
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 17971.0905 | 0.33908 | 5300000 | 0.066379
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 17561.842 | 0.54036 | 3250000 | 0.066379
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 17342.7379 | 0.26277 | 6600000 | 0.031481
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 17342.7379 | 0.26277 | 6600000 | 0.031481
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 17105.1986 | 0.52631 | 3250000 | 0.066379
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 16210.0878 | 0.30585 | 5300000 | 0.034213
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 16113.5118 | 0.4958 | 3250000 | 0.066379
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 15601.2672 | 0.29436 | 5300000 | 0.051329
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 14486.8666 | 0.27334 | 5300000 | 0.031481
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 14142.2129 | 0.094673 | 14938000 | 0.036668
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 14005.5515 | 1.0149 | 1380000 | 0.054892
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 13690.5796 | 0.094673 | 14460953.1406 | 0.036668
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 13151.0135 | 0.40465 | 3250000 | 0.066379
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 12507.3781 | 0.077244 | 16192000 | 0.031494
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV | Current Study |  |  | 12050.9036 | 0.87325 | 1380000 | 0.041869
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 11171.2831 | 0.37614 | 2970000 | 0.055396
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 11011.7097 | 0.79795 | 1380000 | 0.066379
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 10745.6607 | 0.33064 | 3250000 | 0.031481
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 10552.7895 | 0.19911 | 5300000 | 0.034213
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 10543.165 | 0.29952 | 3520000 | 0.044047
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 9734.4575 | 0.29952 | 3250000 | 0.044047
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 9697.3024 | 0.39866 | 2432500 | 0.029933
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 9202.8779 | 0.28317 | 3250000 | 0.031481
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 9121.6976 | 0.28067 | 3250000 | 0.031481
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 9121.1327 | 0.28065 | 3250000 | 0.031481
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 8883.4559 | 0.27334 | 3250000 | 0.031481
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 8275.0245 | 0.37614 | 2200000 | 0.055396
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 6750.2305 | 0.2077 | 3250000 | 0.034213
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 776060 G23-204-TAP 345 1 | Current Study | 17.82 | (1793.00, 1793.00) | 6720.3889 | 0.017142 | 39204000 | 0.0023481
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 6664.887 | 0.12575 | 5300000 | 0.0033992
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 6213.9776 | 0.28086 | 2212500 | 0.051613
GEN-2024-220 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 6136.4423 | 0.11578 | 5300000 | 0.071886
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 5964.0901 | 0.43218 | 1380000 | 0.054892
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 5877.0033 | 0.42587 | 1380000 | 0.075442
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 5078.4387 | 0.20877 | 2432500 | 0.034213
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 5008.0357 | 0.20588 | 2432500 | 0.034213
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 4971.4255 | 0.21615 | 2300000 | 0.055396
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 4741.7502 | 0.19493 | 2432500 | 0.03215
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 4148.07 | 0.30058 | 1380000 | 0.031481
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CHILD4WT 138 kV | Current Study |  |  | 3509.5292 | 0.14428 | 2432500 | 0.027062
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 3107.311 | 0.058629 | 5300000 | 0.030531
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | Current Study | 6.93 | (1793.00, 1793.00) | 2613.4846 | 0.017142 | 15246000 | 0.0023481
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 2342.6563 | 0.10588 | 2212500 | 0.041048
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 1274.529 | 0.077244 | 1650000 | 0.031494
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 43177276.6073 | 4.0211 | 1073760000 | 0.1722
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 36887358.3466 | 2.8703 | 1285130000 | 0.22614
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 36223228.8987 | 2.8486 | 1271630000 | 0.14666
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 31640331.7064 | 2.089 | 1514620000 | 0.03212
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 26222651.9162 | 2.7944 | 938400000 | 0.11852
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 23249755.0292 | 2.4776 | 938400000 | 0.18597
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 20628132.4429 | 2.8462 | 724760000 | 0.1688
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 12453932.1421 | 3.3981 | 366500000 | 0.055837
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 12431671.2674 | 2.5747 | 482840000 | 0.16358
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 12172602.881 | 2.5936 | 469340000 | 0.11074
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 3443515.4558 | 4.0752 | 84500000 | 0.06256
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527799 EDDY_NORTH 6 230 528095 7-RIVERS 6 230 1 | Current Study | 24.1 | (386.00, 386.00) | 2749704.3304 | 6.005 | 45790000 | 0.023402
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 2601352.4388 | 1.3147 | 197860000 | 0.032488
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 2410937.2075 | 2.8532 | 84500000 | 0.090685
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 2405040.5533 | 2.8462 | 84500000 | 0.1688
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 2309603.9629 | 1.1635 | 198511000 | 0.031096
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 2037999.6212 | 1.6327 | 124824000 | 0.053408
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 1887985.0185 | 1.1438 | 165062000 | 0.035983
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 1423945.076 | 1.7474 | 81488000 | 0.058014
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 1015877.2516 | 1.8397 | 55220000 | 0.044867
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 986685.0236 | 2.2697 | 43472000 | 0.034587
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 925365.8693 | 3.4919 | 26500000 | 0.027441
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 888504.5283 | 4.7769 | 18600000 | 0.31732
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 638808.3284 | 3.4345 | 18600000 | 0.33064
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 613602.6117 | 3.2989 | 18600000 | 0.1653
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 600983.8143 | 3.2311 | 18600000 | 0.16878
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 533542.4273 | 2.8685 | 18600000 | 0.22614
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 529598.8378 | 2.8473 | 18600000 | 0.14666
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 529393.5419 | 2.8462 | 18600000 | 0.1688
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 482401.6994 | 2.5936 | 18600000 | 0.11074
GEN-2024-221 | 05 SOUTHWEST | TBD | NRIS | Add 0.09 MVAR switched shunt at GRAY CO3 115 kV | Current Study |  |  | 401037.2951 | 18.126 | 2212500 | 0.16454
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 394441.6933 | 2.1207 | 18600000 | 0.18597
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 394441.6933 | 2.1207 | 18600000 | 0.18597
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 388553.0164 | 2.089 | 18600000 | 0.03212
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528018 RED_BLUFF 3 115 528235 WOLFCAMP_TP3 115 1 | Current Study | 7.81 | (598.00, 598.00) | 352163.2299 | 4.5091 | 7810000 | 0.030227
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 346194.3113 | 1.3848 | 25000000 | 0.010235
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 346194.3113 | 1.3848 | 25000000 | 0.011745
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 18 MVAR switched shunt at FALCNRD4 138 kV | Current Study |  |  | 346102.3521 | 14.2283 | 2432500 | 0.053261
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 0.7 MVAR switched shunt at GEN-2024-161 138 kV | Current Study |  |  | 344349.8645 | 14.1562 | 2432500 | 0.033594
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 0.7 MVAR switched shunt at ROSEVLT2 69 kV | Current Study |  |  | 196349.9469 | 14.2283 | 1380000 | 0.053261
GEN-2024-221 | 05 SOUTHWEST | TBD | NRIS | Add 16 MVAR switched shunt at UNDERWOOD 2 345 kV | Current Study |  |  | 190435.8282 | 3.5931 | 5300000 | 0.14101
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | Current Study | 0.78 | (598.00, 598.00) | 188917.9154 | 3.5699 | 5292000 | 0.025213
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 184189.5793 | 1.1375 | 16192000 | 0.063772
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 166962.9556 | 1.1177 | 14938000 | 0.059524
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 161630.9732 | 1.1177 | 14460953.1406 | 0.059524
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | Current Study | 0.2 | (598.00, 598.00) | 159930.5104 | 3.5699 | 4480000 | 0.025213
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-161-TAP 138 kV | Current Study |  |  | 151255.6522 | 6.2181 | 2432500 | 0.033594
GEN-2024-221 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 140326.6137 | 0.77529 | 18100000 | 0.0059388
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 110013.1792 | 0.91678 | 12000000 | 0.063772
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 85183.8308 | 1.2993 | 6556000 | 0.044867
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 68625.6099 | 3.1017 | 2212500 | 0.063772
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 528184 SENDERO +3 115 528187 SENDERO_345 345 M2 | Current Study |  | (435.00, 435.00) | 36125.3145 | 0.21503 | 16800000 | 0.00042508
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1 | Current Study | 2.13 | (598.00, 598.00) | 30037.9605 | 1.4102 | 2130000 | 0.0076896
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 26469.416 | 1.1964 | 2212500 | 0.063772
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 0.5 MVAR switched shunt at RKY_RDG4 138 kV | Current Study |  |  | 26360.8979 | 1.0837 | 2432500 | 0.033594
GEN-2024-221 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 19610.7616 | 1.4211 | 1380000 | 0.044976
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 18769.3185 | 1.1375 | 1650000 | 0.063772
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 14787.6388 | 0.27901 | 5300000 | 0.019978
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 12466.9975 | 0.56348 | 2212500 | 0.029257
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 11221.2671 | 0.81314 | 1380000 | 0.063772
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 7911.4029 | 0.57329 | 1380000 | 0.029257
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 3841.4696 | 0.27837 | 1380000 | 0.012332
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528184 SENDERO +3 115 528193 BLACKRIVER 3 115 1 | Current Study | 0.25 | (598.00, 598.00) | 3525.5822 | 1.4102 | 250000 | 0.0076896
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 1535.2819 | 0.11125 | 1380000 | 0.00039798
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 344.9479 | 0.024996 | 1380000 | 0.0013036
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1 | Current Study | 56.1 | (1793.00, 1793.00) | 28477036.0391 | 23.0733 | 123420000 | 0.22062
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1 | Current Study | 30.63 | (1793.00, 1793.00) | 7621333.9594 | 11.31 | 67386000 | 0.12346
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | Current Study | 14.95 | (329.00, 329.00) | 5739729.9621 | 38.3928 | 14950000 | 0.056749
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507452 HOPESWI3 115 507453 HOPE 3 115 1 | Current Study | 6.38 | (260.00, 260.00) | 3381068.3396 | 52.9948 | 6380000 | 0.06071
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 337505 3EMMET 115 507448 NHOPE 3 115 1 | Current Study | 12 | (329.00, 329.00) | 3196978.95 | 26.6415 | 12000000 | 0.06071
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 507454 TURK 4 138 507456 TURK 3 115 507458 TURK1 1 13 M2 | Current Study |  | (257.00, 257.00) | 2624239.6423 | 25.2331 | 10400000 | 0.061758
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507449 NWHOPE 3 115 507452 HOPESWI3 115 1 | Current Study | 9.8 | (329.00, 329.00) | 2610866.1425 | 26.6415 | 9800000 | 0.06071
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 2563552.3252 | 1.7063 | 150244000 | 0.025778
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 2184059.3647 | 1.9363 | 112794000 | 0.10995
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 776060 G23-204-TAP 345 1 | Current Study | 17.82 | (1793.00, 1793.00) | 2116200.4174 | 5.3979 | 39204000 | 0.13556
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1573123.6369 | 1.6476 | 95480000 | 0.04442
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 1520995.9197 | 2.4047 | 63250000 | 0.08705
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1484040.719 | 0.67975 | 218320000 | 0.013983
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 1395512.9037 | 1.6476 | 84700000 | 0.04442
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1297948.341 | 0.90263 | 143796000 | 0.030056
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | Current Study | 7.74 | (1793.00, 1793.00) | 1235182.448 | 7.2538 | 17028000 | 0.13556
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1156154.3576 | 1.1512 | 100427000 | 0.0098568
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 504122 MCNAB 3 115 507453 HOPE 3 115 1 | Current Study | 3.32 | (394.00, 394.00) | 1095818.2033 | 33.0066 | 3320000 | 0.12352
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1041828.4537 | 0.52482 | 198511000 | 0.018703
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 907483.7232 | 1.9311 | 46992000 | 0.052142
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 892291.4707 | 0.71484 | 124824000 | 0.031178
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | Current Study | 6.93 | (1793.00, 1793.00) | 822966.829 | 5.3979 | 15246000 | 0.13556
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 791136.5526 | 0.84178 | 93984000 | 0.034822
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 693378.1762 | 0.42007 | 165062000 | 0.01762
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 676761.6659 | 5.6397 | 12000000 | 0.055922
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 504122 MCNAB 3 115 507456 TURK 3 115 1 | Current Study | 2.65 | (394.00, 394.00) | 668676.4473 | 25.2331 | 2650000 | 0.12352
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 638897.6508 | 1.9018 | 33594000 | 0.051734
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 590718.2339 | 0.72491 | 81488000 | 0.032089
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 543655.5096 | 2.1175 | 25674000 | 0.049558
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 764550 G20-087-TAP 345 1 | Current Study | 14.38 | (1793.00, 1793.00) | 528795.4208 | 1.6715 | 31636000 | 0.038001
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at PHILL 7 345 kV | Current Study |  |  | 489447.1003 | 9.2349 | 5300000 | 0.027455
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 470824.3166 | 1.861 | 25300000 | 0.025412
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 387925.1217 | 2.1662 | 17908000 | 0.051536
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1 | Current Study | 11.3 | (1793.00, 1793.00) | 334082.0145 | 1.3439 | 24860000 | 0.027634
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 327568.8507 | 2.7297 | 12000000 | 0.067113
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | Current Study | 8.91 | (2390.00, 2390.00) | 323362.0492 | 1.6496 | 19602000 | 0.038001
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507448 NHOPE 3 115 507449 NWHOPE 3 115 1 | Current Study | 1.2 | (329.00, 329.00) | 319697.895 | 26.6415 | 1200000 | 0.06071
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 319561.7508 | 4.8418 | 6600000 | 0.067113
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 274138.4142 | 2.2845 | 12000000 | 0.067113
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 272638.5203 | 5.1441 | 5300000 | 0.055922
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 251040.6465 | 2.092 | 12000000 | 0.067113
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 228082.296 | 1.9007 | 12000000 | 0.04442
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | Current Study | 5.97 | (2390.00, 2390.00) | 216663.4606 | 1.6496 | 13134000 | 0.038001
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 207318.645 | 1.7277 | 12000000 | 0.038976
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 197841.6721 | 1.6487 | 12000000 | 0.055922
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 196595.4663 | 1.6383 | 12000000 | 0.014748
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 191643.839 | 2.9037 | 6600000 | 0.067113
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 183673.9678 | 1.5306 | 12000000 | 0.024047
GEN-2024-226 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 178122.8232 | 0.9841 | 18100000 | 0.010051
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 170475.3683 | 1.1325 | 15053000 | 0.0099858
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 169068.1952 | 1.4089 | 12000000 | 0.030786
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 169068.1952 | 1.4089 | 12000000 | 0.030786
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 165920.7566 | 1.3827 | 12000000 | 0.031429
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 165734.4168 | 1.3811 | 12000000 | 0.038976
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 161102.4345 | 1.3425 | 12000000 | 0.030188
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 160023.2499 | 4.9238 | 3250000 | 0.067113
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 160023.2499 | 4.9238 | 3250000 | 0.067113
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 158462.8302 | 1.3205 | 12000000 | 0.024047
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 157618.2823 | 1.3135 | 12000000 | 0.030786
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 156285.5707 | 2.9488 | 5300000 | 0.055922
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 107683.145 | 1.6316 | 6600000 | 0.04442
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 107081.6267 | 2.0204 | 5300000 | 0.038976
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 106905.1801 | 0.91685 | 11660000 | 0.034822
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 99108.0872 | 1.87 | 5300000 | 0.067113
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 96851.1379 | 2.98 | 3250000 | 0.067113
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 94439.9324 | 1.4309 | 6600000 | 0.031429
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 94439.9324 | 1.4309 | 6600000 | 0.031429
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 94332.8127 | 2.9025 | 3250000 | 0.067113
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 89993.9732 | 1.698 | 5300000 | 0.034822
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 88863.7969 | 2.7343 | 3250000 | 0.067113
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 85686.1566 | 1.6167 | 5300000 | 0.051684
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 78888.2763 | 1.4885 | 5300000 | 0.031429
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 77827.5916 | 5.6397 | 1380000 | 0.055922
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 77582.7172 | 0.51936 | 14938000 | 0.036879
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 75105.1036 | 0.51936 | 14460953.1406 | 0.036879
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 72526.0267 | 2.2316 | 3250000 | 0.067113
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 68463.1684 | 0.42282 | 16192000 | 0.031605
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 66356.0462 | 2.885 | 2300000 | 0.13556
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 60728.0611 | 4.4006 | 1380000 | 0.067113
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 58586.2006 | 1.1054 | 5300000 | 0.034822
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 58515.5283 | 1.8005 | 3250000 | 0.031429
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 57995.3415 | 1.6476 | 3520000 | 0.04442
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 57355.0106 | 1.9311 | 2970000 | 0.052142
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV | Current Study |  |  | 55572.8389 | 4.027 | 1380000 | 0.035398
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 53546.8418 | 1.6476 | 3250000 | 0.04442
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 53345.3105 | 2.193 | 2432500 | 0.030188
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 50114.2996 | 1.542 | 3250000 | 0.031429
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 49672.232 | 1.5284 | 3250000 | 0.031429
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 49669.1561 | 1.5283 | 3250000 | 0.031429
GEN-2024-226 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 49537.942 | 0.93468 | 5300000 | 0.10639
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 48374.8864 | 1.4885 | 3250000 | 0.031429
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 46719.7083 | 3.3855 | 1380000 | 0.10995
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 42485.193 | 1.9311 | 2200000 | 0.052142
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 37475.4331 | 1.1531 | 3250000 | 0.034822
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 36878.9673 | 0.69583 | 5300000 | 0.0034483
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 33141.9127 | 2.4016 | 1380000 | 0.055922
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 28194.1024 | 1.1591 | 2432500 | 0.034822
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 28184.011 | 1.2739 | 2212500 | 0.042918
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 27803.244 | 1.143 | 2432500 | 0.034822
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 27472.9303 | 1.1294 | 2432500 | 0.03415
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 27325.7488 | 1.2351 | 2212500 | 0.042918
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CHILD4WT 138 kV | Current Study |  |  | 26880.7603 | 1.1051 | 2432500 | 0.038001
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 22588.3279 | 1.6368 | 1380000 | 0.031429
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 17090.6314 | 0.32246 | 5300000 | 0.030786
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 12787.2734 | 0.57796 | 2212500 | 0.041077
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 6976.5457 | 0.42282 | 1650000 | 0.031605
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1 | Current Study | 56.1 | (1793.00, 1793.00) | 18984690.6927 | 15.3822 | 123420000 | 0.22062
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1 | Current Study | 30.63 | (1793.00, 1793.00) | 5080889.3063 | 7.54 | 67386000 | 0.12346
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | Current Study | 14.95 | (329.00, 329.00) | 3826486.6414 | 25.5952 | 14950000 | 0.056749
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507452 HOPESWI3 115 507453 HOPE 3 115 1 | Current Study | 6.38 | (260.00, 260.00) | 2254045.5597 | 35.3299 | 6380000 | 0.06071
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 337505 3EMMET 115 507448 NHOPE 3 115 1 | Current Study | 12 | (329.00, 329.00) | 2131319.3 | 17.761 | 12000000 | 0.06071
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 507454 TURK 4 138 507456 TURK 3 115 507458 TURK1 1 13 M2 | Current Study |  | (257.00, 257.00) | 1749493.0948 | 16.822 | 10400000 | 0.061758
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507449 NWHOPE 3 115 507452 HOPESWI3 115 1 | Current Study | 9.8 | (329.00, 329.00) | 1740577.4283 | 17.761 | 9800000 | 0.06071
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 1709034.8834 | 1.1375 | 150244000 | 0.025778
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 1456039.5764 | 1.2909 | 112794000 | 0.10995
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 776060 G23-204-TAP 345 1 | Current Study | 17.82 | (1793.00, 1793.00) | 1410800.2783 | 3.5986 | 39204000 | 0.13556
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1048749.0913 | 1.0984 | 95480000 | 0.04442
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 1013997.2798 | 1.6032 | 63250000 | 0.08705
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 989360.4793 | 0.45317 | 218320000 | 0.013983
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 930341.9358 | 1.0984 | 84700000 | 0.04442
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 865298.894 | 0.60175 | 143796000 | 0.030056
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | Current Study | 7.74 | (1793.00, 1793.00) | 823454.9653 | 4.8359 | 17028000 | 0.13556
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 770769.5717 | 0.76749 | 100427000 | 0.0098568
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 504122 MCNAB 3 115 507453 HOPE 3 115 1 | Current Study | 3.32 | (394.00, 394.00) | 730545.4688 | 22.0044 | 3320000 | 0.12352
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 694552.3025 | 0.34988 | 198511000 | 0.018703
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 604989.1488 | 1.2874 | 46992000 | 0.052142
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 594860.9805 | 0.47656 | 124824000 | 0.031178
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | Current Study | 6.93 | (1793.00, 1793.00) | 548644.5527 | 3.5986 | 15246000 | 0.13556
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 527424.3684 | 0.56119 | 93984000 | 0.034822
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 462252.1175 | 0.28005 | 165062000 | 0.01762
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 451174.444 | 3.7598 | 12000000 | 0.055922
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 504122 MCNAB 3 115 507456 TURK 3 115 1 | Current Study | 2.65 | (394.00, 394.00) | 445784.2982 | 16.822 | 2650000 | 0.12352
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 425931.7672 | 1.2679 | 33594000 | 0.051734
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 393812.1559 | 0.48328 | 81488000 | 0.032089
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 362437.0064 | 1.4117 | 25674000 | 0.049558
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 764550 G20-087-TAP 345 1 | Current Study | 14.38 | (1793.00, 1793.00) | 352530.2805 | 1.1143 | 31636000 | 0.038001
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at PHILL 7 345 kV | Current Study |  |  | 326298.0669 | 6.1566 | 5300000 | 0.027455
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 313882.8778 | 1.2406 | 25300000 | 0.025412
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 258616.7478 | 1.4441 | 17908000 | 0.051536
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1 | Current Study | 11.3 | (1793.00, 1793.00) | 222721.343 | 0.8959 | 24860000 | 0.027634
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 218379.2338 | 1.8198 | 12000000 | 0.067113
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | Current Study | 8.91 | (2390.00, 2390.00) | 215574.6995 | 1.0998 | 19602000 | 0.038001
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507448 NHOPE 3 115 507449 NWHOPE 3 115 1 | Current Study | 1.2 | (329.00, 329.00) | 213131.93 | 17.761 | 1200000 | 0.06071
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 213041.1672 | 3.2279 | 6600000 | 0.067113
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 182758.9428 | 1.523 | 12000000 | 0.067113
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 181759.0135 | 3.4294 | 5300000 | 0.055922
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 167360.431 | 1.3947 | 12000000 | 0.067113
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 152054.864 | 1.2671 | 12000000 | 0.04442
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | Current Study | 5.97 | (2390.00, 2390.00) | 144442.3071 | 1.0998 | 13134000 | 0.038001
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 138212.43 | 1.1518 | 12000000 | 0.038976
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 131894.4481 | 1.0991 | 12000000 | 0.055922
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 131063.6442 | 1.0922 | 12000000 | 0.014748
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 127762.5594 | 1.9358 | 6600000 | 0.067113
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 122449.3119 | 1.0204 | 12000000 | 0.024047
GEN-2024-227 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 118748.5488 | 0.65607 | 18100000 | 0.010051
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 113650.2455 | 0.755 | 15053000 | 0.0099858
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 112712.1302 | 0.93927 | 12000000 | 0.030786
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 112712.1302 | 0.93927 | 12000000 | 0.030786
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 110613.8377 | 0.92178 | 12000000 | 0.031429
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 110489.6112 | 0.92075 | 12000000 | 0.038976
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 107401.623 | 0.89501 | 12000000 | 0.030188
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 106682.1666 | 3.2825 | 3250000 | 0.067113
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 106682.1666 | 3.2825 | 3250000 | 0.067113
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 105641.8868 | 0.88035 | 12000000 | 0.024047
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 105078.8549 | 0.87566 | 12000000 | 0.030786
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 104190.3805 | 1.9659 | 5300000 | 0.055922
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 71788.7633 | 1.0877 | 6600000 | 0.04442
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 71387.7512 | 1.3469 | 5300000 | 0.038976
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 71270.1201 | 0.61124 | 11660000 | 0.034822
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 66072.0582 | 1.2466 | 5300000 | 0.067113
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 64567.4252 | 1.9867 | 3250000 | 0.067113
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 62959.9549 | 0.95394 | 6600000 | 0.031429
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 62959.9549 | 0.95394 | 6600000 | 0.031429
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 62888.5418 | 1.935 | 3250000 | 0.067113
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 59995.9821 | 1.132 | 5300000 | 0.034822
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 59242.5313 | 1.8228 | 3250000 | 0.067113
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 57124.1044 | 1.0778 | 5300000 | 0.051684
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 52592.1842 | 0.99231 | 5300000 | 0.031429
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 51885.0611 | 3.7598 | 1380000 | 0.055922
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 51721.8115 | 0.34624 | 14938000 | 0.036879
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 50070.0691 | 0.34624 | 14460953.1406 | 0.036879
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 48350.6845 | 1.4877 | 3250000 | 0.067113
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 45642.1123 | 0.28188 | 16192000 | 0.031605
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 44237.3641 | 1.9234 | 2300000 | 0.13556
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 40485.3741 | 2.9337 | 1380000 | 0.067113
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 39057.467 | 0.73693 | 5300000 | 0.034822
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 39010.3522 | 1.2003 | 3250000 | 0.031429
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 38663.561 | 1.0984 | 3520000 | 0.04442
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 38236.6737 | 1.2874 | 2970000 | 0.052142
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV | Current Study |  |  | 37048.5593 | 2.6847 | 1380000 | 0.035398
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 35697.8945 | 1.0984 | 3250000 | 0.04442
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 35563.5404 | 1.462 | 2432500 | 0.030188
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 33409.5331 | 1.028 | 3250000 | 0.031429
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 33114.8213 | 1.0189 | 3250000 | 0.031429
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 33112.7707 | 1.0189 | 3250000 | 0.031429
GEN-2024-227 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 33025.2946 | 0.62312 | 5300000 | 0.10639
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 32249.9243 | 0.99231 | 3250000 | 0.031429
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 31146.4722 | 2.257 | 1380000 | 0.10995
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 28323.462 | 1.2874 | 2200000 | 0.052142
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 24983.6221 | 0.76873 | 3250000 | 0.034822
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 24585.9782 | 0.46389 | 5300000 | 0.0034483
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 22094.6085 | 1.6011 | 1380000 | 0.055922
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 18796.0683 | 0.77271 | 2432500 | 0.034822
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 18789.3407 | 0.84924 | 2212500 | 0.042918
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 18535.496 | 0.76199 | 2432500 | 0.034822
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 18315.2869 | 0.75294 | 2432500 | 0.03415
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 18217.1659 | 0.82337 | 2212500 | 0.042918
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CHILD4WT 138 kV | Current Study |  |  | 17920.5069 | 0.73671 | 2432500 | 0.038001
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 15058.8852 | 1.0912 | 1380000 | 0.031429
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 11393.7542 | 0.21498 | 5300000 | 0.030786
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 8524.8489 | 0.3853 | 2212500 | 0.041077
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 4651.0305 | 0.28188 | 1650000 | 0.031605
GEN-2024-228 | 03 CENTRAL | TBD | ERIS | Add line 532871 CIRCLE 6 230 783810 G24-228-TAP 230 P2 | Current Study | 13.42 | (328.00, 398.00) | 40750000 | 100 | 40750000 | 0.4513
GEN-2024-228 | 03 CENTRAL | TBD | ERIS | Rebuild line 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 | Current Study | 21.74 | (386.00, 386.00) | 21674620.9278 | 52.4733 | 41306000 | 0.28727
GEN-2024-228 | 03 CENTRAL | TBD | ERIS | Rebuild line 530582 S HAYS6 230 539679 GRTBEND6 230 1 | Current Study | 39.2 | (386.00, 386.00) | 9393693.2493 | 12.6124 | 74480000 | 0.084575
GEN-2024-228 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 4901573.9393 | 3.4087 | 143796000 | 0.17025
GEN-2024-228 | 03 CENTRAL | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 3795732.4171 | 1.7386 | 218320000 | 0.053648
GEN-2024-228 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 3469675.2336 | 1.7479 | 198511000 | 0.05908
GEN-2024-228 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 2391952.0772 | 0.2549 | 938400000 | 0.038265
GEN-2024-228 | 03 CENTRAL | TBD | ERIS | Rebuild line 533413 CIRCLE 3 115 533416 RENO 3 115 2 | Current Study | 5.95 | (217.00, 217.00) | 1977846.5641 | 33.2411 | 5950000 | 0.18985
GEN-2024-228 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Current Study | 26.47 | (1793.00, 1793.00) | 1954691.7597 | 3.3566 | 58234000 | 0.057472
GEN-2024-228 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1260177.3884 | 0.63481 | 198511000 | 0.033934
GEN-2024-228 | 03 CENTRAL | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 1155824.5936 | 2.162 | 53460000 | 0.078041
GEN-2024-228 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | Current Study | 19.87 | (1793.00, 1793.00) | 722013.0751 | 1.6517 | 43714000 | 0.028206
GEN-2024-228 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | Current Study | 19.2 | (2390.00, 2390.00) | 610608.9212 | 1.4456 | 42240000 | 0.036937
GEN-2024-228 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 535654.081 | 1.1666 | 45914000 | 0.058977
GEN-2024-228 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | Current Study | 16.71 | (1793.00, 1793.00) | 533841.1555 | 1.4522 | 36762000 | 0.040645
GEN-2024-228 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | Current Study | 16.04 | (2390.00, 2390.00) | 510112.8696 | 1.4456 | 35288000 | 0.036937
GEN-2024-228 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | Current Study | 13 | (2390.00, 2390.00) | 332562.9002 | 1.1628 | 28600000 | 0.036768
GEN-2024-228 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 292338.2838 | 1.1666 | 25058000 | 0.058977
GEN-2024-228 | 03 CENTRAL | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 160530.7658 | 3.0289 | 5300000 | 0.049391
GEN-2024-228 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 105535.7778 | 1.9912 | 5300000 | 0.084672
GEN-2024-228 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 93611.4662 | 0.62667 | 14938000 | 0.066747
GEN-2024-228 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 90621.9725 | 0.62667 | 14460953.1406 | 0.066747
GEN-2024-228 | 03 CENTRAL | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 87760.3326 | 0.73134 | 12000000 | 0.10175
GEN-2024-228 | 03 CENTRAL | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 87559.3318 | 1.6521 | 5300000 | 0.057643
GEN-2024-228 | 03 CENTRAL | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 73588.903 | 3.3261 | 2212500 | 0.10692
GEN-2024-228 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 69985.6767 | 0.37627 | 18600000 | 0.065993
GEN-2024-228 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 69985.6767 | 0.37627 | 18600000 | 0.065993
GEN-2024-228 | 03 CENTRAL | TBD | ERIS | Add 66 MVAR switched shunt at GEN-2021-021 345 kV | Current Study |  |  | 56451.0599 | 1.0651 | 5300000 | 0.0005521
GEN-2024-228 | 03 CENTRAL | TBD | ERIS | Add 0.8 MVAR switched shunt at HARBNGR7 345 kV | Current Study |  |  | 54646.1728 | 1.0311 | 5300000 | 0.107
GEN-2024-228 | 03 CENTRAL | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 49317.9715 | 0.93053 | 5300000 | 0.031892
GEN-2024-228 | 03 CENTRAL | TBD | ERIS | Add 248 MVAR switched shunt at GEN-2022-015 345 kV | Current Study |  |  | 42713.9285 | 0.80592 | 5300000 | 0.057643
GEN-2024-228 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 36965.0222 | 0.19874 | 18600000 | 0.038265
GEN-2024-228 | 03 CENTRAL | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 34782.1265 | 0.65627 | 5300000 | 0.057643
GEN-2024-228 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MED-LDG3 115 kV | Current Study |  |  | 7094.3166 | 0.32065 | 2212500 | 0.011043
GEN-2024-228 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 5514.4712 | 0.33421 | 1650000 | 0.02026
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 13032532.7333 | 1.3864 | 940000000 | 0.01959
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511423 FLE TAP4 138 511467 L.E.S.-4 138 1 | Current Study | 19.98 | (265.00, 265.00) | 5744590.0147 | 23.9598 | 23976000 | 0.031063
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | Current Study | 13.6 | (1793.00, 1793.00) | 5534750.0628 | 18.4985 | 29920000 | 0.3493
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | Current Study | 17.69 | (265.00, 265.00) | 5105942.9174 | 24.0529 | 21228000 | 0.028716
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 532803 BURNS 7 345 1 | Current Study | 50.03 | (1793.00, 1793.00) | 4734015.8829 | 4.3011 | 110066000 | 0.04489
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532803 BURNS 7 345 1 | Current Study | 45.5 | (1793.00, 1793.00) | 4305371.2307 | 4.3011 | 100100000 | 0.04489
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511477 S.W.S.-4 138 511586 TONKAWA4 138 1 | Current Study | 11.5 | (265.00, 265.00) | 3306445.7042 | 23.9598 | 13800000 | 0.031063
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 764550 G20-087-TAP 345 1 | Current Study | 14.38 | (1793.00, 1793.00) | 3082818.4727 | 9.7447 | 31636000 | 0.33231
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511423 FLE TAP4 138 511586 TONKAWA4 138 1 | Current Study | 8.33 | (265.00, 265.00) | 2395016.7579 | 23.9598 | 9996000 | 0.031063
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 2367414.6029 | 2.0186 | 117282000 | 0.042477
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 2311123.7043 | 1.5382 | 150244000 | 0.034859
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2 | Current Study |  | (484.00, 515.00) | 1980474.572 | 10.9418 | 18100000 | 0.053038
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | Current Study | 8.91 | (2390.00, 2390.00) | 1885164.7717 | 9.6172 | 19602000 | 0.33231
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1366318.6885 | 0.62583 | 218320000 | 0.019311
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1311377.7702 | 1.3058 | 100427000 | 0.01677
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | Current Study | 5.97 | (2390.00, 2390.00) | 1263123.8706 | 9.6172 | 13134000 | 0.33231
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | Current Study | 11.1 | (395.00, 395.00) | 1231013.5088 | 9.2418 | 13320000 | 0.026117
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 1143328.9879 | 2.073 | 55154000 | 0.036556
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 1133740.9067 | 1.2606 | 89936000 | 0.014725
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1127823.8471 | 0.78432 | 143796000 | 0.039174
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | Current Study | 3.9 | (265.00, 265.00) | 1125674.2441 | 24.0529 | 4680000 | 0.028716
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1108644.7725 | 1.1611 | 95480000 | 0.046957
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1102007.8039 | 0.55514 | 198511000 | 0.029675
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1025613.0869 | 0.82165 | 124824000 | 0.053754
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 1015489.0774 | 1.5386 | 66000000 | 0.035365
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 996667.1585 | 0.50372 | 197860000 | 0.024895
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 983475.2014 | 1.1611 | 84700000 | 0.046957
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 727492.8524 | 1.5481 | 46992000 | 0.062701
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 716227.5589 | 0.43391 | 165062000 | 0.027301
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 693710.8345 | 0.8513 | 81488000 | 0.056526
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 629973.4625 | 0.47386 | 132946000 | 0.014732
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 554020.4413 | 0.87592 | 63250000 | 0.047562
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 549239.5005 | 0.5844 | 93984000 | 0.036263
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 547265.5706 | 2.073 | 26400000 | 0.036556
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 418948.2639 | 1.6003 | 26180000 | 0.018082
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 391911.4501 | 1.1666 | 33594000 | 0.047602
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 339989.9454 | 0.63597 | 53460000 | 0.022956
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 332041.2047 | 1.3124 | 25300000 | 0.026882
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 323502.6699 | 1.26 | 25674000 | 0.044234
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 122 MVAR switched shunt at HOYT 7 345 kV | Current Study |  |  | 286306.4671 | 5.402 | 5300000 | 0.039881
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | Current Study | 0.93 | (211.00, 211.00) | 270023.7847 | 24.1957 | 1116000 | 0.032275
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 138 MVAR switched shunt at GEN-2024-016 345 kV | Current Study |  |  | 265167.2327 | 5.0032 | 5300000 | 0.031323
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 250310.5436 | 0.54517 | 45914000 | 0.02756
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 247321.3147 | 2.0075 | 12320000 | 0.043075
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 232790.4009 | 1.9399 | 12000000 | 0.043075
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 232790.4009 | 1.9399 | 12000000 | 0.043075
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 229961.0143 | 1.2841 | 17908000 | 0.045826
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 0.06 MVAR switched shunt at G24-125-TAP 345 kV | Current Study |  |  | 219285.0724 | 4.1375 | 5300000 | 0.02955
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at SHARNSP3 115 kV | Current Study |  |  | 217689.4075 | 9.8391 | 2212500 | 0.029173
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 8 MVAR switched shunt at RANSOM 3 115 kV | Current Study |  |  | 217689.4075 | 9.8391 | 2212500 | 0.029173
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 207546.1792 | 1.7296 | 12000000 | 0.043075
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at GRANTTP3 115 kV | Current Study |  |  | 195416.0251 | 8.8324 | 2212500 | 0.049253
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at PNTPR-GOAB3 115 kV | Current Study |  |  | 195416.0251 | 8.8324 | 2212500 | 0.049253
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 194790.4656 | 1.294 | 15053000 | 0.017115
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 173543.6232 | 1.4462 | 12000000 | 0.034081
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 25 MVAR switched shunt at HIGHPT 3 115 kV | Current Study |  |  | 171735.3813 | 7.7621 | 2212500 | 0.029173
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 166052.8895 | 1.3838 | 12000000 | 0.070405
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 160739.0312 | 1.3395 | 12000000 | 0.046957
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 157703.2686 | 1.3142 | 12000000 | 0.043075
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 157703.2686 | 1.3142 | 12000000 | 0.043075
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CHILD4WT 138 kV | Current Study |  |  | 156711.9034 | 6.4424 | 2432500 | 0.33231
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 151373.2464 | 0.1342 | 112794000 | 0.011431
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 151122.3097 | 1.2594 | 12000000 | 0.042477
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 149722.9793 | 1.2477 | 12000000 | 0.034081
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 149563.1442 | 1.2464 | 12000000 | 0.043075
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 148910.7408 | 2.8096 | 5300000 | 0.02756
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 147023.0298 | 1.2252 | 12000000 | 0.043075
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 144924.7634 | 2.7344 | 5300000 | 0.034081
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 142351.6289 | 2.6859 | 5300000 | 0.035662
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 141274.2381 | 1.1773 | 12000000 | 0.039839
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 140959.8599 | 1.1747 | 12000000 | 0.056526
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 140162.546 | 1.168 | 12000000 | 0.043075
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 138115.4826 | 5.6779 | 2432500 | 0.25752
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 136609.348 | 0.54517 | 25058000 | 0.02756
GEN-2024-229 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 135512.3386 | 0.74869 | 18100000 | 0.01147
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 130854.9746 | 1.0905 | 12000000 | 0.014725
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2 | Current Study |  | (478.00, 478.00) | 120658.6445 | 0.66662 | 18100000 | 0.005578
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 112937.2781 | 0.94114 | 12000000 | 0.039839
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 104615.7905 | 0.8718 | 12000000 | 0.029724
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 91809.5061 | 1.7323 | 5300000 | 0.053287
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 89570.0264 | 1.69 | 5300000 | 0.042477
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 85941.695 | 1.6215 | 5300000 | 0.042477
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 81472.7115 | 0.54541 | 14938000 | 0.058092
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 80944.2421 | 0.67454 | 12000000 | 0.029724
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 78870.8705 | 0.54541 | 14460953.1406 | 0.058092
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 77815.9194 | 1.4682 | 5300000 | 0.070405
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 75888.7678 | 1.1498 | 6600000 | 0.046957
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 74217.9685 | 0.63652 | 11660000 | 0.036263
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511477 S.W.S.-4 138 521089 WASHITA4 138 1 | Current Study | 2.05 | (717.00, 717.00) | 74153.004 | 3.0143 | 2460000 | 0.019192
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 72969.1979 | 1.3768 | 5300000 | 0.039839
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 71126.7412 | 0.43927 | 16192000 | 0.049253
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 60606.3648 | 0.91828 | 6600000 | 0.036263
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 59768.115 | 1.1277 | 5300000 | 0.053287
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 59545.9446 | 0.90221 | 6600000 | 0.029724
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 59545.9446 | 0.90221 | 6600000 | 0.029724
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 56586.2517 | 0.85737 | 6600000 | 0.029724
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 55055.7311 | 1.0388 | 5300000 | 0.02955
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 52703.1096 | 0.9944 | 5300000 | 0.034081
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 51769.4196 | 0.97678 | 5300000 | 0.034081
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 50040.6252 | 2.0572 | 2432500 | 0.042477
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 49740.3674 | 0.9385 | 5300000 | 0.029724
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 48824.2668 | 0.92121 | 5300000 | 0.034081
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 45979.1831 | 1.5481 | 2970000 | 0.062701
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 45605.4642 | 2.073 | 2200000 | 0.036556
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 42407.0903 | 0.80013 | 5300000 | 0.043075
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 40871.6967 | 1.1611 | 3520000 | 0.046957
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 39442.6065 | 0.7442 | 5300000 | 0.10657
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 37736.675 | 1.1611 | 3250000 | 0.046957
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 36895.0117 | 1.1352 | 3250000 | 0.029724
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 34058.6541 | 1.5481 | 2200000 | 0.062701
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 33829.5294 | 1.0409 | 3250000 | 0.046957
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 31597.8975 | 0.97224 | 3250000 | 0.029724
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 31319.1666 | 0.96367 | 3250000 | 0.029724
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 31317.2272 | 0.96361 | 3250000 | 0.029724
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 30501.1687 | 0.9385 | 3250000 | 0.029724
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 29719.569 | 0.56075 | 5300000 | 0.049253
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 28597.0209 | 0.87991 | 3250000 | 0.029724
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 27607.4785 | 0.5209 | 5300000 | 0.003872
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 26645.0715 | 2.0186 | 1320000 | 0.042477
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 26238.6164 | 0.80734 | 3250000 | 0.029724
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 26017.083 | 0.80053 | 3250000 | 0.036263
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 25163.4603 | 0.2097 | 12000000 | 0.029173
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 20461.6226 | 0.88964 | 2300000 | 0.062701
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 19573.5778 | 0.80467 | 2432500 | 0.036263
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 19302.2268 | 0.79351 | 2432500 | 0.036263
GEN-2024-229 | 04 SOUTHEAST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 19002.4839 | 1.377 | 1380000 | 0.087162
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 17735.9241 | 1.2852 | 1380000 | 0.04489
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 14045.2815 | 1.0178 | 1380000 | 0.049582
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at SEGNTP 3 115 kV | Current Study |  |  | 13095.8317 | 0.5919 | 2212500 | 0.049253
GEN-2024-229 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 12993.7384 | 0.24516 | 5300000 | 0.04186
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 12760.8552 | 0.9247 | 1380000 | 0.036263
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 7247.9696 | 0.43927 | 1650000 | 0.049253
GEN-2024-229 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 6215.6315 | 0.28093 | 2212500 | 0.029173
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 19548799.1 | 2.0797 | 940000000 | 0.01959
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511423 FLE TAP4 138 511467 L.E.S.-4 138 1 | Current Study | 19.98 | (265.00, 265.00) | 8616885.0221 | 35.9396 | 23976000 | 0.031063
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | Current Study | 13.6 | (1793.00, 1793.00) | 8302125.0942 | 27.7477 | 29920000 | 0.3493
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | Current Study | 17.69 | (265.00, 265.00) | 7658914.3762 | 36.0793 | 21228000 | 0.028716
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 532803 BURNS 7 345 1 | Current Study | 50.03 | (1793.00, 1793.00) | 7101023.8244 | 6.4516 | 110066000 | 0.04489
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532803 BURNS 7 345 1 | Current Study | 45.5 | (1793.00, 1793.00) | 6458056.8461 | 6.4516 | 100100000 | 0.04489
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511477 S.W.S.-4 138 511586 TONKAWA4 138 1 | Current Study | 11.5 | (265.00, 265.00) | 4959668.5563 | 35.9396 | 13800000 | 0.031063
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 764550 G20-087-TAP 345 1 | Current Study | 14.38 | (1793.00, 1793.00) | 4624227.709 | 14.617 | 31636000 | 0.33231
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511423 FLE TAP4 138 511586 TONKAWA4 138 1 | Current Study | 8.33 | (265.00, 265.00) | 3592525.1368 | 35.9396 | 9996000 | 0.031063
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 3551121.9044 | 3.0278 | 117282000 | 0.042477
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 3466685.5564 | 2.3074 | 150244000 | 0.034859
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2 | Current Study |  | (484.00, 515.00) | 2970711.858 | 16.4128 | 18100000 | 0.053038
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | Current Study | 8.91 | (2390.00, 2390.00) | 2827747.1575 | 14.4258 | 19602000 | 0.33231
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 2049478.0327 | 0.93875 | 218320000 | 0.019311
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1967066.6552 | 1.9587 | 100427000 | 0.01677
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | Current Study | 5.97 | (2390.00, 2390.00) | 1894685.8059 | 14.4258 | 13134000 | 0.33231
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | Current Study | 11.1 | (395.00, 395.00) | 1846520.2632 | 13.8628 | 13320000 | 0.026117
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 1714993.4819 | 3.1095 | 55154000 | 0.036556
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 1700611.36 | 1.8909 | 89936000 | 0.014725
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1691735.7706 | 1.1765 | 143796000 | 0.039174
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | Current Study | 3.9 | (265.00, 265.00) | 1688511.3661 | 36.0793 | 4680000 | 0.028716
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1662967.1587 | 1.7417 | 95480000 | 0.046957
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1653011.7058 | 0.83271 | 198511000 | 0.029675
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1538419.6304 | 1.2325 | 124824000 | 0.053754
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 1523233.6162 | 2.3079 | 66000000 | 0.035365
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 1495000.7377 | 0.75559 | 197860000 | 0.024895
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 1475212.8021 | 1.7417 | 84700000 | 0.046957
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 1091239.2786 | 2.3222 | 46992000 | 0.062701
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 1074341.3384 | 0.65087 | 165062000 | 0.027301
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 1040566.2518 | 1.277 | 81488000 | 0.056526
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 944960.1938 | 0.71078 | 132946000 | 0.014732
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 831030.662 | 1.3139 | 63250000 | 0.047562
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 823859.2508 | 0.8766 | 93984000 | 0.036263
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 820898.3559 | 3.1095 | 26400000 | 0.036556
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 628422.3959 | 2.4004 | 26180000 | 0.018082
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 587867.1751 | 1.7499 | 33594000 | 0.047602
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 509984.918 | 0.95396 | 53460000 | 0.022956
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 498061.807 | 1.9686 | 25300000 | 0.026882
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 485254.0048 | 1.8901 | 25674000 | 0.044234
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 122 MVAR switched shunt at HOYT 7 345 kV | Current Study |  |  | 429459.7007 | 8.103 | 5300000 | 0.039881
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | Current Study | 0.93 | (211.00, 211.00) | 405035.677 | 36.2935 | 1116000 | 0.032275
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 138 MVAR switched shunt at GEN-2024-016 345 kV | Current Study |  |  | 397750.8491 | 7.5047 | 5300000 | 0.031323
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 375465.8154 | 0.81776 | 45914000 | 0.02756
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 370981.9721 | 3.0112 | 12320000 | 0.043075
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 349185.6013 | 2.9099 | 12000000 | 0.043075
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 349185.6013 | 2.9099 | 12000000 | 0.043075
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 344941.5215 | 1.9262 | 17908000 | 0.045826
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 0.06 MVAR switched shunt at G24-125-TAP 345 kV | Current Study |  |  | 328927.6086 | 6.2062 | 5300000 | 0.02955
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at SHARNSP3 115 kV | Current Study |  |  | 326534.1112 | 14.7586 | 2212500 | 0.029173
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 8 MVAR switched shunt at RANSOM 3 115 kV | Current Study |  |  | 326534.1112 | 14.7586 | 2212500 | 0.029173
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 311319.2688 | 2.5943 | 12000000 | 0.043075
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at GRANTTP3 115 kV | Current Study |  |  | 293124.0377 | 13.2485 | 2212500 | 0.049253
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at PNTPR-GOAB3 115 kV | Current Study |  |  | 293124.0377 | 13.2485 | 2212500 | 0.049253
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 292185.6984 | 1.941 | 15053000 | 0.017115
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 260315.4348 | 2.1693 | 12000000 | 0.034081
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 25 MVAR switched shunt at HIGHPT 3 115 kV | Current Study |  |  | 257603.0719 | 11.6431 | 2212500 | 0.029173
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 249079.3342 | 2.0757 | 12000000 | 0.070405
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 241108.5468 | 2.0092 | 12000000 | 0.046957
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 236554.9029 | 1.9713 | 12000000 | 0.043075
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 236554.9029 | 1.9713 | 12000000 | 0.043075
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CHILD4WT 138 kV | Current Study |  |  | 235067.8551 | 9.6636 | 2432500 | 0.33231
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 227059.8696 | 0.2013 | 112794000 | 0.011431
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 226683.4646 | 1.889 | 12000000 | 0.042477
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 224584.469 | 1.8715 | 12000000 | 0.034081
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 224344.7162 | 1.8695 | 12000000 | 0.043075
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 223366.1111 | 4.2145 | 5300000 | 0.02756
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 220534.5447 | 1.8378 | 12000000 | 0.043075
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 217387.145 | 4.1016 | 5300000 | 0.034081
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 213527.4433 | 4.0288 | 5300000 | 0.035662
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 211911.3572 | 1.7659 | 12000000 | 0.039839
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 211439.7898 | 1.762 | 12000000 | 0.056526
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 210243.819 | 1.752 | 12000000 | 0.043075
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 207173.2239 | 8.5169 | 2432500 | 0.25752
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 204914.0219 | 0.81776 | 25058000 | 0.02756
GEN-2024-230 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 203268.5079 | 1.123 | 18100000 | 0.01147
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 196282.462 | 1.6357 | 12000000 | 0.014725
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2 | Current Study |  | (478.00, 478.00) | 180987.9667 | 0.99993 | 18100000 | 0.005578
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 169405.9171 | 1.4117 | 12000000 | 0.039839
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 156923.6858 | 1.3077 | 12000000 | 0.029724
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 137714.2592 | 2.5984 | 5300000 | 0.053287
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 134355.0395 | 2.535 | 5300000 | 0.042477
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 128912.5426 | 2.4323 | 5300000 | 0.042477
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 122209.0673 | 0.81811 | 14938000 | 0.058092
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 121416.3632 | 1.0118 | 12000000 | 0.029724
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 118306.3058 | 0.81811 | 14460953.1406 | 0.058092
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 116723.8791 | 2.2023 | 5300000 | 0.070405
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 113833.1517 | 1.7247 | 6600000 | 0.046957
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 111326.9527 | 0.95478 | 11660000 | 0.036263
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511477 S.W.S.-4 138 521089 WASHITA4 138 1 | Current Study | 2.05 | (717.00, 717.00) | 111229.5059 | 4.5215 | 2460000 | 0.019192
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 109453.7968 | 2.0652 | 5300000 | 0.039839
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 106690.1118 | 0.65891 | 16192000 | 0.049253
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 90909.5472 | 1.3774 | 6600000 | 0.036263
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 89652.1726 | 1.6916 | 5300000 | 0.053287
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 89318.9169 | 1.3533 | 6600000 | 0.029724
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 89318.9169 | 1.3533 | 6600000 | 0.029724
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 84879.3775 | 1.2861 | 6600000 | 0.029724
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 82583.5967 | 1.5582 | 5300000 | 0.02955
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 79054.6644 | 1.4916 | 5300000 | 0.034081
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 77654.1294 | 1.4652 | 5300000 | 0.034081
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 75060.9378 | 3.0858 | 2432500 | 0.042477
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 74610.5511 | 1.4077 | 5300000 | 0.029724
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 73236.4002 | 1.3818 | 5300000 | 0.034081
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 68968.7746 | 2.3222 | 2970000 | 0.062701
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 68408.1963 | 3.1095 | 2200000 | 0.036556
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 63610.6355 | 1.2002 | 5300000 | 0.043075
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 61307.545 | 1.7417 | 3520000 | 0.046957
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 59163.9097 | 1.1163 | 5300000 | 0.10657
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 56605.0125 | 1.7417 | 3250000 | 0.046957
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 55342.5175 | 1.7028 | 3250000 | 0.029724
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 51087.9812 | 2.3222 | 2200000 | 0.062701
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 50744.294 | 1.5614 | 3250000 | 0.046957
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 47396.8463 | 1.4584 | 3250000 | 0.029724
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 46978.7499 | 1.4455 | 3250000 | 0.029724
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 46975.8408 | 1.4454 | 3250000 | 0.029724
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 45751.753 | 1.4077 | 3250000 | 0.029724
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 44579.3535 | 0.84112 | 5300000 | 0.049253
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 42895.5313 | 1.3199 | 3250000 | 0.029724
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 41411.2177 | 0.78134 | 5300000 | 0.003872
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 39967.6073 | 3.0278 | 1320000 | 0.042477
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 39357.9246 | 1.211 | 3250000 | 0.029724
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 39025.6245 | 1.2008 | 3250000 | 0.036263
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 37745.1904 | 0.31454 | 12000000 | 0.029173
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 30692.4339 | 1.3345 | 2300000 | 0.062701
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 29360.3666 | 1.207 | 2432500 | 0.036263
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 28953.3402 | 1.1903 | 2432500 | 0.036263
GEN-2024-230 | 04 SOUTHEAST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 28503.7259 | 2.0655 | 1380000 | 0.087162
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 26603.8862 | 1.9278 | 1380000 | 0.04489
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 21067.9222 | 1.5267 | 1380000 | 0.049582
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at SEGNTP 3 115 kV | Current Study |  |  | 19643.7475 | 0.88785 | 2212500 | 0.049253
GEN-2024-230 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 19490.6075 | 0.36775 | 5300000 | 0.04186
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 19141.2828 | 1.387 | 1380000 | 0.036263
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 10871.9543 | 0.65891 | 1650000 | 0.049253
GEN-2024-230 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 9323.4473 | 0.4214 | 2212500 | 0.029173
GEN-2024-231 | 02 NEBRASKA | TBD | ERIS | Rebuild line 532913 KELLY 5 161 532920 TECHILL5 161 1 | Current Study | 52.64 | (160.00, 160.00) | 17171205.6114 | 21.7467 | 78960000 | 0.15204
GEN-2024-231 | 02 NEBRASKA | TBD | ERIS | Rebuild line 533210 ENEMEHA3 115 533212 KINGFISH3 115 1 | Current Study | 16.47 | (115.00, 115.00) | 3657291.1829 | 22.2058 | 16470000 | 0.069047
GEN-2024-231 | 02 NEBRASKA | TBD | NRIS | Rebuild line 647101 AUBRNT 8 69 647975 S975 8 69 1 | Current Study | 14.17 | (106.00, 106.00) | 3274921.8878 | 27.1902 | 12044500 | 0.042879
GEN-2024-231 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 532913 KELLY 5 161 532942 KELLY 1 13 533217 KELLY 3 115 M2 | Current Study |  | (144.00, 144.00) | 2726708.6648 | 22.7226 | 12000000 | 0.1357
GEN-2024-231 | 02 NEBRASKA | TBD | NRIS | Rebuild line 645456 S3456 3 345 645458 S3458 3 345 1 | Current Study | 44.95 | (1793.00, 1793.00) | 2269288.0205 | 2.2948 | 98890000 | 0.031162
GEN-2024-231 | 02 NEBRASKA | TBD | ERIS | Rebuild line 533210 ENEMEHA3 115 533217 KELLY 3 115 1 | Current Study | 8.7 | (115.00, 115.00) | 1929896.0442 | 22.1827 | 8700000 | 0.069112
GEN-2024-231 | 02 NEBRASKA | TBD | NRIS | Rebuild 3-winding transformer 640234 HUMBOLT5 161 647975 S975 8 69 648275 S975T4 9 13 1 | Current Study |  | (102.00, 102.00) | 1651803.7667 | 27.1902 | 6075000 | 0.042879
GEN-2024-231 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640140 COOPER 5 161 778110 G24-038-TAP 161 1 | Current Study | 11.26 | (446.00, 446.00) | 1097396.9553 | 6.4973 | 16890000 | 0.32802
GEN-2024-231 | 02 NEBRASKA | TBD | ERIS | Rebuild line 646263 S1263 5 161 646280 S1280 5 161 1 | Current Study | 8 | (309.00, 309.00) | 788157.6198 | 6.568 | 12000000 | 0.10799
GEN-2024-231 | 02 NEBRASKA | TBD | ERIS | Rebuild line 647963 S963 8 69 647977 S977 8 69 1 | Current Study | 8.02 | (106.00, 106.00) | 623962.9971 | 9.153 | 6817000 | 0.027659
GEN-2024-231 | 02 NEBRASKA | TBD | NRIS | Add 78 MVAR SVC at STEGALL_-MB3 345 kV | Current Study |  |  | 516361.7392 | 4.303 | 12000000 | 0.034744
GEN-2024-231 | 02 NEBRASKA | TBD | ERIS | Rebuild line 647401 NCU903 8 69 647977 S977 8 69 1 | Current Study | 6.05 | (106.00, 106.00) | 470695.2783 | 9.153 | 5142500 | 0.027659
GEN-2024-231 | 02 NEBRASKA | TBD | ERIS | Rebuild 3-winding transformer 646263 S1263 5 161 647111 W BROCK8 69 648263 S1263T19 13 1 | Current Study |  | (121.00, 121.00) | 132009.4398 | 2.173 | 6075000 | 0.0091336
GEN-2024-231 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659202 LO.KVA2_-BE9 13 M2 | Current Study |  | (500.00, 617.00) | 123135.0347 | 0.49254 | 25000000 | 0.008341
GEN-2024-231 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659201 LO.KU1A_-BE9 13 M2 | Current Study |  | (600.00, 637.40) | 121442.7669 | 0.48577 | 25000000 | 0.0094566
GEN-2024-231 | 02 NEBRASKA | TBD | NRIS | Add 0.09 MVAR switched shunt at GRAY CO3 115 kV | Current Study |  |  | 13977.8466 | 0.63177 | 2212500 | 0.035292
GEN-2024-231 | 02 NEBRASKA | TBD | NRIS | Add 16 MVAR switched shunt at UNDERWOOD 2 345 kV | Current Study |  |  | 7745.0226 | 0.14613 | 5300000 | 0.035292
GEN-2024-231 | 02 NEBRASKA | TBD | ERIS | Add 0.5 MVAR switched shunt at RKY_RDG4 138 kV | Current Study |  |  | 3806.9266 | 0.1565 | 2432500 | 0.029855
GEN-2024-231 | 02 NEBRASKA | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 794.7813 | 0.057593 | 1380000 | 0.027796
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 1806056.6058 | 1.2021 | 150244000 | 0.021793
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1144053.9304 | 1.1982 | 95480000 | 0.038765
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 1014886.5512 | 1.1982 | 84700000 | 0.038765
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 993690.3716 | 0.45515 | 218320000 | 0.011236
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 930312.2161 | 0.64697 | 143796000 | 0.025851
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 731169.7537 | 0.36833 | 198511000 | 0.015751
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 728282.918 | 0.64568 | 112794000 | 0.043997
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 667235.5486 | 1.4199 | 46992000 | 0.046006
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 609290.2504 | 0.48812 | 124824000 | 0.025547
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 599729.51 | 0.94819 | 63250000 | 0.041189
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 579220.5935 | 4.8268 | 12000000 | 0.057435
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at PHILL 7 345 kV | Current Study |  |  | 492831.2919 | 9.2987 | 5300000 | 0.033174
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV | Current Study |  |  | 477694.1635 | 34.6155 | 1380000 | 0.36513
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 328862.4865 | 2.7405 | 12000000 | 0.073948
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 300777.6946 | 2.5065 | 12000000 | 0.073948
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 293425.4784 | 4.4458 | 6600000 | 0.073948
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 262040.4378 | 2.1837 | 12000000 | 0.073948
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 251717.2194 | 2.0976 | 12000000 | 0.073948
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 245044.7003 | 2.042 | 12000000 | 0.057435
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 233343.3666 | 4.4027 | 5300000 | 0.057435
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 230508.5687 | 1.9209 | 12000000 | 0.073948
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 223911.569 | 0.87213 | 25674000 | 0.024493
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 175969.6991 | 2.6662 | 6600000 | 0.073948
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 169326.9233 | 1.4111 | 12000000 | 0.057435
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 146935.2904 | 4.5211 | 3250000 | 0.073948
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 146935.2904 | 4.5211 | 3250000 | 0.073948
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 145865.7186 | 1.2155 | 12000000 | 0.032907
GEN-2024-232 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 143886.8015 | 0.79495 | 18100000 | 0.0097431
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 133760.2668 | 2.5238 | 5300000 | 0.057435
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 129036.8004 | 1.0753 | 12000000 | 0.020273
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 114306.6936 | 0.95256 | 12000000 | 0.024977
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 114306.6936 | 0.95256 | 12000000 | 0.024977
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 113874.3005 | 0.94895 | 12000000 | 0.025884
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 111325.1749 | 0.92771 | 12000000 | 0.020273
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 91002.2486 | 1.717 | 5300000 | 0.073948
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 88929.8903 | 2.7363 | 3250000 | 0.073948
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 86617.5336 | 2.6652 | 3250000 | 0.073948
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 82812.4459 | 3.7429 | 2212500 | 0.15132
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 81595.8169 | 2.5106 | 3250000 | 0.073948
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 80290.6336 | 3.629 | 2212500 | 0.15132
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 78312.556 | 1.1866 | 6600000 | 0.038765
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 74179.4322 | 0.49279 | 15053000 | 0.0052142
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 66610.3683 | 4.8268 | 1380000 | 0.057435
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 66594.278 | 2.0491 | 3250000 | 0.073948
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 64815.7678 | 0.98206 | 6600000 | 0.025884
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 64815.7678 | 0.98206 | 6600000 | 0.025884
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 64462.8452 | 0.53719 | 12000000 | 0.015065
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 60439.6949 | 1.1404 | 5300000 | 0.043747
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 55761.2428 | 4.0407 | 1380000 | 0.073948
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 54580.377 | 0.36538 | 14938000 | 0.031134
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 54142.3958 | 1.0216 | 5300000 | 0.025884
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 52837.346 | 0.36538 | 14460953.1406 | 0.031134
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 42177.1034 | 1.1982 | 3520000 | 0.038765
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 42170.7861 | 1.4199 | 2970000 | 0.046006
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 40364.1848 | 0.76159 | 5300000 | 0.02879
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 38941.9351 | 1.1982 | 3250000 | 0.038765
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 34399.6375 | 2.4927 | 1380000 | 0.057435
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 33200.5258 | 1.0216 | 3250000 | 0.025884
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 31237.6193 | 1.4199 | 2200000 | 0.046006
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 28365.1976 | 2.0554 | 1380000 | 0.057435
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 23927.2943 | 0.45146 | 5300000 | 0.0026847
GEN-2024-232 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 23110.0813 | 0.43604 | 5300000 | 0.05956
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 18766.7493 | 0.81595 | 2300000 | 0.046006
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 18414.7232 | 0.75703 | 2432500 | 0.027468
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 15578.852 | 1.1289 | 1380000 | 0.043996
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 12540.3755 | 0.5668 | 2212500 | 0.048341
GEN-2024-234 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659202 LO.KVA2_-BE9 13 M2 | Current Study |  | (500.00, 617.00) | 387442.8461 | 1.5498 | 25000000 | 0.0085296
GEN-2024-234 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659201 LO.KU1A_-BE9 13 M2 | Current Study |  | (600.00, 637.40) | 382118.1466 | 1.5285 | 25000000 | 0.0096704
GEN-2024-234 | 02 NEBRASKA | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 3603.0889 | 0.26109 | 1380000 | 0.040954
GEN-2024-234 | 02 NEBRASKA | TBD | ERIS | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1 | Current Study | 0.06 | (140.00, 140.00) | 1976.6469 | 3.8758 | 51000 | 0.01273
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 3524151.2394 | 6.3341 | 55638000 | 0.11429
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 532803 BURNS 7 345 1 | Current Study | 50.03 | (1793.00, 1793.00) | 2557310.5248 | 2.3234 | 110066000 | 0.0194
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532803 BURNS 7 345 1 | Current Study | 45.5 | (1793.00, 1793.00) | 2325757.1233 | 2.3234 | 100100000 | 0.0194
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 2162903.2825 | 1.4396 | 150244000 | 0.026099
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 2037008.6359 | 4.5432 | 44836000 | 0.085329
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1850307.0121 | 1.8424 | 100427000 | 0.01893
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 1762038.6053 | 1.9592 | 89936000 | 0.018308
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1523170.2841 | 0.69768 | 218320000 | 0.017223
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 1474340.965 | 1.2571 | 117282000 | 0.021162
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 1411218.0415 | 2.1382 | 66000000 | 0.039317
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1209071.1912 | 0.84082 | 143796000 | 0.033597
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1050571.2029 | 1.1003 | 95480000 | 0.035598
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 931958.3251 | 1.1003 | 84700000 | 0.035598
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 731082.8403 | 2.1762 | 33594000 | 0.071039
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 689175.2081 | 0.73329 | 93984000 | 0.036401
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 638046.7708 | 1.1568 | 55154000 | 0.01632
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 616600.9201 | 0.31061 | 198511000 | 0.013283
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 593070.3614 | 1.2917 | 45914000 | 0.052239
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 576554.7156 | 0.3493 | 165062000 | 0.017582
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 542235.569 | 2.0712 | 26180000 | 0.018722
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 506590.5272 | 4.2216 | 12000000 | 0.11429
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 486496.8843 | 0.36594 | 132946000 | 0.0091016
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 404977.9776 | 3.3748 | 12000000 | 0.11429
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 370507.5902 | 0.29682 | 124824000 | 0.015535
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 350076.7633 | 0.74497 | 46992000 | 0.024138
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 337485.7915 | 1.3339 | 25300000 | 0.021858
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 323673.7622 | 1.2917 | 25058000 | 0.052239
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 305407.3095 | 1.1568 | 26400000 | 0.01632
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 273521.2128 | 1.8171 | 15053000 | 0.019226
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 261657.7864 | 4.9369 | 5300000 | 0.11429
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 228652.8107 | 0.2806 | 81488000 | 0.014905
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 0.06 MVAR switched shunt at G24-125-TAP 345 kV | Current Study |  |  | 226326.7932 | 4.2703 | 5300000 | 0.024399
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 203370.3014 | 1.6948 | 12000000 | 0.018308
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 122 MVAR switched shunt at HOYT 7 345 kV | Current Study |  |  | 192054.2849 | 3.6237 | 5300000 | 0.021402
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 168233.8713 | 1.4019 | 12000000 | 0.039317
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 158277.0983 | 1.2847 | 12320000 | 0.022053
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 153264.2816 | 1.2772 | 12000000 | 0.051986
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 148977.5822 | 1.2415 | 12000000 | 0.022053
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 148977.5822 | 1.2415 | 12000000 | 0.022053
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 146253.1138 | 1.2188 | 12000000 | 0.046919
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 140370.276 | 1.1698 | 12000000 | 0.022053
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 132822.1776 | 1.1069 | 12000000 | 0.022053
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 115267.4383 | 2.1749 | 5300000 | 0.023102
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 107390.6417 | 0.89492 | 12000000 | 0.02441
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 105897.7766 | 0.88248 | 12000000 | 0.024399
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 103795.6375 | 1.9584 | 5300000 | 0.041041
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 103693.2617 | 0.86411 | 12000000 | 0.018883
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 100924.4865 | 0.84104 | 12000000 | 0.022053
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 100924.4865 | 0.84104 | 12000000 | 0.022053
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 100370.1735 | 1.8938 | 5300000 | 0.018883
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 98074.599 | 0.81729 | 12000000 | 0.022053
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 94089.5133 | 0.78408 | 12000000 | 0.022053
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 93829.6833 | 1.7704 | 5300000 | 0.035598
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 93127.2857 | 0.79869 | 11660000 | 0.036401
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 89699.0475 | 0.74749 | 12000000 | 0.022053
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 83091.2242 | 0.69243 | 12000000 | 0.02441
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 76047.3587 | 1.1522 | 6600000 | 0.036401
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 71913.4717 | 1.0896 | 6600000 | 0.035598
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 61125.3538 | 0.92614 | 6600000 | 0.02441
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 61125.3538 | 0.92614 | 6600000 | 0.02441
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 58616.9281 | 0.10965 | 53460000 | 0.0031662
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 58087.1573 | 0.88011 | 6600000 | 0.02441
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 57908.3935 | 0.35764 | 16192000 | 0.032079
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 56823.6905 | 1.0721 | 5300000 | 0.024399
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at SLKHILLS 4 138 kV | Current Study |  |  | 54278.2811 | 2.2314 | 2432500 | 0.067113
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 52870.5252 | 0.99756 | 5300000 | 0.11429
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 51059.6913 | 0.96339 | 5300000 | 0.02441
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 51035.5943 | 0.96294 | 5300000 | 0.036401
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 49180.567 | 0.92794 | 5300000 | 0.035598
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 46719.4582 | 0.31276 | 14938000 | 0.02665
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 45227.4666 | 0.31276 | 14460953.1406 | 0.02665
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 44796.1632 | 0.84521 | 5300000 | 0.036401
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 42437.8856 | 0.80071 | 5300000 | 0.0047616
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 38730.7356 | 1.1003 | 3520000 | 0.035598
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 37873.6227 | 1.1653 | 3250000 | 0.02441
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 35853.8148 | 0.67649 | 5300000 | 0.018883
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 35759.9074 | 1.1003 | 3250000 | 0.035598
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 33814.0979 | 0.638 | 5300000 | 0.018883
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 32645.5885 | 1.0045 | 3250000 | 0.036401
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 32436.0068 | 0.99803 | 3250000 | 0.02441
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 32149.8828 | 0.98923 | 3250000 | 0.02441
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 32147.8919 | 0.98917 | 3250000 | 0.02441
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 32057.4305 | 0.98638 | 3250000 | 0.035598
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 31310.1881 | 0.96339 | 3250000 | 0.02441
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 29988.629 | 0.56582 | 5300000 | 0.015514
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 29355.5343 | 0.90325 | 3250000 | 0.02441
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 26934.575 | 0.82876 | 3250000 | 0.02441
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 25450.6091 | 1.1568 | 2200000 | 0.01632
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 24560.4384 | 1.0097 | 2432500 | 0.036401
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 24219.954 | 0.99568 | 2432500 | 0.036401
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 24196.3487 | 0.45653 | 5300000 | 0.032079
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 22125.6381 | 0.74497 | 2970000 | 0.024138
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 19417.3809 | 1.4071 | 1380000 | 0.039317
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 19002.3699 | 0.15835 | 12000000 | 0.017624
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 16593.5956 | 1.2571 | 1320000 | 0.021162
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 16389.3616 | 0.74497 | 2200000 | 0.024138
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 16012.0036 | 1.1603 | 1380000 | 0.036401
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 13128.6694 | 0.59339 | 2212500 | 0.050609
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 11496.3274 | 0.21691 | 5300000 | 0.0053381
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 9846.313 | 0.4281 | 2300000 | 0.024138
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 5900.9912 | 0.35764 | 1650000 | 0.032079
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 2182.648 | 0.089729 | 2432500 | 0.0014822
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 709.9686 | 0.032089 | 2212500 | 0.00082521
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 1 | Current Study |  | (1868.00, 1868.00) | 4802351.336 | 7.8087 | 61500000 | 0.15757
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 2 | Current Study |  | (1868.00, 1868.00) | 4802351.336 | 7.8087 | 61500000 | 0.15757
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 1728074.93 | 1.1502 | 150244000 | 0.021595
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 1492623.392 | 5.8138 | 25674000 | 0.16909
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 1455252.4205 | 1.6181 | 89936000 | 0.015659
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1248674.7597 | 1.2434 | 100427000 | 0.01323
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1212743.0933 | 0.55549 | 218320000 | 0.014201
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at GEN-2024-157 138 kV | Current Study |  |  | 1134623.3538 | 46.6443 | 2432500 | 0.029056
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 1098711.5334 | 2.4505 | 44836000 | 0.047664
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 1068017.0586 | 1.6182 | 66000000 | 0.030815
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 1063452.5116 | 5.9384 | 17908000 | 0.17558
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 976173.5757 | 0.67886 | 143796000 | 0.028092
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 888634.8449 | 0.44912 | 197860000 | 0.01839
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 877668.4099 | 0.91922 | 95480000 | 0.030798
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 827965.6084 | 0.41709 | 198511000 | 0.018472
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 794256.1016 | 0.67722 | 117282000 | 0.011807
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 778576.8152 | 0.91922 | 84700000 | 0.030798
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 733788.2547 | 1.3189 | 55638000 | 0.024644
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 644764.0413 | 0.39062 | 165062000 | 0.020362
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1 | Current Study | 11.3 | (1793.00, 1793.00) | 581324.6926 | 2.3384 | 24860000 | 0.059757
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 551538.0122 | 0.58684 | 93984000 | 0.030169
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 528326.5449 | 1.5727 | 33594000 | 0.053166
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 504535.4507 | 0.3795 | 132946000 | 0.0097754
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 468432.0501 | 0.99683 | 46992000 | 0.033449
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 431225.5448 | 0.34547 | 124824000 | 0.018725
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 414049.6281 | 1.5815 | 26180000 | 0.014806
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 356770.8525 | 0.64686 | 55154000 | 0.0094508
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 68 MVAR SVC at TONTITN7 345 kV | Current Study |  |  | 296089.5646 | 2.4674 | 12000000 | 0.013946
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 290998.5041 | 0.35711 | 81488000 | 0.019645
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 284505.8101 | 1.1245 | 25300000 | 0.019083
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 238788.1672 | 1.9899 | 12000000 | 0.024521
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 226150.7318 | 1.8846 | 12000000 | 0.036796
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 195109.2222 | 1.6259 | 12000000 | 0.036796
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 185082.4901 | 1.2295 | 15053000 | 0.013473
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 170771.848 | 0.64686 | 26400000 | 0.0094508
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 167961.7752 | 1.3997 | 12000000 | 0.015659
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 151587.7355 | 1.2632 | 12000000 | 0.036796
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 141648.6248 | 1.1804 | 12000000 | 0.033344
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 136097.8077 | 1.1341 | 12000000 | 0.030798
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 136097.8077 | 1.1341 | 12000000 | 0.030798
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 132254.7023 | 1.1021 | 12000000 | 0.030798
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 129485.3646 | 0.28202 | 45914000 | 0.011812
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 123531.1081 | 1.0294 | 12000000 | 0.043394
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 120629.8593 | 2.276 | 5300000 | 0.025038
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 119192.5174 | 0.99327 | 12000000 | 0.030348
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 116278.973 | 1.7618 | 6600000 | 0.030348
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 110752.1389 | 0.92293 | 12000000 | 0.036796
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 109597.6097 | 0.91331 | 12000000 | 0.033344
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 105480.7649 | 0.87901 | 12000000 | 0.024644
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 100225.0676 | 1.891 | 5300000 | 0.041041
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 96197.6067 | 1.815 | 5300000 | 0.024521
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 93811.5311 | 1.77 | 5300000 | 0.018278
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 87995.8835 | 0.71425 | 12320000 | 0.012697
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 84578.5808 | 0.70482 | 12000000 | 0.020182
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 84323.3037 | 0.70269 | 12000000 | 0.024644
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 83384.3339 | 0.69487 | 12000000 | 0.020182
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 82825.716 | 0.69021 | 12000000 | 0.012697
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 82825.716 | 0.69021 | 12000000 | 0.012697
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 82745.7845 | 1.5612 | 5300000 | 0.036796
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 80624.5513 | 1.2216 | 6600000 | 0.033344
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 80624.5513 | 1.2216 | 6600000 | 0.033344
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 78387.2162 | 1.479 | 5300000 | 0.030798
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 76617.1597 | 1.1609 | 6600000 | 0.033344
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 74528.5632 | 0.63918 | 11660000 | 0.030169
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 73843.9422 | 0.61537 | 12000000 | 0.012697
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 70667.8631 | 0.28202 | 25058000 | 0.011812
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 68728.4811 | 2.1147 | 3250000 | 0.033344
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 68728.4811 | 2.1147 | 3250000 | 0.033344
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 67347.908 | 1.2707 | 5300000 | 0.033344
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 64136.9065 | 0.3961 | 16192000 | 0.036796
GEN-2024-236 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 63205.7825 | 1.1926 | 5300000 | 0.1687
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 61481.4377 | 0.41158 | 14938000 | 0.03632
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 60859.7176 | 0.92212 | 6600000 | 0.030169
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 60077.9696 | 0.91027 | 6600000 | 0.030798
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 59518.0205 | 0.41158 | 14460953.1406 | 0.03632
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 58227.6794 | 1.7916 | 3250000 | 0.030348
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 58227.6794 | 1.7916 | 3250000 | 0.030348
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 55864.0454 | 1.7189 | 3250000 | 0.033344
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 54481.602 | 1.028 | 5300000 | 0.024644
GEN-2024-236 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 53669.8683 | 0.29652 | 18100000 | 0.0037637
GEN-2024-236 | 04 SOUTHEAST | TBD | NRIS | Add 0.09 MVAR switched shunt at GRAY CO3 115 kV | Current Study |  |  | 52824.5535 | 2.3876 | 2212500 | 0.035913
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 49955.4383 | 1.5371 | 3250000 | 0.033344
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 42783.2042 | 1.3164 | 3250000 | 0.033344
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 42405.8056 | 1.3048 | 3250000 | 0.033344
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 42403.1797 | 1.3047 | 3250000 | 0.033344
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 41755.9175 | 0.078107 | 53460000 | 0.0023358
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 41298.2455 | 1.2707 | 3250000 | 0.033344
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 41086.4409 | 0.77522 | 5300000 | 0.030798
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 40843.126 | 0.77063 | 5300000 | 0.030169
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 39622.3546 | 0.74759 | 5300000 | 0.033344
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 38720.0504 | 1.1914 | 3250000 | 0.033344
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 37713.2509 | 1.1604 | 3250000 | 0.033344
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 35526.7968 | 1.0931 | 3250000 | 0.033344
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 33510.9639 | 0.63228 | 5300000 | 0.018278
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 32356.4391 | 0.91922 | 3520000 | 0.030798
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 31604.5314 | 0.59631 | 5300000 | 0.018278
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 29874.5503 | 0.91922 | 3250000 | 0.030798
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 29605.9582 | 0.99683 | 2970000 | 0.033449
GEN-2024-236 | 04 SOUTHEAST | TBD | NRIS | Add 16 MVAR switched shunt at UNDERWOOD 2 345 kV | Current Study |  |  | 29269.6989 | 0.55226 | 5300000 | 0.035913
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 28875.1311 | 0.88847 | 3250000 | 0.033344
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 27460.6392 | 1.9899 | 1380000 | 0.024521
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 27396.316 | 0.51691 | 5300000 | 0.0031834
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 26939.334 | 0.50829 | 5300000 | 0.014433
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 26798.8603 | 0.50564 | 5300000 | 0.036796
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 26781.4262 | 0.82404 | 3250000 | 0.030798
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 23439.5932 | 1.6985 | 1380000 | 0.033344
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 22097.127 | 1.6012 | 1380000 | 0.030348
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 21930.3394 | 0.99683 | 2200000 | 0.033449
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 20427.4007 | 0.83977 | 2432500 | 0.031556
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 19655.4012 | 0.80803 | 2432500 | 0.030169
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 19429.6613 | 0.16191 | 12000000 | 0.018663
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 19382.9159 | 0.79683 | 2432500 | 0.030169
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 19283.938 | 1.3974 | 1380000 | 0.033344
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 15548.4826 | 0.70276 | 2212500 | 0.030348
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 14695.1738 | 1.0649 | 1380000 | 0.030815
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 14230.9873 | 0.64686 | 2200000 | 0.0094508
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 13175.1908 | 0.57283 | 2300000 | 0.033449
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 12814.1994 | 0.92857 | 1380000 | 0.030169
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 9366.9869 | 0.17674 | 5300000 | 0.0045043
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 9216.9509 | 0.41659 | 2212500 | 0.036796
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 8939.2921 | 0.67722 | 1320000 | 0.011807
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 7287.1034 | 0.32936 | 2212500 | 0.01379
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 6535.6902 | 0.3961 | 1650000 | 0.036796
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 5672.0104 | 0.10702 | 5300000 | 0.012697
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 2264.9823 | 0.093113 | 2432500 | 0.0015929
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 12343090.7937 | 1.3131 | 940000000 | 0.018553
GEN-2024-239 | 04 SOUTHEAST | TBD | NRIS | Add 3-winding transformer 514898 CIMARON4 138 514901 CIMARON7 345 515715 CIMARO21 13 M2 | Current Study |  | (478.00, 478.00) | 5277340.176 | 29.1566 | 18100000 | 0.035845
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 532803 BURNS 7 345 1 | Current Study | 50.03 | (1793.00, 1793.00) | 4619954.7791 | 4.1974 | 110066000 | 0.043808
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532803 BURNS 7 345 1 | Current Study | 45.5 | (1793.00, 1793.00) | 4201637.8663 | 4.1974 | 100100000 | 0.043808
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 2438677.0297 | 2.0793 | 117282000 | 0.043755
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 2340018.846 | 1.5575 | 150244000 | 0.035295
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 1484505.0473 | 2.6681 | 55638000 | 0.060177
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1419201.5034 | 1.4132 | 100427000 | 0.018149
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1401165.6355 | 0.64179 | 218320000 | 0.019804
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 1388245.9045 | 3.0963 | 44836000 | 0.072691
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 1224006.7778 | 1.361 | 89936000 | 0.015897
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1170122.1561 | 1.2255 | 95480000 | 0.049561
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 1159174.2153 | 2.1017 | 55154000 | 0.037063
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1149551.6528 | 0.79943 | 143796000 | 0.039929
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 1097800.2685 | 1.6633 | 66000000 | 0.038231
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1044843.1784 | 0.52634 | 198511000 | 0.028135
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 1038011.5901 | 1.2255 | 84700000 | 0.049561
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 932193.9964 | 0.74681 | 124824000 | 0.048858
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 835221.4471 | 0.42213 | 197860000 | 0.020862
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 707118.4942 | 1.5048 | 46992000 | 0.060945
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 638230.9767 | 1.3901 | 45914000 | 0.070271
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 614092.1407 | 0.7536 | 81488000 | 0.050038
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 601781.2803 | 0.36458 | 165062000 | 0.022939
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 595868.9985 | 0.63401 | 93984000 | 0.039341
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 584995.3458 | 0.44002 | 132946000 | 0.01368
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 554850.0432 | 2.1017 | 26400000 | 0.037063
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 457574.5671 | 1.3621 | 33594000 | 0.055578
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 442736.4895 | 1.6911 | 26180000 | 0.019109
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 348320.5953 | 1.3901 | 25058000 | 0.070271
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 344691.8399 | 1.3624 | 25300000 | 0.027906
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 342927.329 | 0.64147 | 53460000 | 0.023154
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 122 MVAR switched shunt at HOYT 7 345 kV | Current Study |  |  | 290747.9975 | 5.4858 | 5300000 | 0.0405
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 254662.6611 | 2.0671 | 12320000 | 0.044354
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 138 MVAR switched shunt at GEN-2024-016 345 kV | Current Study |  |  | 251001.8047 | 4.7359 | 5300000 | 0.029649
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 239700.6272 | 1.9975 | 12000000 | 0.044354
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 239700.6272 | 1.9975 | 12000000 | 0.044354
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 0.06 MVAR switched shunt at G24-125-TAP 345 kV | Current Study |  |  | 236399.7078 | 4.4604 | 5300000 | 0.031857
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 231789.5382 | 0.90282 | 25674000 | 0.031694
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 213707.0478 | 1.7809 | 12000000 | 0.044354
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 213394.4268 | 1.7783 | 12000000 | 0.060177
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 210212.871 | 1.3965 | 15053000 | 0.01847
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 170591.5108 | 1.4216 | 12000000 | 0.060177
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 170222.7625 | 1.4185 | 12000000 | 0.033429
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 169652.5031 | 1.4138 | 12000000 | 0.049561
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 167095.4969 | 1.3925 | 12000000 | 0.070847
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 165099.2388 | 0.92193 | 17908000 | 0.0329
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 162384.5839 | 1.3532 | 12000000 | 0.044354
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 162384.5839 | 1.3532 | 12000000 | 0.044354
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 155671.435 | 1.2973 | 12000000 | 0.043756
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 154002.8254 | 1.2834 | 12000000 | 0.044354
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 151387.3095 | 1.2616 | 12000000 | 0.044354
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 146857.9409 | 1.2238 | 12000000 | 0.033429
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 144323.1768 | 1.2027 | 12000000 | 0.044354
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 142151.5417 | 2.6821 | 5300000 | 0.033429
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 141273.488 | 1.1773 | 12000000 | 0.015897
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 136138.1845 | 2.5686 | 5300000 | 0.034106
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 124781.5225 | 1.0398 | 12000000 | 0.050038
GEN-2024-239 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 113016.2883 | 0.6244 | 18100000 | 0.009566
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 110219.8133 | 2.0796 | 5300000 | 0.060177
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 108615.7001 | 0.90513 | 12000000 | 0.030861
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 92266.2879 | 1.7409 | 5300000 | 0.043756
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 88528.7355 | 1.6704 | 5300000 | 0.043756
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 84039.0871 | 0.70033 | 12000000 | 0.030861
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 80518.9476 | 0.69056 | 11660000 | 0.039341
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 80097.0326 | 1.2136 | 6600000 | 0.049561
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 78304.5075 | 1.4774 | 5300000 | 0.070847
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 78140.2391 | 0.5231 | 14938000 | 0.055716
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 75644.821 | 0.5231 | 14460953.1406 | 0.055716
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 67781.9131 | 1.2789 | 5300000 | 0.039341
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 65751.655 | 0.99624 | 6600000 | 0.039341
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 61822.641 | 0.93671 | 6600000 | 0.030861
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 61822.641 | 0.93671 | 6600000 | 0.030861
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 59804.5188 | 0.36935 | 16192000 | 0.041412
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 59352.6892 | 1.1199 | 5300000 | 0.031857
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 58749.7864 | 0.89015 | 6600000 | 0.030861
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 51694.6042 | 0.97537 | 5300000 | 0.033429
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 51642.1546 | 0.97438 | 5300000 | 0.030861
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 51546.9618 | 2.1191 | 2432500 | 0.043756
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 50778.7809 | 0.95809 | 5300000 | 0.033429
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 47889.9854 | 0.90358 | 5300000 | 0.033429
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 46237.5036 | 2.1017 | 2200000 | 0.037063
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 44691.4779 | 1.5048 | 2970000 | 0.060945
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 44126.1188 | 0.83257 | 5300000 | 0.039341
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 43665.9162 | 0.82389 | 5300000 | 0.044354
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 43138.144 | 1.2255 | 3520000 | 0.049561
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 39829.2893 | 1.2255 | 3250000 | 0.049561
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 38305.6659 | 1.1786 | 3250000 | 0.030861
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 35705.4805 | 1.0986 | 3250000 | 0.049561
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 33104.7984 | 1.5048 | 2200000 | 0.060945
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 32806.0205 | 1.0094 | 3250000 | 0.030861
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 32516.6324 | 1.0005 | 3250000 | 0.030861
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 32514.6189 | 1.0004 | 3250000 | 0.030861
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 31667.359 | 0.97438 | 3250000 | 0.030861
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 31419.3433 | 0.59282 | 5300000 | 0.0044067
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 29690.4074 | 0.91355 | 3250000 | 0.030861
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 28225.8518 | 0.86849 | 3250000 | 0.039341
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 27447.1247 | 2.0793 | 1320000 | 0.043755
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 27361.0627 | 1.2367 | 2212500 | 0.039753
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 27241.831 | 0.83821 | 3250000 | 0.030861
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 24988.7131 | 0.47149 | 5300000 | 0.041412
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 23475.6413 | 0.19563 | 12000000 | 0.027217
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 21235.3131 | 0.87298 | 2432500 | 0.039341
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 20940.9253 | 0.86088 | 2432500 | 0.039341
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 19888.5701 | 0.86472 | 2300000 | 0.060945
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 19304.4962 | 0.79361 | 2432500 | 0.035994
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 17308.5961 | 1.2542 | 1380000 | 0.043809
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 16415.0038 | 0.30972 | 5300000 | 0.044354
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 13844.2117 | 1.0032 | 1380000 | 0.039341
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 8594.3857 | 0.38845 | 2212500 | 0.041412
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 6094.2105 | 0.36935 | 1650000 | 0.041412
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 7695831.4257 | 8.1884 | 93984000 | 0.33874
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 3950717.2992 | 4.3928 | 89936000 | 0.034207
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 3905750.5139 | 3.8891 | 100427000 | 0.033299
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 3494475.0069 | 3.6599 | 95480000 | 0.098672
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 3099937.5061 | 3.6599 | 84700000 | 0.098672
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 1954286.7189 | 2.961 | 66000000 | 0.045373
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 1939668.4752 | 1.291 | 150244000 | 0.019504
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1660112.0709 | 0.7604 | 218320000 | 0.015642
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1184068.7589 | 0.82344 | 143796000 | 0.027418
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 957202.6874 | 3.6562 | 26180000 | 0.027542
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 849200.0968 | 12.8667 | 6600000 | 0.33874
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512734 FARML 4 138 778710 G24-058-TAP 138 1 | Current Study | 6.69 | (395.00, 395.00) | 734786.7059 | 9.1528 | 8028000 | 0.036288
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 722430.5349 | 6.0203 | 12000000 | 0.13871
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 650220.9885 | 5.4185 | 12000000 | 0.098672
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 645533.9734 | 5.3794 | 12000000 | 0.12228
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 577185.6212 | 3.8344 | 15053000 | 0.033809
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 575509.9208 | 2.2747 | 25300000 | 0.031062
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 569900.5502 | 10.7528 | 5300000 | 0.33874
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 541879.3211 | 4.5157 | 12000000 | 0.098672
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 541879.3211 | 4.5157 | 12000000 | 0.098672
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 526577.8305 | 4.3881 | 12000000 | 0.098672
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 506652.9086 | 4.2221 | 12000000 | 0.098672
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 505181.2832 | 4.2098 | 12000000 | 0.098672
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 500226.5264 | 9.4382 | 5300000 | 0.33874
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 464869.2867 | 3.8739 | 12000000 | 0.11381
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 455982.3763 | 3.7999 | 12000000 | 0.034207
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 419581.7124 | 3.4965 | 12000000 | 0.098672
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 369092.5751 | 3.0758 | 12000000 | 0.098672
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 364544.376 | 11.2168 | 3250000 | 0.33874
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 349082.4014 | 2.909 | 12000000 | 0.098672
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 341977.1448 | 5.1815 | 6600000 | 0.11381
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 341977.1448 | 5.1815 | 6600000 | 0.11381
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 285662.9268 | 5.3899 | 5300000 | 0.11381
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 277297.2743 | 2.3108 | 12000000 | 0.034207
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 277297.2743 | 2.3108 | 12000000 | 0.034207
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 274259.7117 | 11.2748 | 2432500 | 0.33874
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 270457.6148 | 11.1185 | 2432500 | 0.33874
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 263595.7745 | 0.22475 | 117282000 | 0.003153
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 261276.189 | 2.1773 | 12000000 | 0.034207
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 247226.6449 | 2.0602 | 12000000 | 0.034207
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 239203.0402 | 3.6243 | 6600000 | 0.098672
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 236952.9683 | 7.2909 | 3250000 | 0.11381
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 218661.3703 | 0.39646 | 55154000 | 0.0046609
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 181469.2646 | 5.5837 | 3250000 | 0.11381
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 179868.4904 | 5.5344 | 3250000 | 0.11381
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 179857.3523 | 5.5341 | 3250000 | 0.11381
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 178801.6735 | 12.9566 | 1380000 | 0.33874
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 175170.6627 | 5.3899 | 3250000 | 0.11381
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 163587.4455 | 3.0866 | 5300000 | 0.098672
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 159964.5474 | 4.922 | 3250000 | 0.11381
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 154202.2515 | 2.9095 | 5300000 | 0.014418
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 150690.4824 | 4.6366 | 3250000 | 0.11381
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 132526.2486 | 2.5005 | 5300000 | 0.047421
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 128828.5717 | 3.6599 | 3520000 | 0.098672
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 127210.2983 | 1.9274 | 6600000 | 0.044548
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 124554.765 | 2.3501 | 5300000 | 0.041041
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 118946.8171 | 3.6599 | 3250000 | 0.098672
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 108053.1159 | 0.20212 | 53460000 | 0.0048638
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 106631.4094 | 3.281 | 3250000 | 0.098672
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 106357.0656 | 0.88631 | 12000000 | 0.019995
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 104664.3974 | 0.39646 | 26400000 | 0.0046609
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 99421.3924 | 7.2044 | 1380000 | 0.11381
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 89373.9591 | 2.75 | 3250000 | 0.034891
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 89373.9591 | 2.75 | 3250000 | 0.034891
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 81794.7628 | 5.9272 | 1380000 | 0.11381
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 64961.6465 | 1.9988 | 3250000 | 0.034891
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 50351.2393 | 1.5493 | 3250000 | 0.034891
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 34826.5256 | 0.28268 | 12320000 | 0.0040437
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 26889.6282 | 1.9485 | 1380000 | 0.045373
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 19065.09 | 0.35972 | 5300000 | 0.0073771
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 8722.0331 | 0.39646 | 2200000 | 0.0046609
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 2966.7504 | 0.22475 | 1320000 | 0.003153
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1 | Current Study | 30.63 | (1793.00, 1793.00) | 3485965.3654 | 5.1731 | 67386000 | 0.1694
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1 | Current Study | 56.1 | (1793.00, 1793.00) | 2409865.176 | 1.9526 | 123420000 | 0.05601
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 776060 G23-204-TAP 345 1 | Current Study | 17.82 | (1793.00, 1793.00) | 2094207.3673 | 5.3418 | 39204000 | 0.40244
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | Current Study | 7.74 | (1793.00, 1793.00) | 1222345.5592 | 7.1784 | 17028000 | 0.40244
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 883706.3126 | 0.58818 | 150244000 | 0.026658
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | Current Study | 6.93 | (1793.00, 1793.00) | 814413.9762 | 5.3418 | 15246000 | 0.40244
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 796321.0339 | 0.706 | 112794000 | 0.12027
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 556772.4093 | 0.88027 | 63250000 | 0.095596
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 537445.9711 | 0.56289 | 95480000 | 0.045527
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 515008.1601 | 0.2359 | 218320000 | 0.014558
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 476766.5872 | 0.56289 | 84700000 | 0.045527
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 445916.9886 | 0.3101 | 143796000 | 0.030977
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 507454 TURK 4 138 507456 TURK 3 115 507458 TURK1 1 13 M2 | Current Study |  | (257.00, 257.00) | 436917.2182 | 4.2011 | 10400000 | 0.030847
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 424505.5354 | 0.4227 | 100427000 | 0.010857
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 360597.7643 | 0.18165 | 198511000 | 0.01942
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 320550.9466 | 0.68214 | 46992000 | 0.055255
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 311153.2537 | 0.24927 | 124824000 | 0.032616
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 272689.494 | 0.29014 | 93984000 | 0.036008
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 238996.5404 | 0.14479 | 165062000 | 0.01822
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 221041.2859 | 0.65798 | 33594000 | 0.053696
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 206411.5789 | 0.2533 | 81488000 | 0.033638
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 203805.0569 | 0.79382 | 25674000 | 0.055735
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 203165.0072 | 1.693 | 12000000 | 0.050364
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 764550 G20-087-TAP 345 1 | Current Study | 14.38 | (1793.00, 1793.00) | 192566.8384 | 0.6087 | 31636000 | 0.041515
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 504122 MCNAB 3 115 507453 HOPE 3 115 1 | Current Study | 3.32 | (394.00, 394.00) | 182445.9296 | 5.4954 | 3320000 | 0.061694
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 167922.6505 | 0.36573 | 45914000 | 0.036978
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 159289.9167 | 0.6296 | 25300000 | 0.025792
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at PHILL 7 345 kV | Current Study |  |  | 155022.946 | 2.925 | 5300000 | 0.026088
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 145313.822 | 0.81145 | 17908000 | 0.057915
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | Current Study | 8.91 | (2390.00, 2390.00) | 117755.9507 | 0.60073 | 19602000 | 0.041515
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 504122 MCNAB 3 115 507456 TURK 3 115 1 | Current Study | 2.65 | (394.00, 394.00) | 111329.8681 | 4.2011 | 2650000 | 0.061694
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1 | Current Study | 11.3 | (1793.00, 1793.00) | 110011.4727 | 0.44252 | 24860000 | 0.027299
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 95052.0632 | 0.7921 | 12000000 | 0.058423
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 92728.6086 | 1.405 | 6600000 | 0.058423
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 91645.3756 | 0.36573 | 25058000 | 0.036978
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 81846.5491 | 1.5443 | 5300000 | 0.050364
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | Current Study | 5.97 | (2390.00, 2390.00) | 78900.4518 | 0.60073 | 13134000 | 0.041515
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 77922.6159 | 0.64936 | 12000000 | 0.045527
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 77433.9124 | 0.64528 | 12000000 | 0.032142
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 72845.5448 | 0.60705 | 12000000 | 0.058423
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 71431.7695 | 0.59526 | 12000000 | 0.040287
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 65666.4175 | 2.8551 | 2300000 | 0.40244
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 64507.552 | 0.53756 | 12000000 | 0.014518
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 63450.0555 | 0.52875 | 12000000 | 0.024921
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 63110.0372 | 0.52592 | 12000000 | 0.053516
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 62808.6196 | 0.41725 | 15053000 | 0.011037
GEN-2024-241 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 62598.0706 | 0.34585 | 18100000 | 0.010597
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 58837.8987 | 0.49032 | 12000000 | 0.032142
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 58837.8987 | 0.49032 | 12000000 | 0.032142
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 57544.2307 | 0.47954 | 12000000 | 0.0327
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 57103.8975 | 0.47587 | 12000000 | 0.040287
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 56112.5636 | 0.4676 | 12000000 | 0.031544
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 55800.8798 | 0.46501 | 12000000 | 0.032142
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 55610.1176 | 0.84258 | 6600000 | 0.058423
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 54853.1823 | 0.45711 | 12000000 | 0.032142
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 54740.884 | 0.45617 | 12000000 | 0.024921
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 46917.1951 | 0.88523 | 5300000 | 0.050364
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 46434.6351 | 1.4288 | 3250000 | 0.058423
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 46434.6351 | 1.4288 | 3250000 | 0.058423
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 44523.6242 | 0.37103 | 12000000 | 0.0327
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 36895.0418 | 0.69613 | 5300000 | 0.040287
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 36848.1514 | 0.31602 | 11660000 | 0.036008
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 36789.1436 | 0.55741 | 6600000 | 0.045527
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 33257.8546 | 0.62751 | 5300000 | 0.031544
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 32753.4262 | 0.49626 | 6600000 | 0.0327
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 32753.4262 | 0.49626 | 6600000 | 0.0327
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 31910.6347 | 0.60209 | 5300000 | 0.031544
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 31019.1936 | 0.58527 | 5300000 | 0.036008
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 30090.0819 | 0.45591 | 6600000 | 0.036008
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 29574.7071 | 0.55801 | 5300000 | 0.053516
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 28758.6202 | 0.54262 | 5300000 | 0.058423
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 28103.7115 | 0.86473 | 3250000 | 0.058423
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 27372.9583 | 0.84224 | 3250000 | 0.058423
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 27359.8389 | 0.51622 | 5300000 | 0.0327
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 26875.5632 | 0.17991 | 14938000 | 0.038326
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 26017.2888 | 0.17991 | 14460953.1406 | 0.038326
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 23638.9166 | 0.14599 | 16192000 | 0.032738
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 23363.9758 | 1.693 | 1380000 | 0.050364
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV | Current Study |  |  | 21566.3928 | 1.5628 | 1380000 | 0.041211
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 21045.1893 | 0.64754 | 3250000 | 0.058423
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 20294.2123 | 0.62444 | 3250000 | 0.0327
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 20259.5402 | 0.68214 | 2970000 | 0.055255
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 20193.5378 | 0.38101 | 5300000 | 0.036008
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 19813.6764 | 0.56289 | 3520000 | 0.045527
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 18580.3656 | 0.76384 | 2432500 | 0.031544
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 18293.8793 | 0.56289 | 3250000 | 0.045527
GEN-2024-241 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 18113.8072 | 0.34177 | 5300000 | 0.11671
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 17621.7228 | 1.2769 | 1380000 | 0.058423
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 17380.5187 | 0.53479 | 3250000 | 0.0327
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 17227.2019 | 0.53007 | 3250000 | 0.0327
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 17226.1352 | 0.53003 | 3250000 | 0.0327
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 17034.2846 | 1.2344 | 1380000 | 0.12027
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 16777.2597 | 0.51622 | 3250000 | 0.0327
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 15007.0668 | 0.68214 | 2200000 | 0.055255
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 14432.63 | 0.44408 | 3250000 | 0.0327
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 12917.0618 | 0.39745 | 3250000 | 0.036008
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 12892.992 | 0.24326 | 5300000 | 0.0036166
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 10119.4126 | 0.45737 | 2212500 | 0.046228
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 9949.2588 | 0.72096 | 1380000 | 0.050364
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 9811.2553 | 0.44345 | 2212500 | 0.046228
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CHILD4WT 138 kV | Current Study |  |  | 9788.9338 | 0.40242 | 2432500 | 0.041515
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 9717.9654 | 0.39951 | 2432500 | 0.036008
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 9583.2441 | 0.39397 | 2432500 | 0.036008
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 9511.033 | 0.391 | 2432500 | 0.035467
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 7834.0286 | 0.56768 | 1380000 | 0.0327
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 6335.5586 | 0.4591 | 1380000 | 0.036008
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 5947.7588 | 0.11222 | 5300000 | 0.032142
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 3932.0559 | 0.17772 | 2212500 | 0.037894
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 2408.857 | 0.14599 | 1650000 | 0.032738
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520939 HLDTNTP4 138 520981 LOCO 4 138 1 | Current Study | 12.85 | (211.00, 211.00) | 7686309.0479 | 49.8464 | 15420000 | 0.054714
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505600 TUPELO 4 138 505602 S BROWN4 138 1 | Current Study | 36.9 | (281.00, 281.00) | 4281944.2216 | 9.6702 | 44280000 | 0.050005
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515097 WLNUTCK4 138 515100 PAOLI- 4 138 1 | Current Study | 15.55 | (265.00, 265.00) | 3516481.8987 | 18.845 | 18660000 | 0.056193
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515044 SEMINOL4 138 515531 VANOSTP4 138 1 | Current Study | 21.55 | (395.00, 395.00) | 3495094.4162 | 13.5154 | 25860000 | 0.089616
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515117 ARBUCKL4 138 515531 VANOSTP4 138 1 | Current Study | 18.2 | (472.00, 472.00) | 3372709.2953 | 15.4428 | 21840000 | 0.12182
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 1 | Current Study |  | (1868.00, 1868.00) | 3206284.2988 | 5.2135 | 61500000 | 0.10158
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 2 | Current Study |  | (1868.00, 1868.00) | 3206284.2988 | 5.2135 | 61500000 | 0.10158
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1 | Current Study | 56.1 | (1793.00, 1793.00) | 3191713.3674 | 2.5861 | 123420000 | 0.029673
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515134 PRARPNT4 138 515570 MAYSVLT4 138 1 | Current Study | 13.55 | (211.00, 211.00) | 2769999.0214 | 17.0357 | 16260000 | 0.043302
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 2702918.7298 | 2.3046 | 117282000 | 0.038797
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 2626267.3195 | 1.748 | 150244000 | 0.03169
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515133 BLUERIV4 138 515178 PARKLN 4 138 1 | Current Study | 12.7 | (395.00, 395.00) | 2502029.6522 | 16.4175 | 15240000 | 0.087446
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515100 PAOLI- 4 138 515124 MAYSVIL4 138 1 | Current Study | 11.4 | (211.00, 211.00) | 2330478.8815 | 17.0357 | 13680000 | 0.043302
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515129 RATLIFF4 138 515134 PRARPNT4 138 1 | Current Study | 10.62 | (265.00, 265.00) | 2171025.0633 | 17.0357 | 12744000 | 0.043302
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515117 ARBUCKL4 138 515133 BLUERIV4 138 1 | Current Study | 10.35 | (395.00, 395.00) | 2039055.6615 | 16.4175 | 12420000 | 0.087446
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 1795582.1254 | 1.5919 | 112794000 | 0.10847
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515178 PARKLN 4 138 515977 LKKONWA4 138 1 | Current Study | 13.56 | (472.00, 472.00) | 1759767.5977 | 10.8147 | 16272000 | 0.10465
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1571573.9156 | 0.71985 | 218320000 | 0.01777
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1558467.9691 | 1.5518 | 100427000 | 0.015944
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 1549626.3306 | 2.45 | 63250000 | 0.10643
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 1541420.3792 | 1.7139 | 89936000 | 0.016016
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1479983.8049 | 1.55 | 95480000 | 0.050148
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1 | Current Study | 30.63 | (1793.00, 1793.00) | 1464862.5603 | 2.1738 | 67386000 | 0.028475
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 1457623.8744 | 2.6198 | 55638000 | 0.04727
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 764550 G20-087-TAP 345 1 | Current Study | 14.38 | (1793.00, 1793.00) | 1453650.1153 | 4.5949 | 31636000 | 0.12536
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 1360448.6549 | 2.0613 | 66000000 | 0.037903
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 1312888.8592 | 1.55 | 84700000 | 0.050148
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515129 RATLIFF4 138 515561 CARTRCO4 138 1 | Current Study | 7.22 | (265.00, 265.00) | 1307409.6938 | 15.0901 | 8664000 | 0.039953
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1302362.5521 | 0.9057 | 143796000 | 0.036189
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 1257138.9281 | 2.2793 | 55154000 | 0.032156
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1118883.6081 | 0.56364 | 198511000 | 0.024103
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 1060493.4455 | 2.3653 | 44836000 | 0.044423
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 993136.3988 | 0.50194 | 197860000 | 0.019845
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 988797.5845 | 0.79215 | 124824000 | 0.04146
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | Current Study | 13.6 | (1793.00, 1793.00) | 958176.5616 | 3.2025 | 29920000 | 0.048376
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 776060 G23-204-TAP 345 1 | Current Study | 17.82 | (1793.00, 1793.00) | 915424.5464 | 2.335 | 39204000 | 0.070367
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 892296.7991 | 1.8988 | 46992000 | 0.061524
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | Current Study | 8.91 | (2390.00, 2390.00) | 888917.0777 | 4.5348 | 19602000 | 0.12536
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 774963.534 | 0.82457 | 93984000 | 0.040933
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 716265.2456 | 0.43394 | 165062000 | 0.021842
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 668682.8588 | 0.50297 | 132946000 | 0.01251
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 658003.6062 | 0.80749 | 81488000 | 0.042893
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 656368.9376 | 2.5566 | 25674000 | 0.071799
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 624388.073 | 1.8586 | 33594000 | 0.060671
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515124 MAYSVIL4 138 515570 MAYSVLT4 138 1 | Current Study | 3.01 | (211.00, 211.00) | 615328.1959 | 17.0357 | 3612000 | 0.043302
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 601741.8084 | 2.2793 | 26400000 | 0.032156
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | Current Study | 5.97 | (2390.00, 2390.00) | 595604.3719 | 4.5348 | 13134000 | 0.12536
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | Current Study | 7.74 | (1793.00, 1793.00) | 534314.3886 | 3.1379 | 17028000 | 0.070367
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 511799.4505 | 1.9549 | 26180000 | 0.017671
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 495020.7145 | 1.0781 | 45914000 | 0.043603
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 466429.1781 | 2.6046 | 17908000 | 0.074359
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 425428.8519 | 1.6815 | 25300000 | 0.027554
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | Current Study | 6.93 | (1793.00, 1793.00) | 355998.4347 | 2.335 | 15246000 | 0.070367
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 339735.5811 | 0.63549 | 53460000 | 0.018351
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 294491.3266 | 5.5564 | 5300000 | 0.043603
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 282742.9068 | 2.295 | 12320000 | 0.039395
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 270162.2395 | 1.0781 | 25058000 | 0.043603
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 266130.9967 | 2.2178 | 12000000 | 0.039395
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 266130.9967 | 2.2178 | 12000000 | 0.039395
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2 | Current Study |  | (478.00, 478.00) | 248400.7161 | 1.3724 | 18100000 | 0.0091867
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 237271.2592 | 1.9773 | 12000000 | 0.039395
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 230830.8511 | 1.5335 | 15053000 | 0.016225
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 214578.2617 | 1.7882 | 12000000 | 0.050148
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514948 CEDARLN4 138 766111 G21-088-TAP 138 1 | Current Study | 2.86 | (395.00, 395.00) | 214385.7991 | 6.2467 | 3432000 | 0.042831
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 209530.0114 | 1.7461 | 12000000 | 0.04727
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at WILDHRS2 69 kV | Current Study |  |  | 208243.9223 | 15.0901 | 1380000 | 0.039953
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 190736.3164 | 1.5895 | 12000000 | 0.029966
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 187757.8542 | 1.5646 | 12000000 | 0.063686
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 180289.7709 | 1.5024 | 12000000 | 0.039395
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 180289.7709 | 1.5024 | 12000000 | 0.039395
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 177908.6967 | 1.4826 | 12000000 | 0.016016
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 172539.0779 | 1.4378 | 12000000 | 0.038797
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 170983.8055 | 1.4249 | 12000000 | 0.039395
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 168079.8921 | 1.4007 | 12000000 | 0.039395
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 167502.2246 | 1.3959 | 12000000 | 0.04727
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 164555.7989 | 1.3713 | 12000000 | 0.029966
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 160236.8393 | 1.3353 | 12000000 | 0.039395
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 159282.2313 | 3.0053 | 5300000 | 0.029966
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 158134.3155 | 1.3178 | 12000000 | 0.035944
GEN-2024-242 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 157039.7067 | 0.86762 | 18100000 | 0.010634
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 156318.5404 | 1.3027 | 12000000 | 0.050148
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 150298.5174 | 2.8358 | 5300000 | 0.030122
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 131982.9196 | 1.9997 | 6600000 | 0.033262
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 122353.0622 | 1.0196 | 12000000 | 0.035944
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 108223.814 | 2.042 | 5300000 | 0.04727
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 104719.7426 | 0.89811 | 11660000 | 0.040933
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 102263.7212 | 1.9295 | 5300000 | 0.038797
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 101307.5652 | 1.535 | 6600000 | 0.050148
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 98121.1897 | 1.8513 | 5300000 | 0.038797
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 90007.9916 | 1.3638 | 6600000 | 0.035944
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 90007.9916 | 1.3638 | 6600000 | 0.035944
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 88154.3893 | 1.6633 | 5300000 | 0.040933
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 87987.328 | 1.6601 | 5300000 | 0.063686
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 85534.2022 | 1.296 | 6600000 | 0.035944
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 85513.9185 | 1.2957 | 6600000 | 0.040933
GEN-2024-242 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 85339.4838 | 1.6102 | 5300000 | 0.21994
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 83357.9971 | 0.55803 | 14938000 | 0.047549
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 80695.9493 | 0.55803 | 14460953.1406 | 0.047549
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 76727.4044 | 2.3608 | 3250000 | 0.035944
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 76727.4044 | 2.3608 | 3250000 | 0.035944
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 75186.1541 | 1.4186 | 5300000 | 0.035944
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CHILD4WT 138 kV | Current Study |  |  | 73894.8038 | 3.0378 | 2432500 | 0.12536
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 71121.2525 | 0.43924 | 16192000 | 0.039399
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 66091.5634 | 2.0336 | 3250000 | 0.033262
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 66091.5634 | 2.0336 | 3250000 | 0.033262
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 62365.749 | 1.9189 | 3250000 | 0.035944
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 60912.3454 | 1.1493 | 5300000 | 0.026155
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 59062.8997 | 2.4281 | 2432500 | 0.0881
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 57924.3236 | 1.0929 | 5300000 | 0.029966
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 57388.6289 | 1.0828 | 5300000 | 0.040933
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 57132.288 | 2.3487 | 2432500 | 0.038797
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 56898.1344 | 1.0735 | 5300000 | 0.029966
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 56395.1629 | 1.8988 | 2970000 | 0.061524
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 55769.4721 | 1.716 | 3250000 | 0.035944
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 54561.6149 | 1.55 | 3520000 | 0.050148
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 53661.21 | 1.0125 | 5300000 | 0.029966
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 50376.502 | 1.55 | 3250000 | 0.050148
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 50372.4983 | 0.95042 | 5300000 | 0.040933
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 50145.1507 | 2.2793 | 2200000 | 0.032156
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 47762.502 | 1.4696 | 3250000 | 0.035944
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 47341.18 | 1.4567 | 3250000 | 0.035944
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 47338.2485 | 1.4566 | 3250000 | 0.035944
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 46104.7172 | 1.4186 | 3250000 | 0.035944
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 45160.6654 | 1.3896 | 3250000 | 0.050148
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 43226.4603 | 1.33 | 3250000 | 0.035944
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 42102.4851 | 1.2955 | 3250000 | 0.035944
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 41774.1947 | 1.8988 | 2200000 | 0.061524
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 39661.5618 | 1.2204 | 3250000 | 0.035944
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 38705.5327 | 0.73029 | 5300000 | 0.0043429
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 38409.71 | 2.7833 | 1380000 | 0.10847
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 36709.3906 | 1.1295 | 3250000 | 0.040933
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 33027.5117 | 1.436 | 2300000 | 0.080965
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 30421.145 | 2.3046 | 1320000 | 0.038797
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 29717.2866 | 0.5607 | 5300000 | 0.039399
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 27617.7814 | 1.1354 | 2432500 | 0.040933
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 27234.9126 | 1.1196 | 2432500 | 0.040933
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 26762.9699 | 0.22302 | 12000000 | 0.024822
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 26167.5962 | 1.8962 | 1380000 | 0.035944
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 25081.4335 | 1.8175 | 1380000 | 0.033262
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514947 CANADN-4 138 766111 G21-088-TAP 138 1 | Current Study | 0.3 | (395.00, 395.00) | 22488.0209 | 6.2467 | 360000 | 0.042831
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 21528.2876 | 1.56 | 1380000 | 0.035944
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 18773.5445 | 1.3604 | 1380000 | 0.038013
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 18224.9891 | 0.34387 | 5300000 | 0.039395
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 18005.2167 | 1.3047 | 1380000 | 0.040933
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 12265.3734 | 0.55437 | 2212500 | 0.022413
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 11891.8671 | 0.53749 | 2212500 | 0.022413
GEN-2024-242 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 7247.4102 | 0.43924 | 1650000 | 0.039399
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 338110 5HILLTOP% 161 505507 SWPINEY5 161 1 | Current Study | 47.56 | (246.00, 246.00) | 24940072.5069 | 34.9595 | 71340000 | 0.039782
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505507 SWPINEY5 161 505508 DARDANE5 161 1 | Current Study | 15.98 | (246.00, 246.00) | 8379780.4596 | 34.9595 | 23970000 | 0.039782
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Rebuild 3-winding transformer 515336 VBI 2 69 515339 VBI 5 161 515769 VBI 1 13 2 | Current Study |  | (83.00, 83.00) | 1770548.0178 | 29.1448 | 6075000 | 0.042978
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 15 MVAR switched shunt at SALISAWK 2 69 kV | Current Study |  |  | 1380000 | 100 | 1380000 | 0.036415
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 370792.4348 | 0.24679 | 150244000 | 0.022326
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 290221.3684 | 0.30396 | 95480000 | 0.049071
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 257454.4397 | 0.30396 | 84700000 | 0.049071
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 221593.2677 | 0.1015 | 218320000 | 0.012503
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 192633.8682 | 0.13396 | 143796000 | 0.026711
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 179199.2002 | 0.17844 | 100427000 | 0.0091483
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 147741.5818 | 0.1572 | 93984000 | 0.03894
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 146388.2234 | 1.2199 | 12000000 | 0.072434
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 124345.61 | 0.37014 | 33594000 | 0.060292
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 110676.878 | 0.098123 | 112794000 | 0.033364
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 108654.9233 | 0.90546 | 12000000 | 0.12192
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1 | Current Study | 11.3 | (1793.00, 1793.00) | 106171.6741 | 0.42708 | 24860000 | 0.052587
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 99375.8142 | 0.82813 | 12000000 | 0.12192
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 96946.6697 | 1.4689 | 6600000 | 0.12192
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at PHILL 7 345 kV | Current Study |  |  | 92603.892 | 1.7472 | 5300000 | 0.031105
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 86577.1708 | 0.72148 | 12000000 | 0.12192
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 83166.4185 | 0.69305 | 12000000 | 0.12192
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 82277.217 | 0.32521 | 25300000 | 0.026591
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 76159.1604 | 0.63466 | 12000000 | 0.12192
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 61930.9098 | 0.51609 | 12000000 | 0.072434
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 61180.6698 | 0.92698 | 6600000 | 0.12192
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 61180.6698 | 0.92698 | 6600000 | 0.12192
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 58973.5953 | 1.1127 | 5300000 | 0.072434
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 58139.7239 | 0.8809 | 6600000 | 0.12192
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 48546.8649 | 1.4937 | 3250000 | 0.12192
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 48546.8649 | 1.4937 | 3250000 | 0.12192
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 44173.977 | 0.36812 | 12000000 | 0.019843
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 42794.5204 | 0.35662 | 12000000 | 0.072434
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 33805.6486 | 0.63784 | 5300000 | 0.072434
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 33559.738 | 0.27966 | 12000000 | 0.038065
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 32675.1149 | 0.27229 | 12000000 | 0.036784
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 30066.7992 | 0.5673 | 5300000 | 0.12192
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 29382.0998 | 0.90406 | 3250000 | 0.12192
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 28796.8446 | 0.23997 | 12000000 | 0.033108
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 28618.1059 | 0.88056 | 3250000 | 0.12192
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 26958.9497 | 0.82951 | 3250000 | 0.12192
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 26551.4843 | 0.17639 | 15053000 | 0.0093131
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 25750.0094 | 0.21458 | 12000000 | 0.020187
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 24352.8485 | 0.20294 | 12000000 | 0.026554
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 24352.8485 | 0.20294 | 12000000 | 0.026554
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 22215.5563 | 0.18513 | 12000000 | 0.020187
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 22002.4979 | 0.677 | 3250000 | 0.12192
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 19964.1141 | 0.17122 | 11660000 | 0.03894
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 19866.1575 | 0.301 | 6600000 | 0.049071
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 19257.3663 | 0.16048 | 12000000 | 0.022458
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 18423.304 | 1.335 | 1380000 | 0.12192
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 16834.6457 | 1.2199 | 1380000 | 0.072434
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 16805.9966 | 0.31709 | 5300000 | 0.03894
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 16302.6099 | 0.24701 | 6600000 | 0.03894
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 16283.3196 | 0.50103 | 3250000 | 0.038065
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 16283.3196 | 0.50103 | 3250000 | 0.038065
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 15956.2308 | 0.30106 | 5300000 | 0.038065
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 13586.1733 | 0.25634 | 5300000 | 0.049071
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 13370.5861 | 0.60432 | 2212500 | 0.12192
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 13235.446 | 0.40724 | 3250000 | 0.038065
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 12963.4238 | 0.58592 | 2212500 | 0.12192
GEN-2024-243 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 12804.68 | 0.2416 | 5300000 | 0.16467
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 11835.5644 | 0.36417 | 3250000 | 0.038065
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 10940.7269 | 0.20643 | 5300000 | 0.03894
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 10699.4053 | 0.30396 | 3520000 | 0.049071
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 10136.3012 | 0.31189 | 3250000 | 0.038065
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 10046.887 | 0.30913 | 3250000 | 0.038065
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 10046.2649 | 0.30912 | 3250000 | 0.038065
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 9878.7047 | 0.30396 | 3250000 | 0.049071
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 9784.4812 | 0.30106 | 3250000 | 0.038065
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 7168.8247 | 0.51948 | 1380000 | 0.072434
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 6998.3798 | 0.21533 | 3250000 | 0.03894
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 6162.427 | 0.11627 | 5300000 | 0.0034503
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 5553.3656 | 0.40242 | 1380000 | 0.038065
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 5265.1302 | 0.21645 | 2432500 | 0.03894
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 5192.1391 | 0.21345 | 2432500 | 0.03894
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 4568.7977 | 0.33107 | 1380000 | 0.038065
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 3432.5643 | 0.24874 | 1380000 | 0.03894
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 3163.8798 | 0.143 | 2212500 | 0.06086
GEN-2024-243 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 2367.5115 | 0.17156 | 1380000 | 0.033364
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 14763542.7279 | 0.97474 | 1514620000 | 0.039966
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 8022702.2561 | 0.62427 | 1285130000 | 0.13116
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 7890764.491 | 0.62052 | 1271630000 | 0.085197
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 6623509.9947 | 0.70583 | 938400000 | 0.07983
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 6284936.6408 | 0.66975 | 938400000 | 0.13406
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 5849241.1199 | 0.80706 | 724760000 | 0.12764
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523092 HITCHLD_TR11 13 523093 HITCHLAND 3 115 523095 HITCHLAND 6 230 M2 | Current Study |  | (250.00, 288.00) | 5569551.5009 | 40.3591 | 13800000 | 0.16357
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523093 HITCHLAND 3 115 523095 HITCHLAND 6 230 523098 HITCHLD_TR41 13 M2 | Current Study |  | (250.00, 288.00) | 5569190.3859 | 40.3565 | 13800000 | 0.15705
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 3945548.3331 | 0.36745 | 1073760000 | 0.041962
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 3782623.6185 | 0.78341 | 482840000 | 0.13273
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 3524067.0335 | 0.75086 | 469340000 | 0.085491
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523091 HITCHLD_TR01 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2 | Current Study |  | (560.00, 644.00) | 2877163.973 | 11.5087 | 25000000 | 0.14803
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523094 HITCHLD_TR21 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2 | Current Study |  | (560.00, 644.00) | 2877163.973 | 11.5087 | 25000000 | 0.17017
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add line 523869 CHAN+TASCOS6 230 523959 POTTER_CO 6 230 P2 | Current Study | 41.65 | (496.00, 546.00) | 2806460.5024 | 2.521 | 111325000 | 0.032369
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 2504413.562 | 1.2658 | 197860000 | 0.083407
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add line 523221 XIT_INTG 6 230 523869 CHAN+TASCOS6 230 P2 | Current Study | 32.28 | (495.00, 545.00) | 2215680.3896 | 2.5207 | 87900000 | 0.032377
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 1307474.2083 | 0.79211 | 165062000 | 0.066451
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523266 PRINGLE 3 115 523377 RIVERVIEW 3 115 1 | Current Study | 20.25 | (260.00, 260.00) | 937584.6084 | 4.63 | 20250000 | 0.033694
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add 12 MVAR switched shunt at OCHILTREE 6 230 kV | Current Study |  |  | 923135.2164 | 24.1343 | 3825000 | 0.074703
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 833628.0543 | 0.41994 | 198511000 | 0.02993
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 681964.8913 | 0.80706 | 84500000 | 0.12764
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 632270.8398 | 1.4544 | 43472000 | 0.059103
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 631418.0014 | 0.74724 | 84500000 | 0.063334
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 552554.5213 | 0.44267 | 124824000 | 0.038614
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 367118.3646 | 0.45052 | 81488000 | 0.039885
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 190546.2521 | 1.1768 | 16192000 | 0.17593
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 181300.8509 | 0.97474 | 18600000 | 0.039966
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 155288.4209 | 0.28122 | 55220000 | 0.018289
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add 12 MVAR switched shunt at NP-OCHILTRE3 115 kV | Current Study |  |  | 150133.7131 | 6.7857 | 2212500 | 0.00089283
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 150112.982 | 0.80706 | 18600000 | 0.12764
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 139659.1955 | 0.75086 | 18600000 | 0.085491
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 117431.8989 | 0.63135 | 18600000 | 0.13273
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 115765.2495 | 0.62239 | 18600000 | 0.085491
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 113764.8897 | 0.61164 | 18600000 | 0.085197
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 111126.4096 | 0.59745 | 18600000 | 0.07983
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 106626.545 | 0.57326 | 18600000 | 0.13406
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 106626.545 | 0.57326 | 18600000 | 0.13406
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 97126.8718 | 0.52219 | 18600000 | 0.13406
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 83821.3964 | 0.45065 | 18600000 | 0.07983
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 70993.9907 | 3.2088 | 2212500 | 0.17593
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 62228.1216 | 0.41658 | 14938000 | 0.05916
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 60240.8589 | 0.41658 | 14460953.1406 | 0.05916
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 40278.516 | 0.33565 | 12000000 | 0.062263
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 35159.2815 | 0.66338 | 5300000 | 0.12667
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add 1.6 MVAR switched shunt at NP-VALERO-G2 69 kV | Current Study |  |  | 35038.7654 | 2.539 | 1380000 | 0.053396
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 32445.8815 | 0.038397 | 84500000 | 0.0015719
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 27382.9183 | 1.2376 | 2212500 | 0.17593
GEN-2024-244 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 26770.807 | 1.9399 | 1380000 | 0.16373
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 19417.0773 | 1.1768 | 1650000 | 0.17593
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 13021.3198 | 0.19862 | 6556000 | 0.018289
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 12569.2722 | 0.91082 | 1380000 | 0.12667
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 11608.5312 | 0.8412 | 1380000 | 0.17593
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 9949.2046 | 0.44968 | 2212500 | 0.062263
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 9347.8832 | 0.67738 | 1380000 | 0.080022
GEN-2024-244 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 6313.6425 | 0.45751 | 1380000 | 0.062263
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 532803 BURNS 7 345 1 | Current Study | 50.03 | (1793.00, 1793.00) | 4165914.9324 | 3.7849 | 110066000 | 0.039701
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532803 BURNS 7 345 1 | Current Study | 45.5 | (1793.00, 1793.00) | 3788709.3629 | 3.7849 | 100100000 | 0.039701
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 2321477.0695 | 1.9794 | 117282000 | 0.041862
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 2213568.6338 | 1.4733 | 150244000 | 0.033555
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 1 | Current Study |  | (1868.00, 1868.00) | 2129471.9939 | 3.4626 | 61500000 | 0.084758
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 2 | Current Study |  | (1868.00, 1868.00) | 2129471.9939 | 3.4626 | 61500000 | 0.084758
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 1520728.1989 | 2.7333 | 55638000 | 0.061955
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1432365.14 | 1.4263 | 100427000 | 0.01841
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1342174.8413 | 0.61477 | 218320000 | 0.019065
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 1319642.6005 | 1.4673 | 89936000 | 0.017225
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1251891.8673 | 1.3112 | 95480000 | 0.05329
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 1161378.2279 | 2.5903 | 44836000 | 0.061117
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 1153306.7439 | 1.7474 | 66000000 | 0.040366
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 1110549.2371 | 1.3112 | 84700000 | 0.05329
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1098633.3939 | 0.76402 | 143796000 | 0.038352
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 1080389.2308 | 1.9589 | 55154000 | 0.034717
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 870489.6429 | 0.43851 | 198511000 | 0.023558
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 796025.5343 | 0.63772 | 124824000 | 0.041931
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 756961.9644 | 0.38257 | 197860000 | 0.019003
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 684553.4979 | 0.72837 | 93984000 | 0.045424
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 624008.1632 | 1.3279 | 46992000 | 0.054052
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at TXPLSTP2 69 kV | Current Study |  |  | 594610.3343 | 43.0877 | 1380000 | 0.45937
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 576217.7806 | 1.255 | 45914000 | 0.063762
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 572901.6713 | 1.7054 | 33594000 | 0.069935
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 545991.2976 | 0.33078 | 165062000 | 0.020917
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 532108.5614 | 0.40024 | 132946000 | 0.012506
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 522548.406 | 0.64126 | 81488000 | 0.042793
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 517138.842 | 1.9589 | 26400000 | 0.034717
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 447922.0546 | 1.7109 | 26180000 | 0.019429
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 353333.047 | 1.3966 | 25300000 | 0.028749
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 314476.3067 | 1.255 | 25058000 | 0.063762
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 305596.1338 | 0.57164 | 53460000 | 0.020737
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 242571.7308 | 1.9689 | 12320000 | 0.04246
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 228320.1286 | 1.9027 | 12000000 | 0.04246
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 228320.1286 | 1.9027 | 12000000 | 0.04246
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 218601.0934 | 1.8217 | 12000000 | 0.061955
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 0.06 MVAR switched shunt at G24-125-TAP 345 kV | Current Study |  |  | 218402.9419 | 4.1208 | 5300000 | 0.029579
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 212038.6169 | 1.4086 | 15053000 | 0.018724
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 203560.6715 | 1.6963 | 12000000 | 0.04246
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 181507.9685 | 1.5126 | 12000000 | 0.05329
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 174753.8178 | 1.4563 | 12000000 | 0.061955
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 157891.7047 | 1.3158 | 12000000 | 0.067281
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 156503.6936 | 1.3042 | 12000000 | 0.030889
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 154674.8939 | 1.289 | 12000000 | 0.04246
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 154674.8939 | 1.289 | 12000000 | 0.04246
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 152311.546 | 1.2693 | 12000000 | 0.017225
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 148190.0886 | 1.2349 | 12000000 | 0.041862
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 146691.0842 | 1.2224 | 12000000 | 0.04246
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 144199.7477 | 1.2017 | 12000000 | 0.04246
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 137471.0057 | 1.1456 | 12000000 | 0.04246
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 135021.955 | 1.1252 | 12000000 | 0.030889
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 132227.0974 | 1.1019 | 12000000 | 0.05329
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 130694.8671 | 2.4659 | 5300000 | 0.030889
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 125694.093 | 1.0475 | 12000000 | 0.035893
GEN-2024-245 | 04 SOUTHEAST | TBD | NRIS | Add 5 MVAR switched shunt at CTNWOOD4 138 kV | Current Study |  |  | 122154.0353 | 5.0217 | 2432500 | 0.049858
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 120895.2838 | 2.281 | 5300000 | 0.030439
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 112909.0955 | 2.1304 | 5300000 | 0.061955
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 97253.1302 | 0.81044 | 12000000 | 0.035893
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 92502.7604 | 0.79333 | 11660000 | 0.045424
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 87832.1021 | 1.6572 | 5300000 | 0.041862
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 85694.2833 | 1.2984 | 6600000 | 0.05329
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 84274.1712 | 1.5901 | 5300000 | 0.041862
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 77869.951 | 1.4692 | 5300000 | 0.045424
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 75537.528 | 1.1445 | 6600000 | 0.045424
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 73991.4145 | 1.3961 | 5300000 | 0.067281
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 71543.4397 | 1.084 | 6600000 | 0.035893
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 71543.4397 | 1.084 | 6600000 | 0.035893
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 67987.419 | 1.0301 | 6600000 | 0.035893
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 65269.335 | 0.43693 | 14938000 | 0.046772
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 63184.9508 | 0.43693 | 14460953.1406 | 0.046772
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 60987.2783 | 1.8765 | 3250000 | 0.035893
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 60987.2783 | 1.8765 | 3250000 | 0.035893
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 59762.2054 | 1.1276 | 5300000 | 0.035893
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 54834.2553 | 1.0346 | 5300000 | 0.029579
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 54354.6813 | 0.33569 | 16192000 | 0.037828
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 50693.4454 | 0.95648 | 5300000 | 0.045424
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 49571.8227 | 1.5253 | 3250000 | 0.035893
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 49069.6886 | 2.0173 | 2432500 | 0.041862
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 47528.2881 | 0.89676 | 5300000 | 0.030889
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 46686.2754 | 0.88087 | 5300000 | 0.030889
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 46152.6956 | 1.3112 | 3520000 | 0.05329
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 44495.8442 | 0.83954 | 5300000 | 0.045424
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 44328.729 | 1.364 | 3250000 | 0.035893
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 44030.3018 | 0.83076 | 5300000 | 0.030889
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 43094.9035 | 1.9589 | 2200000 | 0.034717
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 42612.5949 | 1.3112 | 3250000 | 0.05329
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 39438.7182 | 1.3279 | 2970000 | 0.054052
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 38200.6107 | 1.1754 | 3250000 | 0.05329
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 37964.3365 | 1.1681 | 3250000 | 0.035893
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 37629.446 | 1.1578 | 3250000 | 0.035893
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 37627.1158 | 1.1578 | 3250000 | 0.035893
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 37606.4844 | 0.70956 | 5300000 | 0.0053009
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 36646.6354 | 1.1276 | 3250000 | 0.035893
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 34358.8342 | 1.0572 | 3250000 | 0.035893
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 33465.4351 | 1.0297 | 3250000 | 0.035893
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 32426.7285 | 0.99775 | 3250000 | 0.045424
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 31525.2513 | 0.97001 | 3250000 | 0.035893
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 29213.8653 | 1.3279 | 2200000 | 0.054052
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 26128.0481 | 1.9794 | 1320000 | 0.041862
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 24395.7823 | 1.0029 | 2432500 | 0.045424
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 24057.5805 | 0.98901 | 2432500 | 0.045424
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 22711.5574 | 0.42852 | 5300000 | 0.037828
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 21395.9432 | 0.1783 | 12000000 | 0.02493
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 20799.4847 | 1.5072 | 1380000 | 0.035893
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 19124.4902 | 1.3858 | 1380000 | 0.031862
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 17802.3322 | 0.73185 | 2432500 | 0.03336
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 17550.9924 | 0.76309 | 2300000 | 0.054052
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 17111.8999 | 1.24 | 1380000 | 0.035893
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 15904.6572 | 1.1525 | 1380000 | 0.045424
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 15869.0184 | 1.1499 | 1380000 | 0.040367
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 15635.6528 | 0.29501 | 5300000 | 0.04246
GEN-2024-245 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 9751.7537 | 0.184 | 5300000 | 0.031573
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 9009.366 | 0.4072 | 2212500 | 0.04363
GEN-2024-245 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 5538.8602 | 0.33569 | 1650000 | 0.037828
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 29862073.1819 | 2.7811 | 1073760000 | 0.23939
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 25113605.3981 | 1.6581 | 1514620000 | 0.051245
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 22465933.3469 | 1.7667 | 1271630000 | 0.18284
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 22440700.4368 | 1.7462 | 1285130000 | 0.27653
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 11036447.1304 | 1.5228 | 724760000 | 0.18153
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 10894493.9588 | 1.161 | 938400000 | 0.098974
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 9914644.7664 | 1.0565 | 938400000 | 0.15941
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 528184 SENDERO +3 115 528187 SENDERO_345 345 M2 | Current Study |  | (435.00, 435.00) | 9886935.0143 | 58.8508 | 16800000 | 0.23385
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 8080759.1897 | 1.6736 | 482840000 | 0.21373
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 8001142.3454 | 1.7048 | 469340000 | 0.14631
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 3845832.7144 | 1.0493 | 366500000 | 0.034659
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528013 PHANTOM 3 115 528228 WOOD_DRAW 3 115 1 | Current Study | 7.71 | (260.00, 260.00) | 1955756.6417 | 25.3665 | 7710000 | 0.037248
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1719811.7742 | 2.0353 | 84500000 | 0.062803
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1286742.8977 | 1.5228 | 84500000 | 0.18153
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 1257843.8994 | 1.4886 | 84500000 | 0.095101
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 1240924.7314 | 0.62717 | 197860000 | 0.031152
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1213461.4919 | 0.97214 | 124824000 | 0.063919
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1144882.6015 | 0.57674 | 198511000 | 0.030984
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 1136624.2359 | 4.2891 | 26500000 | 0.067749
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1 | Current Study | 2.13 | (598.00, 598.00) | 995376.9007 | 46.7313 | 2130000 | 0.51218
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 891662.2745 | 0.5402 | 165062000 | 0.034159
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 839662.5469 | 1.0304 | 81488000 | 0.068762
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 637815.5595 | 1.4672 | 43472000 | 0.04494
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 426015.2927 | 0.77149 | 55220000 | 0.037819
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 378833.8353 | 2.0367 | 18600000 | 0.27196
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 328461.3921 | 1.7659 | 18600000 | 0.18284
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 324584.5275 | 1.7451 | 18600000 | 0.27653
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 323902.0038 | 1.7414 | 18600000 | 0.18284
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 317086.2224 | 1.7048 | 18600000 | 0.14631
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 308402.8076 | 1.6581 | 18600000 | 0.051245
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528016 SAND_DUNES 3 115 528018 RED_BLUFF 3 115 1 | Current Study | 7.69 | (394.00, 394.00) | 284822.7674 | 3.7038 | 7690000 | 0.019838
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 283235.7148 | 1.5228 | 18600000 | 0.18153
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 274627.3747 | 1.4765 | 18600000 | 0.28572
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 191546.1181 | 1.0298 | 18600000 | 0.18153
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 191546.1181 | 1.0298 | 18600000 | 0.18153
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 182783.1466 | 0.98271 | 18600000 | 0.098974
GEN-2024-246 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 131545.4961 | 0.72677 | 18100000 | 0.01119
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528184 SENDERO +3 115 528193 BLACKRIVER 3 115 1 | Current Study | 0.25 | (598.00, 598.00) | 116828.2747 | 46.7313 | 250000 | 0.51218
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 105762.444 | 4.7802 | 2212500 | 0.51218
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528018 RED_BLUFF 3 115 528235 WOLFCAMP_TP3 115 1 | Current Study | 7.81 | (598.00, 598.00) | 102680.9241 | 1.3147 | 7810000 | 0.017715
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 87978.1608 | 0.54334 | 16192000 | 0.061228
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 82919.8634 | 0.55509 | 14938000 | 0.059421
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 80271.8074 | 0.55509 | 14460953.1406 | 0.059421
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 70040.5538 | 1.3215 | 5300000 | 0.1902
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | Current Study | 0.78 | (598.00, 598.00) | 44846.6905 | 0.84744 | 5292000 | 0.012031
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | Current Study | 0.2 | (598.00, 598.00) | 37965.4523 | 0.84744 | 4480000 | 0.012031
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 35722.4404 | 0.54488 | 6556000 | 0.037819
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 27870.2811 | 2.0196 | 1380000 | 0.17984
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 25662.6486 | 0.21386 | 12000000 | 0.029902
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 25039.1576 | 1.8144 | 1380000 | 0.1902
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 17246.8128 | 0.77952 | 2212500 | 0.032215
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 16650.1752 | 1.2065 | 1380000 | 0.1902
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 10414.3865 | 0.75467 | 1380000 | 0.0054264
GEN-2024-246 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 9297.3196 | 0.67372 | 1380000 | 0.04286
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 8965.1658 | 0.54334 | 1650000 | 0.061228
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 6338.9361 | 0.28651 | 2212500 | 0.029902
GEN-2024-246 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 4022.6107 | 0.29149 | 1380000 | 0.029902
GEN-2024-247 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512710 KINZEGR4 138 512731 NORTHTP4 138 1 | Current Study | 9.7 | (395.00, 395.00) | 11640000 | 100 | 11640000 | 0.46578
GEN-2024-247 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 300141 4STILWTR 138 512731 NORTHTP4 138 1 | Current Study | 6.97 | (395.00, 395.00) | 8364000 | 100 | 8364000 | 0.47073
GEN-2024-247 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at CRESENT4 138 kV | Current Study |  |  | 2432500 | 100 | 2432500 | 0.35733
GEN-2024-247 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at GEN-2024-029 138 kV | Current Study |  |  | 2396618.9515 | 98.5249 | 2432500 | 0.35733
GEN-2024-247 | 04 SOUTHEAST | TBD | ERIS | Add 38 MVAR switched shunt at FRNT2WD7 345 kV | Current Study |  |  | 342732.9605 | 6.4667 | 5300000 | 0.083395
GEN-2024-247 | 04 SOUTHEAST | TBD | ERIS | Add 19 MVAR switched shunt at RANCHRD7 345 kV | Current Study |  |  | 313787.0764 | 5.9205 | 5300000 | 0.083395
GEN-2024-247 | 04 SOUTHEAST | TBD | ERIS | Add 10 MVAR switched shunt at G20-007-TAP 345 kV | Current Study |  |  | 271664.3697 | 5.1257 | 5300000 | 0.044027
GEN-2024-249 | 03 CENTRAL | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 20628160.1511 | 38.5862 | 53460000 | 0.38625
GEN-2024-249 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 218463.718 | 4.122 | 5300000 | 0.048607
GEN-2024-249 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 48098.2623 | 2.915 | 1650000 | 0.049006
GEN-2024-249 | 03 CENTRAL | TBD | ERIS | Add 38 MVAR switched shunt at FRNT2WD7 345 kV | Current Study |  |  | 13067.9267 | 0.24656 | 5300000 | 0.0020131
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 4982075.7582 | 4.417 | 112794000 | 0.37811
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 1 | Current Study |  | (1868.00, 1868.00) | 3055584.2998 | 4.9684 | 61500000 | 0.12162
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 2 | Current Study |  | (1868.00, 1868.00) | 3055584.2998 | 4.9684 | 61500000 | 0.12162
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1 | Current Study | 56.1 | (1793.00, 1793.00) | 2878812.0009 | 2.3325 | 123420000 | 0.033623
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 2728058.8391 | 4.3131 | 63250000 | 0.23538
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 2055983.0346 | 1.753 | 117282000 | 0.037074
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 1998100.3838 | 1.3299 | 150244000 | 0.030289
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1 | Current Study | 30.63 | (1793.00, 1793.00) | 1381148.2139 | 2.0496 | 67386000 | 0.033728
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 1268441.6809 | 1.4104 | 89936000 | 0.016557
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1213027.7999 | 1.2705 | 95480000 | 0.051636
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1210335.7098 | 1.2052 | 100427000 | 0.015556
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1202385.511 | 0.55074 | 218320000 | 0.01708
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 1157638.1631 | 2.0807 | 55638000 | 0.047163
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 1107260.4074 | 1.6777 | 66000000 | 0.038755
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 1076073.0483 | 1.2705 | 84700000 | 0.051636
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 998127.8108 | 0.69413 | 143796000 | 0.034843
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 940841.3296 | 1.7058 | 55154000 | 0.030233
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 889938.0519 | 3.4663 | 25674000 | 0.1223
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 837643.4566 | 1.8682 | 44836000 | 0.044081
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 776060 G23-204-TAP 345 1 | Current Study | 17.82 | (1793.00, 1793.00) | 829624.4225 | 2.1162 | 39204000 | 0.080115
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 804186.9813 | 0.40511 | 198511000 | 0.021764
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 729424.5163 | 0.36866 | 197860000 | 0.018311
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 701995.5611 | 0.56239 | 124824000 | 0.036978
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 656149.3405 | 0.69815 | 93984000 | 0.043539
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 647225.2824 | 1.3773 | 46992000 | 0.056063
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 634550.3375 | 3.5434 | 17908000 | 0.12709
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 549503.0973 | 1.6357 | 33594000 | 0.067079
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 526855.028 | 0.31919 | 165062000 | 0.020184
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 497715.5858 | 0.37437 | 132946000 | 0.011698
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | Current Study | 7.74 | (1793.00, 1793.00) | 484234.6295 | 2.8438 | 17028000 | 0.080115
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 465650.9053 | 0.57143 | 81488000 | 0.038133
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 764550 G20-087-TAP 345 1 | Current Study | 14.38 | (1793.00, 1793.00) | 450897.9723 | 1.4253 | 31636000 | 0.048849
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 450342.8781 | 1.7058 | 26400000 | 0.030233
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | Current Study | 13.16 | (395.00, 395.00) | 449571.0869 | 2.8468 | 15792000 | 0.028257
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515044 SEMINOL4 138 515531 VANOSTP4 138 1 | Current Study | 21.55 | (395.00, 395.00) | 428442.6413 | 1.6568 | 25860000 | 0.013801
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 68 MVAR SVC at TONTITN7 345 kV | Current Study |  |  | 410870.7962 | 3.4239 | 12000000 | 0.023475
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 403417.9137 | 1.5409 | 26180000 | 0.017499
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 391703.3038 | 0.85312 | 45914000 | 0.043345
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515117 ARBUCKL4 138 515531 VANOSTP4 138 1 | Current Study | 18.2 | (472.00, 472.00) | 383847.3667 | 1.7575 | 21840000 | 0.017417
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1 | Current Study | 11.3 | (1793.00, 1793.00) | 354336.6234 | 1.4253 | 24860000 | 0.044185
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 341976.8662 | 1.3517 | 25300000 | 0.027825
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | Current Study | 6.93 | (1793.00, 1793.00) | 322631.7198 | 2.1162 | 15246000 | 0.080115
GEN-2024-250 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 308859.3432 | 5.8275 | 5300000 | 1
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 275884.9252 | 2.299 | 12000000 | 0.034367
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | Current Study | 8.91 | (2390.00, 2390.00) | 275727.2219 | 1.4066 | 19602000 | 0.048849
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 241781.5757 | 0.45227 | 53460000 | 0.016407
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515178 PARKLN 4 138 515977 LKKONWA4 138 1 | Current Study | 13.56 | (472.00, 472.00) | 237923.8701 | 1.4622 | 16272000 | 0.017776
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 215220.9406 | 1.7469 | 12320000 | 0.037672
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 213775.7849 | 0.85312 | 25058000 | 0.043345
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 | Current Study | 6.08 | (395.00, 395.00) | 207704.5751 | 2.8468 | 7296000 | 0.028257
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 202576.1464 | 1.6881 | 12000000 | 0.037673
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 202576.1464 | 1.6881 | 12000000 | 0.037673
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | Current Study | 5.97 | (2390.00, 2390.00) | 184746.5224 | 1.4066 | 13134000 | 0.048849
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 180608.4143 | 1.5051 | 12000000 | 0.037673
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 179347.8588 | 1.1914 | 15053000 | 0.015837
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 175873.0938 | 1.4656 | 12000000 | 0.051636
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 166407.5478 | 1.3867 | 12000000 | 0.047162
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 146401.7842 | 1.22 | 12000000 | 0.016557
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 143236.9482 | 1.1936 | 12000000 | 0.028271
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 142770.3582 | 1.1898 | 12000000 | 0.060838
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 137234.6982 | 1.1436 | 12000000 | 0.037673
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 137234.6982 | 1.1436 | 12000000 | 0.037673
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 134795.0233 | 1.1233 | 12000000 | 0.038492
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 133029.3176 | 1.1086 | 12000000 | 0.047162
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 131242.366 | 1.0937 | 12000000 | 0.037075
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 130151.0941 | 1.0846 | 12000000 | 0.037673
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 128122.1365 | 1.0677 | 12000000 | 0.051636
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 127940.6655 | 1.0662 | 12000000 | 0.037673
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 123911.7106 | 1.0326 | 12000000 | 0.038272
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 123576.2066 | 1.0298 | 12000000 | 0.028271
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 120882.8102 | 1.8316 | 6600000 | 0.038272
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 119615.9239 | 2.2569 | 5300000 | 0.028271
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 111142.3143 | 2.097 | 5300000 | 0.034367
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 110694.3002 | 2.0886 | 5300000 | 0.027871
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 106572.7441 | 7.7227 | 1380000 | 0.37811
GEN-2024-250 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 106515.4469 | 0.58848 | 18100000 | 0.009061
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 104294.7814 | 0.86912 | 12000000 | 0.038492
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 88664.5462 | 0.76042 | 11660000 | 0.043539
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 85950.7398 | 1.6217 | 5300000 | 0.047162
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 83033.9233 | 1.2581 | 6600000 | 0.051636
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 77787.2056 | 1.4677 | 5300000 | 0.037075
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 76723.5706 | 1.1625 | 6600000 | 0.038492
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 76723.5706 | 1.1625 | 6600000 | 0.038492
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 74638.8762 | 1.4083 | 5300000 | 0.043539
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 74636.1766 | 1.4082 | 5300000 | 0.037075
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 72910.0748 | 1.1047 | 6600000 | 0.038492
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 72403.2329 | 1.097 | 6600000 | 0.043539
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 66905.2296 | 1.2624 | 5300000 | 0.060838
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 65403.0862 | 2.0124 | 3250000 | 0.038492
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 65403.0862 | 2.0124 | 3250000 | 0.038492
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 64089.3115 | 1.2092 | 5300000 | 0.038492
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 60533.0898 | 1.8626 | 3250000 | 0.038272
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 60533.0898 | 1.8626 | 3250000 | 0.038272
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 60014.8808 | 0.40176 | 14938000 | 0.043007
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 58098.2983 | 0.40176 | 14460953.1406 | 0.043007
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 53161.0901 | 1.6357 | 3250000 | 0.038492
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 52296.9394 | 0.32298 | 16192000 | 0.036396
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 48590.0113 | 0.91679 | 5300000 | 0.043539
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 47538.3681 | 1.4627 | 3250000 | 0.038492
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 45001.7365 | 0.84909 | 5300000 | 0.024275
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 44719.9189 | 1.2705 | 3520000 | 0.051636
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 43499.3372 | 0.82074 | 5300000 | 0.028271
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 43457.8459 | 1.7866 | 2432500 | 0.037075
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 42728.7015 | 0.8062 | 5300000 | 0.028271
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 42649.5685 | 0.80471 | 5300000 | 0.043539
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 41289.6963 | 1.2705 | 3250000 | 0.051636
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 40906.0923 | 1.3773 | 2970000 | 0.056063
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 40713.1592 | 1.2527 | 3250000 | 0.038492
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 40354.0209 | 1.2417 | 3250000 | 0.038492
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 40351.522 | 1.2416 | 3250000 | 0.038492
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 40297.8735 | 0.76034 | 5300000 | 0.028271
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 39300.0495 | 1.2092 | 3250000 | 0.038492
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 37528.5732 | 1.7058 | 2200000 | 0.030233
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 37014.6812 | 1.1389 | 3250000 | 0.051636
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 36846.5991 | 1.1337 | 3250000 | 0.038492
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 35888.5131 | 1.1043 | 3250000 | 0.038492
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 33807.8496 | 1.0402 | 3250000 | 0.038492
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 31768.0704 | 0.5994 | 5300000 | 0.004478
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 31726.7664 | 2.299 | 1380000 | 0.034367
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 31081.2392 | 0.95635 | 3250000 | 0.043539
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 30300.8091 | 1.3773 | 2200000 | 0.056063
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 30021.5675 | 1.3053 | 2300000 | 0.092458
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 23383.5228 | 0.9613 | 2432500 | 0.043539
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 23139.9329 | 1.753 | 1320000 | 0.037074
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 23059.354 | 0.94797 | 2432500 | 0.043539
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 22972.0192 | 1.6646 | 1380000 | 0.038272
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CHILD4WT 138 kV | Current Study |  |  | 22920.9306 | 0.94228 | 2432500 | 0.048849
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 22305.4796 | 1.6163 | 1380000 | 0.038492
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 21851.7421 | 0.4123 | 5300000 | 0.036396
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 21102.119 | 0.86751 | 2432500 | 0.039543
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 19933.3892 | 0.16611 | 12000000 | 0.023226
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 | Current Study | 0.55 | (395.00, 395.00) | 18789.0652 | 2.8468 | 660000 | 0.028257
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 18350.8938 | 1.3298 | 1380000 | 0.038492
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 15244.7218 | 1.1047 | 1380000 | 0.043539
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 15235.4171 | 1.104 | 1380000 | 0.038755
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 13872.6721 | 0.26175 | 5300000 | 0.037673
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 9972.2743 | 0.45072 | 2212500 | 0.022893
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 9668.5977 | 0.437 | 2212500 | 0.022893
GEN-2024-250 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 5329.1718 | 0.32298 | 1650000 | 0.036396
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 15598890.6645 | 1.0299 | 1514620000 | 0.050673
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 15446561.3695 | 1.4385 | 1073760000 | 0.19714
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 13647722.1187 | 1.062 | 1285130000 | 0.26774
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 13589428.8776 | 1.0687 | 1271630000 | 0.17607
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 7613215.7364 | 0.8113 | 938400000 | 0.11011
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 6964180.7335 | 0.96089 | 724760000 | 0.18236
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 6821098.7538 | 0.72689 | 938400000 | 0.17459
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 4977889.6561 | 1.031 | 482840000 | 0.2096
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 4896400.1318 | 1.0433 | 469340000 | 0.14254
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528095 7-RIVERS 6 230 528179 PECOS 6 230 1 | Current Study | 20.61 | (386.00, 386.00) | 4442524.4572 | 11.3448 | 39159000 | 0.14024
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 3504888.9627 | 0.95631 | 366500000 | 0.050285
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527799 EDDY_NORTH 6 230 528095 7-RIVERS 6 230 1 | Current Study | 24.1 | (386.00, 386.00) | 2069613.0626 | 4.5198 | 45790000 | 0.056364
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 527796 EDDY_TR 1 13 527799 EDDY_NORTH 6 230 527802 EDDY_CNTY 7 345 M2 | Current Study |  | (516.00, 558.00) | 1918196.3707 | 7.6728 | 25000000 | 0.20359
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 999994.9293 | 1.1834 | 84500000 | 0.058136
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524875 OASIS 6 230 787680 G24-357-TAP 230 1 | Current Study | 26.02 | (901.00, 901.00) | 958544.1884 | 1.9389 | 49438000 | 0.084768
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3 | Current Study | 39.39 | (478.00, 544.00) | 955004.4665 | 0.90372 | 105675000 | 0.024708
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 811956.0572 | 0.96089 | 84500000 | 0.18236
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 802720.1968 | 0.94996 | 84500000 | 0.09662
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 799175.0982 | 0.40391 | 197860000 | 0.031939
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 768747.5467 | 0.61587 | 124824000 | 0.064466
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524885 SN_JUAN_SS 6 230 787680 G24-357-TAP 230 1 | Current Study | 20.18 | (901.00, 901.00) | 743405.9078 | 1.9389 | 38342000 | 0.084768
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 726263.8726 | 0.36586 | 198511000 | 0.031291
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 573969.6977 | 0.34773 | 165062000 | 0.035006
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 532168.5387 | 0.65306 | 81488000 | 0.069381
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 527529.5613 | 1.9907 | 26500000 | 0.050058
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528013 PHANTOM 3 115 528228 WOOD_DRAW 3 115 1 | Current Study | 7.71 | (260.00, 260.00) | 527218.3517 | 6.8381 | 7710000 | 0.015986
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 453580.2676 | 0.82141 | 55220000 | 0.064104
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 410137.8508 | 0.94345 | 43472000 | 0.046006
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528016 SAND_DUNES 3 115 528018 RED_BLUFF 3 115 1 | Current Study | 7.69 | (394.00, 394.00) | 399021.5351 | 5.1888 | 7690000 | 0.044245
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 528184 SENDERO +3 115 528187 SENDERO_345 345 M2 | Current Study |  | (435.00, 435.00) | 349977.5124 | 2.0832 | 16800000 | 0.013178
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 227048.9338 | 1.2207 | 18600000 | 0.25948
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1 | Current Study | 9.6 | (901.00, 901.00) | 204210.5129 | 1.1196 | 18240000 | 0.059999
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 198683.1643 | 1.0682 | 18600000 | 0.17607
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 197402.0128 | 1.0613 | 18600000 | 0.26774
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 195925.2338 | 1.0534 | 18600000 | 0.17607
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 194044.9194 | 1.0433 | 18600000 | 0.14254
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 191559.1808 | 1.0299 | 18600000 | 0.050673
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528018 RED_BLUFF 3 115 528235 WOLFCAMP_TP3 115 1 | Current Study | 7.81 | (598.00, 598.00) | 188821.5257 | 2.4177 | 7810000 | 0.051862
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 178726.422 | 0.96089 | 18600000 | 0.18236
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 166681.2371 | 0.89614 | 18600000 | 0.27607
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 145211.0664 | 0.58084 | 25000000 | 0.015764
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 145211.0664 | 0.58084 | 25000000 | 0.013738
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 127731.2681 | 0.68673 | 18600000 | 0.11011
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 120868.7696 | 0.64983 | 18600000 | 0.18236
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 120868.7696 | 0.64983 | 18600000 | 0.18236
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | Current Study | 0.78 | (598.00, 598.00) | 96268.3688 | 1.8191 | 5292000 | 0.041114
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | Current Study | 0.2 | (598.00, 598.00) | 81497.0318 | 1.8191 | 4480000 | 0.041114
GEN-2024-251 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 81138.7136 | 0.44828 | 18100000 | 0.010988
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 56653.7229 | 0.34989 | 16192000 | 0.062769
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 52580.9842 | 0.35199 | 14938000 | 0.059986
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1 | Current Study | 2.13 | (598.00, 598.00) | 51277.0908 | 2.4074 | 2130000 | 0.042005
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 50901.8041 | 0.35199 | 14460953.1406 | 0.059986
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 44697.8906 | 0.84336 | 5300000 | 0.19324
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 38033.832 | 0.58014 | 6556000 | 0.064104
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 16849.9248 | 1.221 | 1380000 | 0.17309
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 16360.1953 | 0.13633 | 12000000 | 0.030348
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 15979.2786 | 1.1579 | 1380000 | 0.19324
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 10916.2823 | 0.49339 | 2212500 | 0.032462
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 10625.6685 | 0.76998 | 1380000 | 0.19324
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 8141.572 | 0.36798 | 2212500 | 0.062769
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 7018.6918 | 0.5086 | 1380000 | 0.0058221
GEN-2024-251 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 6195.0429 | 0.44892 | 1380000 | 0.045465
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528184 SENDERO +3 115 528193 BLACKRIVER 3 115 1 | Current Study | 0.25 | (598.00, 598.00) | 6018.4379 | 2.4074 | 250000 | 0.042005
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 5773.1375 | 0.34989 | 1650000 | 0.062769
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 4041.1352 | 0.18265 | 2212500 | 0.030348
GEN-2024-251 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 2564.4546 | 0.18583 | 1380000 | 0.030348
GEN-2024-252 | 04 SOUTHEAST | TBD | NRIS | Add 3-winding transformer 514898 CIMARON4 138 514901 CIMARON7 345 515715 CIMARO21 13 M2 | Current Study |  | (478.00, 478.00) | 7916010.264 | 43.7349 | 18100000 | 0.035845
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 6353605.9861 | 0.67592 | 940000000 | 0.018553
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 532803 BURNS 7 345 1 | Current Study | 50.03 | (1793.00, 1793.00) | 2378121.7226 | 2.1606 | 110066000 | 0.043808
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532803 BURNS 7 345 1 | Current Study | 45.5 | (1793.00, 1793.00) | 2162793.0917 | 2.1606 | 100100000 | 0.043808
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 1255309.001 | 1.0703 | 117282000 | 0.043755
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 1204524.701 | 0.80171 | 150244000 | 0.035295
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at G15048_1 138 kV | Current Study |  |  | 1021418.3173 | 41.9905 | 2432500 | 0.072691
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 764148.9731 | 1.3734 | 55638000 | 0.060177
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 730533.9739 | 0.72743 | 100427000 | 0.018149
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 721250.0109 | 0.33036 | 218320000 | 0.019804
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 714599.5794 | 1.5938 | 44836000 | 0.072691
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 630057.4889 | 0.70056 | 89936000 | 0.015897
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 602320.3799 | 0.63083 | 95480000 | 0.049561
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 596684.9274 | 1.0819 | 55154000 | 0.037063
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 591731.7133 | 0.41151 | 143796000 | 0.039929
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 565092.6882 | 0.8562 | 66000000 | 0.038231
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 537833.0261 | 0.27093 | 198511000 | 0.028135
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 534316.466 | 0.63083 | 84700000 | 0.049561
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 479846.8596 | 0.38442 | 124824000 | 0.048858
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 429930.2399 | 0.21729 | 197860000 | 0.020862
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 363989.2449 | 0.77458 | 46992000 | 0.060945
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 328529.3952 | 0.71553 | 45914000 | 0.070271
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 316103.9294 | 0.38791 | 81488000 | 0.050038
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 309766.914 | 0.18767 | 165062000 | 0.022939
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 306723.567 | 0.32636 | 93984000 | 0.039341
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 301126.3543 | 0.2265 | 132946000 | 0.01368
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 285609.0598 | 1.0819 | 26400000 | 0.037063
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 235536.5084 | 0.70113 | 33594000 | 0.055578
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 227898.608 | 0.87051 | 26180000 | 0.019109
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 179298.0264 | 0.71553 | 25058000 | 0.070271
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 177430.1246 | 0.7013 | 25300000 | 0.027906
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 176521.8426 | 0.33019 | 53460000 | 0.023154
GEN-2024-252 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 169524.4325 | 0.9366 | 18100000 | 0.009566
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 122 MVAR switched shunt at HOYT 7 345 kV | Current Study |  |  | 149662.5317 | 2.8238 | 5300000 | 0.0405
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 131087.6048 | 1.064 | 12320000 | 0.044354
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 138 MVAR switched shunt at GEN-2024-016 345 kV | Current Study |  |  | 129203.179 | 2.4378 | 5300000 | 0.029649
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 123385.8979 | 1.0282 | 12000000 | 0.044354
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 123385.8979 | 1.0282 | 12000000 | 0.044354
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 0.06 MVAR switched shunt at G24-125-TAP 345 kV | Current Study |  |  | 121686.7496 | 2.296 | 5300000 | 0.031857
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 119313.6648 | 0.46473 | 25674000 | 0.031694
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 110005.7029 | 0.91671 | 12000000 | 0.044354
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 109844.7812 | 0.91537 | 12000000 | 0.060177
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 108207.0753 | 0.71884 | 15053000 | 0.01847
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 87811.9802 | 0.73177 | 12000000 | 0.060177
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 87622.167 | 0.73018 | 12000000 | 0.033429
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 87328.626 | 0.72774 | 12000000 | 0.049561
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 86012.407 | 0.71677 | 12000000 | 0.070847
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 84984.8332 | 0.47456 | 17908000 | 0.0329
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 83587.4646 | 0.69656 | 12000000 | 0.044354
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 83587.4646 | 0.69656 | 12000000 | 0.044354
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 80131.8712 | 0.66777 | 12000000 | 0.043756
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 79272.9544 | 0.66061 | 12000000 | 0.044354
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 77926.6176 | 0.64939 | 12000000 | 0.044354
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 75595.1251 | 0.62996 | 12000000 | 0.033429
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 74290.3553 | 0.61909 | 12000000 | 0.044354
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 73172.5061 | 1.3806 | 5300000 | 0.033429
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 72720.5279 | 0.606 | 12000000 | 0.015897
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 0.42 MVAR switched shunt at TWNLKSW4 138 kV | Current Study |  |  | 71904.0852 | 2.956 | 2432500 | 0.11448
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 70077.1305 | 1.3222 | 5300000 | 0.034106
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 64231.2887 | 0.53526 | 12000000 | 0.050038
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 10 MVAR switched shunt at G20-007-TAP 345 kV | Current Study |  |  | 60875.0494 | 1.1486 | 5300000 | 0.043756
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 56735.6489 | 1.0705 | 5300000 | 0.060177
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 55909.9316 | 0.46592 | 12000000 | 0.030861
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 38 MVAR switched shunt at FRNT2WD7 345 kV | Current Study |  |  | 55761.5261 | 1.0521 | 5300000 | 0.060177
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 19 MVAR switched shunt at RANCHRD7 345 kV | Current Study |  |  | 51052.1259 | 0.96325 | 5300000 | 0.060177
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 47494.0717 | 0.89611 | 5300000 | 0.043756
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 45570.1666 | 0.85981 | 5300000 | 0.043756
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 43259.1201 | 0.36049 | 12000000 | 0.030861
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 41447.1283 | 0.35546 | 11660000 | 0.039341
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 41229.9475 | 0.6247 | 6600000 | 0.049561
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 40307.2452 | 0.76051 | 5300000 | 0.070847
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 40222.6881 | 0.26926 | 14938000 | 0.055716
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 38938.1716 | 0.26926 | 14460953.1406 | 0.055716
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 34890.7397 | 0.65832 | 5300000 | 0.039341
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 33845.6644 | 0.51281 | 6600000 | 0.039341
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 31823.2045 | 0.48217 | 6600000 | 0.030861
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 31823.2045 | 0.48217 | 6600000 | 0.030861
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 30784.3761 | 0.19012 | 16192000 | 0.041412
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 30551.7968 | 0.57645 | 5300000 | 0.031857
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 30241.4525 | 0.4582 | 6600000 | 0.030861
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 26609.7975 | 0.50207 | 5300000 | 0.033429
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 26582.7991 | 0.50156 | 5300000 | 0.030861
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 26533.7986 | 1.0908 | 2432500 | 0.043756
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 26138.3775 | 0.49318 | 5300000 | 0.033429
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 24651.37 | 0.46512 | 5300000 | 0.033429
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 23800.755 | 1.0819 | 2200000 | 0.037063
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 23004.9382 | 0.77458 | 2970000 | 0.060945
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 22713.9197 | 0.42856 | 5300000 | 0.039341
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 22477.0304 | 0.42409 | 5300000 | 0.044354
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 22205.3596 | 0.63083 | 3520000 | 0.049561
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 20502.1267 | 0.63083 | 3250000 | 0.049561
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 19717.8415 | 0.6067 | 3250000 | 0.030861
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 18379.3961 | 0.56552 | 3250000 | 0.049561
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at GEN-2024-029 138 kV | Current Study |  |  | 17823.4059 | 0.73272 | 2432500 | 0.011786
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 17040.695 | 0.77458 | 2200000 | 0.060945
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 16886.899 | 0.5196 | 3250000 | 0.030861
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 16737.9365 | 0.51501 | 3250000 | 0.030861
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 16736.9001 | 0.51498 | 3250000 | 0.030861
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 16300.773 | 0.50156 | 3250000 | 0.030861
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 16173.107 | 0.30515 | 5300000 | 0.0044067
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 15283.1372 | 0.47025 | 3250000 | 0.030861
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 14529.2572 | 0.44705 | 3250000 | 0.039341
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 14128.4074 | 1.0703 | 1320000 | 0.043755
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 14084.107 | 0.63657 | 2212500 | 0.039753
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 14022.7325 | 0.43147 | 3250000 | 0.030861
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 12862.9401 | 0.2427 | 5300000 | 0.041412
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 12084.0864 | 0.1007 | 12000000 | 0.027217
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 10930.8774 | 0.44937 | 2432500 | 0.039341
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 10779.3413 | 0.44314 | 2432500 | 0.039341
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 10237.6415 | 0.44511 | 2300000 | 0.060945
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 9936.9894 | 0.40851 | 2432500 | 0.035994
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 8909.5998 | 0.64562 | 1380000 | 0.043809
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 8449.6232 | 0.15943 | 5300000 | 0.044354
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 7126.308 | 0.5164 | 1380000 | 0.039341
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 4470.9973 | 0.084358 | 5300000 | 0.017628
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 4423.96 | 0.19995 | 2212500 | 0.041412
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 3136.9948 | 0.19012 | 1650000 | 0.041412
GEN-2024-253 | 03 CENTRAL | TBD | ERIS | Rebuild line 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | Current Study | 17.54 | (1793.00, 1793.00) | 1454055.5921 | 3.7682 | 38588000 | 0.035174
GEN-2024-253 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 1022813.618 | 0.109 | 938400000 | 0.031787
GEN-2024-253 | 03 CENTRAL | TBD | ERIS | Rebuild line 645458 S3458 3 345 778170 G24-040-TAP 345 1 | Current Study | 13.15 | (1793.00, 1793.00) | 803623.9442 | 2.7778 | 28930000 | 0.08368
GEN-2024-253 | 03 CENTRAL | TBD | ERIS | Rebuild line 640139 COOPER 3 345 778170 G24-040-TAP 345 1 | Current Study | 12.59 | (1793.00, 1793.00) | 769401.1754 | 2.7778 | 27698000 | 0.08368
GEN-2024-253 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 673411.1793 | 0.33923 | 198511000 | 0.022276
GEN-2024-253 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 422316.8223 | 0.29369 | 143796000 | 0.028497
GEN-2024-253 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 402479.3222 | 0.42824 | 93984000 | 0.051623
GEN-2024-253 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 136504.079 | 0.2973 | 45914000 | 0.029198
GEN-2024-253 | 03 CENTRAL | TBD | ERIS | Rebuild line 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 | Current Study | 3.23 | (1793.00, 1793.00) | 120445.693 | 1.695 | 7106000 | 0.037117
GEN-2024-253 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 74498.3929 | 0.2973 | 25058000 | 0.029198
GEN-2024-253 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 54386.4701 | 0.46644 | 11660000 | 0.051623
GEN-2024-253 | 03 CENTRAL | TBD | ERIS | Add 38 MVAR switched shunt at FRNT2WD7 345 kV | Current Study |  |  | 39913.5759 | 0.75309 | 5300000 | 0.043074
GEN-2024-253 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 28024.1281 | 0.15067 | 18600000 | 0.051336
GEN-2024-253 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 28024.1281 | 0.15067 | 18600000 | 0.051336
GEN-2024-253 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 17344.298 | 0.11611 | 14938000 | 0.024025
GEN-2024-253 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 16790.4057 | 0.11611 | 14460953.1406 | 0.024025
GEN-2024-253 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 15806.4739 | 0.084981 | 18600000 | 0.031787
GEN-2024-253 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 6831.6783 | 0.41404 | 1650000 | 0.048761
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 6446618.7777 | 0.68581 | 940000000 | 0.018825
GEN-2024-254 | 04 SOUTHEAST | TBD | NRIS | Add 3-winding transformer 514898 CIMARON4 138 514901 CIMARON7 345 515715 CIMARO21 13 M2 | Current Study |  | (478.00, 478.00) | 4906649.56 | 27.1086 | 18100000 | 0.022218
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 532803 BURNS 7 345 1 | Current Study | 50.03 | (1793.00, 1793.00) | 2439865.2049 | 2.2167 | 110066000 | 0.044946
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532803 BURNS 7 345 1 | Current Study | 45.5 | (1793.00, 1793.00) | 2218945.9689 | 2.2167 | 100100000 | 0.044946
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 1277917.1525 | 1.0896 | 117282000 | 0.044544
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 1226846.2732 | 0.81657 | 150244000 | 0.035949
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at G15048_1 138 kV | Current Study |  |  | 1166050.4733 | 47.9363 | 2432500 | 0.082984
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 815786.1765 | 1.8195 | 44836000 | 0.082984
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 785292.3712 | 1.4114 | 55638000 | 0.061842
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 739978.3675 | 0.73683 | 100427000 | 0.018384
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 733756.8142 | 0.33609 | 218320000 | 0.020147
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 623865.3217 | 0.69368 | 89936000 | 0.015741
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 610229.7659 | 1.1064 | 55154000 | 0.037904
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 601583.0555 | 0.41836 | 143796000 | 0.040594
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 596560.469 | 0.6248 | 95480000 | 0.049087
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 562401.7996 | 0.85212 | 66000000 | 0.038049
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 559168.4489 | 0.28168 | 198511000 | 0.029251
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 529206.8676 | 0.6248 | 84700000 | 0.049087
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 494441.5067 | 0.39611 | 124824000 | 0.050344
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 428933.3654 | 0.21679 | 197860000 | 0.020814
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 371681.1723 | 0.80952 | 45914000 | 0.079501
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 343007.1477 | 0.72993 | 46992000 | 0.057431
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 324470.9776 | 0.39818 | 81488000 | 0.051363
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 309089.4084 | 0.18726 | 165062000 | 0.022889
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 305492.0004 | 0.22979 | 132946000 | 0.013879
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 302373.6626 | 0.32173 | 93984000 | 0.038783
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 292092.4288 | 1.1064 | 26400000 | 0.037904
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 229523.1865 | 0.87671 | 26180000 | 0.019245
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 228606.9724 | 0.6805 | 33594000 | 0.053942
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 202848.5171 | 0.80952 | 25058000 | 0.079501
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 182872.0648 | 0.34207 | 53460000 | 0.023987
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 177157.1586 | 0.70023 | 25300000 | 0.027863
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 122 MVAR switched shunt at HOYT 7 345 kV | Current Study |  |  | 152228.6373 | 2.8722 | 5300000 | 0.041194
GEN-2024-254 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 149915.9863 | 0.82827 | 18100000 | 0.0084595
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 133416.6621 | 1.0829 | 12320000 | 0.045142
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 138 MVAR switched shunt at GEN-2024-016 345 kV | Current Study |  |  | 131127.321 | 2.4741 | 5300000 | 0.030091
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 125578.1214 | 1.0465 | 12000000 | 0.045142
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 125578.1214 | 1.0465 | 12000000 | 0.045142
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 0.06 MVAR switched shunt at G24-125-TAP 345 kV | Current Study |  |  | 125531.8236 | 2.3685 | 5300000 | 0.032863
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 112884.1334 | 0.9407 | 12000000 | 0.061842
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 111960.1976 | 0.933 | 12000000 | 0.045142
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 109584.7861 | 0.72799 | 15053000 | 0.018705
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 103869.8601 | 0.40457 | 25674000 | 0.027592
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 0.42 MVAR switched shunt at TWNLKSW4 138 kV | Current Study |  |  | 91688.1105 | 3.7693 | 2432500 | 0.14598
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 90241.6954 | 0.75201 | 12000000 | 0.061842
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 89443.2145 | 0.74536 | 12000000 | 0.034124
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 87550.6771 | 0.72959 | 12000000 | 0.072114
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 86493.5275 | 0.72078 | 12000000 | 0.049087
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 85072.5808 | 0.70894 | 12000000 | 0.045142
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 85072.5808 | 0.70894 | 12000000 | 0.045142
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 81575.051 | 0.67979 | 12000000 | 0.044544
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 80681.4138 | 0.67235 | 12000000 | 0.045142
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 79311.1564 | 0.66093 | 12000000 | 0.045142
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 77166.2151 | 0.64305 | 12000000 | 0.034124
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 75610.2878 | 0.63009 | 12000000 | 0.045142
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 74693.2469 | 1.4093 | 5300000 | 0.034124
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 72005.8595 | 0.60005 | 12000000 | 0.015741
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 71867.5519 | 1.356 | 5300000 | 0.034977
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 65931.4519 | 0.54943 | 12000000 | 0.051363
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 10 MVAR switched shunt at G20-007-TAP 345 kV | Current Study |  |  | 61971.4127 | 1.1693 | 5300000 | 0.044544
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 58305.497 | 1.1001 | 5300000 | 0.061842
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 38 MVAR switched shunt at FRNT2WD7 345 kV | Current Study |  |  | 57304.4206 | 1.0812 | 5300000 | 0.061842
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 52650.4947 | 0.43875 | 12000000 | 0.029062
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 19 MVAR switched shunt at RANCHRD7 345 kV | Current Study |  |  | 52464.7136 | 0.9899 | 5300000 | 0.061842
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 48349.4428 | 0.91225 | 5300000 | 0.044544
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 46390.888 | 0.8753 | 5300000 | 0.044544
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 41865.5529 | 0.28026 | 14938000 | 0.057992
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 41028.1113 | 0.77412 | 5300000 | 0.072114
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 40859.3317 | 0.35042 | 11660000 | 0.038783
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 40835.6774 | 0.61872 | 6600000 | 0.049087
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 40737.2001 | 0.33948 | 12000000 | 0.029062
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 40528.5713 | 0.28026 | 14460953.1406 | 0.057992
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 34395.932 | 0.64898 | 5300000 | 0.038783
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 33365.6776 | 0.50554 | 6600000 | 0.038783
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 31517.1765 | 0.59466 | 5300000 | 0.032863
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 30714.0537 | 0.18969 | 16192000 | 0.041318
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 29967.9755 | 0.45406 | 6600000 | 0.029062
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 29967.9755 | 0.45406 | 6600000 | 0.029062
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 28478.4365 | 0.43149 | 6600000 | 0.029062
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 27162.8277 | 0.51251 | 5300000 | 0.034124
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 27011.6739 | 1.1104 | 2432500 | 0.044544
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 26681.6102 | 0.50343 | 5300000 | 0.034124
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 25163.6983 | 0.47479 | 5300000 | 0.034124
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 25033.0752 | 0.47232 | 5300000 | 0.029062
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 24341.0357 | 1.1064 | 2200000 | 0.037904
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 22876.3846 | 0.43163 | 5300000 | 0.045142
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 22391.7992 | 0.42249 | 5300000 | 0.038783
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 21993.0127 | 0.6248 | 3520000 | 0.049087
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 21678.8225 | 0.72993 | 2970000 | 0.057431
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 20306.0707 | 0.6248 | 3250000 | 0.049087
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 18568.3309 | 0.57133 | 3250000 | 0.029062
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 18203.6392 | 0.56011 | 3250000 | 0.049087
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at GEN-2024-029 138 kV | Current Study |  |  | 18057.6426 | 0.74235 | 2432500 | 0.011941
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 16058.3871 | 0.72993 | 2200000 | 0.057431
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 16000.2385 | 0.30189 | 5300000 | 0.0043596
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 15902.4267 | 0.48931 | 3250000 | 0.029062
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 15762.1484 | 0.48499 | 3250000 | 0.029062
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 15761.1724 | 0.48496 | 3250000 | 0.029062
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 15350.4706 | 0.47232 | 3250000 | 0.029062
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 14392.161 | 0.44284 | 3250000 | 0.029062
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 14382.8605 | 1.0896 | 1320000 | 0.044544
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 14323.2086 | 0.44071 | 3250000 | 0.038783
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 14320.9633 | 0.64728 | 2212500 | 0.040421
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 13205.2353 | 0.40631 | 3250000 | 0.029062
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 12833.5577 | 0.24214 | 5300000 | 0.041318
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 12264.0977 | 0.1022 | 12000000 | 0.027622
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 10775.8597 | 0.443 | 2432500 | 0.038783
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 10626.4726 | 0.43685 | 2432500 | 0.038783
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 9647.4967 | 0.41946 | 2300000 | 0.057432
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 9140.9208 | 0.66239 | 1380000 | 0.044946
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 8599.7494 | 0.16226 | 5300000 | 0.045142
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 7025.2453 | 0.50908 | 1380000 | 0.038783
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 4413.8545 | 0.1995 | 2212500 | 0.041318
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 3129.8288 | 0.18969 | 1650000 | 0.041318
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 6206141.6259 | 0.66023 | 940000000 | 0.018123
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 532803 BURNS 7 345 1 | Current Study | 50.03 | (1793.00, 1793.00) | 2358486.0508 | 2.1428 | 110066000 | 0.043446
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532803 BURNS 7 345 1 | Current Study | 45.5 | (1793.00, 1793.00) | 2144935.345 | 2.1428 | 100100000 | 0.043446
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 1294015.9679 | 1.1033 | 117282000 | 0.045105
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 1218886.7731 | 0.81127 | 150244000 | 0.035716
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 1014415.1149 | 1.8232 | 55638000 | 0.079885
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 787303.214 | 1.756 | 44836000 | 0.080087
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 767642.5271 | 0.76438 | 100427000 | 0.019071
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 734288.1972 | 0.33634 | 218320000 | 0.020162
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 655849.4709 | 0.72924 | 89936000 | 0.016548
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 616346.4244 | 0.64552 | 95480000 | 0.050715
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 608356.195 | 1.103 | 55154000 | 0.037788
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 601371.2806 | 0.41821 | 143796000 | 0.040579
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 595337.0577 | 0.90203 | 66000000 | 0.040277
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 546758.9249 | 0.64552 | 84700000 | 0.050715
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 499219.2986 | 0.25148 | 198511000 | 0.026115
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 458933.4779 | 0.36766 | 124824000 | 0.046729
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 408221.783 | 0.20632 | 197860000 | 0.019809
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 367216.2983 | 0.79979 | 45914000 | 0.078546
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 337701.0882 | 0.71864 | 46992000 | 0.056543
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 314748.6168 | 0.3349 | 93984000 | 0.040371
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 299999.6307 | 0.36815 | 81488000 | 0.047489
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 294231.4854 | 0.17826 | 165062000 | 0.021788
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 291412.6667 | 0.2192 | 132946000 | 0.013239
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 291195.6258 | 1.103 | 26400000 | 0.037788
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 250519.6157 | 0.74573 | 33594000 | 0.059113
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 235869.4812 | 0.90095 | 26180000 | 0.019777
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 200411.7699 | 0.79979 | 25058000 | 0.078546
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 181323.125 | 0.71669 | 25300000 | 0.028518
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 179617.4437 | 0.33598 | 53460000 | 0.02356
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 122 MVAR switched shunt at HOYT 7 345 kV | Current Study |  |  | 151793.9908 | 2.864 | 5300000 | 0.041076
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 145819.8518 | 1.2152 | 12000000 | 0.079885
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 135075.1375 | 1.0964 | 12320000 | 0.045703
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 0.06 MVAR switched shunt at G24-125-TAP 345 kV | Current Study |  |  | 131797.9286 | 2.4868 | 5300000 | 0.034504
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 127139.2492 | 1.0595 | 12000000 | 0.045703
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 127139.2492 | 1.0595 | 12000000 | 0.045703
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 138 MVAR switched shunt at GEN-2024-016 345 kV | Current Study |  |  | 126139.6369 | 2.38 | 5300000 | 0.028946
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 116571.127 | 0.97143 | 12000000 | 0.079885
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 113633.5791 | 0.75489 | 15053000 | 0.019396
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 113352.0338 | 0.9446 | 12000000 | 0.045703
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 89362.2586 | 0.74469 | 12000000 | 0.050715
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 86899.6337 | 0.72416 | 12000000 | 0.071578
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 86232.089 | 0.7186 | 12000000 | 0.032899
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 86130.1629 | 0.71775 | 12000000 | 0.045703
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 86130.1629 | 0.71775 | 12000000 | 0.045703
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 82602.7692 | 0.68836 | 12000000 | 0.045105
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 81684.407 | 0.6807 | 12000000 | 0.045703
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 80297.1151 | 0.66914 | 12000000 | 0.045703
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 76550.2391 | 0.63792 | 12000000 | 0.045703
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 75697.4903 | 0.63081 | 12000000 | 0.016548
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 75317.0413 | 1.4211 | 5300000 | 0.079885
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 74395.8495 | 0.61997 | 12000000 | 0.032899
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 38 MVAR switched shunt at FRNT2WD7 345 kV | Current Study |  |  | 74023.8852 | 1.3967 | 5300000 | 0.079885
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 72011.6641 | 1.3587 | 5300000 | 0.032899
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 19 MVAR switched shunt at RANCHRD7 345 kV | Current Study |  |  | 67772.1176 | 1.2787 | 5300000 | 0.079885
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 67468.8644 | 1.273 | 5300000 | 0.032836
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 65099.6877 | 0.5425 | 12000000 | 0.050715
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 10 MVAR switched shunt at G20-007-TAP 345 kV | Current Study |  |  | 62752.1558 | 1.184 | 5300000 | 0.045105
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 54116.8107 | 0.45097 | 12000000 | 0.029871
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 0.42 MVAR switched shunt at TWNLKSW4 138 kV | Current Study |  |  | 52773.2039 | 2.1695 | 2432500 | 0.084021
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 48958.5703 | 0.92375 | 5300000 | 0.045105
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 46975.3408 | 0.88633 | 5300000 | 0.045105
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 42531.5421 | 0.36476 | 11660000 | 0.040371
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 42190.0745 | 0.63924 | 6600000 | 0.050715
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 41871.7309 | 0.34893 | 12000000 | 0.029871
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 40723.0185 | 0.76836 | 5300000 | 0.071578
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 37447.0425 | 0.25068 | 14938000 | 0.051871
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 36251.1666 | 0.25068 | 14460953.1406 | 0.051871
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 35803.5821 | 0.67554 | 5300000 | 0.040371
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 34731.1646 | 0.52623 | 6600000 | 0.040371
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 33090.4026 | 0.62435 | 5300000 | 0.034504
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 30802.5834 | 0.46671 | 6600000 | 0.029871
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 30802.5834 | 0.46671 | 6600000 | 0.029871
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 29290.7258 | 0.1809 | 16192000 | 0.039403
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 29271.5608 | 0.44351 | 6600000 | 0.029871
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 27351.9788 | 1.1244 | 2432500 | 0.045105
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 26187.6475 | 0.49411 | 5300000 | 0.032899
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 25730.2462 | 0.48548 | 5300000 | 0.029871
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 25723.7063 | 0.48535 | 5300000 | 0.032899
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 24266.3022 | 1.103 | 2200000 | 0.037788
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 24260.2894 | 0.45774 | 5300000 | 0.032899
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 23308.1813 | 0.43978 | 5300000 | 0.040371
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 23160.773 | 0.437 | 5300000 | 0.045703
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 22722.4488 | 0.64552 | 3520000 | 0.050715
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 21343.4677 | 0.71864 | 2970000 | 0.056543
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 20979.5622 | 0.64552 | 3250000 | 0.050715
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 19085.4588 | 0.58724 | 3250000 | 0.029871
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 18807.3993 | 0.57869 | 3250000 | 0.050715
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 17070.1731 | 0.32208 | 5300000 | 0.0046511
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 16345.3092 | 0.50293 | 3250000 | 0.029871
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 16201.1241 | 0.4985 | 3250000 | 0.029871
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 16200.1209 | 0.49847 | 3250000 | 0.029871
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 15809.976 | 0.71864 | 2200000 | 0.056543
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 15777.9811 | 0.48548 | 3250000 | 0.029871
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 14909.3845 | 0.45875 | 3250000 | 0.040371
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 14792.9826 | 0.45517 | 3250000 | 0.029871
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 14564.0514 | 1.1033 | 1320000 | 0.045105
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 14319.1864 | 0.64719 | 2212500 | 0.040416
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 13573.0011 | 0.41763 | 3250000 | 0.029871
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 12238.8379 | 0.23092 | 5300000 | 0.039403
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 11724.8875 | 0.097707 | 12000000 | 0.026408
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 11216.8607 | 0.46112 | 2432500 | 0.040371
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 11061.36 | 0.45473 | 2432500 | 0.040371
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 9498.2563 | 0.41297 | 2300000 | 0.056543
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 8836.034 | 0.64029 | 1380000 | 0.043447
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 8706.6575 | 0.16428 | 5300000 | 0.045703
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 7796.8014 | 0.32053 | 2432500 | 0.028242
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 7312.7528 | 0.52991 | 1380000 | 0.040371
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 4293.2653 | 0.19405 | 2212500 | 0.040189
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 2984.7886 | 0.1809 | 1650000 | 0.039403
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 15749713.9835 | 1.6755 | 940000000 | 0.021522
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 539753 PRATTENERGY3 115 539756 SKLYVL_GOAB3 115 1 | Current Study | 12.52 | (260.00, 260.00) | 12520000 | 100 | 12520000 | 1
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 530582 S HAYS6 230 539679 GRTBEND6 230 1 | Current Study | 39.2 | (386.00, 386.00) | 12218756.1281 | 16.4054 | 74480000 | 0.10001
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 530618 HUNTSVL3 115 530624 ST JOHN3 115 1 | Current Study | 26.5 | (297.00, 297.00) | 8119155.6092 | 30.6383 | 26500000 | 0.19568
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 539649 SAWYER 3 115 539760 BARBER 3 115 1 | Current Study | 19 | (598.00, 598.00) | 6940577.1103 | 36.5294 | 19000000 | 0.50967
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 539010 SADLHRN3 115 539648 PRICHRD3 115 1 | Current Study | 9.47 | (598.00, 598.00) | 5612179.6251 | 59.2627 | 9470000 | 0.49032
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 539010 SADLHRN3 115 539696 ST-JOHN3 115 1 | Current Study | 9.4 | (598.00, 598.00) | 5570695.7208 | 59.2627 | 9400000 | 0.49032
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | Current Study | 14.69 | (260.00, 260.00) | 5408594.9086 | 36.8182 | 14690000 | 0.29464
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 539642 ELLSWTP3 115 539678 GRTBEND3 115 1 | Current Study | 30.21 | (115.00, 115.00) | 5374220.9587 | 17.7895 | 30210000 | 0.033033
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 | Current Study | 21.74 | (386.00, 386.00) | 5316448.5025 | 12.8709 | 41306000 | 0.064057
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 5117717.3635 | 2.5781 | 198511000 | 0.07922
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 539648 PRICHRD3 115 539753 PRATTENERGY3 115 1 | Current Study | 4.57 | (260.00, 260.00) | 4570000 | 100 | 4570000 | 1
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 539638 FLATRDG4 138 539674 BARBER 4 138 1 | Current Study | 8.92 | (472.00, 472.00) | 3878866.1183 | 36.2375 | 10704000 | 0.45521
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 530618 HUNTSVL3 115 530724 CENTENNIAL3 115 1 | Current Study | 12.45 | (297.00, 297.00) | 3814471.2202 | 30.6383 | 12450000 | 0.19568
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 539674 BARBER 4 138 539760 BARBER 3 115 539917 BARBER-1 13 M2 | Current Study |  | (324.00, 324.00) | 3768704.0014 | 36.2375 | 10400000 | 0.2276
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | Current Study | 13.1 | (297.00, 297.00) | 3764607.0619 | 28.7375 | 13100000 | 0.23631
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 530724 CENTENNIAL3 115 533412 ARKVALJ3 115 1 | Current Study | 10.96 | (297.00, 297.00) | 3357960.2067 | 30.6383 | 10960000 | 0.19568
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 2532831.9786 | 0.26991 | 938400000 | 0.036836
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 2448333.325 | 1.1214 | 218320000 | 0.031458
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 539666 GBENDTP3 115 539678 GRTBEND3 115 1 | Current Study | 7.21 | (176.00, 176.00) | 2071967.6278 | 28.7374 | 7210000 | 0.15283
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 2010942.6108 | 1.013 | 198511000 | 0.049228
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 530565 SEWARD 2 69 530569 GB STH 2 69 1 | Current Study | 8.56 | (69.00, 69.00) | 1946405.6415 | 26.751 | 7276000 | 0.033463
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 539668 HARPER 4 138 539881 SPRVLSTR 138 1 | Current Study | 12.1 | (281.00, 281.00) | 1805828.0805 | 12.4368 | 14520000 | 0.05228
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Current Study | 26.47 | (1793.00, 1793.00) | 1660049.4742 | 2.8507 | 58234000 | 0.044372
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 533412 ARKVALJ3 115 533413 CIRCLE 3 115 1 | Current Study | 5.2 | (297.00, 297.00) | 1593192.7988 | 30.6383 | 5200000 | 0.19568
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 539009 CONWAY 4 138 539881 SPRVLSTR 138 1 | Current Study | 10.66 | (281.00, 281.00) | 1590919.6147 | 12.4368 | 12792000 | 0.05228
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Current Study | 38.26 | (1793.00, 1793.00) | 1514118.5345 | 1.7988 | 84172000 | 0.039554
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Current Study | 37.4 | (1793.00, 1793.00) | 1496433.8638 | 1.8187 | 82280000 | 0.039554
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1277929.7681 | 0.88871 | 143796000 | 0.040353
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild 3-winding transformer 530565 SEWARD 2 69 530631 SWRD1 1 12 530679 SEWRDMW3 115 1 | Current Study |  | (87.00, 87.00) | 1268126.2935 | 26.8387 | 4725000 | 0.058332
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Add 32 MVAR switched shunt at BARBER 3 115 kV | Current Study |  |  | 1046869.5127 | 47.3161 | 2212500 | 0.50967
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 533413 CIRCLE 3 115 533416 RENO 3 115 2 | Current Study | 5.95 | (217.00, 217.00) | 986405.3505 | 16.5782 | 5950000 | 0.086075
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 533075 VIOLA 4 138 539009 CONWAY 4 138 1 | Current Study | 5.62 | (281.00, 281.00) | 838739.9845 | 12.4368 | 6744000 | 0.05228
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Add 21 MVAR switched shunt at LARNED3 115 kV | Current Study |  |  | 808211.3831 | 36.5293 | 2212500 | 0.50967
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Add 63 MVAR switched shunt at SADLHRN3 115 kV | Current Study |  |  | 808200.7711 | 36.5288 | 2212500 | 0.50967
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Add 45 MVAR switched shunt at HUNTSVL3 115 kV | Current Study |  |  | 808161.2093 | 36.5271 | 2212500 | 0.50967
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 775364.2044 | 1.4504 | 53460000 | 0.047593
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 523077.9489 | 1.1393 | 45914000 | 0.052357
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | Current Study | 16.71 | (1793.00, 1793.00) | 493031.0933 | 1.3411 | 36762000 | 0.034125
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR SVC at GEN-2021-076 345 kV | Current Study |  |  | 432731.966 | 3.6061 | 12000000 | 0.039554
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | Current Study | 19.2 | (2390.00, 2390.00) | 413948.9695 | 0.97999 | 42240000 | 0.022764
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 379539.2689 | 0.22994 | 165062000 | 0.013152
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | Current Study | 16.04 | (2390.00, 2390.00) | 345819.8682 | 0.97999 | 35288000 | 0.022764
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 285474.7407 | 1.1393 | 25058000 | 0.052357
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | Current Study | 13 | (2390.00, 2390.00) | 225453.748 | 0.7883 | 28600000 | 0.02266
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 147934.7293 | 0.99032 | 14938000 | 0.095892
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 143210.4156 | 0.99032 | 14460953.1406 | 0.095892
GEN-2024-257 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 121303.6905 | 2.2887 | 5300000 | 0.088475
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 120365.7289 | 2.2711 | 5300000 | 0.07076
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 118233.3258 | 2.2308 | 5300000 | 0.07076
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Add 66 MVAR switched shunt at GEN-2021-021 345 kV | Current Study |  |  | 102298.73 | 1.9302 | 5300000 | 0.00090955
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 68892.0017 | 0.5741 | 12000000 | 0.072609
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 66098.2291 | 0.35537 | 18600000 | 0.056661
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 66098.2291 | 0.35537 | 18600000 | 0.056661
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Add 248 MVAR switched shunt at GEN-2022-015 345 kV | Current Study |  |  | 57677.5738 | 1.0883 | 5300000 | 0.07076
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 48008.3889 | 2.1699 | 2212500 | 0.06341
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 46967.084 | 0.88617 | 5300000 | 0.07076
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 39142.1682 | 0.21044 | 18600000 | 0.036836
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MED-LDG3 115 kV | Current Study |  |  | 38485.0816 | 1.7394 | 2212500 | 0.054462
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Add 0.8 MVAR switched shunt at HARBNGR7 345 kV | Current Study |  |  | 33015.571 | 0.62294 | 5300000 | 0.058772
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 530624 ST JOHN3 115 539696 ST-JOHN3 115 Z1 | Current Study | 0.1 | (326.00, 326.00) | 30638.3231 | 30.6383 | 100000 | 0.19568
GEN-2024-257 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 2562.5957 | 0.15531 | 1650000 | 0.0085591
GEN-2024-258 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 3484084.0975 | 0.37128 | 938400000 | 0.037158
GEN-2024-258 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 2110912.2845 | 2.246 | 93984000 | 0.092913
GEN-2024-258 | 03 CENTRAL | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1669391.6732 | 0.76465 | 218320000 | 0.01573
GEN-2024-258 | 03 CENTRAL | TBD | ERIS | Rebuild line 645458 S3458 3 345 778170 G24-040-TAP 345 1 | Current Study | 13.15 | (1793.00, 1793.00) | 1371297.3041 | 4.7401 | 28930000 | 0.049001
GEN-2024-258 | 03 CENTRAL | TBD | ERIS | Rebuild line 640139 COOPER 3 345 778170 G24-040-TAP 345 1 | Current Study | 12.59 | (1793.00, 1793.00) | 1312899.8523 | 4.7401 | 27698000 | 0.049001
GEN-2024-258 | 03 CENTRAL | TBD | ERIS | Rebuild line 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 | Current Study | 3.23 | (1793.00, 1793.00) | 931922.1857 | 13.1146 | 7106000 | 0.098552
GEN-2024-258 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 770936.2296 | 0.38836 | 198511000 | 0.0087514
GEN-2024-258 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 613609.9882 | 1.3364 | 45914000 | 0.04504
GEN-2024-258 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 334883.4578 | 1.3364 | 25058000 | 0.04504
GEN-2024-258 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 315020.5773 | 5.9438 | 5300000 | 0.1685
GEN-2024-258 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 285244.636 | 2.4464 | 11660000 | 0.092913
GEN-2024-258 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 100904.7985 | 0.5425 | 18600000 | 0.063432
GEN-2024-258 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 100904.7985 | 0.5425 | 18600000 | 0.063432
GEN-2024-258 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 53842.7368 | 0.28948 | 18600000 | 0.037158
GEN-2024-258 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 12846.5353 | 0.77858 | 1650000 | 0.031466
GEN-2024-258 | 03 CENTRAL | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 1231.5073 | 0.055661 | 2212500 | 0.0011928
GEN-2024-259 | 03 CENTRAL | TBD | ERIS | Rebuild line 547476 ASB349 5 161 547477 CJ 366 5 161 1 | Current Study | 12.3 | (551.00, 551.00) | 10266700.7723 | 55.6461 | 18450000 | 0.40636
GEN-2024-259 | 03 CENTRAL | TBD | ERIS | Rebuild line 547476 ASB349 5 161 547491 PUR421 5 161 1 | Current Study | 11.94 | (551.00, 551.00) | 9917906.7206 | 55.3764 | 17910000 | 0.31044
GEN-2024-259 | 03 CENTRAL | TBD | ERIS | Rebuild line 547485 CAR395 5 161 547491 PUR421 5 161 1 | Current Study | 7.89 | (551.00, 551.00) | 6553792.632 | 55.3764 | 11835000 | 0.31044
GEN-2024-259 | 03 CENTRAL | TBD | NRIS | Add 3-winding transformer 505488 CARTHAG5 161 505489 CRG X2 1 13 505490 CARTHG 2 69 M2 | Current Study |  | (84.00, 84.00) | 4725288.7822 | 45.1102 | 10475000 | 0.016164
GEN-2024-259 | 03 CENTRAL | TBD | NRIS | Add 3-winding transformer 505487 CRG X1 1 13 505488 CARTHAG5 161 505490 CARTHG 2 69 M2 | Current Study |  | (84.00, 84.00) | 4725288.7822 | 45.1102 | 10475000 | 0.016482
GEN-2024-259 | 03 CENTRAL | TBD | ERIS | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1 | Current Study | 4.14 | (551.00, 551.00) | 3436490.3933 | 55.338 | 6210000 | 0.31044
GEN-2024-259 | 03 CENTRAL | TBD | ERIS | Rebuild line 547477 CJ 366 5 161 547490 FIR417 5 161 1 | Current Study | 3.26 | (551.00, 551.00) | 2721093.0502 | 55.6461 | 4890000 | 0.40636
GEN-2024-259 | 03 CENTRAL | TBD | ERIS | Rebuild line 547467 ORO110 5 161 547490 FIR417 5 161 1 | Current Study | 2.86 | (551.00, 551.00) | 2387216.6023 | 55.6461 | 4290000 | 0.40636
GEN-2024-259 | 03 CENTRAL | TBD | ERIS | Rebuild line 547554 BAX492 2 69 547601 HOC404 2 69 1 | Current Study | 3.59 | (106.00, 106.00) | 1777686.1205 | 58.2561 | 3051500 | 0.015942
GEN-2024-259 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 1642823.0572 | 0.17507 | 938400000 | 0.026307
GEN-2024-259 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1140346.276 | 1.2133 | 93984000 | 0.075365
GEN-2024-259 | 03 CENTRAL | TBD | ERIS | Rebuild line 533763 HUDSON-2 69 533770 PITTSBG2 69 1 | Current Study | 1.75 | (69.00, 69.00) | 411494.6616 | 27.6635 | 1487500 | 0.03008
GEN-2024-259 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 179891.883 | 0.090621 | 198511000 | 0.0030662
GEN-2024-259 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 154093.4035 | 1.3216 | 11660000 | 0.075365
GEN-2024-259 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 71651.7403 | 1.3519 | 5300000 | 0.057544
GEN-2024-259 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 36254.4704 | 0.19492 | 18600000 | 0.03422
GEN-2024-259 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 36254.4704 | 0.19492 | 18600000 | 0.03422
GEN-2024-259 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 25388.0466 | 0.13649 | 18600000 | 0.026307
GEN-2024-259 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 5405.315 | 0.32759 | 1650000 | 0.019879
GEN-2024-260 | 03 CENTRAL | TBD | ERIS | Rebuild line 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | Current Study | 17.54 | (1793.00, 1793.00) | 4125987.5784 | 10.6924 | 38588000 | 0.051428
GEN-2024-260 | 03 CENTRAL | TBD | ERIS | Rebuild line 645458 S3458 3 345 778170 G24-040-TAP 345 1 | Current Study | 13.15 | (1793.00, 1793.00) | 2460740.812 | 8.5058 | 28930000 | 0.13203
GEN-2024-260 | 03 CENTRAL | TBD | ERIS | Rebuild line 640139 COOPER 3 345 778170 G24-040-TAP 345 1 | Current Study | 12.59 | (1793.00, 1793.00) | 2355948.8079 | 8.5058 | 27698000 | 0.13203
GEN-2024-260 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 1883621.6016 | 0.20073 | 938400000 | 0.030163
GEN-2024-260 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 1501079.7223 | 0.75617 | 198511000 | 0.025585
GEN-2024-260 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 947010.7609 | 0.65858 | 143796000 | 0.032927
GEN-2024-260 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 674804.1119 | 0.718 | 93984000 | 0.044597
GEN-2024-260 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 529077.3075 | 0.26652 | 198511000 | 0.014261
GEN-2024-260 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 256671.4772 | 0.55903 | 45914000 | 0.028289
GEN-2024-260 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 140080.8876 | 0.55903 | 25058000 | 0.028289
GEN-2024-260 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 91185.3395 | 0.78204 | 11660000 | 0.044597
GEN-2024-260 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 49957.6144 | 0.26859 | 18600000 | 0.047155
GEN-2024-260 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 49957.6144 | 0.26859 | 18600000 | 0.047155
GEN-2024-260 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 38922.939 | 0.26056 | 14938000 | 0.027781
GEN-2024-260 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 37679.9301 | 0.26056 | 14460953.1406 | 0.027781
GEN-2024-260 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 29109.3267 | 0.1565 | 18600000 | 0.030163
GEN-2024-260 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 15453.0839 | 0.93655 | 1650000 | 0.056832
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 18754899.7521 | 1.2383 | 1514620000 | 0.050771
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 16449389.5021 | 1.28 | 1285130000 | 0.26892
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 16390576.0118 | 1.2889 | 1271630000 | 0.17697
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 15905189.7628 | 1.4813 | 1073760000 | 0.16916
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527891 HOBBS_INT 3 115 784800 G24-261-TAP 115 1 | Current Study | 11.57 | (217.00, 217.00) | 11570000 | 100 | 11570000 | 0.65983
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 8823076.1764 | 0.94023 | 938400000 | 0.10634
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 8316043.6084 | 1.1474 | 724760000 | 0.18146
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 7913062.7743 | 0.84325 | 938400000 | 0.16879
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 5994980.1335 | 1.2416 | 482840000 | 0.21036
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 5901740.033 | 1.2575 | 469340000 | 0.14317
GEN-2024-261 | 05 SOUTHWEST | TBD | NRIS | Rebuild 2-winding transformer 528334 LE-NRTH_INT3 115 528618 LE-LOVINTON2 69 1 | Current Study |  | (124.00, 124.00) | 4725000 | 100 | 4725000 | 0.093599
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 4268852.2351 | 1.1648 | 366500000 | 0.051038
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526460 AMOCO_SS 6 230 777420 G24-015-TAP 230 1 | Current Study | 25.97 | (519.00, 519.00) | 2197909.836 | 4.4543 | 49343000 | 0.067708
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 9.3 MVAR switched shunt at LE-LEWIS 2 69 kV | Current Study |  |  | 1380000 | 100 | 1380000 | 0.030853
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1208750.4899 | 1.4305 | 84500000 | 0.05856
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 969570.1817 | 1.1474 | 84500000 | 0.18146
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 954934.1274 | 1.1301 | 84500000 | 0.095784
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 954351.0284 | 0.48234 | 197860000 | 0.031784
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 917934.4847 | 0.73538 | 124824000 | 0.064148
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 870020.8503 | 0.43827 | 198511000 | 0.031237
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 841089.7838 | 1.5232 | 55220000 | 0.099059
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 685375.995 | 0.41522 | 165062000 | 0.034834
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 634966.209 | 0.77921 | 81488000 | 0.068985
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 590448.7645 | 2.2281 | 26500000 | 0.046691
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 487879.3369 | 1.1223 | 43472000 | 0.045605
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1 | Current Study | 0.47 | (260.00, 260.00) | 470000 | 100 | 470000 | 0.34017
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528016 SAND_DUNES 3 115 528018 RED_BLUFF 3 115 1 | Current Study | 7.69 | (394.00, 394.00) | 349921.478 | 4.5503 | 7690000 | 0.032334
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 248279.5101 | 1.3348 | 18600000 | 0.23646
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 239637.1133 | 1.2884 | 18600000 | 0.17697
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 237925.6091 | 1.2792 | 18600000 | 0.26892
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 236310.699 | 1.2705 | 18600000 | 0.17697
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 233886.6592 | 1.2575 | 18600000 | 0.14317
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 233443.3759 | 0.93377 | 25000000 | 0.018404
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 233443.3759 | 0.93377 | 25000000 | 0.021119
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 230315.9442 | 1.2383 | 18600000 | 0.050771
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527956 SBCRDWRDLEA 115 528505 LEA_ROAD 3 115 1 | Current Study | 4 | (217.00, 217.00) | 227363.3053 | 5.6841 | 4000000 | 0.054772
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528018 RED_BLUFF 3 115 528235 WOLFCAMP_TP3 115 1 | Current Study | 7.81 | (598.00, 598.00) | 226283.1965 | 2.8974 | 7810000 | 0.051793
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 213420.182 | 1.1474 | 18600000 | 0.18146
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1 | Current Study | 3.54 | (217.00, 217.00) | 201216.5252 | 5.6841 | 3540000 | 0.054772
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 183872.341 | 0.98856 | 18600000 | 0.25379
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1 | Current Study | 3.11 | (217.00, 217.00) | 176774.9698 | 5.6841 | 3110000 | 0.054772
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 148029.7876 | 0.79586 | 18600000 | 0.10634
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 144331.4005 | 0.77598 | 18600000 | 0.18146
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 144331.4005 | 0.77598 | 18600000 | 0.18146
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | Current Study | 0.78 | (598.00, 598.00) | 131101.5689 | 2.4774 | 5292000 | 0.046659
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | Current Study | 0.2 | (598.00, 598.00) | 110985.4552 | 2.4774 | 4480000 | 0.046659
GEN-2024-261 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 97849.0053 | 0.5406 | 18100000 | 0.011043
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 70527.4675 | 1.0758 | 6556000 | 0.099059
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 67617.4142 | 0.4176 | 16192000 | 0.06243
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 62990.5547 | 0.42168 | 14938000 | 0.059885
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 60978.9436 | 0.42168 | 14460953.1406 | 0.059885
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 53173.6222 | 1.0033 | 5300000 | 0.19157
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 20348.8714 | 1.4746 | 1380000 | 0.1742
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 19566.1073 | 0.16305 | 12000000 | 0.030245
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 19009.3115 | 1.3775 | 1380000 | 0.19157
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1 | Current Study | 2.13 | (598.00, 598.00) | 13364.6929 | 0.62745 | 2130000 | 0.0091234
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 13072.7443 | 0.59086 | 2212500 | 0.032395
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 12640.5357 | 0.91598 | 1380000 | 0.19157
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 9717.138 | 0.43919 | 2212500 | 0.06243
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 8485.0941 | 0.61486 | 1380000 | 0.0058654
GEN-2024-261 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 7399.9002 | 0.53622 | 1380000 | 0.045256
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 6890.3615 | 0.4176 | 1650000 | 0.06243
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 4833.0282 | 0.21844 | 2212500 | 0.030245
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 3066.9801 | 0.22224 | 1380000 | 0.030245
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528184 SENDERO +3 115 528193 BLACKRIVER 3 115 1 | Current Study | 0.25 | (598.00, 598.00) | 1568.6259 | 0.62745 | 250000 | 0.0091234
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 528184 SENDERO +3 115 528187 SENDERO_345 345 M2 | Current Study |  | (435.00, 435.00) | 762.7958 | 0.0045405 | 16800000 | 2.3935e-05
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 19379835.947 | 1.2795 | 1514620000 | 0.05077
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 16995648.4916 | 1.3225 | 1285130000 | 0.26889
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 16933367.0005 | 1.3316 | 1271630000 | 0.17693
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 16049009.1137 | 1.4947 | 1073760000 | 0.16518
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 9096675.1728 | 0.96938 | 938400000 | 0.1061
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 8588457.1611 | 1.185 | 724760000 | 0.18136
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 8155361.0755 | 0.86907 | 938400000 | 0.16834
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 6195069.3095 | 1.283 | 482840000 | 0.21037
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 6098245.3736 | 1.2993 | 469340000 | 0.14317
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 4470911.6991 | 1.2199 | 366500000 | 0.05173
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526460 AMOCO_SS 6 230 777420 G24-015-TAP 230 1 | Current Study | 25.97 | (519.00, 519.00) | 2324564.0324 | 4.711 | 49343000 | 0.0693
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1248163.2744 | 1.4771 | 84500000 | 0.058519
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1001330.9649 | 1.185 | 84500000 | 0.18136
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 986254.5068 | 0.49846 | 197860000 | 0.031787
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 985990.5134 | 1.1669 | 84500000 | 0.095709
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 948081.01 | 0.75953 | 124824000 | 0.064117
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 908643.475 | 1.6455 | 55220000 | 0.10356
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 899035.5472 | 0.45289 | 198511000 | 0.031238
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 708267.8548 | 0.42909 | 165062000 | 0.034836
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 655764.9026 | 0.80474 | 81488000 | 0.068947
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 595730.6364 | 2.248 | 26500000 | 0.045589
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 503843.2146 | 1.159 | 43472000 | 0.045578
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528016 SAND_DUNES 3 115 528018 RED_BLUFF 3 115 1 | Current Study | 7.69 | (394.00, 394.00) | 350518.9036 | 4.5581 | 7690000 | 0.031344
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 259476.3079 | 1.0379 | 25000000 | 0.019797
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 259476.3079 | 1.0379 | 25000000 | 0.022716
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 251855.979 | 1.3541 | 18600000 | 0.23213
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 247572.9458 | 1.331 | 18600000 | 0.17693
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 245826.7536 | 1.3216 | 18600000 | 0.26889
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 244136.3738 | 1.3126 | 18600000 | 0.17693
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 241674.1892 | 1.2993 | 18600000 | 0.14317
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 237990.3531 | 1.2795 | 18600000 | 0.05077
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528018 RED_BLUFF 3 115 528235 WOLFCAMP_TP3 115 1 | Current Study | 7.81 | (598.00, 598.00) | 228298.8482 | 2.9232 | 7810000 | 0.050569
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527956 SBCRDWRDLEA 115 528505 LEA_ROAD 3 115 1 | Current Study | 4 | (217.00, 217.00) | 222851.4544 | 5.5713 | 4000000 | 0.051953
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 220411.313 | 1.185 | 18600000 | 0.18136
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1 | Current Study | 3.54 | (217.00, 217.00) | 197223.5372 | 5.5713 | 3540000 | 0.051953
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 186953.3352 | 1.0051 | 18600000 | 0.24972
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1 | Current Study | 3.11 | (217.00, 217.00) | 173267.0058 | 5.5713 | 3110000 | 0.051953
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 152620.1142 | 0.82054 | 18600000 | 0.1061
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 149059.3495 | 0.80139 | 18600000 | 0.18136
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 149059.3495 | 0.80139 | 18600000 | 0.18136
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | Current Study | 0.78 | (598.00, 598.00) | 132616.4796 | 2.506 | 5292000 | 0.045675
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | Current Study | 0.2 | (598.00, 598.00) | 112267.9192 | 2.506 | 4480000 | 0.045675
GEN-2024-265 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 101132.6329 | 0.55874 | 18100000 | 0.011045
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 76192.0123 | 1.1622 | 6556000 | 0.10356
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 69870.0129 | 0.43151 | 16192000 | 0.062429
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 65090.3776 | 0.43574 | 14938000 | 0.059885
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 63011.7085 | 0.43574 | 14460953.1406 | 0.059885
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 54902.9357 | 1.0359 | 5300000 | 0.19142
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 21026.6584 | 1.5237 | 1380000 | 0.17419
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 20217.4167 | 0.16848 | 12000000 | 0.030244
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 19627.5327 | 1.4223 | 1380000 | 0.19142
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 13507.4276 | 0.61051 | 2212500 | 0.032393
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1 | Current Study | 2.13 | (598.00, 598.00) | 13338.4344 | 0.62622 | 2130000 | 0.0088118
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 13051.6315 | 0.94577 | 1380000 | 0.19142
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 10040.8536 | 0.45382 | 2212500 | 0.062429
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 8798.607 | 0.63758 | 1380000 | 0.0058859
GEN-2024-265 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 7651.5256 | 0.55446 | 1380000 | 0.045286
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 7119.9062 | 0.43151 | 1650000 | 0.062429
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 4993.9083 | 0.22571 | 2212500 | 0.030244
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 3169.0726 | 0.22964 | 1380000 | 0.030244
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528184 SENDERO +3 115 528193 BLACKRIVER 3 115 1 | Current Study | 0.25 | (598.00, 598.00) | 1565.5439 | 0.62622 | 250000 | 0.0088118
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 528184 SENDERO +3 115 528187 SENDERO_345 345 M2 | Current Study |  | (435.00, 435.00) | 994.9832 | 0.0059225 | 16800000 | 3.0214e-05
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 55573124.7785 | 3.6691 | 1514620000 | 0.045132
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 49572312.6011 | 5.2826 | 938400000 | 0.17924
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 45184189.6748 | 4.815 | 938400000 | 0.28913
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 37070238.2431 | 2.8846 | 1285130000 | 0.18181
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 36480503.5484 | 2.8688 | 1271630000 | 0.11816
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 27869729.905 | 3.8454 | 724760000 | 0.18244
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 23731824.8534 | 2.2102 | 1073760000 | 0.075719
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 15756764.357 | 3.2634 | 482840000 | 0.16587
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 14900199.3202 | 3.1747 | 469340000 | 0.10844
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 4951044.5677 | 2.5023 | 197860000 | 0.049467
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 3577672.5451 | 2.1675 | 165062000 | 0.05455
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 3401322.0185 | 4.0252 | 84500000 | 0.10235
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 3249340.7155 | 3.8454 | 84500000 | 0.18244
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 3245737.8913 | 1.635 | 198511000 | 0.03496
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 3044348.2699 | 2.4389 | 124824000 | 0.063824
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 2120362.9941 | 2.6021 | 81488000 | 0.06911
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 1992694.1291 | 4.5839 | 43472000 | 0.055881
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1096918.4032 | 1.2981 | 84500000 | 0.015943
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 849685.6573 | 1.5387 | 55220000 | 0.030021
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 831702.9976 | 4.4715 | 18600000 | 0.17924
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 766568.4332 | 4.1213 | 18600000 | 0.28913
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 766568.4332 | 4.1213 | 18600000 | 0.28913
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 715239.4948 | 3.8454 | 18600000 | 0.18244
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 698272.5917 | 3.7542 | 18600000 | 0.28913
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 682455.085 | 3.6691 | 18600000 | 0.045132
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 627344.1831 | 3.3728 | 18600000 | 0.17924
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 590496.6705 | 3.1747 | 18600000 | 0.10844
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 548023.3656 | 2.1921 | 25000000 | 0.012961
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 548023.3656 | 2.1921 | 25000000 | 0.014873
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 536187.6203 | 2.8827 | 18600000 | 0.18181
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 533360.3014 | 2.8675 | 18600000 | 0.11816
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 525956.7015 | 2.8277 | 18600000 | 0.11816
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 350071.8726 | 2.162 | 16192000 | 0.096965
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 234680.1381 | 1.571 | 14938000 | 0.066933
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 227185.5991 | 1.571 | 14460953.1406 | 0.066933
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 189395.9561 | 3.5735 | 5300000 | 0.2047
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 130430.3475 | 5.8952 | 2212500 | 0.096965
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 83696.1469 | 0.69747 | 12000000 | 0.038813
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 71248.2528 | 1.0868 | 6556000 | 0.030021
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 67708.1339 | 4.9064 | 1380000 | 0.2047
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 50307.97 | 2.2738 | 2212500 | 0.096965
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 45023.5709 | 3.2626 | 1380000 | 0.2047
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 44839.4855 | 3.2492 | 1380000 | 0.11515
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 35673.0848 | 2.162 | 1650000 | 0.096965
GEN-2024-266 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 33457.0622 | 2.4244 | 1380000 | 0.061385
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 20673.8026 | 0.93441 | 2212500 | 0.038813
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 13119.3402 | 0.95068 | 1380000 | 0.038813
GEN-2024-266 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 9480.9901 | 0.68703 | 1380000 | 0.0019662
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520826 BENNGTN4 138 520884 DURANTP4 138 1 | Current Study | 15.8 | (395.00, 395.00) | 18960000 | 100 | 18960000 | 0.26124
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505600 TUPELO 4 138 505602 S BROWN4 138 1 | Current Study | 36.9 | (281.00, 281.00) | 13947555.8202 | 31.4985 | 44280000 | 0.20882
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515150 CANEYCK4 138 515151 LTLCITY4 138 1 | Current Study | 11.79 | (265.00, 265.00) | 6390990.0746 | 45.1724 | 14148000 | 0.24992
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 521049 SCLMNJC4 138 784980 G24-267-TAP 138 1 | Current Study | 6.96 | (472.00, 472.00) | 5335247.3523 | 63.8799 | 8352000 | 0.73876
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520939 HLDTNTP4 138 520981 LOCO 4 138 1 | Current Study | 12.85 | (211.00, 211.00) | 4917938.4775 | 31.8932 | 15420000 | 0.044882
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505598 ALLEN 4 138 505600 TUPELO 4 138 1 | Current Study | 19.4 | (211.00, 211.00) | 4141571.9932 | 17.7903 | 23280000 | 0.049667
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505592 WELEETK4 138 505595 GREASYC4 138 1 | Current Study | 16.28 | (211.00, 211.00) | 3857230.8853 | 19.7442 | 19536000 | 0.049458
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1 | Current Study | 56.1 | (1793.00, 1793.00) | 3673829.7617 | 2.9767 | 123420000 | 0.043788
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 521098 WSBNKTP4 138 778530 G24-052-TAP 138 1 | Current Study | 9.45 | (472.00, 472.00) | 3659788.2545 | 32.2733 | 11340000 | 0.26124
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515151 LTLCITY4 138 515157 BROWN 4 138 1 | Current Study | 6.37 | (265.00, 265.00) | 3452977.6739 | 45.1724 | 7644000 | 0.24992
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520884 DURANTP4 138 784980 G24-267-TAP 138 1 | Current Study | 2.79 | (395.00, 395.00) | 3348000 | 100 | 3348000 | 0.26124
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505596 EXPLOR 4 138 505598 ALLEN 4 138 1 | Current Study | 14.8 | (211.00, 211.00) | 3156611.5321 | 17.7737 | 17760000 | 0.049458
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520918 FROGVIL4 138 520948 HUGO PP4 138 1 | Current Study | 6.55 | (717.00, 717.00) | 2324519.9931 | 29.574 | 7860000 | 0.26124
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520918 FROGVIL4 138 773820 G23-092-TAP 138 1 | Current Study | 6.3 | (717.00, 717.00) | 2235797.8559 | 29.574 | 7560000 | 0.26124
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 1 | Current Study |  | (1868.00, 1868.00) | 2132825.8156 | 3.468 | 61500000 | 0.086633
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 2 | Current Study |  | (1868.00, 1868.00) | 2132825.8156 | 3.468 | 61500000 | 0.086633
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 2033094.9651 | 1.7335 | 117282000 | 0.037414
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 1983614.5383 | 1.3203 | 150244000 | 0.030686
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 521049 SCLMNJC4 138 769060 G22-104-TAP 138 1 | Current Study | 2.27 | (472.00, 472.00) | 1970414.0922 | 72.3353 | 2724000 | 0.73876
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1 | Current Study | 30.63 | (1793.00, 1793.00) | 1820410.617 | 2.7015 | 67386000 | 0.045367
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 1708251.8316 | 1.5145 | 112794000 | 0.1323
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515044 SEMINOL4 138 515531 VANOSTP4 138 1 | Current Study | 21.55 | (395.00, 395.00) | 1666182.1112 | 6.4431 | 25860000 | 0.054772
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505595 GREASYC4 138 505596 EXPLOR 4 138 1 | Current Study | 6.91 | (211.00, 211.00) | 1637190.7505 | 19.7442 | 8292000 | 0.049458
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505602 S BROWN4 138 769060 G22-104-TAP 138 1 | Current Study | 1.62 | (717.00, 717.00) | 1339421.4237 | 68.9003 | 1944000 | 0.73876
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 1338632.2806 | 2.1164 | 63250000 | 0.11787
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 521098 WSBNKTP4 138 773820 G23-092-TAP 138 1 | Current Study | 3.4 | (472.00, 472.00) | 1316749.2132 | 32.2733 | 4080000 | 0.26124
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 1198820.2907 | 1.333 | 89936000 | 0.015969
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1185404.7286 | 0.54297 | 218320000 | 0.017184
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515178 PARKLN 4 138 515977 LKKONWA4 138 1 | Current Study | 13.56 | (472.00, 472.00) | 1179891.6433 | 7.2511 | 16272000 | 0.08996
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1158983.6647 | 1.1541 | 100427000 | 0.015201
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515117 ARBUCKL4 138 515531 VANOSTP4 138 1 | Current Study | 18.2 | (472.00, 472.00) | 1153408.4294 | 5.2812 | 21840000 | 0.053411
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1149796.7942 | 1.2042 | 95480000 | 0.049948
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 1120564.3368 | 2.014 | 55638000 | 0.046589
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 1060151.6331 | 1.6063 | 66000000 | 0.037867
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 1019981.0271 | 1.2042 | 84700000 | 0.049948
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 776060 G23-204-TAP 345 1 | Current Study | 17.82 | (1793.00, 1793.00) | 1017539.7252 | 2.5955 | 39204000 | 0.10028
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 987493.3524 | 0.68673 | 143796000 | 0.035179
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | Current Study | 13.16 | (395.00, 395.00) | 987008.5175 | 6.2501 | 15792000 | 0.06331
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 937513.0669 | 1.6998 | 55154000 | 0.030744
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 764550 G20-087-TAP 345 1 | Current Study | 14.38 | (1793.00, 1793.00) | 840405.2357 | 2.6565 | 31636000 | 0.092914
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 828168.6726 | 0.41719 | 198511000 | 0.022873
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 813860.9896 | 1.8152 | 44836000 | 0.043708
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 740802.4849 | 0.37441 | 197860000 | 0.018978
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 727045.7103 | 0.58246 | 124824000 | 0.039083
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515133 BLUERIV4 138 515178 PARKLN 4 138 1 | Current Study | 12.7 | (395.00, 395.00) | 676387.5155 | 4.4382 | 15240000 | 0.030307
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 653889.7777 | 1.3915 | 46992000 | 0.057802
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520854 CIVIT 4 138 521023 PAOLI 4 138 1 | Current Study | 11.15 | (211.00, 211.00) | 611943.7702 | 4.5736 | 13380000 | 0.039906
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | Current Study | 13.6 | (1793.00, 1793.00) | 607753.1576 | 2.0313 | 29920000 | 0.039339
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 605454.3575 | 0.64421 | 93984000 | 0.040999
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | Current Study | 7.74 | (1793.00, 1793.00) | 593916.908 | 3.4879 | 17028000 | 0.10028
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515117 ARBUCKL4 138 515133 BLUERIV4 138 1 | Current Study | 10.35 | (395.00, 395.00) | 551229.1957 | 4.4382 | 12420000 | 0.030307
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 534767.088 | 0.32398 | 165062000 | 0.020907
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 516173.4722 | 2.0105 | 25674000 | 0.072389
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | Current Study | 8.91 | (2390.00, 2390.00) | 513913.6016 | 2.6217 | 19602000 | 0.092914
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 501549.7039 | 0.37726 | 132946000 | 0.01203
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 493824.0338 | 1.47 | 33594000 | 0.061518
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 482864.2876 | 0.59256 | 81488000 | 0.040354
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 | Current Study | 6.08 | (395.00, 395.00) | 456003.9351 | 6.2501 | 7296000 | 0.06331
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 448749.7727 | 1.6998 | 26400000 | 0.030744
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | Current Study | 6.93 | (1793.00, 1793.00) | 395709.8931 | 2.5955 | 15246000 | 0.10028
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 380561.5822 | 0.82886 | 45914000 | 0.042975
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 365970.0298 | 2.0436 | 17908000 | 0.074799
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | Current Study | 5.97 | (2390.00, 2390.00) | 344339.4166 | 2.6217 | 13134000 | 0.092914
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 330008.0195 | 1.3044 | 25300000 | 0.027402
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 274202.0796 | 2.285 | 12000000 | 0.034858
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 244137.8675 | 0.45667 | 53460000 | 0.016907
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 226398.8261 | 4.2717 | 5300000 | 0.042975
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 212794.3691 | 1.7272 | 12320000 | 0.038012
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 207695.0849 | 0.82886 | 25058000 | 0.042975
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 200292.1308 | 1.6691 | 12000000 | 0.038012
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 200292.1308 | 1.6691 | 12000000 | 0.038012
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 178572.0816 | 1.4881 | 12000000 | 0.038012
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 171523.1329 | 1.1395 | 15053000 | 0.015457
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 166705.4589 | 1.3892 | 12000000 | 0.049948
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 161078.3928 | 1.3423 | 12000000 | 0.046588
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 143292.1358 | 1.1941 | 12000000 | 0.028862
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 141701.7341 | 1.1808 | 12000000 | 0.061621
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 138366.2128 | 1.1531 | 12000000 | 0.015969
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 135687.3976 | 1.1307 | 12000000 | 0.038012
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 135687.3976 | 1.1307 | 12000000 | 0.038012
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514948 CEDARLN4 138 766111 G21-088-TAP 138 1 | Current Study | 2.86 | (395.00, 395.00) | 134931.6667 | 3.9316 | 3432000 | 0.03456
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 129781.3131 | 1.0815 | 12000000 | 0.037414
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 128769.0911 | 1.0731 | 12000000 | 0.046588
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 128683.6601 | 1.0724 | 12000000 | 0.038012
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 126498.1537 | 1.0542 | 12000000 | 0.038012
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 123867.8642 | 1.0322 | 12000000 | 0.036097
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 123623.8192 | 1.0302 | 12000000 | 0.028862
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 121443.588 | 1.012 | 12000000 | 0.049948
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 120595.4149 | 1.005 | 12000000 | 0.038012
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 119662.0106 | 2.2578 | 5300000 | 0.028862
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 112099.0849 | 2.1151 | 5300000 | 0.028803
GEN-2024-267 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 111798.5455 | 0.61767 | 18100000 | 0.0097055
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 110464.3673 | 2.0842 | 5300000 | 0.034858
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 107887.4351 | 1.6347 | 6600000 | 0.034858
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 95840.1245 | 0.79867 | 12000000 | 0.036097
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 83198.1915 | 1.5698 | 5300000 | 0.046588
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 81814.2038 | 0.70167 | 11660000 | 0.040999
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 78705.662 | 1.1925 | 6600000 | 0.049948
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 76921.2412 | 1.4513 | 5300000 | 0.037414
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 73805.2909 | 1.3926 | 5300000 | 0.037414
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 70503.9741 | 1.0682 | 6600000 | 0.036097
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 70503.9741 | 1.0682 | 6600000 | 0.036097
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 68872.1962 | 1.2995 | 5300000 | 0.040999
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 66999.6193 | 1.0151 | 6600000 | 0.036097
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 66809.2811 | 1.0123 | 6600000 | 0.040999
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 66404.4495 | 1.2529 | 5300000 | 0.061621
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 61715.7853 | 0.41315 | 14938000 | 0.045133
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 60101.1847 | 1.8493 | 3250000 | 0.036097
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 60101.1847 | 1.8493 | 3250000 | 0.036097
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 59744.8841 | 0.41315 | 14460953.1406 | 0.045133
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 58893.9112 | 1.1112 | 5300000 | 0.036097
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 54025.5457 | 1.6623 | 3250000 | 0.034858
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 54025.5457 | 1.6623 | 3250000 | 0.034858
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 53070.4219 | 0.32776 | 16192000 | 0.037692
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 48851.5861 | 1.5031 | 3250000 | 0.036097
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 45350.5568 | 0.85567 | 5300000 | 0.024965
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 44835.8946 | 0.84596 | 5300000 | 0.040999
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 43684.6701 | 1.3441 | 3250000 | 0.036097
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 43516.097 | 0.82106 | 5300000 | 0.028862
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 42974.0523 | 1.7667 | 2432500 | 0.037414
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 42745.1644 | 0.80651 | 5300000 | 0.028862
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CHILD4WT 138 kV | Current Study |  |  | 42721.1316 | 1.7563 | 2432500 | 0.092914
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 42388.8219 | 1.2042 | 3520000 | 0.049948
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 41327.3034 | 1.3915 | 2970000 | 0.057802
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 | Current Study | 0.55 | (395.00, 395.00) | 41250.356 | 6.2501 | 660000 | 0.06331
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 40313.3999 | 0.76063 | 5300000 | 0.028862
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 39354.4169 | 0.74254 | 5300000 | 0.040999
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 39137.4122 | 1.2042 | 3250000 | 0.049948
GEN-2024-267 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 38962.0885 | 0.73513 | 5300000 | 0.12874
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 37412.7468 | 1.1512 | 3250000 | 0.036097
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 37395.8144 | 1.6998 | 2200000 | 0.030744
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 37082.722 | 1.141 | 3250000 | 0.036097
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 37080.4257 | 1.1409 | 3250000 | 0.036097
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 36541.6084 | 2.6479 | 1380000 | 0.1323
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 36114.1908 | 1.1112 | 3250000 | 0.036097
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 35889.9113 | 1.5604 | 2300000 | 0.1128
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 35085.2383 | 1.0795 | 3250000 | 0.049948
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 33859.6294 | 1.0418 | 3250000 | 0.036097
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 32979.2107 | 1.0147 | 3250000 | 0.036097
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 32597.0588 | 1.3401 | 2432500 | 0.062337
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 31533.2391 | 2.285 | 1380000 | 0.034858
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 31067.2161 | 0.95591 | 3250000 | 0.036097
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 30612.8173 | 1.3915 | 2200000 | 0.057802
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 29956.5829 | 0.56522 | 5300000 | 0.0043092
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 28679.8692 | 0.88246 | 3250000 | 0.040999
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 22882.3294 | 1.7335 | 1320000 | 0.037414
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 22174.9327 | 0.41839 | 5300000 | 0.037692
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 21576.8866 | 0.88703 | 2432500 | 0.040999
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 21277.7635 | 0.87473 | 2432500 | 0.040999
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 20497.2858 | 1.4853 | 1380000 | 0.036097
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 20464.1674 | 1.4829 | 1380000 | 0.034793
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 20062.8026 | 0.16719 | 12000000 | 0.023856
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 16863.2785 | 1.222 | 1380000 | 0.036097
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 14587.2226 | 1.057 | 1380000 | 0.037868
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514947 CANADN-4 138 766111 G21-088-TAP 138 1 | Current Study | 0.3 | (395.00, 395.00) | 14153.6713 | 3.9316 | 360000 | 0.03456
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 14066.8981 | 1.0193 | 1380000 | 0.040999
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 13716.2598 | 0.2588 | 5300000 | 0.038012
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 10756.7759 | 0.48618 | 2212500 | 0.0252
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 10429.2096 | 0.47138 | 2212500 | 0.0252
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520854 CIVIT 4 138 782580 G24-187-TAP 138 1 | Current Study | 0.12 | (265.00, 265.00) | 6585.9419 | 4.5736 | 144000 | 0.039906
GEN-2024-267 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 5407.9914 | 0.32776 | 1650000 | 0.037692
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1 | Current Study | 11.3 | (1793.00, 1793.00) | 3856968.0975 | 15.5148 | 24860000 | 0.24541
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 3731033.0145 | 3.1812 | 117282000 | 0.03433
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 3603828.5615 | 2.3987 | 150244000 | 0.027876
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 2855160.9082 | 3.1747 | 89936000 | 0.019016
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 2707910.4324 | 2.8361 | 95480000 | 0.058817
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 2522782.0345 | 2.5121 | 100427000 | 0.016545
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 2402178.6094 | 2.8361 | 84700000 | 0.058817
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 2369750.7415 | 3.5905 | 66000000 | 0.042322
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 2337952.2037 | 4.2021 | 55638000 | 0.048601
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 2239208.3197 | 1.0257 | 218320000 | 0.01623
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1833060.8289 | 1.2748 | 143796000 | 0.032651
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1675629.9048 | 1.7829 | 93984000 | 0.056734
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 1638931.5758 | 2.9716 | 55154000 | 0.026873
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 1593382.2649 | 3.5538 | 44836000 | 0.042786
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 1531749.9602 | 4.5596 | 33594000 | 0.095409
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 68 MVAR SVC at TONTITN7 345 kV | Current Study |  |  | 1267031.5627 | 10.5586 | 12000000 | 0.036938
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 1198936.045 | 1.0629 | 112794000 | 0.046429
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1187626.692 | 0.59827 | 198511000 | 0.0164
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 942670.8364 | 0.7552 | 124824000 | 0.025337
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 844917.8244 | 0.51188 | 165062000 | 0.016516
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 835941.8823 | 3.1931 | 26180000 | 0.018502
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 784490.5827 | 2.9716 | 26400000 | 0.026873
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 763056.8181 | 1.6619 | 45914000 | 0.043085
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 710476.9373 | 2.8082 | 25300000 | 0.029497
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 642472.9706 | 5.3539 | 12000000 | 0.040838
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 416445.4795 | 1.6619 | 25058000 | 0.043085
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 398248.0255 | 3.3187 | 12000000 | 0.062764
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 391061.3843 | 3.1742 | 12320000 | 0.034928
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 388513.2424 | 5.8866 | 6600000 | 0.062764
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 373426.6689 | 2.4807 | 15053000 | 0.016826
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 368085.6036 | 3.0674 | 12000000 | 0.034928
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 368085.6036 | 3.0674 | 12000000 | 0.034928
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 336073.5601 | 2.8006 | 12000000 | 0.048601
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 329538.3736 | 2.7462 | 12000000 | 0.019016
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 328169.7199 | 2.7347 | 12000000 | 0.034928
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 308493.5326 | 2.5708 | 12000000 | 0.04495
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 305207.4139 | 2.5434 | 12000000 | 0.062764
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 270507.9609 | 2.2542 | 12000000 | 0.058817
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 268663.513 | 2.2389 | 12000000 | 0.048601
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 258825.0618 | 4.8835 | 5300000 | 0.040838
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 249358.6616 | 2.078 | 12000000 | 0.034928
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 249358.6616 | 2.078 | 12000000 | 0.034928
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 248475.001 | 2.0706 | 12000000 | 0.025024
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 238690.3074 | 1.9891 | 12000000 | 0.04495
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 238168.1801 | 1.9847 | 12000000 | 0.03433
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 236487.587 | 1.9707 | 12000000 | 0.034928
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 232994.6219 | 3.5302 | 6600000 | 0.062764
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 232471.1864 | 1.9373 | 12000000 | 0.034928
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 226425.5345 | 1.9419 | 11660000 | 0.056734
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 214369.2563 | 1.7864 | 12000000 | 0.025024
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 194551.2926 | 5.9862 | 3250000 | 0.062764
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 194551.2926 | 5.9862 | 3250000 | 0.062764
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 190607.4974 | 3.5964 | 5300000 | 0.056734
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 185361.1824 | 2.8085 | 6600000 | 0.058817
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 184898.2693 | 2.8015 | 6600000 | 0.056734
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 175590.4985 | 2.6605 | 6600000 | 0.04495
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 175590.4985 | 2.6605 | 6600000 | 0.04495
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 173584.5009 | 3.2752 | 5300000 | 0.048601
GEN-2024-268 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 150221.9317 | 2.8344 | 5300000 | 0.24818
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 149682.3 | 4.6056 | 3250000 | 0.04495
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 149682.3 | 4.6056 | 3250000 | 0.04495
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 146675.5791 | 2.7675 | 5300000 | 0.04495
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 141162.0177 | 2.6634 | 5300000 | 0.03433
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 138071.0408 | 1.1506 | 12000000 | 0.020684
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 135443.7815 | 2.5555 | 5300000 | 0.03433
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 126765.7898 | 2.3918 | 5300000 | 0.058817
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 124085.7435 | 2.3412 | 5300000 | 0.056734
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 121665.1185 | 3.7435 | 3250000 | 0.04495
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 120492.5315 | 2.2734 | 5300000 | 0.062764
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 117748.6026 | 3.623 | 3250000 | 0.062764
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 114686.9012 | 3.5288 | 3250000 | 0.062764
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 108796.8884 | 3.3476 | 3250000 | 0.04495
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 99830.7994 | 2.8361 | 3520000 | 0.058817
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 93176.6322 | 2.867 | 3250000 | 0.04495
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 92354.7038 | 2.8417 | 3250000 | 0.04495
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 92348.9848 | 2.8415 | 3250000 | 0.04495
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 92173.2543 | 2.8361 | 3250000 | 0.058817
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 89942.5721 | 2.7675 | 3250000 | 0.04495
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 89269.2951 | 0.5976 | 14938000 | 0.032642
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 88174.8887 | 2.7131 | 3250000 | 0.062764
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 86418.4692 | 0.5976 | 14460953.1406 | 0.032642
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 83963.8773 | 0.51855 | 16192000 | 0.029816
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 79373.0764 | 2.4422 | 3250000 | 0.056734
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 78863.8332 | 3.2421 | 2432500 | 0.03433
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 77373.0564 | 2.3807 | 3250000 | 0.04495
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 74207.2846 | 1.4001 | 5300000 | 0.020425
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 73884.3916 | 5.3539 | 1380000 | 0.040838
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 73831.2888 | 5.3501 | 1380000 | 0.062764
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 72782.5073 | 1.3733 | 5300000 | 0.0052349
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 65374.2152 | 2.9716 | 2200000 | 0.026873
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 59715.191 | 2.4549 | 2432500 | 0.056734
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 58887.3518 | 2.4209 | 2432500 | 0.056734
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 53582.5499 | 2.4218 | 2212500 | 0.062764
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 51950.849 | 2.3481 | 2212500 | 0.062764
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 51048.5923 | 3.6992 | 1380000 | 0.04495
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 41998.0791 | 3.0433 | 1380000 | 0.04495
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 41992.4931 | 3.1812 | 1320000 | 0.03433
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 38930.8952 | 2.8211 | 1380000 | 0.056734
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 32606.7124 | 2.3628 | 1380000 | 0.042323
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 25646.7115 | 1.8585 | 1380000 | 0.046429
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 25206.9702 | 0.4756 | 5300000 | 0.034928
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 24041.0282 | 1.0866 | 2212500 | 0.059407
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 8556.1016 | 0.51855 | 1650000 | 0.029816
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 30894967.8185 | 2.0398 | 1514620000 | 0.050181
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 26565770.1059 | 2.0672 | 1285130000 | 0.26058
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 26284461.856 | 2.067 | 1271630000 | 0.17028
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 26226228.2865 | 2.4425 | 1073760000 | 0.16735
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1 | Current Study | 52.45 | (1046.00, 1046.00) | 22691892.0426 | 22.7705 | 99655000 | 0.60114
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 16448660.9694 | 1.7528 | 938400000 | 0.11895
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 14498905.3288 | 1.5451 | 938400000 | 0.18556
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 13956782.7216 | 1.9257 | 724760000 | 0.18273
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 10271435.4292 | 2.8026 | 366500000 | 0.073683
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 9796329.0319 | 2.0289 | 482840000 | 0.20625
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 9570915.2481 | 2.0392 | 469340000 | 0.13931
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3 | Current Study | 39.39 | (478.00, 544.00) | 7517444.0832 | 7.1137 | 105675000 | 0.097248
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524875 OASIS 6 230 787680 G24-357-TAP 230 1 | Current Study | 26.02 | (901.00, 901.00) | 6577308.8569 | 13.3042 | 49438000 | 0.29083
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527799 EDDY_NORTH 6 230 528095 7-RIVERS 6 230 1 | Current Study | 24.1 | (386.00, 386.00) | 6541111.4635 | 14.285 | 45790000 | 0.089071
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527597 TWEEDY 3 115 527798 EDDY_NTH 3 115 1 | Current Study | 44.83 | (394.00, 394.00) | 6232939.9703 | 13.9035 | 44830000 | 0.10695
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528095 7-RIVERS 6 230 528179 PECOS 6 230 1 | Current Study | 20.61 | (386.00, 386.00) | 5953576.9156 | 15.2036 | 39159000 | 0.093973
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Current Study | 54.58 | (637.00, 637.00) | 5312689.8984 | 5.123 | 103702000 | 0.047585
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524885 SN_JUAN_SS 6 230 787680 G24-357-TAP 230 1 | Current Study | 20.18 | (901.00, 901.00) | 5101079.6592 | 13.3042 | 38342000 | 0.29083
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add line 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 P2 | Current Study | 2.51 | (478.00, 478.00) | 4899714.4784 | 36.3615 | 13475000 | 0.33321
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 527796 EDDY_TR 1 13 527799 EDDY_NORTH 6 230 527802 EDDY_CNTY 7 345 M2 | Current Study |  | (516.00, 558.00) | 3973150.0339 | 15.8926 | 25000000 | 0.21085
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1869249.9139 | 2.2121 | 84500000 | 0.054335
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 1638111.1791 | 0.82791 | 197860000 | 0.032734
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1627225.7575 | 1.9257 | 84500000 | 0.18273
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 1620517.3449 | 1.9178 | 84500000 | 0.097527
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1546118.1145 | 1.2386 | 124824000 | 0.064828
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1465154.2743 | 0.73807 | 198511000 | 0.031563
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1 | Current Study | 9.6 | (901.00, 901.00) | 1423947.7624 | 7.8067 | 18240000 | 0.20918
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 524872 OASIS_TR1 1 13 524874 OASIS 3 115 524875 OASIS 6 230 M2 | Current Study |  | (239.00, 239.00) | 1316497.4387 | 9.5398 | 13800000 | 0.019734
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 1175736.485 | 0.7123 | 165062000 | 0.035854
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 1116774.8195 | 2.0224 | 55220000 | 0.078917
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 1069394.6634 | 1.3123 | 81488000 | 0.06971
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 840977.5285 | 3.1735 | 26500000 | 0.039901
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 833463.8789 | 1.9172 | 43472000 | 0.046746
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528013 PHANTOM 3 115 528228 WOOD_DRAW 3 115 1 | Current Study | 7.71 | (260.00, 260.00) | 786907.1446 | 10.2063 | 7710000 | 0.01193
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528016 SAND_DUNES 3 115 528018 RED_BLUFF 3 115 1 | Current Study | 7.69 | (394.00, 394.00) | 637657.391 | 8.292 | 7690000 | 0.035353
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 483889.2141 | 1.9356 | 25000000 | 0.026265
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 483889.2141 | 1.9356 | 25000000 | 0.022889
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1 | Current Study | 18.95 | (901.00, 901.00) | 463910.4858 | 1.2885 | 36005000 | 0.030106
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 384289.8846 | 2.0661 | 18600000 | 0.17028
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 384249.9463 | 2.0659 | 18600000 | 0.26058
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 379399.7184 | 2.0398 | 18600000 | 0.050181
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 379296.5092 | 2.0392 | 18600000 | 0.13931
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 378955.5382 | 2.0374 | 18600000 | 0.17028
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 358182.2377 | 1.9257 | 18600000 | 0.18273
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1 | Current Study | 2.49 | (394.00, 394.00) | 346197.2011 | 13.9035 | 2490000 | 0.10695
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528018 RED_BLUFF 3 115 528235 WOLFCAMP_TP3 115 1 | Current Study | 7.81 | (598.00, 598.00) | 311823.2122 | 3.9926 | 7810000 | 0.042823
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 279585.3165 | 1.5031 | 18600000 | 0.23154
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 275968.5784 | 1.4837 | 18600000 | 0.11895
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 245979.9151 | 1.3225 | 18600000 | 0.18556
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 245979.9151 | 1.3225 | 18600000 | 0.18556
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 528184 SENDERO +3 115 528187 SENDERO_345 345 M2 | Current Study |  | (435.00, 435.00) | 233847.2477 | 1.3919 | 16800000 | 0.0044026
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 208159.9836 | 1.1191 | 18600000 | 0.11895
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | Current Study | 0.78 | (598.00, 598.00) | 161326.9496 | 3.0485 | 5292000 | 0.034449
GEN-2024-271 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 160149.3581 | 0.8848 | 18100000 | 0.010844
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | Current Study | 0.2 | (598.00, 598.00) | 136573.0791 | 3.0485 | 4480000 | 0.034449
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 115700.1907 | 0.71455 | 16192000 | 0.064094
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 105913.8579 | 0.70902 | 14938000 | 0.060415
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 102531.4859 | 0.70902 | 14460953.1406 | 0.060415
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 93644.3425 | 1.4284 | 6556000 | 0.078917
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 90235.3133 | 1.7026 | 5300000 | 0.19505
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1 | Current Study | 2.13 | (598.00, 598.00) | 49578.5705 | 2.3276 | 2130000 | 0.020307
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 33119.2036 | 0.27599 | 12000000 | 0.030718
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 32756.2717 | 2.3736 | 1380000 | 0.16824
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 32258.686 | 2.3376 | 1380000 | 0.19505
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 21957.9742 | 0.99245 | 2212500 | 0.032648
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 21450.9122 | 1.5544 | 1380000 | 0.19505
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 16626.9991 | 0.7515 | 2212500 | 0.064094
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 15181.2241 | 1.1001 | 1380000 | 0.0062965
GEN-2024-271 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 12913.4015 | 0.93575 | 1380000 | 0.047386
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 11790.101 | 0.71455 | 1650000 | 0.064094
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 8180.7814 | 0.36975 | 2212500 | 0.030718
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528184 SENDERO +3 115 528193 BLACKRIVER 3 115 1 | Current Study | 0.25 | (598.00, 598.00) | 5819.081 | 2.3276 | 250000 | 0.020307
GEN-2024-271 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 5191.423 | 0.37619 | 1380000 | 0.030718
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 14663203.8068 | 1.5599 | 940000000 | 0.022152
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Rebuild line 530582 S HAYS6 230 539679 GRTBEND6 230 1 | Current Study | 39.2 | (386.00, 386.00) | 8590127.3382 | 11.5335 | 74480000 | 0.077729
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Rebuild line 539649 SAWYER 3 115 539760 BARBER 3 115 1 | Current Study | 19 | (598.00, 598.00) | 7727948.7693 | 40.6734 | 19000000 | 0.62738
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Rebuild line 530618 HUNTSVL3 115 530624 ST JOHN3 115 1 | Current Study | 26.5 | (297.00, 297.00) | 5597263.0041 | 21.1217 | 26500000 | 0.14914
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 4506195.3887 | 2.27 | 198511000 | 0.077115
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Rebuild line 539638 FLATRDG4 138 539674 BARBER 4 138 1 | Current Study | 8.92 | (472.00, 472.00) | 4306189.9267 | 40.2297 | 10704000 | 0.55869
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 539674 BARBER 4 138 539760 BARBER 3 115 539917 BARBER-1 13 M2 | Current Study |  | (324.00, 324.00) | 4183891.5581 | 40.2297 | 10400000 | 0.27934
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Rebuild line 539010 SADLHRN3 115 539648 PRICHRD3 115 1 | Current Study | 9.47 | (598.00, 598.00) | 3857820.3749 | 40.7373 | 9470000 | 0.37261
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Rebuild line 539010 SADLHRN3 115 539696 ST-JOHN3 115 1 | Current Study | 9.4 | (598.00, 598.00) | 3829304.2792 | 40.7373 | 9400000 | 0.37261
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Rebuild line 539642 ELLSWTP3 115 539678 GRTBEND3 115 1 | Current Study | 30.21 | (115.00, 115.00) | 3827029.6695 | 12.6681 | 30210000 | 0.026005
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Rebuild line 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | Current Study | 14.69 | (260.00, 260.00) | 3710733.7601 | 25.2603 | 14690000 | 0.22348
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Rebuild line 530618 HUNTSVL3 115 530724 CENTENNIAL3 115 1 | Current Study | 12.45 | (297.00, 297.00) | 2629657.5246 | 21.1217 | 12450000 | 0.14914
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Rebuild line 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | Current Study | 13.1 | (297.00, 297.00) | 2582482.6257 | 19.7136 | 13100000 | 0.17921
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 2371255.423 | 0.25269 | 938400000 | 0.038125
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Rebuild line 530724 CENTENNIAL3 115 533412 ARKVALJ3 115 1 | Current Study | 10.96 | (297.00, 297.00) | 2314943.4915 | 21.1217 | 10960000 | 0.14914
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 2096105.1251 | 0.96011 | 218320000 | 0.029775
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Rebuild line 539668 HARPER 4 138 539881 SPRVLSTR 138 1 | Current Study | 12.1 | (281.00, 281.00) | 1984040.5849 | 13.6642 | 14520000 | 0.063501
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1792864.1825 | 0.90316 | 198511000 | 0.048521
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Rebuild line 539009 CONWAY 4 138 539881 SPRVLSTR 138 1 | Current Study | 10.66 | (281.00, 281.00) | 1747923.3583 | 13.6642 | 12792000 | 0.063501
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Rebuild line 539666 GBENDTP3 115 539678 GRTBEND3 115 1 | Current Study | 7.21 | (176.00, 176.00) | 1421344.2844 | 19.7135 | 7210000 | 0.11591
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Current Study | 26.47 | (1793.00, 1793.00) | 1413465.8385 | 2.4272 | 58234000 | 0.041768
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Rebuild line 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Current Study | 38.26 | (1793.00, 1793.00) | 1356276.2414 | 1.6113 | 84172000 | 0.03917
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Rebuild line 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Current Study | 37.4 | (1793.00, 1793.00) | 1340435.1443 | 1.6291 | 82280000 | 0.03917
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Rebuild line 530565 SEWARD 2 69 530569 GB STH 2 69 1 | Current Study | 8.56 | (69.00, 69.00) | 1335098.3503 | 18.3493 | 7276000 | 0.025375
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Add 32 MVAR switched shunt at BARBER 3 115 kV | Current Study |  |  | 1165630.4873 | 52.6839 | 2212500 | 0.62738
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Rebuild line 533412 ARKVALJ3 115 533413 CIRCLE 3 115 1 | Current Study | 5.2 | (297.00, 297.00) | 1098330.8536 | 21.1217 | 5200000 | 0.14914
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Rebuild line 533075 VIOLA 4 138 539009 CONWAY 4 138 1 | Current Study | 5.62 | (281.00, 281.00) | 921513.0651 | 13.6642 | 6744000 | 0.063501
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Add 21 MVAR switched shunt at LARNED3 115 kV | Current Study |  |  | 899898.0454 | 40.6734 | 2212500 | 0.62738
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Add 63 MVAR switched shunt at SADLHRN3 115 kV | Current Study |  |  | 899886.2295 | 40.6728 | 2212500 | 0.62738
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Add 45 MVAR switched shunt at HUNTSVL3 115 kV | Current Study |  |  | 899842.1796 | 40.6708 | 2212500 | 0.62738
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Rebuild 3-winding transformer 530565 SEWARD 2 69 530631 SWRD1 1 12 530679 SEWRDMW3 115 1 | Current Study |  | (87.00, 87.00) | 870504.562 | 18.4234 | 4725000 | 0.044267
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Rebuild line 533413 CIRCLE 3 115 533416 RENO 3 115 2 | Current Study | 5.95 | (217.00, 217.00) | 675151.4377 | 11.3471 | 5950000 | 0.065132
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 663856.8367 | 1.2418 | 53460000 | 0.045048
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 597081.9297 | 0.41523 | 143796000 | 0.020843
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 473772.4647 | 1.0319 | 45914000 | 0.052426
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR SVC at GEN-2021-076 345 kV | Current Study |  |  | 387621.1881 | 3.2302 | 12000000 | 0.03917
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 258565.8061 | 1.0319 | 25058000 | 0.052426
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 131499.896 | 0.8803 | 14938000 | 0.094234
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 127300.4307 | 0.8803 | 14460953.1406 | 0.094234
GEN-2024-272 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 111540.5377 | 2.1045 | 5300000 | 0.08994
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 102215.5117 | 1.9286 | 5300000 | 0.066431
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 100404.6584 | 1.8944 | 5300000 | 0.066431
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Add 66 MVAR switched shunt at GEN-2021-021 345 kV | Current Study |  |  | 93569.2959 | 1.7655 | 5300000 | 0.00091972
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 61458.9481 | 0.33042 | 18600000 | 0.058244
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 61458.9481 | 0.33042 | 18600000 | 0.058244
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Add 248 MVAR switched shunt at GEN-2022-015 345 kV | Current Study |  |  | 49626.0134 | 0.93634 | 5300000 | 0.067307
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MED-LDG3 115 kV | Current Study |  |  | 43905.2807 | 1.9844 | 2212500 | 0.068689
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 40998.8655 | 1.8531 | 2212500 | 0.059866
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 40410.6655 | 0.76247 | 5300000 | 0.067307
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 36645.1779 | 0.19702 | 18600000 | 0.038125
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Add 0.8 MVAR switched shunt at HARBNGR7 345 kV | Current Study |  |  | 28708.7034 | 0.54167 | 5300000 | 0.056498
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Rebuild line 530624 ST JOHN3 115 539696 ST-JOHN3 115 Z1 | Current Study | 0.1 | (326.00, 326.00) | 21121.7472 | 21.1217 | 100000 | 0.14914
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 19393.4138 | 0.16161 | 12000000 | 0.022597
GEN-2024-272 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 2341.2828 | 0.1419 | 1650000 | 0.0086451
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 2029370.2172 | 0.13399 | 1514620000 | 0.050823
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 2021098.7953 | 0.18823 | 1073760000 | 0.19886
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 1784346.4165 | 0.13885 | 1285130000 | 0.26987
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 1779892.9463 | 0.13997 | 1271630000 | 0.17779
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 958889.6562 | 0.10218 | 938400000 | 0.10692
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 901771.6239 | 0.12442 | 724760000 | 0.18204
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 863270.6861 | 0.091994 | 938400000 | 0.17035
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 648907.5112 | 0.13439 | 482840000 | 0.21065
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 639514.4204 | 0.13626 | 469340000 | 0.14353
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 406949.1218 | 0.11104 | 366500000 | 0.045012
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526460 AMOCO_SS 6 230 777420 G24-015-TAP 230 1 | Current Study | 25.97 | (519.00, 519.00) | 141796.2111 | 0.28737 | 49343000 | 0.040411
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 132131.3532 | 0.15637 | 84500000 | 0.05922
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 105137.8418 | 0.12442 | 84500000 | 0.18204
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 103575.632 | 0.12257 | 84500000 | 0.096112
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 102896.3891 | 0.052005 | 197860000 | 0.031703
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 99450.1859 | 0.079672 | 124824000 | 0.064295
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 93956.4068 | 0.047331 | 198511000 | 0.031208
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 76695.7308 | 0.28942 | 26500000 | 0.056107
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 73911.3532 | 0.044778 | 165062000 | 0.034752
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 68817.8511 | 0.084452 | 81488000 | 0.069169
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 62154.5754 | 0.11256 | 55220000 | 0.067721
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528013 PHANTOM 3 115 528228 WOOD_DRAW 3 115 1 | Current Study | 7.71 | (260.00, 260.00) | 53860.4234 | 0.69858 | 7710000 | 0.01259
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 52816.3657 | 0.1215 | 43472000 | 0.045674
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528016 SAND_DUNES 3 115 528018 RED_BLUFF 3 115 1 | Current Study | 7.69 | (394.00, 394.00) | 52254.779 | 0.67952 | 7690000 | 0.04467
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528018 RED_BLUFF 3 115 528235 WOLFCAMP_TP3 115 1 | Current Study | 7.81 | (598.00, 598.00) | 30107.5783 | 0.3855 | 7810000 | 0.063752
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 30078.8039 | 0.16171 | 18600000 | 0.26502
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 26022.7833 | 0.13991 | 18600000 | 0.17779
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 25808.9644 | 0.13876 | 18600000 | 0.26987
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 25661.5598 | 0.13797 | 18600000 | 0.17779
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 25344.0325 | 0.13626 | 18600000 | 0.14353
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 24921.2912 | 0.13399 | 18600000 | 0.050823
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 23142.7675 | 0.12442 | 18600000 | 0.18204
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 21956.5454 | 0.11805 | 18600000 | 0.28036
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | Current Study | 0.78 | (598.00, 598.00) | 16498.3385 | 0.31176 | 5292000 | 0.054321
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 16087.8394 | 0.086494 | 18600000 | 0.10692
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 16047.977 | 0.064192 | 25000000 | 0.011705
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 16047.977 | 0.064192 | 25000000 | 0.013431
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 15650.9474 | 0.084145 | 18600000 | 0.18204
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 15650.9474 | 0.084145 | 18600000 | 0.18204
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | Current Study | 0.2 | (598.00, 598.00) | 13966.8474 | 0.31176 | 4480000 | 0.054321
GEN-2024-273 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 10580.7379 | 0.058457 | 18100000 | 0.011047
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 7293.2482 | 0.045042 | 16192000 | 0.062296
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 6802.6467 | 0.045539 | 14938000 | 0.05983
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 6585.4034 | 0.045539 | 14460953.1406 | 0.05983
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 5767.4047 | 0.10882 | 5300000 | 0.19222
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 5211.8155 | 0.079497 | 6556000 | 0.067721
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 528184 SENDERO +3 115 528187 SENDERO_345 345 M2 | Current Study |  | (435.00, 435.00) | 4121.441 | 0.024532 | 16800000 | 0.0011964
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 2208.102 | 0.16001 | 1380000 | 0.17487
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 2112.6622 | 0.017606 | 12000000 | 0.030212
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 2061.8191 | 0.14941 | 1380000 | 0.19222
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1 | Current Study | 2.13 | (598.00, 598.00) | 1567.1975 | 0.073577 | 2130000 | 0.0098975
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 1412.7713 | 0.063854 | 2212500 | 0.032388
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 1371.0385 | 0.099351 | 1380000 | 0.19222
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 1048.0954 | 0.047372 | 2212500 | 0.062296
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 891.9901 | 0.064637 | 1380000 | 0.0057043
GEN-2024-273 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 792.1616 | 0.057403 | 1380000 | 0.04482
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 743.1978 | 0.045042 | 1650000 | 0.062296
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 521.8491 | 0.023586 | 2212500 | 0.030212
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 331.159 | 0.023997 | 1380000 | 0.030212
GEN-2024-273 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528184 SENDERO +3 115 528193 BLACKRIVER 3 115 1 | Current Study | 0.25 | (598.00, 598.00) | 183.9434 | 0.073577 | 250000 | 0.0098975
GEN-2024-274 | 03 CENTRAL | TBD | ERIS | Rebuild line 539668 HARPER 4 138 539881 SPRVLSTR 138 1 | Current Study | 12.1 | (281.00, 281.00) | 9710450.5448 | 66.8764 | 14520000 | 0.35342
GEN-2024-274 | 03 CENTRAL | TBD | ERIS | Rebuild line 539009 CONWAY 4 138 539881 SPRVLSTR 138 1 | Current Study | 10.66 | (281.00, 281.00) | 8554826.6783 | 66.8764 | 12792000 | 0.35342
GEN-2024-274 | 03 CENTRAL | TBD | ERIS | Rebuild line 533075 VIOLA 4 138 539009 CONWAY 4 138 1 | Current Study | 5.62 | (281.00, 281.00) | 4510143.1456 | 66.8764 | 6744000 | 0.35342
GEN-2024-274 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 4325674.1617 | 0.46096 | 938400000 | 0.044687
GEN-2024-274 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 3800381.7684 | 0.40499 | 938400000 | 0.069482
GEN-2024-274 | 03 CENTRAL | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1746136.5249 | 0.79981 | 218320000 | 0.028205
GEN-2024-274 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 1111387.613 | 0.55986 | 198511000 | 0.021628
GEN-2024-274 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Current Study | 26.47 | (1793.00, 1793.00) | 953266.5986 | 1.637 | 58234000 | 0.032032
GEN-2024-274 | 03 CENTRAL | TBD | ERIS | Rebuild line 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Current Study | 38.26 | (1793.00, 1793.00) | 919625.115 | 1.0926 | 84172000 | 0.030202
GEN-2024-274 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 816549.3538 | 1.7784 | 45914000 | 0.10275
GEN-2024-274 | 03 CENTRAL | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 525645.9665 | 0.98325 | 53460000 | 0.040562
GEN-2024-274 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 445639.5371 | 1.7784 | 25058000 | 0.10275
GEN-2024-274 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR SVC at GEN-2021-076 345 kV | Current Study |  |  | 262827.4762 | 2.1902 | 12000000 | 0.030202
GEN-2024-274 | 03 CENTRAL | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 243956.2239 | 1.3116 | 18600000 | 0.15021
GEN-2024-274 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 146915.3355 | 0.78987 | 18600000 | 0.15832
GEN-2024-274 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 146915.3355 | 0.78987 | 18600000 | 0.15832
GEN-2024-274 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 109594.1891 | 2.0678 | 5300000 | 0.10049
GEN-2024-274 | 03 CENTRAL | TBD | ERIS | Add 66 MVAR switched shunt at GEN-2021-021 345 kV | Current Study |  |  | 64245.844 | 1.2122 | 5300000 | 0.0007181
GEN-2024-274 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 58730.7739 | 0.31576 | 18600000 | 0.069482
GEN-2024-274 | 03 CENTRAL | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 55209.23 | 1.0417 | 5300000 | 0.040802
GEN-2024-274 | 03 CENTRAL | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 54741.9796 | 0.29431 | 18600000 | 0.044687
GEN-2024-274 | 03 CENTRAL | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 54231.1415 | 1.0232 | 5300000 | 0.040802
GEN-2024-274 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 39037.6754 | 0.26133 | 14938000 | 0.031811
GEN-2024-274 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 37791.0025 | 0.26133 | 14460953.1406 | 0.031811
GEN-2024-274 | 03 CENTRAL | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 33775.0675 | 1.5266 | 2212500 | 0.056082
GEN-2024-274 | 03 CENTRAL | TBD | ERIS | Add 248 MVAR switched shunt at GEN-2022-015 345 kV | Current Study |  |  | 31425.2366 | 0.59293 | 5300000 | 0.048467
GEN-2024-274 | 03 CENTRAL | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 25589.6985 | 0.48282 | 5300000 | 0.048467
GEN-2024-274 | 03 CENTRAL | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 19197.0389 | 0.15998 | 12000000 | 0.025436
GEN-2024-274 | 03 CENTRAL | TBD | ERIS | Add 24 MVAR switched shunt at NESSCTY3 115 kV | Current Study |  |  | 6508.1901 | 0.29416 | 2212500 | 0.025436
GEN-2024-274 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 3391.9953 | 0.20558 | 1650000 | 0.014243
GEN-2024-274 | 03 CENTRAL | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 3009.1288 | 0.21805 | 1380000 | 0.025436
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Rebuild line 532856 SWISVAL6 230 785250 G24-276-TAP 230 1 | Current Study | 14.81 | (386.00, 386.00) | 14069500 | 50 | 28139000 | 0.59697
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Rebuild line 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | Current Study | 17.54 | (1793.00, 1793.00) | 1799675.1129 | 4.6638 | 38588000 | 0.029879
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 1626177.1757 | 0.17329 | 938400000 | 0.034686
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 1041553.5617 | 0.52468 | 198511000 | 0.023647
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1017530.3562 | 0.46607 | 218320000 | 0.019175
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Rebuild line 645458 S3458 3 345 778170 G24-040-TAP 345 1 | Current Study | 13.15 | (1793.00, 1793.00) | 949953.2436 | 3.2836 | 28930000 | 0.06789
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Rebuild line 640139 COOPER 3 345 778170 G24-040-TAP 345 1 | Current Study | 12.59 | (1793.00, 1793.00) | 909498.9609 | 3.2836 | 27698000 | 0.06789
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 729141.383 | 0.50707 | 143796000 | 0.033768
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 525743.4371 | 0.5594 | 93984000 | 0.046282
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 369214.7949 | 0.18599 | 198511000 | 0.013256
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 245744.8513 | 0.53523 | 45914000 | 0.036076
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Rebuild line 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 | Current Study | 3.23 | (1793.00, 1793.00) | 170756.3481 | 2.403 | 7106000 | 0.036116
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 134117.5782 | 0.53523 | 25058000 | 0.036076
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | Current Study | 0.09 | (386.00, 386.00) | 85500 | 50 | 171000 | 0.40303
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 71042.9782 | 0.60929 | 11660000 | 0.046282
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 47138.395 | 0.25343 | 18600000 | 0.059266
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 47138.395 | 0.25343 | 18600000 | 0.059266
GEN-2024-276 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 27473.9112 | 0.51838 | 5300000 | 0.02939
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 26928.0575 | 0.18027 | 14938000 | 0.0256
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 26068.1067 | 0.18027 | 14460953.1406 | 0.0256
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 25130.8026 | 0.13511 | 18600000 | 0.034686
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 19696.9155 | 0.89026 | 2212500 | 0.038157
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 9793.2396 | 0.59353 | 1650000 | 0.047974
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Rebuild line 532856 SWISVAL6 230 785250 G24-276-TAP 230 1 | Current Study | 14.81 | (386.00, 386.00) | 14069500 | 50 | 28139000 | 0.59697
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Rebuild line 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | Current Study | 17.54 | (1793.00, 1793.00) | 1799675.1129 | 4.6638 | 38588000 | 0.029879
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 1626177.1757 | 0.17329 | 938400000 | 0.034686
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 1041553.5617 | 0.52468 | 198511000 | 0.023647
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1017530.3562 | 0.46607 | 218320000 | 0.019175
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Rebuild line 645458 S3458 3 345 778170 G24-040-TAP 345 1 | Current Study | 13.15 | (1793.00, 1793.00) | 949953.2436 | 3.2836 | 28930000 | 0.06789
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Rebuild line 640139 COOPER 3 345 778170 G24-040-TAP 345 1 | Current Study | 12.59 | (1793.00, 1793.00) | 909498.9609 | 3.2836 | 27698000 | 0.06789
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 729141.383 | 0.50707 | 143796000 | 0.033768
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 525743.4371 | 0.5594 | 93984000 | 0.046282
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 369214.7949 | 0.18599 | 198511000 | 0.013256
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 245744.8513 | 0.53523 | 45914000 | 0.036076
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Rebuild line 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 | Current Study | 3.23 | (1793.00, 1793.00) | 170756.3481 | 2.403 | 7106000 | 0.036116
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 134117.5782 | 0.53523 | 25058000 | 0.036076
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | Current Study | 0.09 | (386.00, 386.00) | 85500 | 50 | 171000 | 0.40303
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 71042.9782 | 0.60929 | 11660000 | 0.046282
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 47138.395 | 0.25343 | 18600000 | 0.059266
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 47138.395 | 0.25343 | 18600000 | 0.059266
GEN-2024-277 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 27473.9112 | 0.51838 | 5300000 | 0.02939
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 26928.0575 | 0.18027 | 14938000 | 0.0256
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 26068.1067 | 0.18027 | 14460953.1406 | 0.0256
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 25130.8026 | 0.13511 | 18600000 | 0.034686
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 19696.9155 | 0.89026 | 2212500 | 0.038157
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 9793.2396 | 0.59353 | 1650000 | 0.047974
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 32702318.6156 | 2.1591 | 1514620000 | 0.050243
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 31076582.0696 | 2.8942 | 1073760000 | 0.18758
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 28126502.1113 | 2.1886 | 1285130000 | 0.26096
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 27932441.9392 | 2.1966 | 1271630000 | 0.17116
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 17604515.4674 | 1.876 | 938400000 | 0.12042
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 15705224.9165 | 1.6736 | 938400000 | 0.19012
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 14841642.3614 | 2.0478 | 724760000 | 0.1838
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 10357780.6647 | 2.1452 | 482840000 | 0.20627
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 10147225.9668 | 2.162 | 469340000 | 0.13971
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 7719562.7947 | 2.1063 | 366500000 | 0.052381
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527799 EDDY_NORTH 6 230 528095 7-RIVERS 6 230 1 | Current Study | 24.1 | (386.00, 386.00) | 3353045.7102 | 7.3227 | 45790000 | 0.043188
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1989265.8515 | 2.3542 | 84500000 | 0.054695
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1730391.8256 | 2.0478 | 84500000 | 0.1838
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 1725474.7766 | 2.042 | 84500000 | 0.098225
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 1717793.8589 | 0.86819 | 197860000 | 0.032469
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1642032.4773 | 1.3155 | 124824000 | 0.065124
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1546703.3725 | 0.77915 | 198511000 | 0.031517
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 1233637.1469 | 0.74738 | 165062000 | 0.035584
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 1136809.0166 | 1.3951 | 81488000 | 0.070095
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524875 OASIS 6 230 787680 G24-357-TAP 230 1 | Current Study | 26.02 | (901.00, 901.00) | 1003101.0132 | 2.029 | 49438000 | 0.041954
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 908446.4408 | 1.6451 | 55220000 | 0.060722
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 884917.402 | 2.0356 | 43472000 | 0.046946
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 827719.8776 | 3.1235 | 26500000 | 0.037147
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524885 SN_JUAN_SS 6 230 787680 G24-357-TAP 230 1 | Current Study | 20.18 | (901.00, 901.00) | 777962.277 | 2.029 | 38342000 | 0.041954
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528016 SAND_DUNES 3 115 528018 RED_BLUFF 3 115 1 | Current Study | 7.69 | (394.00, 394.00) | 629664.8762 | 8.1881 | 7690000 | 0.033021
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 547999.1215 | 2.9462 | 18600000 | 0.2962
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 408384.0463 | 2.1956 | 18600000 | 0.17116
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 406824.5296 | 2.1872 | 18600000 | 0.26096
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 402715.2478 | 2.1651 | 18600000 | 0.17116
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 402135.7715 | 2.162 | 18600000 | 0.13971
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 401594.5427 | 2.1591 | 18600000 | 0.050243
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 397121.5599 | 2.1351 | 18600000 | 0.31108
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 380890.9817 | 2.0478 | 18600000 | 0.1838
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 322749.1393 | 1.291 | 25000000 | 0.014441
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 322749.1393 | 1.291 | 25000000 | 0.016571
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528018 RED_BLUFF 3 115 528235 WOLFCAMP_TP3 115 1 | Current Study | 7.81 | (598.00, 598.00) | 312738.4704 | 4.0043 | 7810000 | 0.040625
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 295361.0093 | 1.588 | 18600000 | 0.12042
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 266445.625 | 1.4325 | 18600000 | 0.19012
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 266445.625 | 1.4325 | 18600000 | 0.19012
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add 18 MVAR switched shunt at FALCNRD4 138 kV | Current Study |  |  | 253436.3076 | 10.4188 | 2432500 | 0.059025
GEN-2024-278 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 169048.8685 | 0.93397 | 18100000 | 0.010828
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | Current Study | 0.78 | (598.00, 598.00) | 162717.47 | 3.0748 | 5292000 | 0.032866
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add 0.7 MVAR switched shunt at ROSEVLT2 69 kV | Current Study |  |  | 143778.8713 | 10.4188 | 1380000 | 0.059025
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | Current Study | 0.2 | (598.00, 598.00) | 137750.2392 | 3.0748 | 4480000 | 0.032866
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 121770.8431 | 0.75204 | 16192000 | 0.063808
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 111925.337 | 0.74927 | 14938000 | 0.06039
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 108350.9877 | 0.74927 | 14460953.1406 | 0.06039
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 96079.6618 | 1.8128 | 5300000 | 0.19645
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 76175.4905 | 1.1619 | 6556000 | 0.060722
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 528184 SENDERO +3 115 528187 SENDERO_345 345 M2 | Current Study |  | (435.00, 435.00) | 57022.9063 | 0.33942 | 16800000 | 0.0010155
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 34947.8232 | 0.29123 | 12000000 | 0.03066
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 34614.2309 | 2.5083 | 1380000 | 0.16817
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 34348.0122 | 2.489 | 1380000 | 0.19645
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1 | Current Study | 2.13 | (598.00, 598.00) | 31709.1598 | 1.4887 | 2130000 | 0.012285
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 23216.8164 | 1.0493 | 2212500 | 0.032652
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 22840.242 | 1.6551 | 1380000 | 0.19645
GEN-2024-278 | 05 SOUTHWEST | TBD | NRIS | Add 16 MVAR switched shunt at UNDERWOOD 2 345 kV | Current Study |  |  | 22522.5971 | 0.42495 | 5300000 | 0.02524
GEN-2024-278 | 05 SOUTHWEST | TBD | NRIS | Add 0.09 MVAR switched shunt at GRAY CO3 115 kV | Current Study |  |  | 21631.4538 | 0.97769 | 2212500 | 0.013432
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add 0.5 MVAR switched shunt at RKY_RDG4 138 kV | Current Study |  |  | 20628.2082 | 0.84803 | 2432500 | 0.039786
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 17499.3983 | 0.79093 | 2212500 | 0.063808
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 15086.803 | 1.0932 | 1380000 | 0.0059188
GEN-2024-278 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 13594.2539 | 0.98509 | 1380000 | 0.047185
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 12408.7136 | 0.75204 | 1650000 | 0.063808
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 8632.469 | 0.39017 | 2212500 | 0.03066
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 5478.0584 | 0.39696 | 1380000 | 0.03066
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528184 SENDERO +3 115 528193 BLACKRIVER 3 115 1 | Current Study | 0.25 | (598.00, 598.00) | 3721.7324 | 1.4887 | 250000 | 0.012285
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add 0.7 MVAR switched shunt at GEN-2024-161 138 kV | Current Study |  |  | 1812.2827 | 0.074503 | 2432500 | 0.00026758
GEN-2024-278 | 05 SOUTHWEST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-161-TAP 138 kV | Current Study |  |  | 796.045 | 0.032725 | 2432500 | 0.00026758
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 43802674.9564 | 2.892 | 1514620000 | 0.050819
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 43393854.6103 | 4.0413 | 1073760000 | 0.19779
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 38504096.5413 | 2.9961 | 1285130000 | 0.26977
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 38408772.8483 | 3.0204 | 1271630000 | 0.17773
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 20717330.1053 | 2.2077 | 938400000 | 0.10701
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 19467063.6938 | 2.686 | 724760000 | 0.18205
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 18653221.9641 | 1.9878 | 938400000 | 0.17052
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 14004763.1129 | 2.9005 | 482840000 | 0.21061
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 13801814.9373 | 2.9407 | 469340000 | 0.1435
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 8748433.2152 | 2.387 | 366500000 | 0.044827
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526460 AMOCO_SS 6 230 777420 G24-015-TAP 230 1 | Current Study | 25.97 | (519.00, 519.00) | 3100798.9797 | 6.2842 | 49343000 | 0.040938
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 2849716.4242 | 3.3724 | 84500000 | 0.059168
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 2269671.1768 | 2.686 | 84500000 | 0.18205
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 2236123.9663 | 2.6463 | 84500000 | 0.096126
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 2221226.2159 | 1.1226 | 197860000 | 0.031704
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 2146961.3531 | 1.72 | 124824000 | 0.064301
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 2028304.2906 | 1.0218 | 198511000 | 0.03121
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 1715494.9598 | 6.4736 | 26500000 | 0.058138
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 1595534.9157 | 0.96663 | 165062000 | 0.034754
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 1485667.909 | 1.8232 | 81488000 | 0.069175
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 1357862.4786 | 2.459 | 55220000 | 0.068538
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 1140266.58 | 2.623 | 43472000 | 0.045681
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528016 SAND_DUNES 3 115 528018 RED_BLUFF 3 115 1 | Current Study | 7.69 | (394.00, 394.00) | 791789.1011 | 10.2963 | 7690000 | 0.031356
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528018 RED_BLUFF 3 115 528235 WOLFCAMP_TP3 115 1 | Current Study | 7.81 | (598.00, 598.00) | 655754.2476 | 8.3963 | 7810000 | 0.064325
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 652002.1743 | 3.5054 | 18600000 | 0.26612
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 561552.4094 | 3.0191 | 18600000 | 0.17773
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 556927.0897 | 2.9942 | 18600000 | 0.26977
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 553757.4734 | 2.9772 | 18600000 | 0.17773
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 546967.5669 | 2.9407 | 18600000 | 0.1435
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 537910.3367 | 2.892 | 18600000 | 0.050819
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 499596.259 | 2.686 | 18600000 | 0.18205
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 475664.0883 | 2.5573 | 18600000 | 0.28137
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | Current Study | 0.78 | (598.00, 598.00) | 410186.7002 | 7.7511 | 5292000 | 0.062565
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 347586.4781 | 1.8687 | 18600000 | 0.10701
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | Current Study | 0.2 | (598.00, 598.00) | 347248.0001 | 7.7511 | 4480000 | 0.062565
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 337866.0213 | 1.8165 | 18600000 | 0.18205
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 337866.0213 | 1.8165 | 18600000 | 0.18205
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 335293.8844 | 1.3412 | 25000000 | 0.011329
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 335293.8844 | 1.3412 | 25000000 | 0.013
GEN-2024-280 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 228373.7399 | 1.2617 | 18100000 | 0.011046
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 157431.7846 | 0.97228 | 16192000 | 0.062295
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 146850.6672 | 0.98307 | 14938000 | 0.059833
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 142160.9732 | 0.98307 | 14460953.1406 | 0.059833
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 124514.1504 | 2.3493 | 5300000 | 0.19225
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 113860.1415 | 1.7367 | 6556000 | 0.068538
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 47651.7848 | 3.453 | 1380000 | 0.17482
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 45605.0784 | 0.38004 | 12000000 | 0.030213
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 44513.2036 | 3.2256 | 1380000 | 0.19225
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 30497.4048 | 1.3784 | 2212500 | 0.032389
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 29599.7433 | 2.1449 | 1380000 | 0.19225
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 528184 SENDERO +3 115 528187 SENDERO_345 345 M2 | Current Study |  | (435.00, 435.00) | 29063.5133 | 0.173 | 16800000 | 0.00039084
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1 | Current Study | 2.13 | (598.00, 598.00) | 25666.9947 | 1.205 | 2130000 | 0.0075093
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 22624.1481 | 1.0226 | 2212500 | 0.062295
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 19235.5436 | 1.3939 | 1380000 | 0.0056986
GEN-2024-280 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 17106.7777 | 1.2396 | 1380000 | 0.044838
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 16042.6411 | 0.97228 | 1650000 | 0.062295
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 11264.9199 | 0.50915 | 2212500 | 0.030213
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 7148.5792 | 0.51801 | 1380000 | 0.030213
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528184 SENDERO +3 115 528193 BLACKRIVER 3 115 1 | Current Study | 0.25 | (598.00, 598.00) | 3012.5581 | 1.205 | 250000 | 0.0075093
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 31855562.1503 | 2.9667 | 1073760000 | 0.20328
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 31330872.5803 | 2.0686 | 1514620000 | 0.050889
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 27615935.6553 | 2.1489 | 1285130000 | 0.27088
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 27563326.3305 | 2.1676 | 1271630000 | 0.17856
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 14602482.2368 | 1.5561 | 938400000 | 0.1056
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 13895647.1669 | 1.9173 | 724760000 | 0.18193
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 13167542.074 | 1.4032 | 938400000 | 0.16852
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 10028129.8403 | 2.0769 | 482840000 | 0.21113
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528547 S_JAL 3 115 785400 G24-281-TAP 115 1 | Current Study | 10.82 | (260.00, 260.00) | 9939732.9618 | 91.8644 | 10820000 | 0.45731
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 9890292.8251 | 2.1073 | 469340000 | 0.14396
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1 | Current Study | 6.81 | (260.00, 260.00) | 6810000 | 100 | 6810000 | 0.54269
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 6053119.8198 | 1.6516 | 366500000 | 0.043423
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | Current Study | 2.6 | (260.00, 260.00) | 2600000 | 100 | 2600000 | 0.54269
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526460 AMOCO_SS 6 230 777420 G24-015-TAP 230 1 | Current Study | 25.97 | (519.00, 519.00) | 2143778.904 | 4.3446 | 49343000 | 0.039624
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 2055736.7865 | 2.4328 | 84500000 | 0.059756
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1620097.9436 | 1.9173 | 84500000 | 0.18193
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 1593839.2936 | 1.8862 | 84500000 | 0.095922
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 1583260.4931 | 5.9746 | 26500000 | 0.075119
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 1582070.3153 | 0.79959 | 197860000 | 0.031614
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1531781.7735 | 1.2272 | 124824000 | 0.064227
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1447060.5553 | 0.72896 | 198511000 | 0.031173
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 1136470.2955 | 0.68851 | 165062000 | 0.034656
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 1059883.0542 | 1.3007 | 81488000 | 0.06909
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 917088.2012 | 1.6608 | 55220000 | 0.064806
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 812020.3045 | 1.8679 | 43472000 | 0.045543
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 464623.4037 | 2.498 | 18600000 | 0.2655
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528018 RED_BLUFF 3 115 528235 WOLFCAMP_TP3 115 1 | Current Study | 7.81 | (598.00, 598.00) | 457357.8449 | 5.8561 | 7810000 | 0.06281
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528016 SAND_DUNES 3 115 528018 RED_BLUFF 3 115 1 | Current Study | 7.69 | (394.00, 394.00) | 454438.1748 | 5.9095 | 7690000 | 0.025195
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 402987.4209 | 2.1666 | 18600000 | 0.17856
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 399439.6455 | 2.1475 | 18600000 | 0.27088
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | Current Study | 0.78 | (598.00, 598.00) | 398123.6742 | 7.5231 | 5292000 | 0.085015
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 397393.5332 | 2.1365 | 18600000 | 0.17856
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 391953.4805 | 2.1073 | 18600000 | 0.14396
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 384752.7631 | 2.0686 | 18600000 | 0.050889
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 356613.2752 | 1.9173 | 18600000 | 0.18193
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 338834.9493 | 1.8217 | 18600000 | 0.2806
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | Current Study | 0.2 | (598.00, 598.00) | 337035.9146 | 7.5231 | 4480000 | 0.085015
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 244994.1835 | 1.3172 | 18600000 | 0.1056
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 241169.7571 | 1.2966 | 18600000 | 0.18193
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 241169.7571 | 1.2966 | 18600000 | 0.18193
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 228318.4214 | 0.91327 | 25000000 | 0.0108
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 228318.4214 | 0.91327 | 25000000 | 0.012393
GEN-2024-281 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 163505.9065 | 0.90335 | 18100000 | 0.011072
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 112117.5635 | 0.69243 | 16192000 | 0.06211
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 104768.3681 | 0.70135 | 14938000 | 0.059762
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 101422.5774 | 0.70135 | 14460953.1406 | 0.059762
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 88749.7955 | 1.6745 | 5300000 | 0.19184
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 76900.1235 | 1.173 | 6556000 | 0.064806
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 34205.6438 | 2.4787 | 1380000 | 0.17569
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 32516.519 | 0.27097 | 12000000 | 0.030159
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 31727.6206 | 2.2991 | 1380000 | 0.19184
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 21762.9999 | 0.98364 | 2212500 | 0.032358
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 21097.7721 | 1.5288 | 1380000 | 0.19184
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1 | Current Study | 2.13 | (598.00, 598.00) | 18417.0412 | 0.86465 | 2130000 | 0.0075435
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 16112.149 | 0.72823 | 2212500 | 0.06211
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 13643.764 | 0.98868 | 1380000 | 0.0056588
GEN-2024-281 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 12128.7017 | 0.87889 | 1380000 | 0.044506
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 11425.0235 | 0.69243 | 1650000 | 0.06211
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 8031.9121 | 0.36302 | 2212500 | 0.030159
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 528184 SENDERO +3 115 528187 SENDERO_345 345 M2 | Current Study |  | (435.00, 435.00) | 5813.0694 | 0.034602 | 16800000 | 0.00010944
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 5096.9524 | 0.36934 | 1380000 | 0.030159
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528184 SENDERO +3 115 528193 BLACKRIVER 3 115 1 | Current Study | 0.25 | (598.00, 598.00) | 2161.6246 | 0.86465 | 250000 | 0.0075435
GEN-2024-282 | 01 NORTH | TBD | NRIS | Rebuild line 652497 MAURINE4 230 785430 G24-282-TAP 230 1 | Current Study | 36.92 | (637.00, 637.00) | 32519481.5542 | 46.3584 | 70148000 | 0.45336
GEN-2024-282 | 01 NORTH | TBD | ERIS | Rebuild line 640404 WAYSIDE 4 230 652484 NUNDRWD4 230 1 | Current Study | 80.12 | (519.00, 519.00) | 21000473.367 | 13.7954 | 152228000 | 0.10556
GEN-2024-282 | 01 NORTH | TBD | ERIS | Rebuild line 652884 NUNDRWD-LNX3 230 785430 G24-282-TAP 230 1 | Current Study | 35.21 | (519.00, 519.00) | 18969630.7693 | 28.3556 | 66899000 | 0.55178
GEN-2024-282 | 01 NORTH | TBD | NRIS | Rebuild line 652216 WATFORD4 230 659302 CHARL_CK-BE4 230 1 | Current Study | 34.26 | (637.00, 637.00) | 11155480.1762 | 17.1375 | 65094000 | 0.013507
GEN-2024-282 | 01 NORTH | TBD | NRIS | Rebuild line 652424 BELFELD3 345 659183 CHARL_CK-BE3 345 1 | Current Study | 40.74 | (1793.00, 1793.00) | 10106128.8384 | 11.2756 | 89628000 | 0.15286
GEN-2024-282 | 01 NORTH | TBD | ERIS | Rebuild line 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Current Study | 36.8 | (1793.00, 1793.00) | 3613719.1886 | 4.4636 | 80960000 | 0.083321
GEN-2024-282 | 01 NORTH | TBD | NRIS | Add 0.6 MVAR switched shunt at BISON___-GE4 230 kV | Current Study |  |  | 1515445.6981 | 39.6195 | 3825000 | 0.10075
GEN-2024-282 | 01 NORTH | TBD | ERIS | Rebuild line 652529 WATERTN3 345 659165 CROCKER_-BE3 345 1 | Current Study | 44.23 | (1793.00, 1793.00) | 1348357.6465 | 1.3857 | 97306000 | 0.044299
GEN-2024-282 | 01 NORTH | TBD | ERIS | Add 24 MVAR switched shunt at DH_CS_EA-TS4 230 kV | Current Study |  |  | 732218.4119 | 19.143 | 3825000 | 0.072534
GEN-2024-282 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 659120 BROADLND-BE3 345 659204 BD.KU2A_-BE9 13 659205 BROADLND-BE4 230 M2 | Current Study |  | (471.00, 478.00) | 518048.3795 | 2.0722 | 25000000 | 0.023413
GEN-2024-282 | 01 NORTH | TBD | ERIS | Add 60 MVAR switched shunt at WAYSIDE 4 230 kV | Current Study |  |  | 267762.584 | 7.0003 | 3825000 | 0.15039
GEN-2024-282 | 01 NORTH | TBD | ERIS | Add 24 MVAR switched shunt at DAYTON__-ER7 115 kV | Current Study |  |  | 98756.9011 | 4.4636 | 2212500 | 0.083321
GEN-2024-282 | 01 NORTH | TBD | ERIS | Add 0.4 MVAR switched shunt at SHINDLER-ER7 115 kV | Current Study |  |  | 95428.3532 | 4.3131 | 2212500 | 0.08855
GEN-2024-282 | 01 NORTH | TBD | ERIS | Add 4.4 MVAR switched shunt at DESMET-ER7 115 kV | Current Study |  |  | 87021.1805 | 3.9332 | 2212500 | 0.15039
GEN-2024-282 | 01 NORTH | TBD | ERIS | Rebuild line 652484 NUNDRWD4 230 652884 NUNDRWD-LNX3 230 Z | Current Study | 0.14514 | (519.00, 519.00) | 78195.0746 | 28.3556 | 275765.6361 | 0.55178
GEN-2024-282 | 01 NORTH | TBD | ERIS | Add 14.4 MVAR switched shunt at SW145-ER8 69 kV | Current Study |  |  | 61597.5247 | 4.4636 | 1380000 | 0.083321
GEN-2024-282 | 01 NORTH | TBD | ERIS | Add 0.5 MVAR switched shunt at ORLAND-ER8 69 kV | Current Study |  |  | 61597.5247 | 4.4636 | 1380000 | 0.083321
GEN-2024-282 | 01 NORTH | TBD | ERIS | Add 5.5 MVAR switched shunt at LOOMIS-ER8 69 kV | Current Study |  |  | 53091.8299 | 3.8472 | 1380000 | 0.15039
GEN-2024-282 | 01 NORTH | TBD | ERIS | Add 10 MVAR switched shunt at REDFIELD 115 kV | Current Study |  |  | 30658.3543 | 1.3857 | 2212500 | 0.044299
GEN-2024-282 | 01 NORTH | TBD | ERIS | Add 54 MVAR switched shunt at REDFELD-ER7 115 kV | Current Study |  |  | 30658.3543 | 1.3857 | 2212500 | 0.044299
GEN-2024-282 | 01 NORTH | TBD | ERIS | Add 4 MVAR switched shunt at MOS-RDFL-ER8 69 kV | Current Study |  |  | 19122.4989 | 1.3857 | 1380000 | 0.044299
GEN-2024-282 | 01 NORTH | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 9923.1219 | 0.71907 | 1380000 | 0.15039
GEN-2024-282 | 01 NORTH | TBD | ERIS | Rebuild line 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Current Study | 0 | (880.00, 880.00) | 9819.8891 | 4.4636 | 220000 | 0.083321
GEN-2024-283 | 01 NORTH | TBD | NRIS | Rebuild line 652497 MAURINE4 230 785430 G24-282-TAP 230 1 | Current Study | 36.92 | (637.00, 637.00) | 32519481.5542 | 46.3584 | 70148000 | 0.45336
GEN-2024-283 | 01 NORTH | TBD | ERIS | Rebuild line 640404 WAYSIDE 4 230 652484 NUNDRWD4 230 1 | Current Study | 80.12 | (519.00, 519.00) | 21000473.367 | 13.7954 | 152228000 | 0.10556
GEN-2024-283 | 01 NORTH | TBD | ERIS | Rebuild line 652884 NUNDRWD-LNX3 230 785430 G24-282-TAP 230 1 | Current Study | 35.21 | (519.00, 519.00) | 18969630.7693 | 28.3556 | 66899000 | 0.55178
GEN-2024-283 | 01 NORTH | TBD | NRIS | Rebuild line 652216 WATFORD4 230 659302 CHARL_CK-BE4 230 1 | Current Study | 34.26 | (637.00, 637.00) | 11155480.1762 | 17.1375 | 65094000 | 0.013507
GEN-2024-283 | 01 NORTH | TBD | NRIS | Rebuild line 652424 BELFELD3 345 659183 CHARL_CK-BE3 345 1 | Current Study | 40.74 | (1793.00, 1793.00) | 10106128.8384 | 11.2756 | 89628000 | 0.15286
GEN-2024-283 | 01 NORTH | TBD | ERIS | Rebuild line 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Current Study | 36.8 | (1793.00, 1793.00) | 3613719.1886 | 4.4636 | 80960000 | 0.083321
GEN-2024-283 | 01 NORTH | TBD | NRIS | Add 0.6 MVAR switched shunt at BISON___-GE4 230 kV | Current Study |  |  | 1515445.6981 | 39.6195 | 3825000 | 0.10075
GEN-2024-283 | 01 NORTH | TBD | ERIS | Rebuild line 652529 WATERTN3 345 659165 CROCKER_-BE3 345 1 | Current Study | 44.23 | (1793.00, 1793.00) | 1348357.6465 | 1.3857 | 97306000 | 0.044299
GEN-2024-283 | 01 NORTH | TBD | ERIS | Add 24 MVAR switched shunt at DH_CS_EA-TS4 230 kV | Current Study |  |  | 732218.4119 | 19.143 | 3825000 | 0.072534
GEN-2024-283 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 659120 BROADLND-BE3 345 659204 BD.KU2A_-BE9 13 659205 BROADLND-BE4 230 M2 | Current Study |  | (471.00, 478.00) | 518048.3795 | 2.0722 | 25000000 | 0.023413
GEN-2024-283 | 01 NORTH | TBD | ERIS | Add 60 MVAR switched shunt at WAYSIDE 4 230 kV | Current Study |  |  | 267762.584 | 7.0003 | 3825000 | 0.15039
GEN-2024-283 | 01 NORTH | TBD | ERIS | Add 24 MVAR switched shunt at DAYTON__-ER7 115 kV | Current Study |  |  | 98756.9011 | 4.4636 | 2212500 | 0.083321
GEN-2024-283 | 01 NORTH | TBD | ERIS | Add 0.4 MVAR switched shunt at SHINDLER-ER7 115 kV | Current Study |  |  | 95428.3532 | 4.3131 | 2212500 | 0.08855
GEN-2024-283 | 01 NORTH | TBD | ERIS | Add 4.4 MVAR switched shunt at DESMET-ER7 115 kV | Current Study |  |  | 87021.1805 | 3.9332 | 2212500 | 0.15039
GEN-2024-283 | 01 NORTH | TBD | ERIS | Rebuild line 652484 NUNDRWD4 230 652884 NUNDRWD-LNX3 230 Z | Current Study | 0.14514 | (519.00, 519.00) | 78195.0746 | 28.3556 | 275765.6361 | 0.55178
GEN-2024-283 | 01 NORTH | TBD | ERIS | Add 14.4 MVAR switched shunt at SW145-ER8 69 kV | Current Study |  |  | 61597.5247 | 4.4636 | 1380000 | 0.083321
GEN-2024-283 | 01 NORTH | TBD | ERIS | Add 0.5 MVAR switched shunt at ORLAND-ER8 69 kV | Current Study |  |  | 61597.5247 | 4.4636 | 1380000 | 0.083321
GEN-2024-283 | 01 NORTH | TBD | ERIS | Add 5.5 MVAR switched shunt at LOOMIS-ER8 69 kV | Current Study |  |  | 53091.8299 | 3.8472 | 1380000 | 0.15039
GEN-2024-283 | 01 NORTH | TBD | ERIS | Add 10 MVAR switched shunt at REDFIELD 115 kV | Current Study |  |  | 30658.3543 | 1.3857 | 2212500 | 0.044299
GEN-2024-283 | 01 NORTH | TBD | ERIS | Add 54 MVAR switched shunt at REDFELD-ER7 115 kV | Current Study |  |  | 30658.3543 | 1.3857 | 2212500 | 0.044299
GEN-2024-283 | 01 NORTH | TBD | ERIS | Add 4 MVAR switched shunt at MOS-RDFL-ER8 69 kV | Current Study |  |  | 19122.4989 | 1.3857 | 1380000 | 0.044299
GEN-2024-283 | 01 NORTH | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 9923.1219 | 0.71907 | 1380000 | 0.15039
GEN-2024-283 | 01 NORTH | TBD | ERIS | Rebuild line 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Current Study | 0 | (880.00, 880.00) | 9819.8891 | 4.4636 | 220000 | 0.083321
GEN-2024-284 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 659120 BROADLND-BE3 345 659204 BD.KU2A_-BE9 13 659205 BROADLND-BE4 230 M2 | Current Study |  | (471.00, 478.00) | 10736139.8025 | 42.9446 | 25000000 | 0.36573
GEN-2024-284 | 01 NORTH | TBD | ERIS | Rebuild line 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Current Study | 36.8 | (1793.00, 1793.00) | 7839591.2754 | 9.6833 | 80960000 | 0.13625
GEN-2024-284 | 01 NORTH | TBD | ERIS | Rebuild line 640404 WAYSIDE 4 230 652484 NUNDRWD4 230 1 | Current Study | 80.12 | (519.00, 519.00) | 6636210.9714 | 4.3594 | 152228000 | 0.025144
GEN-2024-284 | 01 NORTH | TBD | ERIS | Rebuild line 652529 WATERTN3 345 659165 CROCKER_-BE3 345 1 | Current Study | 44.23 | (1793.00, 1793.00) | 1080432.3235 | 1.1103 | 97306000 | 0.026756
GEN-2024-284 | 01 NORTH | TBD | ERIS | Rebuild line 652884 NUNDRWD-LNX3 230 785430 G24-282-TAP 230 1 | Current Study | 35.21 | (519.00, 519.00) | 772012.7925 | 1.154 | 66899000 | 0.016927
GEN-2024-284 | 01 NORTH | TBD | ERIS | Add 24 MVAR switched shunt at DAYTON__-ER7 115 kV | Current Study |  |  | 214242.917 | 9.6833 | 2212500 | 0.13625
GEN-2024-284 | 01 NORTH | TBD | ERIS | Add 0.4 MVAR switched shunt at SHINDLER-ER7 115 kV | Current Study |  |  | 202272.8305 | 9.1423 | 2212500 | 0.14148
GEN-2024-284 | 01 NORTH | TBD | NRIS | Rebuild line 652515 HURON 7 115 660009 HUR B TAP 115 1 | Current Study | 0.2 | (176.00, 176.00) | 200000 | 100 | 200000 | 0.043069
GEN-2024-284 | 01 NORTH | TBD | ERIS | Add 14.4 MVAR switched shunt at SW145-ER8 69 kV | Current Study |  |  | 133629.4804 | 9.6833 | 1380000 | 0.13625
GEN-2024-284 | 01 NORTH | TBD | ERIS | Add 0.5 MVAR switched shunt at ORLAND-ER8 69 kV | Current Study |  |  | 133629.4804 | 9.6833 | 1380000 | 0.13625
GEN-2024-284 | 01 NORTH | TBD | ERIS | Add 60 MVAR switched shunt at WAYSIDE 4 230 kV | Current Study |  |  | 111602.3044 | 2.9177 | 3825000 | 0.047246
GEN-2024-284 | 01 NORTH | TBD | ERIS | Add 4.4 MVAR switched shunt at DESMET-ER7 115 kV | Current Study |  |  | 104595.3642 | 4.7275 | 2212500 | 0.13625
GEN-2024-284 | 01 NORTH | TBD | ERIS | Add 5.5 MVAR switched shunt at LOOMIS-ER8 69 kV | Current Study |  |  | 66263.0724 | 4.8017 | 1380000 | 0.14148
GEN-2024-284 | 01 NORTH | TBD | ERIS | Add 10 MVAR switched shunt at REDFIELD 115 kV | Current Study |  |  | 24566.3879 | 1.1103 | 2212500 | 0.026756
GEN-2024-284 | 01 NORTH | TBD | ERIS | Add 54 MVAR switched shunt at REDFELD-ER7 115 kV | Current Study |  |  | 24566.3879 | 1.1103 | 2212500 | 0.026756
GEN-2024-284 | 01 NORTH | TBD | ERIS | Rebuild line 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Current Study | 0 | (880.00, 880.00) | 21303.2372 | 9.6833 | 220000 | 0.13625
GEN-2024-284 | 01 NORTH | TBD | ERIS | Add 4 MVAR switched shunt at MOS-RDFL-ER8 69 kV | Current Study |  |  | 15322.764 | 1.1103 | 1380000 | 0.026756
GEN-2024-284 | 01 NORTH | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 5012.513 | 0.36323 | 1380000 | 0.05726
GEN-2024-284 | 01 NORTH | TBD | ERIS | Rebuild line 652484 NUNDRWD4 230 652884 NUNDRWD-LNX3 230 Z | Current Study | 0.14514 | (519.00, 519.00) | 3182.3286 | 1.154 | 275765.6361 | 0.016927
GEN-2024-285 | 01 NORTH | TBD | ERIS | Rebuild line 652529 WATERTN3 345 659165 CROCKER_-BE3 345 1 | Current Study | 44.23 | (1793.00, 1793.00) | 33013520.5631 | 33.9275 | 97306000 | 0.65078
GEN-2024-285 | 01 NORTH | TBD | ERIS | Rebuild line 652568 GROTONSOUTH7 115 655481 REDFELD-ER7 115 1 | Current Study | 42.57 | (176.00, 176.00) | 17100022.9688 | 40.1692 | 42570000 | 0.043856
GEN-2024-285 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 652237 WATERT19 13 652529 WATERTN3 345 652530 WATERTN4 230 M2 | Current Study |  | (400.00, 478.00) | 12686450.5105 | 50.7458 | 25000000 | 0.14569
GEN-2024-285 | 01 NORTH | TBD | ERIS | Rebuild line 652515 HURON 7 115 655481 REDFELD-ER7 115 1 | Current Study | 30.85 | (176.00, 176.00) | 12356585.5136 | 40.0538 | 30850000 | 0.043576
GEN-2024-285 | 01 NORTH | TBD | ERIS | Rebuild line 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | Current Study | 32.97 | (217.00, 217.00) | 12214976.05 | 37.0488 | 32970000 | 0.035577
GEN-2024-285 | 01 NORTH | TBD | ERIS | Rebuild line 652512 GROTON 7 115 660001 ABR SIEBRCHT 115 1 | Current Study | 25.8 | (260.00, 260.00) | 10230826.3237 | 39.6544 | 25800000 | 0.055985
GEN-2024-285 | 01 NORTH | TBD | ERIS | Rebuild line 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | Current Study | 21.31 | (217.00, 217.00) | 7895090.6771 | 37.0488 | 21310000 | 0.035577
GEN-2024-285 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 659160 GROTON__-BE3 345 659161 GRT.KU2A-BE9 13 659187 GROTON__-BE7 115 M2 | Current Study |  | (400.00, 400.00) | 5750274.2379 | 34.2278 | 16800000 | 0.087297
GEN-2024-285 | 01 NORTH | TBD | ERIS | Rebuild line 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Current Study | 36.8 | (1793.00, 1793.00) | 4823574.7651 | 5.958 | 80960000 | 0.06673
GEN-2024-285 | 01 NORTH | TBD | ERIS | Rebuild line 652522 SUMMIT-7 115 652531 WATERTN7 115 1 | Current Study | 30.78 | (176.00, 176.00) | 4545325.5223 | 14.7671 | 30780000 | 0.015098
GEN-2024-285 | 01 NORTH | TBD | ERIS | Add 34 MVAR switched shunt at OUTLAW_WF7 345 kV | Current Study |  |  | 1560828.2089 | 29.4496 | 5300000 | 0.030316
GEN-2024-285 | 01 NORTH | TBD | ERIS | Add line and rebuild line 652568 GROTONSOUTH7 115 659187 GROTON__-BE7 115 M2 | Current Study | 0.1 | (598.00, 598.00) | 1442930.956 | 33.2473 | 4340000 | 0.087297
GEN-2024-285 | 01 NORTH | TBD | ERIS | Add 10 MVAR switched shunt at REDFIELD 115 kV | Current Study |  |  | 750646.6408 | 33.9275 | 2212500 | 0.65078
GEN-2024-285 | 01 NORTH | TBD | ERIS | Add 54 MVAR switched shunt at REDFELD-ER7 115 kV | Current Study |  |  | 750646.6408 | 33.9275 | 2212500 | 0.65078
GEN-2024-285 | 01 NORTH | TBD | ERIS | Add 4.4 MVAR switched shunt at DESMET-ER7 115 kV | Current Study |  |  | 627627.3668 | 28.3673 | 2212500 | 0.65078
GEN-2024-285 | 01 NORTH | TBD | ERIS | Add 4 MVAR switched shunt at MOS-RDFL-ER8 69 kV | Current Study |  |  | 468199.9387 | 33.9275 | 1380000 | 0.65078
GEN-2024-285 | 01 NORTH | TBD | ERIS | Add 5.5 MVAR switched shunt at LOOMIS-ER8 69 kV | Current Study |  |  | 382916.9541 | 27.7476 | 1380000 | 0.65078
GEN-2024-285 | 01 NORTH | TBD | ERIS | Add 0.4 MVAR switched shunt at SHINDLER-ER7 115 kV | Current Study |  |  | 152518.3925 | 6.8935 | 2212500 | 0.084915
GEN-2024-285 | 01 NORTH | TBD | ERIS | Add 24 MVAR switched shunt at DAYTON__-ER7 115 kV | Current Study |  |  | 131820.0292 | 5.958 | 2212500 | 0.06673
GEN-2024-285 | 01 NORTH | TBD | ERIS | Add 60 MVAR switched shunt at WAYSIDE 4 230 kV | Current Study |  |  | 115793.8451 | 3.0273 | 3825000 | 0.039021
GEN-2024-285 | 01 NORTH | TBD | ERIS | Rebuild line 652512 GROTON 7 115 652568 GROTONSOUTH7 115 Z | Current Study | 0.25 | (598.00, 598.00) | 96498.9126 | 38.5996 | 250000 | 0.091561
GEN-2024-285 | 01 NORTH | TBD | ERIS | Add 0.5 MVAR switched shunt at ORLAND-ER8 69 kV | Current Study |  |  | 82219.9504 | 5.958 | 1380000 | 0.06673
GEN-2024-285 | 01 NORTH | TBD | ERIS | Add 14.4 MVAR switched shunt at SW145-ER8 69 kV | Current Study |  |  | 82219.9504 | 5.958 | 1380000 | 0.06673
GEN-2024-285 | 01 NORTH | TBD | NRIS | Add 16 MVAR switched shunt at UNDERWOOD 2 345 kV | Current Study |  |  | 33089.6843 | 0.62433 | 5300000 | 0.039204
GEN-2024-285 | 01 NORTH | TBD | ERIS | Add 0.9 MVAR switched shunt at GEN-2024-157 138 kV | Current Study |  |  | 30344.7179 | 1.2475 | 2432500 | 0.048669
GEN-2024-285 | 01 NORTH | TBD | ERIS | Rebuild line 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Current Study | 0 | (880.00, 880.00) | 13107.5401 | 5.958 | 220000 | 0.06673
GEN-2024-285 | 01 NORTH | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 5352.3353 | 0.38785 | 1380000 | 0.048669
GEN-2024-286 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1 | Current Study | 11.3 | (1793.00, 1793.00) | 326057.1023 | 1.3116 | 24860000 | 0.059493
GEN-2024-286 | 04 SOUTHEAST | TBD | ERIS | Add 10 MVAR switched shunt at G20-007-TAP 345 kV | Current Study |  |  | 48591.5779 | 0.91682 | 5300000 | 0.026439
GEN-2024-286 | 04 SOUTHEAST | TBD | ERIS | Add 38 MVAR switched shunt at FRNT2WD7 345 kV | Current Study |  |  | 46461.2055 | 0.87663 | 5300000 | 0.037955
GEN-2024-286 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 46165.3559 | 0.87104 | 5300000 | 0.13779
GEN-2024-286 | 04 SOUTHEAST | TBD | ERIS | Add 19 MVAR switched shunt at RANCHRD7 345 kV | Current Study |  |  | 42537.274 | 0.80259 | 5300000 | 0.037955
GEN-2024-287 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 2009901.2048 | 0.21418 | 938400000 | 0.032186
GEN-2024-287 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1515826.2033 | 1.6129 | 93984000 | 0.10018
GEN-2024-287 | 03 CENTRAL | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1221457.8546 | 0.55948 | 218320000 | 0.017281
GEN-2024-287 | 03 CENTRAL | TBD | ERIS | Rebuild line 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 | Current Study | 3.23 | (1793.00, 1793.00) | 791602.1937 | 11.1399 | 7106000 | 0.1257
GEN-2024-287 | 03 CENTRAL | TBD | ERIS | Rebuild line 645458 S3458 3 345 778170 G24-040-TAP 345 1 | Current Study | 13.15 | (1793.00, 1793.00) | 667483.2983 | 2.3072 | 28930000 | 0.035813
GEN-2024-287 | 03 CENTRAL | TBD | ERIS | Rebuild line 640139 COOPER 3 345 778170 G24-040-TAP 345 1 | Current Study | 12.59 | (1793.00, 1793.00) | 639058.154 | 2.3072 | 27698000 | 0.035813
GEN-2024-287 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 227647.9848 | 0.11468 | 198511000 | 0.0038802
GEN-2024-287 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 213247.556 | 4.0235 | 5300000 | 0.17126
GEN-2024-287 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 204831.483 | 1.7567 | 11660000 | 0.10018
GEN-2024-287 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 137764.5248 | 0.30005 | 45914000 | 0.015184
GEN-2024-287 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 75186.2931 | 0.30005 | 25058000 | 0.015184
GEN-2024-287 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 54378.3132 | 0.29236 | 18600000 | 0.051327
GEN-2024-287 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 54378.3132 | 0.29236 | 18600000 | 0.051327
GEN-2024-287 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 31060.8408 | 0.16699 | 18600000 | 0.032186
GEN-2024-287 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 6439.4478 | 0.39027 | 1650000 | 0.023682
GEN-2024-288 | 03 CENTRAL | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 11453817.3616 | 5.2463 | 218320000 | 0.24906
GEN-2024-288 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Current Study | 26.47 | (1793.00, 1793.00) | 4652804.696 | 7.9898 | 58234000 | 0.21047
GEN-2024-288 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 2027301.7721 | 1.4098 | 143796000 | 0.10833
GEN-2024-288 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 1610019.5669 | 0.81105 | 198511000 | 0.042176
GEN-2024-288 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | Current Study | 19.87 | (1793.00, 1793.00) | 1373058.5485 | 3.141 | 43714000 | 0.082523
GEN-2024-288 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 1342426.5093 | 0.14305 | 938400000 | 0.033039
GEN-2024-288 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | Current Study | 16.71 | (1793.00, 1793.00) | 1071098.0369 | 2.9136 | 36762000 | 0.12546
GEN-2024-288 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 570270.4899 | 0.28727 | 198511000 | 0.023625
GEN-2024-288 | 03 CENTRAL | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 390409.4011 | 0.73028 | 53460000 | 0.040554
GEN-2024-288 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | Current Study | 19.2 | (2390.00, 2390.00) | 282493.6799 | 0.66878 | 42240000 | 0.02629
GEN-2024-288 | 03 CENTRAL | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 261962.1691 | 0.15871 | 165062000 | 0.015362
GEN-2024-288 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 252370.5548 | 0.54966 | 45914000 | 0.042749
GEN-2024-288 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | Current Study | 16.04 | (2390.00, 2390.00) | 235999.9284 | 0.66878 | 35288000 | 0.02629
GEN-2024-288 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | Current Study | 13 | (2390.00, 2390.00) | 153857.7545 | 0.53796 | 28600000 | 0.02617
GEN-2024-288 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 137733.6185 | 0.54966 | 25058000 | 0.042749
GEN-2024-288 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 42286.0908 | 0.28308 | 14938000 | 0.046386
GEN-2024-288 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 41632.7703 | 0.78552 | 5300000 | 0.051388
GEN-2024-288 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 40935.6793 | 0.28308 | 14460953.1406 | 0.046386
GEN-2024-288 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 37792.7693 | 0.20319 | 18600000 | 0.054826
GEN-2024-288 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 37792.7693 | 0.20319 | 18600000 | 0.054826
GEN-2024-288 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 26613.4632 | 0.16436 | 16192000 | 0.028352
GEN-2024-288 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 20745.7441 | 0.11154 | 18600000 | 0.033039
GEN-2024-288 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 9358.8986 | 0.56721 | 1650000 | 0.0529
GEN-2024-288 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MED-LDG3 115 kV | Current Study |  |  | 6364.48 | 0.28766 | 2212500 | 0.015242
GEN-2024-288 | 03 CENTRAL | TBD | ERIS | Add 0.8 MVAR switched shunt at HARBNGR7 345 kV | Current Study |  |  | 3533.5764 | 0.066671 | 5300000 | 0.010645
GEN-2024-288 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 2711.9698 | 0.16436 | 1650000 | 0.028352
GEN-2024-289 | 03 CENTRAL | TBD | ERIS | Rebuild line 541207 ARCHIE 5 161 785640 G24-289-TAP 161 1 | Current Study | 24.2 | (364.00, 364.00) | 36300000 | 100 | 36300000 | 0.38494
GEN-2024-289 | 03 CENTRAL | TBD | ERIS | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | Current Study | 11.77 | (446.00, 446.00) | 16033822.8107 | 90.8175 | 17655000 | 0.46844
GEN-2024-289 | 03 CENTRAL | TBD | ERIS | Rebuild line 761278 G17-108-TAP 161 785640 G24-289-TAP 161 1 | Current Study | 4.53 | (364.00, 364.00) | 6145494.0906 | 90.4414 | 6795000 | 0.61506
GEN-2024-289 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 3273986.2987 | 0.34889 | 938400000 | 0.029929
GEN-2024-289 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 1570113.8712 | 0.79095 | 198511000 | 0.015277
GEN-2024-289 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1481188.6166 | 1.576 | 93984000 | 0.055882
GEN-2024-289 | 03 CENTRAL | TBD | ERIS | Rebuild line 645458 S3458 3 345 778170 G24-040-TAP 345 1 | Current Study | 13.15 | (1793.00, 1793.00) | 1462636.6263 | 5.0558 | 28930000 | 0.044798
GEN-2024-289 | 03 CENTRAL | TBD | ERIS | Rebuild line 640139 COOPER 3 345 778170 G24-040-TAP 345 1 | Current Study | 12.59 | (1793.00, 1793.00) | 1400349.4392 | 5.0558 | 27698000 | 0.044798
GEN-2024-289 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 613003.1806 | 0.4263 | 143796000 | 0.012167
GEN-2024-289 | 03 CENTRAL | TBD | ERIS | Rebuild line 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 | Current Study | 3.23 | (1793.00, 1793.00) | 462015.1074 | 6.5018 | 7106000 | 0.041879
GEN-2024-289 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 332120.8066 | 0.72335 | 45914000 | 0.020896
GEN-2024-289 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 200150.9541 | 1.7166 | 11660000 | 0.055882
GEN-2024-289 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 181258.0732 | 0.72335 | 25058000 | 0.020896
GEN-2024-289 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 85138.0829 | 0.45773 | 18600000 | 0.045875
GEN-2024-289 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 85138.0829 | 0.45773 | 18600000 | 0.045875
GEN-2024-289 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 50595.9034 | 0.27202 | 18600000 | 0.029929
GEN-2024-289 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 14150.8862 | 0.85763 | 1650000 | 0.029709
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 6876412.8356 | 10.8718 | 63250000 | 0.47226
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 3839241.8611 | 3.4038 | 112794000 | 0.23193
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 1 | Current Study |  | (1868.00, 1868.00) | 2717797.393 | 4.4192 | 61500000 | 0.086107
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 2 | Current Study |  | (1868.00, 1868.00) | 2717797.393 | 4.4192 | 61500000 | 0.086107
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1 | Current Study | 56.1 | (1793.00, 1793.00) | 2267504.6217 | 1.8372 | 123420000 | 0.02108
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 1874121.8678 | 7.2997 | 25674000 | 0.20501
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 1685954.58 | 1.1221 | 150244000 | 0.020344
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 1516289.0269 | 1.686 | 89936000 | 0.015754
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 1334743.8812 | 7.4533 | 17908000 | 0.21279
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at GEN-2024-157 138 kV | Current Study |  |  | 1297876.6462 | 53.3557 | 2432500 | 0.032093
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1218948.8868 | 1.2138 | 100427000 | 0.012471
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1194748.3562 | 0.54725 | 218320000 | 0.013509
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 1109739.5881 | 1.6814 | 66000000 | 0.030918
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 1086888.0114 | 2.4241 | 44836000 | 0.045529
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 965580.0803 | 0.67149 | 143796000 | 0.026831
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 916901.1085 | 0.96031 | 95480000 | 0.031068
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 813380.0156 | 0.96031 | 84700000 | 0.031068
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 785235.3688 | 0.39556 | 198511000 | 0.016916
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1 | Current Study | 11.3 | (1793.00, 1793.00) | 776143.567 | 3.1221 | 24860000 | 0.077039
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 722891.5217 | 1.2993 | 55638000 | 0.023443
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 702361.4288 | 0.59887 | 117282000 | 0.010082
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 776060 G23-204-TAP 345 1 | Current Study | 17.82 | (1793.00, 1793.00) | 633150.7676 | 1.615 | 39204000 | 0.048669
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 631115.3012 | 0.38235 | 165062000 | 0.019246
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 599314.0204 | 0.63768 | 93984000 | 0.031655
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 584520.2908 | 1.74 | 33594000 | 0.056797
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 414886.2292 | 1.5847 | 26180000 | 0.014325
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 364255.4634 | 0.29182 | 124824000 | 0.015273
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 301208.3073 | 0.54612 | 55154000 | 0.0077045
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 293625.958 | 1.1606 | 25300000 | 0.019017
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 284034.6729 | 2.367 | 12000000 | 0.028165
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 263367.8025 | 0.56045 | 46992000 | 0.018159
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | Current Study | 8.91 | (2390.00, 2390.00) | 256367.6684 | 1.3079 | 19602000 | 0.036153
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | Current Study | 6.93 | (1793.00, 1793.00) | 246225.2985 | 1.615 | 15246000 | 0.048669
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 245676.7465 | 0.30149 | 81488000 | 0.016015
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 221360.9673 | 1.8447 | 12000000 | 0.034777
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 68 MVAR SVC at TONTITN7 345 kV | Current Study |  |  | 201663.9413 | 1.6805 | 12000000 | 0.0091716
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 190976.9021 | 1.5915 | 12000000 | 0.034777
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 180644.8409 | 1.2001 | 15053000 | 0.012698
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 175006.4767 | 1.4584 | 12000000 | 0.015754
GEN-2024-291 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 172985.7905 | 3.2639 | 5300000 | 0.44582
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | Current Study | 5.97 | (2390.00, 2390.00) | 171774.9697 | 1.3079 | 13134000 | 0.036153
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 157551.6319 | 1.3129 | 12000000 | 0.035427
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 148377.1797 | 1.2365 | 12000000 | 0.034777
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 145127.3692 | 1.2094 | 12000000 | 0.032988
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 144176.2939 | 0.54612 | 26400000 | 0.0077045
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 144096.7535 | 1.2008 | 12000000 | 0.035427
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 142181.524 | 1.1848 | 12000000 | 0.031068
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 142181.524 | 1.1848 | 12000000 | 0.031068
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 140574.4494 | 2.1299 | 6600000 | 0.035427
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 136614.344 | 1.1385 | 12000000 | 0.022683
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 120429.3492 | 1.0036 | 12000000 | 0.040849
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 114425.5014 | 2.159 | 5300000 | 0.028165
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 113552.2823 | 0.24732 | 45914000 | 0.010002
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 112289.2142 | 0.93574 | 12000000 | 0.032988
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 110432.1796 | 0.92027 | 12000000 | 0.035427
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 103914.3776 | 0.86595 | 12000000 | 0.023443
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 103795.6375 | 1.9584 | 5300000 | 0.041041
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 96981.4015 | 0.80818 | 12000000 | 0.022345
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 94358.0468 | 0.78632 | 12000000 | 0.022052
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 84303.6661 | 1.2773 | 6600000 | 0.035427
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 83071.1042 | 0.69226 | 12000000 | 0.023443
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 82604.6073 | 1.2516 | 6600000 | 0.032988
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 82604.6073 | 1.2516 | 6600000 | 0.032988
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 81891.2079 | 1.5451 | 5300000 | 0.031068
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 80993.2683 | 1.5282 | 5300000 | 0.034777
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 80984.4686 | 0.69455 | 11660000 | 0.031655
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 78748.945 | 0.6392 | 12320000 | 0.010972
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 75606.0733 | 0.14143 | 53460000 | 0.0040839
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 74122.0782 | 0.61768 | 12000000 | 0.010972
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 74122.0782 | 0.61768 | 12000000 | 0.010972
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 70416.3819 | 2.1667 | 3250000 | 0.032988
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 70416.3819 | 2.1667 | 3250000 | 0.032988
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 70393.8447 | 2.166 | 3250000 | 0.035427
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 70393.8447 | 2.166 | 3250000 | 0.035427
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 69001.9033 | 1.3019 | 5300000 | 0.032988
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 66131.5832 | 1.002 | 6600000 | 0.031655
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 62778.5175 | 0.38771 | 16192000 | 0.034777
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 62763.5185 | 0.95096 | 6600000 | 0.031068
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 61972.2326 | 0.24732 | 25058000 | 0.010002
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 58382.9433 | 0.39084 | 14938000 | 0.033303
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 57236.0089 | 1.7611 | 3250000 | 0.032988
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 56518.4769 | 0.39084 | 14460953.1406 | 0.033303
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 53672.5512 | 1.0127 | 5300000 | 0.023443
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 51182.2924 | 1.5748 | 3250000 | 0.032988
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 44381.0897 | 0.83738 | 5300000 | 0.031655
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 43833.9157 | 1.3487 | 3250000 | 0.032988
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 43597.4104 | 0.82259 | 5300000 | 0.035427
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 43447.2486 | 1.3368 | 3250000 | 0.032988
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 43444.5582 | 1.3368 | 3250000 | 0.032988
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 42923.0484 | 0.80987 | 5300000 | 0.031068
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 42604.5838 | 1.3109 | 3250000 | 0.035427
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 42312.4879 | 1.3019 | 3250000 | 0.032988
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 41496.7786 | 1.2768 | 3250000 | 0.035427
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 36399.2983 | 1.12 | 3250000 | 0.032988
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 33802.8058 | 0.96031 | 3520000 | 0.031068
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 32663.9874 | 2.367 | 1380000 | 0.028165
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 31904.0256 | 0.98166 | 3250000 | 0.035427
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 31209.9744 | 0.96031 | 3250000 | 0.031068
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 29584.2746 | 0.91029 | 3250000 | 0.032988
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at SLKHILLS 4 138 kV | Current Study |  |  | 29239.4456 | 1.202 | 2432500 | 0.036153
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 28437.5446 | 0.53656 | 5300000 | 0.0031908
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 26714.1287 | 1.9358 | 1380000 | 0.035427
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 24015.2455 | 1.7402 | 1380000 | 0.032988
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 22663.1627 | 0.93168 | 2432500 | 0.033805
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 22452.5273 | 0.9762 | 2300000 | 0.055041
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 21358.0156 | 0.87803 | 2432500 | 0.031655
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 21061.9268 | 0.86586 | 2432500 | 0.031655
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 19757.5317 | 1.4317 | 1380000 | 0.032988
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 18797.2023 | 0.84959 | 2212500 | 0.035427
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 16645.437 | 0.56045 | 2970000 | 0.018159
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 15269.247 | 1.1065 | 1380000 | 0.030918
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 13924.2068 | 1.009 | 1380000 | 0.031655
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 12329.9533 | 0.56045 | 2200000 | 0.018159
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 12014.6912 | 0.54612 | 2200000 | 0.0077045
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 10845.066 | 0.20462 | 5300000 | 0.023443
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 9544.9042 | 0.18009 | 5300000 | 0.004432
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 9021.7403 | 0.40776 | 2212500 | 0.034777
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 8045.7405 | 0.36365 | 2212500 | 0.014702
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 7905.0245 | 0.59887 | 1320000 | 0.010082
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 6397.2674 | 0.38771 | 1650000 | 0.034777
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 2474.6099 | 0.10173 | 2432500 | 0.0016805
GEN-2024-291 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 259.4739 | 0.018802 | 1380000 | 0.00073278
GEN-2024-293 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 610970.633 | 11.5277 | 5300000 | 1
GEN-2024-293 | 04 SOUTHEAST | TBD | ERIS | Add 10 MVAR switched shunt at G20-007-TAP 345 kV | Current Study |  |  | 115550.2803 | 2.1802 | 5300000 | 0.034478
GEN-2024-293 | 04 SOUTHEAST | TBD | ERIS | Add 38 MVAR switched shunt at FRNT2WD7 345 kV | Current Study |  |  | 109454.4806 | 2.0652 | 5300000 | 0.049034
GEN-2024-293 | 04 SOUTHEAST | TBD | ERIS | Add 19 MVAR switched shunt at RANCHRD7 345 kV | Current Study |  |  | 100210.3836 | 1.8908 | 5300000 | 0.049034
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Current Study | 11.41 | (395.00, 395.00) | 13489988.0141 | 98.5246 | 13692000 | 0.060158
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 9223535.4726 | 19.6279 | 46992000 | 0.31798
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 5396037.3978 | 4.6009 | 117282000 | 0.038727
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 4804946.8898 | 3.1981 | 150244000 | 0.02899
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 68 MVAR SVC at TONTITN7 345 kV | Current Study |  |  | 4606140.9894 | 38.3845 | 12000000 | 0.10474
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 4262238.4208 | 4.7392 | 89936000 | 0.022143
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 4130378.8617 | 4.1128 | 100427000 | 0.021128
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 3946376.9549 | 4.1332 | 95480000 | 0.06686
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 38 MVAR SVC at WROGERS 5 161 kV | Current Study |  |  | 3700260.8584 | 56.0646 | 6600000 | 0.098994
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 3500818.2664 | 4.1332 | 84700000 | 0.06686
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 3443786.3307 | 5.2179 | 66000000 | 0.047972
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 3115891.0976 | 1.4272 | 218320000 | 0.017616
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 37 MVAR switched shunt at CHAMSPR7 345 kV | Current Study |  |  | 3044843.7302 | 57.4499 | 5300000 | 0.10474
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 2846252.2291 | 5.1157 | 55638000 | 0.046151
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR SVC at JAY 4 138 kV | Current Study |  |  | 2494585.0775 | 47.0676 | 5300000 | 0.10474
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 2440036.5038 | 1.6969 | 143796000 | 0.033901
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 2287689.0214 | 4.1478 | 55154000 | 0.029258
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509752 INOLATP4 138 510442 GUAVA 4 138 1 | Current Study | 1.63 | (395.00, 395.00) | 1927141.1449 | 98.5246 | 1956000 | 0.060158
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 1894471.2361 | 4.2253 | 44836000 | 0.039679
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1679866.7276 | 1.7874 | 93984000 | 0.044364
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 1547817.9147 | 4.6074 | 33594000 | 0.0752
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1517829.1275 | 0.76461 | 198511000 | 0.016349
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at LIN314 2 69 kV | Current Study |  |  | 1380000 | 100 | 1380000 | 0.00082616
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 1267575.5198 | 4.8418 | 26180000 | 0.021883
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at CENTRTN5 161 kV | Current Study |  |  | 1257100.0721 | 38.68 | 3250000 | 0.098994
GEN-2024-294 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 1212808.1042 | 6.7006 | 18100000 | 0.041062
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1168069.5736 | 0.93577 | 124824000 | 0.024488
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 1120607.681 | 0.6789 | 165062000 | 0.017086
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 1095024.6612 | 4.1478 | 26400000 | 0.029258
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 991138.6053 | 3.9175 | 25300000 | 0.032097
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 904197.6803 | 1.9693 | 45914000 | 0.039822
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 872401.1065 | 7.27 | 12000000 | 0.09915
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 4.8 MVAR switched shunt at COWSKIN2 69 kV | Current Study |  |  | 778277.8331 | 56.3969 | 1380000 | 0.10474
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 675001.7951 | 5.625 | 12000000 | 0.09915
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 611245.0849 | 4.0606 | 15053000 | 0.021483
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 582948.1689 | 19.6279 | 2970000 | 0.31798
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 573815.5849 | 1.0734 | 53460000 | 0.015497
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 564476.2261 | 4.5818 | 12320000 | 0.039325
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 545218.9747 | 23.7052 | 2300000 | 1
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 531311.6534 | 4.4276 | 12000000 | 0.039325
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 531311.6534 | 4.4276 | 12000000 | 0.039325
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 500614.672 | 4.1718 | 12000000 | 0.039325
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 496559.3408 | 7.5236 | 6600000 | 0.09915
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 496559.3408 | 7.5236 | 6600000 | 0.09915
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 493474.4408 | 1.9693 | 25058000 | 0.039822
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 491940.784 | 4.0995 | 12000000 | 0.022143
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 473695.235 | 3.9475 | 12000000 | 0.039325
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 471878.1778 | 7.1497 | 6600000 | 0.09915
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 431813.4585 | 19.6279 | 2200000 | 0.31798
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 423292.5176 | 13.0244 | 3250000 | 0.09915
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 423292.5176 | 13.0244 | 3250000 | 0.09915
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 416822.6587 | 3.4735 | 12000000 | 0.066859
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 414789.6923 | 7.8262 | 5300000 | 0.09915
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 409139.6105 | 3.4095 | 12000000 | 0.04615
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 403273.6356 | 3.3606 | 12000000 | 0.046458
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 394224.8217 | 3.2852 | 12000000 | 0.066859
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 359935.7364 | 2.9995 | 12000000 | 0.039325
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 359935.7364 | 2.9995 | 12000000 | 0.039325
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 344452.5301 | 2.8704 | 12000000 | 0.038727
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 344061.618 | 10.5865 | 3250000 | 0.09915
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 335559.5797 | 2.7963 | 12000000 | 0.039325
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 327073.8853 | 2.7256 | 12000000 | 0.04615
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 319901.4812 | 2.6658 | 12000000 | 0.039325
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 307671.0394 | 9.4668 | 3250000 | 0.09915
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 287073.1108 | 2.3923 | 12000000 | 0.026138
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 270136.1499 | 4.093 | 6600000 | 0.066859
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 263497.8969 | 8.1076 | 3250000 | 0.09915
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 261173.5328 | 8.0361 | 3250000 | 0.09915
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 261157.36 | 8.0356 | 3250000 | 0.09915
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 254352.1698 | 7.8262 | 3250000 | 0.09915
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 244030.5091 | 4.6043 | 5300000 | 0.09915
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 238473.2986 | 7.3376 | 3250000 | 0.09915
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 237698.5882 | 1.9808 | 12000000 | 0.027776
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 232272.5113 | 7.1468 | 3250000 | 0.09915
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 226998.0505 | 1.9468 | 11660000 | 0.044364
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 218806.3376 | 6.7325 | 3250000 | 0.09915
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 216392.6098 | 4.0829 | 5300000 | 0.046458
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 211323.661 | 3.9872 | 5300000 | 0.04615
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 204156.6348 | 3.852 | 5300000 | 0.038727
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 195886.5924 | 3.696 | 5300000 | 0.038727
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 191089.6543 | 3.6055 | 5300000 | 0.044364
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 185365.9842 | 2.8086 | 6600000 | 0.044364
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 184742.1448 | 3.4857 | 5300000 | 0.066859
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 177839.3287 | 5.472 | 3250000 | 0.09915
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 145488.5513 | 4.1332 | 3520000 | 0.06686
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 144362.3407 | 10.461 | 1380000 | 0.09915
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 134328.7074 | 4.1332 | 3250000 | 0.066859
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 124399.6283 | 2.3472 | 5300000 | 0.044364
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 120420.7036 | 3.7053 | 3250000 | 0.066859
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 118768.035 | 8.6064 | 1380000 | 0.09915
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 114057.4147 | 4.6889 | 2432500 | 0.038727
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 113991.1203 | 0.76309 | 14938000 | 0.032511
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 111521.128 | 0.68874 | 16192000 | 0.03089
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 110350.7999 | 0.76309 | 14460953.1406 | 0.032511
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 95675.7993 | 1.8052 | 5300000 | 0.0053675
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 91252.0551 | 4.1478 | 2200000 | 0.029258
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 60731.991 | 4.6009 | 1320000 | 0.038727
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 59866.2454 | 2.4611 | 2432500 | 0.044364
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 59036.3121 | 2.427 | 2432500 | 0.044364
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 47384.9026 | 3.4337 | 1380000 | 0.047973
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 39029.374 | 2.8282 | 1380000 | 0.044364
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 36384.8977 | 0.68651 | 5300000 | 0.039325
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 11364.2454 | 0.68874 | 1650000 | 0.03089
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 17528944.0978 | 1.6325 | 1073760000 | 0.24316
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 14525857.2194 | 0.95904 | 1514620000 | 0.05129
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 13021493.0855 | 1.024 | 1271630000 | 0.18338
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 13001853.6707 | 1.0117 | 1285130000 | 0.27725
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 6375485.978 | 0.87967 | 724760000 | 0.18146
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 6239104.5379 | 0.66487 | 938400000 | 0.098083
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 5685217.0404 | 0.60584 | 938400000 | 0.15817
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 528184 SENDERO +3 115 528187 SENDERO_345 345 M2 | Current Study |  | (435.00, 435.00) | 4940952.0824 | 29.4104 | 16800000 | 0.20222
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 4677099.3589 | 0.96866 | 482840000 | 0.21406
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 4633325.4566 | 0.9872 | 469340000 | 0.14661
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 2151529.5991 | 0.58705 | 366500000 | 0.033553
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 1036707.7865 | 3.9121 | 26500000 | 0.10693
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 999905.2697 | 1.1833 | 84500000 | 0.063185
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528013 PHANTOM 3 115 528228 WOOD_DRAW 3 115 1 | Current Study | 7.71 | (260.00, 260.00) | 886802.1707 | 11.502 | 7710000 | 0.029226
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 743319.9475 | 0.87967 | 84500000 | 0.18146
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 725938.0999 | 0.8591 | 84500000 | 0.094976
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 715716.7321 | 0.36173 | 197860000 | 0.031091
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 700762.8151 | 0.5614 | 124824000 | 0.063875
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 661094.375 | 0.33303 | 198511000 | 0.03096
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 514294.1769 | 0.31158 | 165062000 | 0.034094
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1 | Current Study | 2.13 | (598.00, 598.00) | 496252.6751 | 23.2982 | 2130000 | 0.44187
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 484872.0258 | 0.59502 | 81488000 | 0.068711
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 367864.2261 | 0.84621 | 43472000 | 0.044852
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 228338.4673 | 0.41351 | 55220000 | 0.035077
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 219327.7026 | 1.1792 | 18600000 | 0.27246
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 190379.7043 | 1.0235 | 18600000 | 0.18338
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 188060.1072 | 1.0111 | 18600000 | 0.27725
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 187737.0344 | 1.0093 | 18600000 | 0.18338
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 183619.2387 | 0.9872 | 18600000 | 0.14661
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 178381.9996 | 0.95904 | 18600000 | 0.05129
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 163618.3553 | 0.87967 | 18600000 | 0.18146
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 158890.3557 | 0.85425 | 18600000 | 0.28605
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 110651.5145 | 0.5949 | 18600000 | 0.18146
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 110651.5145 | 0.5949 | 18600000 | 0.18146
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 104677.0198 | 0.56278 | 18600000 | 0.098083
GEN-2024-295 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 76132.9796 | 0.42062 | 18100000 | 0.011207
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528184 SENDERO +3 115 528193 BLACKRIVER 3 115 1 | Current Study | 0.25 | (598.00, 598.00) | 58245.6191 | 23.2982 | 250000 | 0.44187
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 52728.6656 | 2.3832 | 2212500 | 0.44187
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 50737.3106 | 0.31335 | 16192000 | 0.061102
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 47880.3096 | 0.32053 | 14938000 | 0.059374
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 46351.2461 | 0.32053 | 14460953.1406 | 0.059374
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 40422.4296 | 0.76269 | 5300000 | 0.18995
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528018 RED_BLUFF 3 115 528235 WOLFCAMP_TP3 115 1 | Current Study | 7.81 | (598.00, 598.00) | 28907.8282 | 0.37014 | 7810000 | 0.0086303
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 19146.7476 | 0.29205 | 6556000 | 0.035077
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 16157.0771 | 1.1708 | 1380000 | 0.18041
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 14812.0425 | 0.12343 | 12000000 | 0.029865
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 14450.8221 | 1.0472 | 1380000 | 0.18995
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 9960.4403 | 0.45019 | 2212500 | 0.032195
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | Current Study | 0.78 | (598.00, 598.00) | 9734.0716 | 0.18394 | 5292000 | 0.0045187
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 9609.2977 | 0.69633 | 1380000 | 0.18995
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | Current Study | 0.2 | (598.00, 598.00) | 8240.4839 | 0.18394 | 4480000 | 0.0045187
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 5983.5991 | 0.43359 | 1380000 | 0.0053951
GEN-2024-295 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 5345.0392 | 0.38732 | 1380000 | 0.042638
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 5170.2423 | 0.31335 | 1650000 | 0.061102
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 3658.7257 | 0.16537 | 2212500 | 0.029865
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 2321.7822 | 0.16825 | 1380000 | 0.029865
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 5491543.8252 | 8.6823 | 63250000 | 0.5646
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 1998714.4849 | 1.772 | 112794000 | 0.18076
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 1 | Current Study |  | (1868.00, 1868.00) | 1994951.6224 | 3.2438 | 61500000 | 0.094619
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 2 | Current Study |  | (1868.00, 1868.00) | 1994951.6224 | 3.2438 | 61500000 | 0.094619
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 1674207.9412 | 1.4275 | 117282000 | 0.035975
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 1620609.6035 | 1.0787 | 150244000 | 0.029274
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 1469542.6172 | 5.7239 | 25674000 | 0.24065
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 1143277.7205 | 1.2712 | 89936000 | 0.017783
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1088467.3395 | 1.14 | 95480000 | 0.055212
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1056449.1072 | 1.052 | 100427000 | 0.01618
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 1049654.1509 | 5.8614 | 17908000 | 0.2505
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 992587.6902 | 1.784 | 55638000 | 0.048187
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 990346.6535 | 0.45362 | 218320000 | 0.016763
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 972159.5402 | 1.473 | 66000000 | 0.040546
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 965575.8657 | 1.14 | 84700000 | 0.055212
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 815964.1709 | 0.56745 | 143796000 | 0.033942
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 752712.5271 | 1.3647 | 55154000 | 0.028822
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 698696.1459 | 1.5583 | 44836000 | 0.043814
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 631170.9426 | 0.67157 | 93984000 | 0.049907
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1 | Current Study | 11.3 | (1793.00, 1793.00) | 629308.3449 | 2.5314 | 24860000 | 0.09351
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 598443.6215 | 0.30147 | 198511000 | 0.019299
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 554808.4327 | 1.6515 | 33594000 | 0.080704
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 504100.5944 | 0.40385 | 124824000 | 0.031642
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 776060 G23-204-TAP 345 1 | Current Study | 17.82 | (1793.00, 1793.00) | 422825.1155 | 1.0785 | 39204000 | 0.048655
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 405335.4418 | 0.24557 | 165062000 | 0.018504
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 360293.1921 | 1.3647 | 26400000 | 0.028822
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 349841.7814 | 1.3363 | 26180000 | 0.018083
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 343021.8248 | 0.72996 | 46992000 | 0.035406
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 332196.8122 | 0.40766 | 81488000 | 0.032417
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 330646.9472 | 0.72014 | 45914000 | 0.043599
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 295797.8898 | 1.1692 | 25300000 | 0.02868
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 68 MVAR SVC at TONTITN7 345 kV | Current Study |  |  | 247404.7381 | 2.0617 | 12000000 | 0.016844
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 244779.291 | 2.0398 | 12000000 | 0.036335
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 185992.8777 | 0.34791 | 53460000 | 0.01504
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 180453.7005 | 0.72014 | 25058000 | 0.043599
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 175341.633 | 1.4232 | 12320000 | 0.036573
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 165039.8747 | 1.3753 | 12000000 | 0.036573
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 165039.8747 | 1.3753 | 12000000 | 0.036573
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | Current Study | 6.93 | (1793.00, 1793.00) | 164431.9894 | 1.0785 | 15246000 | 0.048655
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 157813.4069 | 1.3151 | 12000000 | 0.055212
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 156451.7133 | 1.0393 | 15053000 | 0.016463
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 147142.6454 | 1.2262 | 12000000 | 0.036573
GEN-2024-296 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 144146.9808 | 2.7198 | 5300000 | 0.55614
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 142681.7363 | 1.189 | 12000000 | 0.048187
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 133443.9288 | 1.112 | 12000000 | 0.049114
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 131955.4658 | 1.0996 | 12000000 | 0.017783
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 130182.0226 | 1.9725 | 6600000 | 0.049114
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 122907.3316 | 1.0242 | 12000000 | 0.041822
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 115615.8793 | 0.96347 | 12000000 | 0.058707
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 114965.7996 | 0.95805 | 12000000 | 0.055212
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 114138.1911 | 0.95115 | 12000000 | 0.026844
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 114062.4586 | 0.95052 | 12000000 | 0.048187
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 111805.8459 | 0.93172 | 12000000 | 0.036573
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 111805.8459 | 0.93172 | 12000000 | 0.036573
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 106872.011 | 0.8906 | 12000000 | 0.035975
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 106034.7956 | 0.88362 | 12000000 | 0.036573
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 104233.9475 | 0.86862 | 12000000 | 0.036573
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 98611.1759 | 1.8606 | 5300000 | 0.036335
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 98471.5526 | 0.8206 | 12000000 | 0.026844
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 95096.9329 | 0.79247 | 12000000 | 0.041822
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 85289.2501 | 0.73147 | 11660000 | 0.049907
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 78071.2414 | 1.1829 | 6600000 | 0.049114
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 74507.5101 | 1.1289 | 6600000 | 0.055212
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 73696.1812 | 1.3905 | 5300000 | 0.048187
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 71797.4669 | 1.3547 | 5300000 | 0.049907
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 69957.2514 | 1.06 | 6600000 | 0.041822
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 69957.2514 | 1.06 | 6600000 | 0.041822
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 69646.9318 | 1.0553 | 6600000 | 0.049907
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 65189.749 | 2.0058 | 3250000 | 0.049114
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 65189.749 | 2.0058 | 3250000 | 0.049114
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 63342.9231 | 1.1951 | 5300000 | 0.035975
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 60777.0077 | 1.1467 | 5300000 | 0.035975
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 59635.1305 | 1.8349 | 3250000 | 0.041822
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 59635.1305 | 1.8349 | 3250000 | 0.041822
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 58437.2187 | 1.1026 | 5300000 | 0.041822
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 54180.0626 | 1.0223 | 5300000 | 0.058707
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 48472.7668 | 1.4915 | 3250000 | 0.041822
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 46740.2499 | 0.88189 | 5300000 | 0.049907
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 44792.5283 | 0.29986 | 14938000 | 0.038249
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 43362.0734 | 0.29986 | 14460953.1406 | 0.038249
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 43345.9176 | 1.3337 | 3250000 | 0.041822
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 42754.9653 | 3.0982 | 1380000 | 0.18076
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 41025.9524 | 0.77407 | 5300000 | 0.049907
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 40258.3178 | 0.24863 | 16192000 | 0.033386
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 40127.8282 | 1.14 | 3520000 | 0.055212
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 39454.9003 | 1.214 | 3250000 | 0.049114
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 38428.9932 | 1.1824 | 3250000 | 0.049114
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 37122.6299 | 1.1422 | 3250000 | 0.041822
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 37049.8267 | 1.14 | 3250000 | 0.055212
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 36795.1642 | 1.1322 | 3250000 | 0.041822
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 36792.8858 | 1.1321 | 3250000 | 0.041822
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 35834.1435 | 1.1026 | 3250000 | 0.041822
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 35388.1717 | 1.4548 | 2432500 | 0.035975
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 35161.7102 | 0.66343 | 5300000 | 0.022602
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 33213.7953 | 1.022 | 3250000 | 0.055212
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 30826.3056 | 0.9485 | 3250000 | 0.041822
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 30024.4327 | 1.3647 | 2200000 | 0.028822
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 29898.0151 | 0.91994 | 3250000 | 0.049907
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 29009.2512 | 0.54734 | 5300000 | 0.0048726
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 28149.6185 | 2.0398 | 1380000 | 0.036335
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 24739.1992 | 1.7927 | 1380000 | 0.049114
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 22493.3411 | 0.9247 | 2432500 | 0.049907
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 22181.5131 | 0.91188 | 2432500 | 0.049907
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 21679.7502 | 0.72996 | 2970000 | 0.035406
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 20338.3397 | 1.4738 | 1380000 | 0.041822
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 18843.0832 | 1.4275 | 1320000 | 0.035975
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 17954.3036 | 0.81149 | 2212500 | 0.049114
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 17407.5575 | 0.78678 | 2212500 | 0.049114
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 16732.5123 | 1.2125 | 1380000 | 0.041822
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 16059.0742 | 0.72996 | 2200000 | 0.035406
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 14890.3418 | 0.64741 | 2300000 | 0.054645
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 14664.3742 | 1.0626 | 1380000 | 0.049907
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 14434.8981 | 0.59342 | 2432500 | 0.032233
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 13376.4853 | 0.96931 | 1380000 | 0.040547
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 11302.1405 | 0.21325 | 5300000 | 0.036573
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 7234.4537 | 0.32698 | 2212500 | 0.041748
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 4102.4101 | 0.24863 | 1650000 | 0.033386
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 5491543.8252 | 8.6823 | 63250000 | 0.5646
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 1998714.4849 | 1.772 | 112794000 | 0.18076
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 1 | Current Study |  | (1868.00, 1868.00) | 1994951.6224 | 3.2438 | 61500000 | 0.094619
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 2 | Current Study |  | (1868.00, 1868.00) | 1994951.6224 | 3.2438 | 61500000 | 0.094619
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 1674207.9412 | 1.4275 | 117282000 | 0.035975
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 1620609.6035 | 1.0787 | 150244000 | 0.029274
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 1469542.6172 | 5.7239 | 25674000 | 0.24065
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 1143277.7205 | 1.2712 | 89936000 | 0.017783
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1088467.3395 | 1.14 | 95480000 | 0.055212
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1056449.1072 | 1.052 | 100427000 | 0.01618
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 1049654.1509 | 5.8614 | 17908000 | 0.2505
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 992587.6902 | 1.784 | 55638000 | 0.048187
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 990346.6535 | 0.45362 | 218320000 | 0.016763
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 972159.5402 | 1.473 | 66000000 | 0.040546
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 965575.8657 | 1.14 | 84700000 | 0.055212
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 815964.1709 | 0.56745 | 143796000 | 0.033942
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 752712.5271 | 1.3647 | 55154000 | 0.028822
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 698696.1459 | 1.5583 | 44836000 | 0.043814
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 631170.9426 | 0.67157 | 93984000 | 0.049907
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1 | Current Study | 11.3 | (1793.00, 1793.00) | 629308.3449 | 2.5314 | 24860000 | 0.09351
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 598443.6215 | 0.30147 | 198511000 | 0.019299
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 554808.4327 | 1.6515 | 33594000 | 0.080704
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 504100.5944 | 0.40385 | 124824000 | 0.031642
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 776060 G23-204-TAP 345 1 | Current Study | 17.82 | (1793.00, 1793.00) | 422825.1155 | 1.0785 | 39204000 | 0.048655
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 405335.4418 | 0.24557 | 165062000 | 0.018504
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 360293.1921 | 1.3647 | 26400000 | 0.028822
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 349841.7814 | 1.3363 | 26180000 | 0.018083
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 343021.8248 | 0.72996 | 46992000 | 0.035406
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 332196.8122 | 0.40766 | 81488000 | 0.032417
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 330646.9472 | 0.72014 | 45914000 | 0.043599
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 295797.8898 | 1.1692 | 25300000 | 0.02868
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 68 MVAR SVC at TONTITN7 345 kV | Current Study |  |  | 247404.7381 | 2.0617 | 12000000 | 0.016844
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 244779.291 | 2.0398 | 12000000 | 0.036335
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 185992.8777 | 0.34791 | 53460000 | 0.01504
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 180453.7005 | 0.72014 | 25058000 | 0.043599
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 175341.633 | 1.4232 | 12320000 | 0.036573
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 165039.8747 | 1.3753 | 12000000 | 0.036573
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 165039.8747 | 1.3753 | 12000000 | 0.036573
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | Current Study | 6.93 | (1793.00, 1793.00) | 164431.9894 | 1.0785 | 15246000 | 0.048655
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 157813.4069 | 1.3151 | 12000000 | 0.055212
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 156451.7133 | 1.0393 | 15053000 | 0.016463
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 147142.6454 | 1.2262 | 12000000 | 0.036573
GEN-2024-297 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 144146.9808 | 2.7198 | 5300000 | 0.55614
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 142681.7363 | 1.189 | 12000000 | 0.048187
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 133443.9288 | 1.112 | 12000000 | 0.049114
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 131955.4658 | 1.0996 | 12000000 | 0.017783
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 130182.0226 | 1.9725 | 6600000 | 0.049114
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 122907.3316 | 1.0242 | 12000000 | 0.041822
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 115615.8793 | 0.96347 | 12000000 | 0.058707
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 114965.7996 | 0.95805 | 12000000 | 0.055212
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 114138.1911 | 0.95115 | 12000000 | 0.026844
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 114062.4586 | 0.95052 | 12000000 | 0.048187
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 111805.8459 | 0.93172 | 12000000 | 0.036573
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 111805.8459 | 0.93172 | 12000000 | 0.036573
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 106872.011 | 0.8906 | 12000000 | 0.035975
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 106034.7956 | 0.88362 | 12000000 | 0.036573
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 104233.9475 | 0.86862 | 12000000 | 0.036573
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 98611.1759 | 1.8606 | 5300000 | 0.036335
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 98471.5526 | 0.8206 | 12000000 | 0.026844
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 95096.9329 | 0.79247 | 12000000 | 0.041822
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 85289.2501 | 0.73147 | 11660000 | 0.049907
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 78071.2414 | 1.1829 | 6600000 | 0.049114
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 74507.5101 | 1.1289 | 6600000 | 0.055212
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 73696.1812 | 1.3905 | 5300000 | 0.048187
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 71797.4669 | 1.3547 | 5300000 | 0.049907
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 69957.2514 | 1.06 | 6600000 | 0.041822
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 69957.2514 | 1.06 | 6600000 | 0.041822
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 69646.9318 | 1.0553 | 6600000 | 0.049907
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 65189.749 | 2.0058 | 3250000 | 0.049114
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 65189.749 | 2.0058 | 3250000 | 0.049114
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 63342.9231 | 1.1951 | 5300000 | 0.035975
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 60777.0077 | 1.1467 | 5300000 | 0.035975
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 59635.1305 | 1.8349 | 3250000 | 0.041822
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 59635.1305 | 1.8349 | 3250000 | 0.041822
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 58437.2187 | 1.1026 | 5300000 | 0.041822
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 54180.0626 | 1.0223 | 5300000 | 0.058707
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 48472.7668 | 1.4915 | 3250000 | 0.041822
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 46740.2499 | 0.88189 | 5300000 | 0.049907
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 44792.5283 | 0.29986 | 14938000 | 0.038249
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 43362.0734 | 0.29986 | 14460953.1406 | 0.038249
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 43345.9176 | 1.3337 | 3250000 | 0.041822
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 42754.9653 | 3.0982 | 1380000 | 0.18076
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 41025.9524 | 0.77407 | 5300000 | 0.049907
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 40258.3178 | 0.24863 | 16192000 | 0.033386
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 40127.8282 | 1.14 | 3520000 | 0.055212
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 39454.9003 | 1.214 | 3250000 | 0.049114
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 38428.9932 | 1.1824 | 3250000 | 0.049114
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 37122.6299 | 1.1422 | 3250000 | 0.041822
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 37049.8267 | 1.14 | 3250000 | 0.055212
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 36795.1642 | 1.1322 | 3250000 | 0.041822
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 36792.8858 | 1.1321 | 3250000 | 0.041822
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 35834.1435 | 1.1026 | 3250000 | 0.041822
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 35388.1717 | 1.4548 | 2432500 | 0.035975
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 35161.7102 | 0.66343 | 5300000 | 0.022602
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 33213.7953 | 1.022 | 3250000 | 0.055212
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 30826.3056 | 0.9485 | 3250000 | 0.041822
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 30024.4327 | 1.3647 | 2200000 | 0.028822
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 29898.0151 | 0.91994 | 3250000 | 0.049907
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 29009.2512 | 0.54734 | 5300000 | 0.0048726
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 28149.6185 | 2.0398 | 1380000 | 0.036335
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 24739.1992 | 1.7927 | 1380000 | 0.049114
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 22493.3411 | 0.9247 | 2432500 | 0.049907
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 22181.5131 | 0.91188 | 2432500 | 0.049907
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 21679.7502 | 0.72996 | 2970000 | 0.035406
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 20338.3397 | 1.4738 | 1380000 | 0.041822
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 18843.0832 | 1.4275 | 1320000 | 0.035975
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 17954.3036 | 0.81149 | 2212500 | 0.049114
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 17407.5575 | 0.78678 | 2212500 | 0.049114
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 16732.5123 | 1.2125 | 1380000 | 0.041822
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 16059.0742 | 0.72996 | 2200000 | 0.035406
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 14890.3418 | 0.64741 | 2300000 | 0.054645
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 14664.3742 | 1.0626 | 1380000 | 0.049907
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 14434.8981 | 0.59342 | 2432500 | 0.032233
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 13376.4853 | 0.96931 | 1380000 | 0.040547
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 11302.1405 | 0.21325 | 5300000 | 0.036573
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 7234.4537 | 0.32698 | 2212500 | 0.041748
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 4102.4101 | 0.24863 | 1650000 | 0.033386
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 5491543.8252 | 8.6823 | 63250000 | 0.5646
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 1998714.4849 | 1.772 | 112794000 | 0.18076
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 1 | Current Study |  | (1868.00, 1868.00) | 1994951.6224 | 3.2438 | 61500000 | 0.094619
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 2 | Current Study |  | (1868.00, 1868.00) | 1994951.6224 | 3.2438 | 61500000 | 0.094619
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 1674207.9412 | 1.4275 | 117282000 | 0.035975
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 1620609.6035 | 1.0787 | 150244000 | 0.029274
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 1469542.6172 | 5.7239 | 25674000 | 0.24065
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 1143277.7205 | 1.2712 | 89936000 | 0.017783
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1088467.3395 | 1.14 | 95480000 | 0.055212
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1056449.1072 | 1.052 | 100427000 | 0.01618
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 1049654.1509 | 5.8614 | 17908000 | 0.2505
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 992587.6902 | 1.784 | 55638000 | 0.048187
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 990346.6535 | 0.45362 | 218320000 | 0.016763
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 972159.5402 | 1.473 | 66000000 | 0.040546
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 965575.8657 | 1.14 | 84700000 | 0.055212
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 815964.1709 | 0.56745 | 143796000 | 0.033942
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 752712.5271 | 1.3647 | 55154000 | 0.028822
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 698696.1459 | 1.5583 | 44836000 | 0.043814
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 631170.9426 | 0.67157 | 93984000 | 0.049907
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1 | Current Study | 11.3 | (1793.00, 1793.00) | 629308.3449 | 2.5314 | 24860000 | 0.09351
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 598443.6215 | 0.30147 | 198511000 | 0.019299
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 554808.4327 | 1.6515 | 33594000 | 0.080704
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 504100.5944 | 0.40385 | 124824000 | 0.031642
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 776060 G23-204-TAP 345 1 | Current Study | 17.82 | (1793.00, 1793.00) | 422825.1155 | 1.0785 | 39204000 | 0.048655
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 405335.4418 | 0.24557 | 165062000 | 0.018504
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 360293.1921 | 1.3647 | 26400000 | 0.028822
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 349841.7814 | 1.3363 | 26180000 | 0.018083
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 343021.8248 | 0.72996 | 46992000 | 0.035406
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 332196.8122 | 0.40766 | 81488000 | 0.032417
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 330646.9472 | 0.72014 | 45914000 | 0.043599
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 295797.8898 | 1.1692 | 25300000 | 0.02868
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 68 MVAR SVC at TONTITN7 345 kV | Current Study |  |  | 247404.7381 | 2.0617 | 12000000 | 0.016844
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 244779.291 | 2.0398 | 12000000 | 0.036335
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 185992.8777 | 0.34791 | 53460000 | 0.01504
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 180453.7005 | 0.72014 | 25058000 | 0.043599
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 175341.633 | 1.4232 | 12320000 | 0.036573
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 165039.8747 | 1.3753 | 12000000 | 0.036573
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 165039.8747 | 1.3753 | 12000000 | 0.036573
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | Current Study | 6.93 | (1793.00, 1793.00) | 164431.9894 | 1.0785 | 15246000 | 0.048655
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 157813.4069 | 1.3151 | 12000000 | 0.055212
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 156451.7133 | 1.0393 | 15053000 | 0.016463
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 147142.6454 | 1.2262 | 12000000 | 0.036573
GEN-2024-298 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 144146.9808 | 2.7198 | 5300000 | 0.55614
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 142681.7363 | 1.189 | 12000000 | 0.048187
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 133443.9288 | 1.112 | 12000000 | 0.049114
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 131955.4658 | 1.0996 | 12000000 | 0.017783
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 130182.0226 | 1.9725 | 6600000 | 0.049114
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 122907.3316 | 1.0242 | 12000000 | 0.041822
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 115615.8793 | 0.96347 | 12000000 | 0.058707
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 114965.7996 | 0.95805 | 12000000 | 0.055212
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 114138.1911 | 0.95115 | 12000000 | 0.026844
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 114062.4586 | 0.95052 | 12000000 | 0.048187
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 111805.8459 | 0.93172 | 12000000 | 0.036573
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 111805.8459 | 0.93172 | 12000000 | 0.036573
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 106872.011 | 0.8906 | 12000000 | 0.035975
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 106034.7956 | 0.88362 | 12000000 | 0.036573
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 104233.9475 | 0.86862 | 12000000 | 0.036573
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 98611.1759 | 1.8606 | 5300000 | 0.036335
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 98471.5526 | 0.8206 | 12000000 | 0.026844
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 95096.9329 | 0.79247 | 12000000 | 0.041822
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 85289.2501 | 0.73147 | 11660000 | 0.049907
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 78071.2414 | 1.1829 | 6600000 | 0.049114
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 74507.5101 | 1.1289 | 6600000 | 0.055212
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 73696.1812 | 1.3905 | 5300000 | 0.048187
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 71797.4669 | 1.3547 | 5300000 | 0.049907
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 69957.2514 | 1.06 | 6600000 | 0.041822
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 69957.2514 | 1.06 | 6600000 | 0.041822
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 69646.9318 | 1.0553 | 6600000 | 0.049907
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 65189.749 | 2.0058 | 3250000 | 0.049114
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 65189.749 | 2.0058 | 3250000 | 0.049114
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 63342.9231 | 1.1951 | 5300000 | 0.035975
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 60777.0077 | 1.1467 | 5300000 | 0.035975
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 59635.1305 | 1.8349 | 3250000 | 0.041822
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 59635.1305 | 1.8349 | 3250000 | 0.041822
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 58437.2187 | 1.1026 | 5300000 | 0.041822
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 54180.0626 | 1.0223 | 5300000 | 0.058707
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 48472.7668 | 1.4915 | 3250000 | 0.041822
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 46740.2499 | 0.88189 | 5300000 | 0.049907
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 44792.5283 | 0.29986 | 14938000 | 0.038249
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 43362.0734 | 0.29986 | 14460953.1406 | 0.038249
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 43345.9176 | 1.3337 | 3250000 | 0.041822
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 42754.9653 | 3.0982 | 1380000 | 0.18076
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 41025.9524 | 0.77407 | 5300000 | 0.049907
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 40258.3178 | 0.24863 | 16192000 | 0.033386
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 40127.8282 | 1.14 | 3520000 | 0.055212
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 39454.9003 | 1.214 | 3250000 | 0.049114
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 38428.9932 | 1.1824 | 3250000 | 0.049114
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 37122.6299 | 1.1422 | 3250000 | 0.041822
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 37049.8267 | 1.14 | 3250000 | 0.055212
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 36795.1642 | 1.1322 | 3250000 | 0.041822
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 36792.8858 | 1.1321 | 3250000 | 0.041822
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 35834.1435 | 1.1026 | 3250000 | 0.041822
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 35388.1717 | 1.4548 | 2432500 | 0.035975
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 35161.7102 | 0.66343 | 5300000 | 0.022602
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 33213.7953 | 1.022 | 3250000 | 0.055212
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 30826.3056 | 0.9485 | 3250000 | 0.041822
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 30024.4327 | 1.3647 | 2200000 | 0.028822
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 29898.0151 | 0.91994 | 3250000 | 0.049907
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 29009.2512 | 0.54734 | 5300000 | 0.0048726
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 28149.6185 | 2.0398 | 1380000 | 0.036335
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 24739.1992 | 1.7927 | 1380000 | 0.049114
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 22493.3411 | 0.9247 | 2432500 | 0.049907
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 22181.5131 | 0.91188 | 2432500 | 0.049907
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 21679.7502 | 0.72996 | 2970000 | 0.035406
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 20338.3397 | 1.4738 | 1380000 | 0.041822
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 18843.0832 | 1.4275 | 1320000 | 0.035975
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 17954.3036 | 0.81149 | 2212500 | 0.049114
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 17407.5575 | 0.78678 | 2212500 | 0.049114
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 16732.5123 | 1.2125 | 1380000 | 0.041822
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 16059.0742 | 0.72996 | 2200000 | 0.035406
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 14890.3418 | 0.64741 | 2300000 | 0.054645
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 14664.3742 | 1.0626 | 1380000 | 0.049907
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 14434.8981 | 0.59342 | 2432500 | 0.032233
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 13376.4853 | 0.96931 | 1380000 | 0.040547
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 11302.1405 | 0.21325 | 5300000 | 0.036573
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 7234.4537 | 0.32698 | 2212500 | 0.041748
GEN-2024-298 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 4102.4101 | 0.24863 | 1650000 | 0.033386
GEN-2024-299 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1 | Current Study | 11.3 | (1793.00, 1793.00) | 3708503.758 | 14.9176 | 24860000 | 0.12369
GEN-2024-299 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 339132.0898 | 6.3987 | 5300000 | 0.18502
GEN-2024-299 | 04 SOUTHEAST | TBD | ERIS | Add 10 MVAR switched shunt at G20-007-TAP 345 kV | Current Study |  |  | 278484.1937 | 5.2544 | 5300000 | 0.027698
GEN-2024-299 | 04 SOUTHEAST | TBD | ERIS | Add 38 MVAR switched shunt at FRNT2WD7 345 kV | Current Study |  |  | 269325.8166 | 5.0816 | 5300000 | 0.040218
GEN-2024-299 | 04 SOUTHEAST | TBD | ERIS | Add 19 MVAR switched shunt at RANCHRD7 345 kV | Current Study |  |  | 246579.6124 | 4.6524 | 5300000 | 0.040218
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 61130133.3091 | 4.036 | 1514620000 | 0.049645
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 53314538.2096 | 4.9652 | 1073760000 | 0.17011
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 51313017.3009 | 3.9928 | 1285130000 | 0.25166
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 50725213.0804 | 3.989 | 1271630000 | 0.1643
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 37114996.6689 | 3.9551 | 938400000 | 0.1342
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 32886579.2632 | 3.5045 | 938400000 | 0.21044
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 28347886.6923 | 3.9113 | 724760000 | 0.18557
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 19163025.578 | 3.9688 | 482840000 | 0.20172
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 18655907.0609 | 3.9749 | 469340000 | 0.13577
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 16392054.4669 | 4.4726 | 366500000 | 0.058795
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 3436018.4353 | 4.0663 | 84500000 | 0.049939
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 3335893.3442 | 3.9478 | 84500000 | 0.10038
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 3326300.9696 | 1.6811 | 197860000 | 0.033234
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 3305089.1681 | 3.9113 | 84500000 | 0.18557
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 3146598.9097 | 2.5208 | 124824000 | 0.065968
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 2955383.5586 | 1.4888 | 198511000 | 0.031833
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 2388339.598 | 1.4469 | 165062000 | 0.036416
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 2179792.296 | 2.675 | 81488000 | 0.071047
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 1719973.0505 | 3.9565 | 43472000 | 0.048233
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 1652844.348 | 2.9932 | 55220000 | 0.058399
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 1160391.9825 | 6.2387 | 18600000 | 0.33154
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 834277.6054 | 4.4854 | 18600000 | 0.34545
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 822802.7179 | 3.1049 | 26500000 | 0.019519
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 750696.861 | 4.036 | 18600000 | 0.049645
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 742196.5961 | 3.9903 | 18600000 | 0.25166
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 741623.9444 | 3.9872 | 18600000 | 0.1643
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 739335.8148 | 3.9749 | 18600000 | 0.13577
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 731329.4269 | 3.9319 | 18600000 | 0.1643
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 727510.7518 | 3.9113 | 18600000 | 0.18557
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 695093.5381 | 2.7804 | 25000000 | 0.01644
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 695093.5381 | 2.7804 | 25000000 | 0.018865
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 622699.4942 | 3.3478 | 18600000 | 0.1342
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 557934.3952 | 2.9996 | 18600000 | 0.21044
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 557934.3952 | 2.9996 | 18600000 | 0.21044
GEN-2024-303 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 313229.2075 | 1.7305 | 18100000 | 0.010605
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 235708.5651 | 1.4557 | 16192000 | 0.065288
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 213723.0381 | 1.4307 | 14938000 | 0.060956
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 206897.7667 | 1.4307 | 14460953.1406 | 0.060956
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 185752.6526 | 3.5048 | 5300000 | 0.20076
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | Current Study | 0.78 | (598.00, 598.00) | 180584.9798 | 3.4124 | 5292000 | 0.019281
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | Current Study | 0.2 | (598.00, 598.00) | 152876.1734 | 3.4124 | 4480000 | 0.019281
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 138595.1039 | 2.114 | 6556000 | 0.058399
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 67066.2659 | 0.55889 | 12000000 | 0.031101
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 66405.6706 | 4.812 | 1380000 | 0.20076
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 62812.1781 | 4.5516 | 1380000 | 0.16131
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 44277.8048 | 2.0013 | 2212500 | 0.032917
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 44157.4778 | 3.1998 | 1380000 | 0.20076
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 33873.1165 | 1.531 | 2212500 | 0.065288
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 29399.7005 | 2.1304 | 1380000 | 0.0060969
GEN-2024-303 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 27040.5413 | 1.9595 | 1380000 | 0.049612
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 24019.2152 | 1.4557 | 1650000 | 0.065288
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 16566.0522 | 0.74875 | 2212500 | 0.031101
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 10512.6125 | 0.76178 | 1380000 | 0.031101
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 61130133.3091 | 4.036 | 1514620000 | 0.049645
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 53314538.2096 | 4.9652 | 1073760000 | 0.17011
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 51313017.3009 | 3.9928 | 1285130000 | 0.25166
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 50725213.0804 | 3.989 | 1271630000 | 0.1643
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 37114996.6689 | 3.9551 | 938400000 | 0.1342
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 32886579.2632 | 3.5045 | 938400000 | 0.21044
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 28347886.6923 | 3.9113 | 724760000 | 0.18557
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 19163025.578 | 3.9688 | 482840000 | 0.20172
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 18655907.0609 | 3.9749 | 469340000 | 0.13577
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 16392054.4669 | 4.4726 | 366500000 | 0.058795
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 3436018.4353 | 4.0663 | 84500000 | 0.049939
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 3335893.3442 | 3.9478 | 84500000 | 0.10038
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 3326300.9696 | 1.6811 | 197860000 | 0.033234
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 3305089.1681 | 3.9113 | 84500000 | 0.18557
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 3146598.9097 | 2.5208 | 124824000 | 0.065968
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 2955383.5586 | 1.4888 | 198511000 | 0.031833
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 2388339.598 | 1.4469 | 165062000 | 0.036416
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 2179792.296 | 2.675 | 81488000 | 0.071047
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 1719973.0505 | 3.9565 | 43472000 | 0.048233
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 1652844.348 | 2.9932 | 55220000 | 0.058399
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 1160391.9825 | 6.2387 | 18600000 | 0.33154
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 834277.6054 | 4.4854 | 18600000 | 0.34545
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 822802.7179 | 3.1049 | 26500000 | 0.019519
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 750696.861 | 4.036 | 18600000 | 0.049645
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 742196.5961 | 3.9903 | 18600000 | 0.25166
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 741623.9444 | 3.9872 | 18600000 | 0.1643
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 739335.8148 | 3.9749 | 18600000 | 0.13577
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 731329.4269 | 3.9319 | 18600000 | 0.1643
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 727510.7518 | 3.9113 | 18600000 | 0.18557
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 695093.5381 | 2.7804 | 25000000 | 0.01644
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 695093.5381 | 2.7804 | 25000000 | 0.018865
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 622699.4942 | 3.3478 | 18600000 | 0.1342
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 557934.3952 | 2.9996 | 18600000 | 0.21044
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 557934.3952 | 2.9996 | 18600000 | 0.21044
GEN-2024-304 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 313229.2075 | 1.7305 | 18100000 | 0.010605
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 235708.5651 | 1.4557 | 16192000 | 0.065288
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 213723.0381 | 1.4307 | 14938000 | 0.060956
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 206897.7667 | 1.4307 | 14460953.1406 | 0.060956
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 185752.6526 | 3.5048 | 5300000 | 0.20076
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | Current Study | 0.78 | (598.00, 598.00) | 180584.9798 | 3.4124 | 5292000 | 0.019281
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | Current Study | 0.2 | (598.00, 598.00) | 152876.1734 | 3.4124 | 4480000 | 0.019281
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 138595.1039 | 2.114 | 6556000 | 0.058399
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 67066.2659 | 0.55889 | 12000000 | 0.031101
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 66405.6706 | 4.812 | 1380000 | 0.20076
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 62812.1781 | 4.5516 | 1380000 | 0.16131
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 44277.8048 | 2.0013 | 2212500 | 0.032917
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 44157.4778 | 3.1998 | 1380000 | 0.20076
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 33873.1165 | 1.531 | 2212500 | 0.065288
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 29399.7005 | 2.1304 | 1380000 | 0.0060969
GEN-2024-304 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 27040.5413 | 1.9595 | 1380000 | 0.049612
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 24019.2152 | 1.4557 | 1650000 | 0.065288
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 16566.0522 | 0.74875 | 2212500 | 0.031101
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 10512.6125 | 0.76178 | 1380000 | 0.031101
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508813 PLAINDL2 69 778290 G24-044-TAP 69 1 | Current Study | 9.39 | (69.00, 69.00) | 2106287.8369 | 26.3896 | 7981500 | 0.13673
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508812 OILCITY2 69 508815 SUPEROR2 69 1 | Current Study | 4.66 | (106.00, 106.00) | 1869293.353 | 47.1925 | 3961000 | 0.4276
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508830 BALDWIN2 69 508842 WOODLWN2 69 1 | Current Study | 2.73 | (69.00, 69.00) | 1714162.3117 | 73.8704 | 2320500 | 0.066274
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508805 LIEBERM2 69 508812 OILCITY2 69 1 | Current Study | 3.4 | (106.00, 106.00) | 1363862.1031 | 47.1925 | 2890000 | 0.4276
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 419970.2672 | 0.27953 | 150244000 | 0.025338
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 257198.8618 | 0.26937 | 95480000 | 0.043575
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 241542.5953 | 0.11064 | 218320000 | 0.013656
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 228160.2807 | 0.26937 | 84700000 | 0.043575
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 212928.8634 | 0.14808 | 143796000 | 0.029584
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 181133.8297 | 0.18036 | 100427000 | 0.0092656
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 171238.393 | 0.086261 | 198511000 | 0.018444
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 169048.0608 | 0.35974 | 46992000 | 0.058279
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 150273.3186 | 0.23759 | 63250000 | 0.051603
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 147534.2133 | 0.11819 | 124824000 | 0.03093
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 142402.4809 | 0.12625 | 112794000 | 0.043014
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 126865.1355 | 0.13499 | 93984000 | 0.033504
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 114473.6029 | 0.069352 | 165062000 | 0.017454
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 109919.1143 | 0.91599 | 12000000 | 0.054497
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 101742.2909 | 0.30286 | 33594000 | 0.049431
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 97803.235 | 0.12002 | 81488000 | 0.031877
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at PHILL 7 345 kV | Current Study |  |  | 83408.5339 | 1.5737 | 5300000 | 0.028073
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | Current Study | 10.42 | (395.00, 395.00) | 82645.8973 | 0.66096 | 12504000 | 0.010677
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 77560.5941 | 0.30656 | 25300000 | 0.025117
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508089 WATLANT2 69 779100 G24-071-TAP 69 1 | Current Study | 1.78 | (106.00, 106.00) | 67584.3229 | 4.4669 | 1513000 | 0.073431
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 65716.7492 | 0.25597 | 25674000 | 0.035943
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 54287.9521 | 0.4524 | 12000000 | 0.066735
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 52960.9363 | 0.80244 | 6600000 | 0.066735
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 46987.0758 | 0.26238 | 17908000 | 0.037454
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 45432.9314 | 0.37861 | 12000000 | 0.066735
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 44281.7408 | 0.8355 | 5300000 | 0.054497
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 41604.9407 | 0.34671 | 12000000 | 0.066735
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 37290.462 | 0.31075 | 12000000 | 0.043575
GEN-2024-305 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 35747.1435 | 0.1975 | 18100000 | 0.012103
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 33558.5664 | 0.27965 | 12000000 | 0.037854
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 33541.578 | 0.27951 | 12000000 | 0.015097
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 32133.2937 | 0.26778 | 12000000 | 0.054497
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 31761.1138 | 0.48123 | 6600000 | 0.066735
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 30106.7513 | 0.25089 | 12000000 | 0.02365
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 27618.3304 | 0.23015 | 12000000 | 0.031389
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 27610.7781 | 0.23009 | 12000000 | 0.030166
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 27610.7781 | 0.23009 | 12000000 | 0.030166
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 26827.348 | 0.22356 | 12000000 | 0.037854
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 26740.7423 | 0.17764 | 15053000 | 0.0093982
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 26520.6368 | 0.81602 | 3250000 | 0.066735
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 26520.6368 | 0.81602 | 3250000 | 0.066735
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 26299.1694 | 0.21916 | 12000000 | 0.029568
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 25974.2906 | 0.21645 | 12000000 | 0.02365
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 25740.8758 | 0.21451 | 12000000 | 0.030166
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 25383.7834 | 0.47894 | 5300000 | 0.054497
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 17605.7252 | 0.26675 | 6600000 | 0.043575
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 17143.109 | 0.14702 | 11660000 | 0.033504
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 16425.1732 | 0.30991 | 5300000 | 0.066735
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 16051.1292 | 0.49388 | 3250000 | 0.066735
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 15719.9938 | 0.23818 | 6600000 | 0.031389
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 15719.9938 | 0.23818 | 6600000 | 0.031389
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 15633.7674 | 0.48104 | 3250000 | 0.066735
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 14727.388 | 0.45315 | 3250000 | 0.066735
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 14431.2597 | 0.27229 | 5300000 | 0.033504
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | Current Study | 1.8 | (395.00, 395.00) | 14276.6425 | 0.66096 | 2160000 | 0.010677
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 14045.4096 | 0.26501 | 5300000 | 0.050831
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 13131.3437 | 0.24776 | 5300000 | 0.031389
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 12747.089 | 0.085333 | 14938000 | 0.036356
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 12640.6981 | 0.91599 | 1380000 | 0.054497
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 12340.0092 | 0.085333 | 14460953.1406 | 0.036356
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 12019.731 | 0.36984 | 3250000 | 0.066735
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV | Current Study |  |  | 11592.3686 | 0.84003 | 1380000 | 0.044304
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 11299.4956 | 0.069784 | 16192000 | 0.031298
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 10684.2173 | 0.35974 | 2970000 | 0.058279
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 10064.4554 | 0.72931 | 1380000 | 0.066735
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 9740.1991 | 0.2997 | 3250000 | 0.031389
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 9481.9857 | 0.26937 | 3520000 | 0.043575
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 9394.7699 | 0.17726 | 5300000 | 0.033504
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 8754.6754 | 0.26937 | 3250000 | 0.043575
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 8341.773 | 0.25667 | 3250000 | 0.031389
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 8268.1887 | 0.25441 | 3250000 | 0.031389
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 8267.6767 | 0.25439 | 3250000 | 0.031389
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 8052.2391 | 0.24776 | 3250000 | 0.031389
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 7914.2351 | 0.35974 | 2200000 | 0.058279
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 6429.3468 | 0.29059 | 2212500 | 0.058742
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 6233.5598 | 0.28174 | 2212500 | 0.058742
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 6009.488 | 0.18491 | 3250000 | 0.033504
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 5943.6313 | 0.11214 | 5300000 | 0.0033344
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 5382.8842 | 0.39006 | 1380000 | 0.054497
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 4754.672 | 0.20672 | 2300000 | 0.058279
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 4521.1518 | 0.18586 | 2432500 | 0.033504
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 4458.4745 | 0.18329 | 2432500 | 0.033504
GEN-2024-305 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 4455.2458 | 0.084061 | 5300000 | 0.057411
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 4047.4709 | 0.16639 | 2432500 | 0.030187
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 3759.9389 | 0.27246 | 1380000 | 0.031389
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 3671.985 | 0.26609 | 1380000 | 0.051851
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 2144.6606 | 0.096934 | 2212500 | 0.041337
GEN-2024-305 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 1151.4432 | 0.069784 | 1650000 | 0.031298
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 18757659.5528 | 1.2384 | 1514620000 | 0.050778
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 16457586.5423 | 1.2806 | 1285130000 | 0.26905
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 16401455.683 | 1.2898 | 1271630000 | 0.17709
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 16313368.9725 | 1.5193 | 1073760000 | 0.1735
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 8830717.2003 | 0.94104 | 938400000 | 0.10643
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 8320017.6076 | 1.148 | 724760000 | 0.18155
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 7924555.5437 | 0.84448 | 938400000 | 0.16903
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 5996113.7627 | 1.2418 | 482840000 | 0.2104
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 5903820.3029 | 1.2579 | 469340000 | 0.14322
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 4191559.3506 | 1.1437 | 366500000 | 0.050114
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526460 AMOCO_SS 6 230 777420 G24-015-TAP 230 1 | Current Study | 25.97 | (519.00, 519.00) | 2052998.4054 | 4.1607 | 49343000 | 0.063244
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1210695.4965 | 1.4328 | 84500000 | 0.058654
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 970033.5116 | 1.148 | 84500000 | 0.18155
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 955422.8638 | 1.1307 | 84500000 | 0.095833
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 953992.9267 | 0.48216 | 197860000 | 0.031772
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 918252.9183 | 0.73564 | 124824000 | 0.06417
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 869905.1052 | 0.43822 | 198511000 | 0.031233
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 802017.7126 | 1.4524 | 55220000 | 0.094457
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 685140.0995 | 0.41508 | 165062000 | 0.034822
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 635218.7604 | 0.77952 | 81488000 | 0.069013
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 612381.5861 | 2.3109 | 26500000 | 0.048425
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 487988.3752 | 1.1225 | 43472000 | 0.045616
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528016 SAND_DUNES 3 115 528018 RED_BLUFF 3 115 1 | Current Study | 7.69 | (394.00, 394.00) | 356193.1104 | 4.6319 | 7690000 | 0.032913
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 252838.4599 | 1.3593 | 18600000 | 0.2408
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 239796.1787 | 1.2892 | 18600000 | 0.17709
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 238044.1719 | 1.2798 | 18600000 | 0.26905
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 236467.5564 | 1.2713 | 18600000 | 0.17709
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528018 RED_BLUFF 3 115 528235 WOLFCAMP_TP3 115 1 | Current Study | 7.81 | (598.00, 598.00) | 234029.8984 | 2.9965 | 7810000 | 0.053566
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 233969.1005 | 1.2579 | 18600000 | 0.14322
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 230349.8354 | 1.2384 | 18600000 | 0.050778
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 221751.0049 | 0.887 | 25000000 | 0.020061
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 221751.0049 | 0.887 | 25000000 | 0.017482
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527956 SBCRDWRDLEA 115 528505 LEA_ROAD 3 115 1 | Current Study | 4 | (217.00, 217.00) | 216890.2446 | 5.4223 | 4000000 | 0.052249
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 213522.1694 | 1.148 | 18600000 | 0.18155
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1 | Current Study | 3.54 | (217.00, 217.00) | 191947.8664 | 5.4223 | 3540000 | 0.052249
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 186796.0343 | 1.0043 | 18600000 | 0.25782
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1 | Current Study | 3.11 | (217.00, 217.00) | 168632.1651 | 5.4223 | 3110000 | 0.052249
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 148157.9854 | 0.79655 | 18600000 | 0.10643
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 144400.3724 | 0.77635 | 18600000 | 0.18155
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 144400.3724 | 0.77635 | 18600000 | 0.18155
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | Current Study | 0.78 | (598.00, 598.00) | 136836.0447 | 2.5857 | 5292000 | 0.0487
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | Current Study | 0.2 | (598.00, 598.00) | 115840.0379 | 2.5857 | 4480000 | 0.0487
GEN-2024-306 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 97854.4841 | 0.54063 | 18100000 | 0.011044
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 67594.7555 | 0.41746 | 16192000 | 0.062409
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 67251.1773 | 1.0258 | 6556000 | 0.094457
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 62981.9246 | 0.42162 | 14938000 | 0.059877
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 60970.5891 | 0.42162 | 14460953.1406 | 0.059877
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 53200.8366 | 1.0038 | 5300000 | 0.19167
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 20360.5638 | 1.4754 | 1380000 | 0.1743
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 19562.7994 | 0.16302 | 12000000 | 0.03024
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 19019.0405 | 1.3782 | 1380000 | 0.19167
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1 | Current Study | 2.13 | (598.00, 598.00) | 13363.8746 | 0.62741 | 2130000 | 0.0091229
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 13072.3022 | 0.59084 | 2212500 | 0.032394
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 12647.0052 | 0.91645 | 1380000 | 0.19167
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 9713.8818 | 0.43905 | 2212500 | 0.062409
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 8449.5608 | 0.61229 | 1380000 | 0.0058409
GEN-2024-306 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 7389.3053 | 0.53546 | 1380000 | 0.045192
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 6888.0525 | 0.41746 | 1650000 | 0.062409
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 4832.2111 | 0.21841 | 2212500 | 0.03024
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 3066.4616 | 0.22221 | 1380000 | 0.03024
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 528184 SENDERO +3 115 528187 SENDERO_345 345 M2 | Current Study |  | (435.00, 435.00) | 2785.951 | 0.016583 | 16800000 | 8.7418e-05
GEN-2024-306 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528184 SENDERO +3 115 528193 BLACKRIVER 3 115 1 | Current Study | 0.25 | (598.00, 598.00) | 1568.5299 | 0.62741 | 250000 | 0.0091229
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520848 CDRDLTP4 138 521016 OKEENE 4 138 1 | Current Study | 33.95 | (211.00, 211.00) | 40740000 | 100 | 40740000 | 0.11605
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 515375 WWRDEHV7 345 515376 WWRDEHV4 138 515795 WWDEHV21 13 M2 | Current Study |  | (478.00, 478.00) | 18100000 | 100 | 18100000 | 0.11201
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 515375 WWRDEHV7 345 515376 WWRDEHV4 138 515799 WWDEHV31 13 M2 | Current Study |  | (478.00, 478.00) | 18100000 | 100 | 18100000 | 0.11509
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 14993692.1737 | 1.5951 | 940000000 | 0.022651
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520425 PIC4 138 520848 CDRDLTP4 138 1 | Current Study | 10.31 | (211.00, 211.00) | 12372000 | 100 | 12372000 | 0.11605
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | Current Study | 12.07 | (395.00, 395.00) | 12022135.3157 | 83.0029 | 14484000 | 0.34943
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520425 PIC4 138 786210 G24-308-TAP 138 1 | Current Study | 8.91 | (211.00, 211.00) | 10692000 | 100 | 10692000 | 0.11605
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 521096 WOODWRD2 69 521197 CRTSJCT2 69 1 | Current Study | 9.13 | (106.00, 106.00) | 7760500 | 100 | 7760500 | 0.03754
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 532803 BURNS 7 345 1 | Current Study | 50.03 | (1793.00, 1793.00) | 5694574.074 | 5.1738 | 110066000 | 0.054269
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild 3-winding transformer 520995 MOORLND2 69 520999 MOORLND4 138 521180 MLNDTERT 2 1 | Current Study |  | (86.00, 86.00) | 5400000 | 100 | 5400000 | 0.03754
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532803 BURNS 7 345 1 | Current Study | 45.5 | (1793.00, 1793.00) | 5178955.0343 | 5.1738 | 100100000 | 0.054269
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515376 WWRDEHV4 138 515425 WWDPST 4 138 1 | Current Study | 4.4 | (472.00, 472.00) | 4345665.0501 | 82.3043 | 5280000 | 0.39472
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add phase shifting xfmr 514785 WOODWRD4 138 515425 WWDPST 4 138 M2 | Current Study |  | (421.00, 421.00) | 3909452.4599 | 82.3043 | 4750000 | 0.19736
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514782 WODWRD 2 69 521096 WOODWRD2 69 1 | Current Study | 3.5 | (140.00, 140.00) | 2975000 | 100 | 2975000 | 0.045369
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 2605928.726 | 2.2219 | 117282000 | 0.046991
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 2572387.0729 | 1.7121 | 150244000 | 0.038995
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 10 MVAR switched shunt at CUSTER 4 138 kV | Current Study |  |  | 2432500 | 100 | 2432500 | 0.076047
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at NINMLTP4 138 kV | Current Study |  |  | 2432500 | 100 | 2432500 | 0.09522
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 8 MVAR switched shunt at ELLIS 4 138 kV | Current Study |  |  | 2432500 | 100 | 2432500 | 0.09522
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 2121750.0192 | 5.9558 | 35625000 | 0.062428
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1511536.0492 | 0.69235 | 218320000 | 0.021471
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1420188.6563 | 0.71542 | 198511000 | 0.038435
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1357585.5758 | 1.3518 | 100427000 | 0.017448
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 1315579.3864 | 2.3853 | 55154000 | 0.042275
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1216727.4588 | 0.84615 | 143796000 | 0.042474
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520999 MOORLND4 138 786210 G24-308-TAP 138 1 | Current Study | 1.19 | (395.00, 395.00) | 1210748.3169 | 84.7863 | 1428000 | 0.88395
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520995 MOORLND2 69 521197 CRTSJCT2 69 1 | Current Study | 1.16 | (106.00, 106.00) | 986000 | 100 | 986000 | 0.03754
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 967637.5273 | 1.0134 | 95480000 | 0.04119
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 945886.2882 | 1.0517 | 89936000 | 0.012347
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 935275.3731 | 0.4727 | 197860000 | 0.023479
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 891319.5936 | 0.71406 | 124824000 | 0.04695
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 876303.1056 | 1.3277 | 66000000 | 0.030671
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 858388.129 | 1.0134 | 84700000 | 0.04119
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 857176.7747 | 6.1227 | 14000000 | 0.031214
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514827 CTNWOOD4 138 515377 CRESENT4 138 1 | Current Study | 13.6 | (472.00, 472.00) | 842826.7105 | 5.1644 | 16320000 | 0.040338
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520893 EL RENO4 138 520899 SCOTTSW4 138 1 | Current Study | 6.45 | (265.00, 265.00) | 765255.6481 | 9.887 | 7740000 | 0.024144
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514710 WAUKOMI4 138 514774 HENESEY4 138 1 | Current Study | 11.86 | (395.00, 395.00) | 736315.9494 | 5.1737 | 14232000 | 0.028256
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 728207.036 | 0.54775 | 132946000 | 0.017115
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 672709.6707 | 0.40755 | 165062000 | 0.025771
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 629714.9037 | 2.3853 | 26400000 | 0.042275
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 597171.3401 | 0.73283 | 81488000 | 0.048904
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 526797.0401 | 1.121 | 46992000 | 0.045631
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 446246.662 | 0.47481 | 93984000 | 0.029611
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 431769.459 | 0.80765 | 53460000 | 0.029299
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 417619.0381 | 1.5952 | 26180000 | 0.018115
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514710 WAUKOMI4 138 514711 WAUKOTP4 138 1 | Current Study | 6.7 | (395.00, 395.00) | 415962.6358 | 5.1737 | 8040000 | 0.028256
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 362391.6664 | 0.78928 | 45914000 | 0.040101
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild 3-winding transformer 521015 OKEENE 2 69 521016 OKEENE 4 138 521173 OKENTERT 13 1 | Current Study |  | (103.00, 103.00) | 342078.3908 | 6.3348 | 5400000 | 0.0038967
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 122 MVAR switched shunt at HOYT 7 345 kV | Current Study |  |  | 316612.8697 | 5.9738 | 5300000 | 0.044324
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 312168.2133 | 1.2339 | 25300000 | 0.0254
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 138 MVAR switched shunt at GEN-2024-016 345 kV | Current Study |  |  | 309881.0487 | 5.8468 | 5300000 | 0.036788
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515785 WINDFRM4 138 520999 MOORLND4 138 1 | Current Study | 0.28 | (395.00, 395.00) | 278881.189 | 83.0004 | 336000 | 0.34945
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 271875.5062 | 2.2068 | 12320000 | 0.047589
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 259067.5851 | 2.1589 | 12000000 | 0.029299
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 255901.7556 | 2.1325 | 12000000 | 0.047589
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 255901.7556 | 2.1325 | 12000000 | 0.047589
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at SHARNSP3 115 kV | Current Study |  |  | 255423.9678 | 11.5446 | 2212500 | 0.034402
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 8 MVAR switched shunt at RANSOM 3 115 kV | Current Study |  |  | 255423.9678 | 11.5446 | 2212500 | 0.034402
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 0.06 MVAR switched shunt at G24-125-TAP 345 kV | Current Study |  |  | 251566.2794 | 4.7465 | 5300000 | 0.034071
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 228151.2958 | 1.9013 | 12000000 | 0.047589
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 220443.8391 | 1.837 | 12000000 | 0.063808
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 215862.8783 | 1.7989 | 12000000 | 0.042605
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 215588.4966 | 4.0677 | 5300000 | 0.040101
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520535 BULFTTP4 138 520882 DOVERSW4 138 1 | Current Study | 3.3 | (472.00, 472.00) | 204877.1191 | 5.1737 | 3960000 | 0.028256
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 25 MVAR switched shunt at HIGHPT 3 115 kV | Current Study |  |  | 201504.2119 | 9.1075 | 2212500 | 0.034402
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 200192.5786 | 1.3299 | 15053000 | 0.017678
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 197778.6814 | 0.78928 | 25058000 | 0.040101
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 191889.5087 | 3.6206 | 5300000 | 0.048314
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at GRANTTP3 115 kV | Current Study |  |  | 186270.6885 | 8.419 | 2212500 | 0.047184
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at PNTPR-GOAB3 115 kV | Current Study |  |  | 186270.6885 | 8.419 | 2212500 | 0.047184
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 186233.4823 | 1.5519 | 12000000 | 0.042605
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 183921.5025 | 1.5327 | 12000000 | 0.078373
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 180265.2036 | 3.4012 | 5300000 | 0.042605
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 173359.9974 | 1.4447 | 12000000 | 0.047589
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 173359.9974 | 1.4447 | 12000000 | 0.047589
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 6 MVAR switched shunt at REDHLSW4 138 kV | Current Study |  |  | 170376.8563 | 7.0042 | 2432500 | 0.075819
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 166347.5655 | 1.3862 | 12000000 | 0.046991
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 162090.2357 | 1.3508 | 12000000 | 0.047589
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 161619.428 | 1.3468 | 12000000 | 0.047589
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514774 HENESEY4 138 520535 BULFTTP4 138 1 | Current Study | 2.53 | (395.00, 395.00) | 157072.458 | 5.1737 | 3036000 | 0.028256
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 154077.8376 | 1.284 | 12000000 | 0.047589
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 134658.1261 | 1.1222 | 12000000 | 0.05427
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 128945.8811 | 1.0745 | 12000000 | 0.047589
GEN-2024-308 | 04 SOUTHEAST | TBD | NRIS | Add 0.33 MVAR switched shunt at TWNLAKE4 138 kV | Current Study |  |  | 126819.6722 | 5.2136 | 2432500 | 0.040781
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 112500.5597 | 0.75312 | 14938000 | 0.080619
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 108907.8405 | 0.75312 | 14460953.1406 | 0.080619
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 101158.4022 | 0.84299 | 12000000 | 0.02867
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 98594.0186 | 1.8603 | 5300000 | 0.046991
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 94600.1405 | 1.7849 | 5300000 | 0.046991
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 86189.5319 | 1.6262 | 5300000 | 0.078373
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 80867.9258 | 0.6739 | 12000000 | 0.02867
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 76526.704 | 1.1595 | 6600000 | 0.047589
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 67798.053 | 0.41871 | 16192000 | 0.047183
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 65554.958 | 1.2369 | 5300000 | 0.042605
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 64393.5843 | 1.215 | 5300000 | 0.042605
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 63160.5485 | 1.1917 | 5300000 | 0.034071
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 62333.3344 | 1.1761 | 5300000 | 0.036361
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 60730.2451 | 1.1459 | 5300000 | 0.042605
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 60300.6897 | 0.51716 | 11660000 | 0.029611
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 59309.4901 | 0.49425 | 12000000 | 0.016936
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 52476.242 | 2.3853 | 2200000 | 0.042275
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 46617.2523 | 0.87957 | 5300000 | 0.047589
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 40579.0866 | 0.76564 | 5300000 | 0.036361
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 35673.2729 | 1.0134 | 3520000 | 0.04119
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 34113.9072 | 1.0497 | 3250000 | 0.047589
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 33294.7567 | 1.121 | 2970000 | 0.045631
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 32937.0097 | 1.0134 | 3250000 | 0.04119
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 29540.0999 | 1.3351 | 2212500 | 0.043134
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 29525.3267 | 0.24604 | 12000000 | 0.034402
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 29329.5298 | 2.2219 | 1320000 | 0.046991
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 28328.7135 | 0.5345 | 5300000 | 0.047184
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 24662.7828 | 1.121 | 2200000 | 0.045631
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 22490.2876 | 0.42435 | 5300000 | 0.0031702
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 21334.6247 | 1.546 | 1380000 | 0.05427
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 21138.462 | 0.65041 | 3250000 | 0.029611
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at SLKHILLS 4 138 kV | Current Study |  |  | 20139.7884 | 0.82795 | 2432500 | 0.031284
GEN-2024-308 | 04 SOUTHEAST | TBD | NRIS | Add 0.09 MVAR switched shunt at GRAY CO3 115 kV | Current Study |  |  | 18676.5551 | 0.84414 | 2212500 | 0.015403
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 0.5 MVAR switched shunt at RKY_RDG4 138 kV | Current Study |  |  | 18419.6998 | 0.75723 | 2432500 | 0.047184
GEN-2024-308 | 04 SOUTHEAST | TBD | NRIS | Add 16 MVAR switched shunt at UNDERWOOD 2 345 kV | Current Study |  |  | 18279.5682 | 0.3449 | 5300000 | 0.027207
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 16694.5204 | 0.68631 | 2432500 | 0.031284
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 15903.2175 | 0.65378 | 2432500 | 0.029611
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 15682.7492 | 0.64472 | 2432500 | 0.029611
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 14816.8341 | 0.64421 | 2300000 | 0.045632
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CHILD4WT 138 kV | Current Study |  |  | 14679.1767 | 0.60346 | 2432500 | 0.031284
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at SEGNTP 3 115 kV | Current Study |  |  | 12482.9557 | 0.5642 | 2212500 | 0.047184
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 7293.0571 | 0.32963 | 2212500 | 0.034402
GEN-2024-308 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 6908.769 | 0.41871 | 1650000 | 0.047183
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 9347338.9637 | 0.61714 | 1514620000 | 0.050608
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 9096135.6691 | 0.84713 | 1073760000 | 0.19348
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 8158016.2 | 0.6348 | 1285130000 | 0.26674
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 8118477.773 | 0.63843 | 1271630000 | 0.17531
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 4623974.5109 | 0.49275 | 938400000 | 0.11146
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 4181499.564 | 0.57695 | 724760000 | 0.18249
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 4137210.346 | 0.44088 | 938400000 | 0.17649
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 2979933.9781 | 0.61717 | 482840000 | 0.20913
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 2929022.4696 | 0.62407 | 469340000 | 0.14211
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527799 EDDY_NORTH 6 230 528095 7-RIVERS 6 230 1 | Current Study | 24.1 | (386.00, 386.00) | 2830679.2115 | 6.1819 | 45790000 | 0.12849
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528095 7-RIVERS 6 230 528179 PECOS 6 230 1 | Current Study | 20.61 | (386.00, 386.00) | 2315203.953 | 5.9123 | 39159000 | 0.12181
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 2161623.4889 | 0.5898 | 366500000 | 0.051689
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 527796 EDDY_TR 1 13 527799 EDDY_NORTH 6 230 527802 EDDY_CNTY 7 345 M2 | Current Study |  | (516.00, 558.00) | 1578668.8939 | 6.3147 | 25000000 | 0.27926
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524875 OASIS 6 230 787680 G24-357-TAP 230 1 | Current Study | 26.02 | (901.00, 901.00) | 601141.6709 | 1.216 | 49438000 | 0.088602
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3 | Current Study | 39.39 | (478.00, 544.00) | 599596.6255 | 0.5674 | 105675000 | 0.025855
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 594590.2792 | 0.70366 | 84500000 | 0.057612
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 487522.3704 | 0.57695 | 84500000 | 0.18249
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 482707.1502 | 0.57125 | 84500000 | 0.096835
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 480819.6854 | 0.24301 | 197860000 | 0.032027
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524885 SN_JUAN_SS 6 230 787680 G24-357-TAP 230 1 | Current Study | 20.18 | (901.00, 901.00) | 466219.7893 | 1.216 | 38342000 | 0.088602
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 461770.6352 | 0.36994 | 124824000 | 0.064539
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 436241.3558 | 0.21976 | 198511000 | 0.031325
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 345311.4759 | 0.2092 | 165062000 | 0.0351
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 319721.4584 | 0.39235 | 81488000 | 0.069472
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 302648.0324 | 1.1421 | 26500000 | 0.047865
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528013 PHANTOM 3 115 528228 WOOD_DRAW 3 115 1 | Current Study | 7.71 | (260.00, 260.00) | 288037.8214 | 3.7359 | 7710000 | 0.014556
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 278814.2823 | 0.50492 | 55220000 | 0.065675
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 246832.8237 | 0.5678 | 43472000 | 0.046146
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528016 SAND_DUNES 3 115 528018 RED_BLUFF 3 115 1 | Current Study | 7.69 | (394.00, 394.00) | 233386.4019 | 3.0349 | 7690000 | 0.043131
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 136455.0738 | 0.73363 | 18600000 | 0.25991
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1 | Current Study | 9.6 | (901.00, 901.00) | 128121.7307 | 0.70242 | 18240000 | 0.062739
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 118695.5587 | 0.63815 | 18600000 | 0.17531
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 117998.3593 | 0.6344 | 18600000 | 0.26674
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 117047.94 | 0.62929 | 18600000 | 0.17531
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 116077.5087 | 0.62407 | 18600000 | 0.14211
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 114788.2008 | 0.61714 | 18600000 | 0.050608
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528018 RED_BLUFF 3 115 528235 WOLFCAMP_TP3 115 1 | Current Study | 7.81 | (598.00, 598.00) | 112367.6115 | 1.4388 | 7810000 | 0.051439
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 107312.6164 | 0.57695 | 18600000 | 0.18249
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 100227.5283 | 0.53886 | 18600000 | 0.27668
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 91318.1609 | 0.36527 | 25000000 | 0.014399
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 91318.1609 | 0.36527 | 25000000 | 0.016522
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 77579.061 | 0.41709 | 18600000 | 0.11146
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 528184 SENDERO +3 115 528187 SENDERO_345 345 M2 | Current Study |  | (435.00, 435.00) | 74597.8986 | 0.44404 | 16800000 | 0.0046815
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 72573.175 | 0.39018 | 18600000 | 0.18249
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 72573.175 | 0.39018 | 18600000 | 0.18249
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | Current Study | 0.78 | (598.00, 598.00) | 57741.083 | 1.0911 | 5292000 | 0.0411
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | Current Study | 0.2 | (598.00, 598.00) | 48881.3401 | 1.0911 | 4480000 | 0.0411
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 34092.4468 | 0.21055 | 16192000 | 0.062954
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 31584.6012 | 0.21144 | 14938000 | 0.060055
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 30575.9431 | 0.21144 | 14460953.1406 | 0.060055
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 26878.5955 | 0.50714 | 5300000 | 0.19367
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 23379.2701 | 0.35661 | 6556000 | 0.065674
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1 | Current Study | 2.13 | (598.00, 598.00) | 17094.5566 | 0.80256 | 2130000 | 0.023339
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 10062.0856 | 0.72914 | 1380000 | 0.17227
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 9833.6216 | 0.081947 | 12000000 | 0.030402
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 9608.9673 | 0.6963 | 1380000 | 0.19367
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 6555.9906 | 0.29632 | 2212500 | 0.032492
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 6389.6314 | 0.46302 | 1380000 | 0.19367
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 4899.3445 | 0.22144 | 2212500 | 0.062954
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 4238.765 | 0.30716 | 1380000 | 0.0058602
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 3474.0944 | 0.21055 | 1650000 | 0.062954
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 2429.0049 | 0.10979 | 2212500 | 0.030402
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528184 SENDERO +3 115 528193 BLACKRIVER 3 115 1 | Current Study | 0.25 | (598.00, 598.00) | 2006.4034 | 0.80256 | 250000 | 0.023339
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 1541.4166 | 0.1117 | 1380000 | 0.030402
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 28042016.8912 | 1.8514 | 1514620000 | 0.050608
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 27288407.0073 | 2.5414 | 1073760000 | 0.19348
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 24474048.5999 | 1.9044 | 1285130000 | 0.26674
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 24355433.3189 | 1.9153 | 1271630000 | 0.17531
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 13871923.5326 | 1.4783 | 938400000 | 0.11146
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 12544498.6921 | 1.7308 | 724760000 | 0.18249
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 12411631.038 | 1.3226 | 938400000 | 0.17649
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 8939801.9343 | 1.8515 | 482840000 | 0.20913
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 8787067.4087 | 1.8722 | 469340000 | 0.14211
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527799 EDDY_NORTH 6 230 528095 7-RIVERS 6 230 1 | Current Study | 24.1 | (386.00, 386.00) | 8492037.6344 | 18.5456 | 45790000 | 0.12849
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528095 7-RIVERS 6 230 528179 PECOS 6 230 1 | Current Study | 20.61 | (386.00, 386.00) | 6945611.8589 | 17.7369 | 39159000 | 0.12181
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 6484870.4668 | 1.7694 | 366500000 | 0.051689
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 527796 EDDY_TR 1 13 527799 EDDY_NORTH 6 230 527802 EDDY_CNTY 7 345 M2 | Current Study |  | (516.00, 558.00) | 4736006.6818 | 18.944 | 25000000 | 0.27926
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524875 OASIS 6 230 787680 G24-357-TAP 230 1 | Current Study | 26.02 | (901.00, 901.00) | 1803425.0126 | 3.6479 | 49438000 | 0.088602
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3 | Current Study | 39.39 | (478.00, 544.00) | 1798789.8766 | 1.7022 | 105675000 | 0.025855
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1783770.8375 | 2.111 | 84500000 | 0.057612
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1462567.1112 | 1.7308 | 84500000 | 0.18249
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 1448121.4506 | 1.7138 | 84500000 | 0.096835
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 1442459.0563 | 0.72903 | 197860000 | 0.032027
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524885 SN_JUAN_SS 6 230 787680 G24-357-TAP 230 1 | Current Study | 20.18 | (901.00, 901.00) | 1398659.368 | 3.6479 | 38342000 | 0.088602
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1385311.9057 | 1.1098 | 124824000 | 0.064539
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1308724.0673 | 0.65927 | 198511000 | 0.031325
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 1035934.4277 | 0.6276 | 165062000 | 0.0351
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 959164.3753 | 1.1771 | 81488000 | 0.069472
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 907944.0972 | 3.4262 | 26500000 | 0.047865
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528013 PHANTOM 3 115 528228 WOOD_DRAW 3 115 1 | Current Study | 7.71 | (260.00, 260.00) | 864113.4642 | 11.2077 | 7710000 | 0.014556
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 836442.8468 | 1.5147 | 55220000 | 0.065675
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 740498.4712 | 1.7034 | 43472000 | 0.046146
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528016 SAND_DUNES 3 115 528018 RED_BLUFF 3 115 1 | Current Study | 7.69 | (394.00, 394.00) | 700159.2058 | 9.1048 | 7690000 | 0.043131
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 409365.2215 | 2.2009 | 18600000 | 0.25991
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1 | Current Study | 9.6 | (901.00, 901.00) | 384365.1922 | 2.1073 | 18240000 | 0.062739
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 356086.6762 | 1.9144 | 18600000 | 0.17531
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 353995.078 | 1.9032 | 18600000 | 0.26674
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 351143.82 | 1.8879 | 18600000 | 0.17531
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 348232.5261 | 1.8722 | 18600000 | 0.14211
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 344364.6025 | 1.8514 | 18600000 | 0.050608
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528018 RED_BLUFF 3 115 528235 WOLFCAMP_TP3 115 1 | Current Study | 7.81 | (598.00, 598.00) | 337102.8344 | 4.3163 | 7810000 | 0.051439
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 321937.8493 | 1.7308 | 18600000 | 0.18249
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 300682.585 | 1.6166 | 18600000 | 0.27668
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 273954.4828 | 1.0958 | 25000000 | 0.016522
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 273954.4828 | 1.0958 | 25000000 | 0.014399
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 232737.1829 | 1.2513 | 18600000 | 0.11146
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 528184 SENDERO +3 115 528187 SENDERO_345 345 M2 | Current Study |  | (435.00, 435.00) | 223793.6958 | 1.3321 | 16800000 | 0.0046815
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 217719.5251 | 1.1705 | 18600000 | 0.18249
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 217719.5251 | 1.1705 | 18600000 | 0.18249
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | Current Study | 0.78 | (598.00, 598.00) | 173223.249 | 3.2733 | 5292000 | 0.0411
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | Current Study | 0.2 | (598.00, 598.00) | 146644.0203 | 3.2733 | 4480000 | 0.0411
GEN-2024-311 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 145715.1243 | 0.80506 | 18100000 | 0.010963
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 102277.3405 | 0.63165 | 16192000 | 0.062954
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 94753.8036 | 0.63431 | 14938000 | 0.060055
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 91727.8293 | 0.63431 | 14460953.1406 | 0.060055
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 80635.7865 | 1.5214 | 5300000 | 0.19367
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 70137.8103 | 1.0698 | 6556000 | 0.065674
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1 | Current Study | 2.13 | (598.00, 598.00) | 51283.6698 | 2.4077 | 2130000 | 0.023339
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 30186.2568 | 2.1874 | 1380000 | 0.17227
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 29500.8649 | 0.24584 | 12000000 | 0.030402
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 28826.9018 | 2.0889 | 1380000 | 0.19367
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 19667.9717 | 0.88895 | 2212500 | 0.032492
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 19168.8943 | 1.3891 | 1380000 | 0.19367
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 14698.0336 | 0.66432 | 2212500 | 0.062954
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 12716.295 | 0.92147 | 1380000 | 0.0058602
GEN-2024-311 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 11225.0907 | 0.81341 | 1380000 | 0.045767
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 10422.2833 | 0.63165 | 1650000 | 0.062954
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 7287.0148 | 0.32936 | 2212500 | 0.030402
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528184 SENDERO +3 115 528193 BLACKRIVER 3 115 1 | Current Study | 0.25 | (598.00, 598.00) | 6019.2101 | 2.4077 | 250000 | 0.023339
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 4624.2497 | 0.33509 | 1380000 | 0.030402
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 338110 5HILLTOP% 161 505507 SWPINEY5 161 1 | Current Study | 47.56 | (246.00, 246.00) | 46399927.4931 | 65.0405 | 71340000 | 0.074161
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505507 SWPINEY5 161 505508 DARDANE5 161 1 | Current Study | 15.98 | (246.00, 246.00) | 15590219.5404 | 65.0405 | 23970000 | 0.074161
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Rebuild 3-winding transformer 515336 VBI 2 69 515339 VBI 5 161 515769 VBI 1 13 2 | Current Study |  | (83.00, 83.00) | 1343160.2939 | 22.1096 | 6075000 | 0.032669
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 341962.9914 | 0.22761 | 150244000 | 0.020632
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 270962.0173 | 0.28379 | 95480000 | 0.045906
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 240369.5315 | 0.28379 | 84700000 | 0.045906
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 200961.917 | 0.092049 | 218320000 | 0.011361
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 179207.3206 | 0.12463 | 143796000 | 0.024899
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 160214.7582 | 1.3351 | 12000000 | 0.079433
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 131691.4196 | 0.14012 | 93984000 | 0.034779
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 114679.4793 | 0.95566 | 12000000 | 0.12893
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 105966.3127 | 0.31543 | 33594000 | 0.051483
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 104923.1989 | 0.093022 | 112794000 | 0.031693
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 104885.8742 | 0.87405 | 12000000 | 0.12893
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1 | Current Study | 11.3 | (1793.00, 1793.00) | 103175.896 | 0.41503 | 24860000 | 0.051206
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 102322.0417 | 1.5503 | 6600000 | 0.12893
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at PHILL 7 345 kV | Current Study |  |  | 100783.2067 | 1.9016 | 5300000 | 0.03392
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 91377.5885 | 0.76148 | 12000000 | 0.12893
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 87777.7212 | 0.73148 | 12000000 | 0.12893
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 80381.9338 | 0.66985 | 12000000 | 0.12893
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 79286.5543 | 0.31339 | 25300000 | 0.025676
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 67780.3549 | 0.56484 | 12000000 | 0.079433
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 64572.9355 | 0.97838 | 6600000 | 0.12893
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 64572.9355 | 0.97838 | 6600000 | 0.12893
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 64543.7187 | 1.2178 | 5300000 | 0.079433
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 61363.3792 | 0.92975 | 6600000 | 0.12893
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 51238.6279 | 1.5766 | 3250000 | 0.12893
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 51238.6279 | 1.5766 | 3250000 | 0.12893
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 46836.5117 | 0.3903 | 12000000 | 0.079433
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 36998.6307 | 0.69809 | 5300000 | 0.079433
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 31733.9037 | 0.59875 | 5300000 | 0.12893
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 31011.2401 | 0.95419 | 3250000 | 0.12893
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 30204.8852 | 0.92938 | 3250000 | 0.12893
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 29515.5139 | 0.24596 | 12000000 | 0.033293
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 28481.7743 | 0.23735 | 12000000 | 0.03237
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 28453.7342 | 0.8755 | 3250000 | 0.12893
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 28254.8571 | 0.23546 | 12000000 | 0.03255
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 23813.9093 | 0.19845 | 12000000 | 0.018707
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 23222.4636 | 0.71454 | 3250000 | 0.12893
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 21796.9537 | 0.18164 | 12000000 | 0.023814
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 21796.9537 | 0.18164 | 12000000 | 0.023814
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 20545.2058 | 0.17121 | 12000000 | 0.018707
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 19541.4335 | 0.12982 | 15053000 | 0.006868
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 19485.7643 | 0.16238 | 12000000 | 0.02277
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 19444.8152 | 1.409 | 1380000 | 0.12893
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 18547.8255 | 0.28103 | 6600000 | 0.045906
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 18424.6972 | 1.3351 | 1380000 | 0.079433
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 17795.2781 | 0.15262 | 11660000 | 0.034779
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 14980.2382 | 0.28265 | 5300000 | 0.034779
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 14111.9409 | 0.63783 | 2212500 | 0.12893
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 13682.2027 | 0.6184 | 2212500 | 0.12893
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 13541.8746 | 0.25551 | 5300000 | 0.03237
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 12684.5854 | 0.23933 | 5300000 | 0.045906
GEN-2024-312 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 11905.321 | 0.22463 | 5300000 | 0.15341
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 10044.7111 | 0.30907 | 3250000 | 0.03237
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 9989.3831 | 0.28379 | 3520000 | 0.045906
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 9752.1557 | 0.184 | 5300000 | 0.034779
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 9515.0788 | 0.6895 | 1380000 | 0.079433
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 9223.147 | 0.28379 | 3250000 | 0.045906
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 8650.4765 | 0.26617 | 3250000 | 0.03255
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 8574.169 | 0.26382 | 3250000 | 0.03255
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 8526.1526 | 0.26234 | 3250000 | 0.03237
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 8303.9797 | 0.25551 | 3250000 | 0.03237
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 7845.9283 | 0.56855 | 1380000 | 0.079433
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 6238.0946 | 0.19194 | 3250000 | 0.034779
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 5146.051 | 0.097095 | 5300000 | 0.002887
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 4693.1406 | 0.19293 | 2432500 | 0.034779
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 4628.079 | 0.19026 | 2432500 | 0.034779
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 3515.0645 | 0.15887 | 2212500 | 0.06775
GEN-2024-312 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 2244.4322 | 0.16264 | 1380000 | 0.031693
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1 | Current Study | 56.1 | (1793.00, 1793.00) | 10117655.8611 | 8.1977 | 123420000 | 0.078385
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1 | Current Study | 30.63 | (1793.00, 1793.00) | 5706387.2696 | 8.4682 | 67386000 | 0.092436
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 4315650.5605 | 3.8261 | 112794000 | 0.21726
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 776060 G23-204-TAP 345 1 | Current Study | 17.82 | (1793.00, 1793.00) | 2920229.3733 | 7.4488 | 39204000 | 0.18706
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 2875829.6141 | 2.4521 | 117282000 | 0.034399
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 2840288.2387 | 1.8905 | 150244000 | 0.02856
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 2633255.8915 | 4.1633 | 63250000 | 0.15071
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 1785421.9766 | 1.9852 | 89936000 | 0.015459
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1712700.6138 | 1.7938 | 95480000 | 0.048361
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | Current Study | 7.74 | (1793.00, 1793.00) | 1704477.5326 | 10.0099 | 17028000 | 0.18706
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1682447.4896 | 0.77063 | 218320000 | 0.015853
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1546008.9936 | 1.5394 | 100427000 | 0.013181
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 1519331.1897 | 1.7938 | 84700000 | 0.048361
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1424569.1745 | 0.99069 | 143796000 | 0.032988
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 1304137.0461 | 2.3645 | 55154000 | 0.027798
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 1172863.4287 | 2.6159 | 44836000 | 0.040942
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1158326.0137 | 0.58351 | 198511000 | 0.020794
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | Current Study | 6.93 | (1793.00, 1793.00) | 1135644.7563 | 7.4488 | 15246000 | 0.18706
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 1052509.6865 | 0.53195 | 197860000 | 0.017526
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 507454 TURK 4 138 507456 TURK 3 115 507458 TURK1 1 13 M2 | Current Study |  | (257.00, 257.00) | 1007492.6213 | 9.6874 | 10400000 | 0.02371
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1006266.2126 | 0.80615 | 124824000 | 0.03516
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 965261.0342 | 2.0541 | 46992000 | 0.055462
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 904517.9047 | 3.5231 | 25674000 | 0.082453
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 896200.709 | 0.95357 | 93984000 | 0.039447
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 764550 G20-087-TAP 345 1 | Current Study | 14.38 | (1793.00, 1793.00) | 805674.4341 | 2.5467 | 31636000 | 0.057898
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 761248.4152 | 0.46119 | 165062000 | 0.019345
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 736341.1869 | 2.1919 | 33594000 | 0.059625
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 667775.3913 | 0.81948 | 81488000 | 0.036275
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | Current Study | 13.6 | (1793.00, 1793.00) | 650504.6647 | 2.1741 | 29920000 | 0.027369
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 644395.2123 | 3.5984 | 17908000 | 0.085608
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 624237.916 | 2.3645 | 26400000 | 0.027798
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | Current Study | 13.16 | (395.00, 395.00) | 560808.9901 | 3.5512 | 15792000 | 0.023382
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 545412.5215 | 1.1879 | 45914000 | 0.040034
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515178 PARKLN 4 138 515977 LKKONWA4 138 1 | Current Study | 13.56 | (472.00, 472.00) | 518927.8741 | 3.1891 | 16272000 | 0.025718
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 514736.7231 | 4.2895 | 12000000 | 0.042534
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 495757.5179 | 1.9595 | 25300000 | 0.026757
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | Current Study | 8.91 | (2390.00, 2390.00) | 492675.4767 | 2.5134 | 19602000 | 0.057898
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1 | Current Study | 11.3 | (1793.00, 1793.00) | 399478.5362 | 1.6069 | 24860000 | 0.033043
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | Current Study | 5.97 | (2390.00, 2390.00) | 330109.1578 | 2.5134 | 13134000 | 0.057898
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 301414.3912 | 2.4465 | 12320000 | 0.034997
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 297664.045 | 1.1879 | 25058000 | 0.040034
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 | Current Study | 6.08 | (395.00, 395.00) | 259097.1626 | 3.5512 | 7296000 | 0.023382
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 504122 MCNAB 3 115 507456 TURK 3 115 1 | Current Study | 2.65 | (394.00, 394.00) | 256716.8699 | 9.6874 | 2650000 | 0.04742
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 252939.9352 | 2.1078 | 12000000 | 0.034997
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 248319.1106 | 2.0693 | 12000000 | 0.048361
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 232035.491 | 1.9336 | 12000000 | 0.043622
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 228955.4979 | 1.521 | 15053000 | 0.013411
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 216629.3581 | 1.8052 | 12000000 | 0.044383
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 211334.0656 | 3.202 | 6600000 | 0.044383
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 207365.5551 | 3.9126 | 5300000 | 0.042534
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 206070.8754 | 1.7173 | 12000000 | 0.015459
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 204093.3271 | 1.7008 | 12000000 | 0.02672
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 202916.2757 | 1.691 | 12000000 | 0.057357
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 192195.5619 | 1.6016 | 12000000 | 0.034997
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 192195.5619 | 1.6016 | 12000000 | 0.034997
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 185901.8856 | 1.5492 | 12000000 | 0.035213
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 185493.5275 | 1.5458 | 12000000 | 0.043622
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 183576.7347 | 1.5298 | 12000000 | 0.034399
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 182275.0587 | 1.519 | 12000000 | 0.034997
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 180898.4779 | 1.5075 | 12000000 | 0.048361
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 179179.3796 | 1.4932 | 12000000 | 0.034997
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 176079.4227 | 1.4673 | 12000000 | 0.02672
GEN-2024-316 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 173492.822 | 0.95852 | 18100000 | 0.0097899
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 143837.6288 | 1.1986 | 12000000 | 0.035213
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 126738.7963 | 1.9203 | 6600000 | 0.044383
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 121102.3532 | 1.0386 | 11660000 | 0.039447
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 119848.0621 | 2.2613 | 5300000 | 0.043622
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 117237.4326 | 1.7763 | 6600000 | 0.048361
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 108805.7283 | 2.0529 | 5300000 | 0.034399
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 105827.321 | 3.2562 | 3250000 | 0.044383
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 105827.321 | 3.2562 | 3250000 | 0.044383
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 105812.9307 | 1.6032 | 6600000 | 0.035213
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 105812.9307 | 1.6032 | 6600000 | 0.035213
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 105775.7926 | 4.5989 | 2300000 | 0.21609
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 104398.191 | 1.9698 | 5300000 | 0.034399
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 101945.384 | 1.9235 | 5300000 | 0.039447
GEN-2024-316 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 99502.2427 | 1.8774 | 5300000 | 0.2137
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 98891.8344 | 1.4984 | 6600000 | 0.039447
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 95090.8871 | 1.7942 | 5300000 | 0.057357
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 92317.0799 | 6.6896 | 1380000 | 0.21726
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 90200.3409 | 2.7754 | 3250000 | 0.035213
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 90200.3409 | 2.7754 | 3250000 | 0.035213
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 88388.455 | 1.6677 | 5300000 | 0.035213
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 86373.8422 | 0.57822 | 14938000 | 0.041058
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 83615.483 | 0.57822 | 14460953.1406 | 0.041058
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 75435.2241 | 0.46588 | 16192000 | 0.034824
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 73316.8529 | 2.2559 | 3250000 | 0.035213
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 66366.5855 | 1.2522 | 5300000 | 0.039447
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 65562.3038 | 2.0173 | 3250000 | 0.035213
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 65542.6219 | 1.2367 | 5300000 | 0.044383
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 64050.0456 | 1.9708 | 3250000 | 0.044383
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 63141.0365 | 1.7938 | 3520000 | 0.048361
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 62931.0612 | 1.1874 | 5300000 | 0.022518
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 62384.6151 | 1.9195 | 3250000 | 0.044383
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 61006.6665 | 2.0541 | 2970000 | 0.055462
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 60787.1504 | 2.499 | 2432500 | 0.034399
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 59194.7232 | 4.2895 | 1380000 | 0.042534
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 58297.8353 | 1.7938 | 3250000 | 0.048361
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 56149.3509 | 1.7277 | 3250000 | 0.035213
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 55654.0471 | 1.7124 | 3250000 | 0.035213
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 55650.6007 | 1.7123 | 3250000 | 0.035213
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 54200.4677 | 1.6677 | 3250000 | 0.035213
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 52261.8469 | 1.6081 | 3250000 | 0.048361
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 52019.8263 | 2.3645 | 2200000 | 0.027798
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 46625.9275 | 1.4346 | 3250000 | 0.035213
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 45190.1233 | 2.0541 | 2200000 | 0.055462
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 43040.4066 | 0.81208 | 5300000 | 0.0040244
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 42452.2585 | 1.3062 | 3250000 | 0.039447
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CHILD4WT 138 kV | Current Study |  |  | 40955.6231 | 1.6837 | 2432500 | 0.057898
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 40160.9642 | 2.9102 | 1380000 | 0.044383
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 32367.2438 | 2.4521 | 1320000 | 0.034399
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 31976.3708 | 1.3145 | 2432500 | 0.039747
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 31938.3454 | 1.313 | 2432500 | 0.039447
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 31495.5801 | 1.2948 | 2432500 | 0.039447
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 30762.4912 | 2.2292 | 1380000 | 0.035213
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 25308.5439 | 1.834 | 1380000 | 0.035213
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 25207.3373 | 1.8266 | 1380000 | 0.042534
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 | Current Study | 0.55 | (395.00, 395.00) | 23438.0657 | 3.5512 | 660000 | 0.023382
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 22211.8207 | 1.0039 | 2212500 | 0.033823
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 21535.4243 | 0.97335 | 2212500 | 0.033823
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 20821.9777 | 1.5088 | 1380000 | 0.039447
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 19428.5122 | 0.36658 | 5300000 | 0.034997
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 10840.6398 | 0.48997 | 2212500 | 0.034824
GEN-2024-316 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 7687.0133 | 0.46588 | 1650000 | 0.034824
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 36476168.5731 | 2.4083 | 1514620000 | 0.049372
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 24582863.1275 | 1.9332 | 1271630000 | 0.13271
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 24252389.0334 | 1.8872 | 1285130000 | 0.19824
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 13705579.4738 | 1.8911 | 724760000 | 0.14953
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 10900383.7175 | 2.2576 | 482840000 | 0.19124
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 10536060.7992 | 2.2449 | 469340000 | 0.1278
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 8881888.7359 | 0.94649 | 938400000 | 0.053524
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 8470171.7924 | 0.90262 | 938400000 | 0.090335
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 3486520.5147 | 0.3247 | 1073760000 | 0.01854
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 2551458.6087 | 7.162 | 35625000 | 0.049797
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1911522.0619 | 0.96293 | 198511000 | 0.034315
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 1695788.391 | 0.85706 | 197860000 | 0.028238
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1597937.8905 | 1.8911 | 84500000 | 0.14953
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1591388.0646 | 1.2749 | 124824000 | 0.055605
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 1548660.557 | 1.8327 | 84500000 | 0.077669
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 1220497.3415 | 0.73942 | 165062000 | 0.031015
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 1096881.9371 | 1.3461 | 81488000 | 0.059585
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 1030776.9724 | 7.3627 | 14000000 | 0.024898
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 898763.9969 | 2.0675 | 43472000 | 0.042007
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 447938.5823 | 2.4083 | 18600000 | 0.049372
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 417545.3421 | 2.2449 | 18600000 | 0.1278
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 393809.7631 | 2.1173 | 18600000 | 0.14145
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 359411.7957 | 1.9323 | 18600000 | 0.13271
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 354422.7833 | 1.9055 | 18600000 | 0.13271
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 351735.441 | 1.8911 | 18600000 | 0.14953
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 350788.972 | 1.886 | 18600000 | 0.19824
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 288955.5277 | 0.34196 | 84500000 | 0.0069994
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 237870.9845 | 1.2789 | 18600000 | 0.14953
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 237870.9845 | 1.2789 | 18600000 | 0.14953
GEN-2024-317 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 191387.8485 | 1.0574 | 18100000 | 0.0108
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 139916.3023 | 0.93665 | 14938000 | 0.066509
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 135448.0581 | 0.93665 | 14460953.1406 | 0.066509
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 130897.3084 | 0.70375 | 18600000 | 0.090335
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 120373.2476 | 0.74341 | 16192000 | 0.055569
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 112401.4786 | 0.60431 | 18600000 | 0.053524
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 86234.0748 | 1.6271 | 5300000 | 0.15534
GEN-2024-317 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 44850.2368 | 3.25 | 1380000 | 0.13715
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 37961.4511 | 0.31635 | 12000000 | 0.029341
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 30828.2627 | 2.2339 | 1380000 | 0.15534
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 30292.4478 | 2.1951 | 1380000 | 0.12966
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 26459.5321 | 1.1959 | 2212500 | 0.032784
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 20499.7301 | 1.4855 | 1380000 | 0.15534
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 17298.5549 | 0.78186 | 2212500 | 0.055569
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 12266.2956 | 0.74341 | 1650000 | 0.055569
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 11423.9704 | 0.82782 | 1380000 | 0.0039485
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 9376.8659 | 0.42381 | 2212500 | 0.029341
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 5950.4435 | 0.43119 | 1380000 | 0.029341
GEN-2024-318 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 509817 T.NO.--4 138 509900 46ST-TP-4 138 1 | Current Study | 5.18 | (211.00, 211.00) | 4968063.5257 | 79.9238 | 6216000 | 0.098658
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 512623 CATSAGD4 138 512638 CATSAGR5 161 512833 CATTER1 1 13 M2 | Current Study |  | (150.00, 188.00) | 4428467.1998 | 35.7134 | 12400000 | 0.022394
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 512636 CATSAGR4 138 512638 CATSAGR5 161 512834 CATTER2 1 13 M2 | Current Study |  | (150.00, 188.00) | 4428467.1998 | 35.7134 | 12400000 | 0.02275
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 2154991.2109 | 1.8374 | 117282000 | 0.03886
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 1998232.5977 | 1.33 | 150244000 | 0.030291
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1761725.4044 | 1.7542 | 100427000 | 0.022643
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 1749701.4134 | 1.9455 | 89936000 | 0.022839
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1656064.6732 | 1.7345 | 95480000 | 0.070495
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 1499970.8679 | 2.6959 | 55638000 | 0.061109
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 1469089.6294 | 1.7345 | 84700000 | 0.070495
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 1369286.2535 | 2.0747 | 66000000 | 0.047926
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1290962.9818 | 0.59132 | 218320000 | 0.018338
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1064663.5249 | 1.1328 | 93984000 | 0.070646
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 1019763.9002 | 3.0356 | 33594000 | 0.12448
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1016643.387 | 0.707 | 143796000 | 0.03549
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 950573.506 | 1.7235 | 55154000 | 0.030546
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 885092.3641 | 1.9741 | 44836000 | 0.046578
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 68 MVAR SVC at TONTITN7 345 kV | Current Study |  |  | 754944.8904 | 6.2912 | 12000000 | 0.043134
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 38 MVAR SVC at WROGERS 5 161 kV | Current Study |  |  | 641690.0729 | 9.7226 | 6600000 | 0.043134
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 549902.6161 | 0.27701 | 198511000 | 0.014882
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 524634.6871 | 2.004 | 26180000 | 0.022757
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 37 MVAR switched shunt at CHAMSPR7 345 kV | Current Study |  |  | 499048.818 | 9.416 | 5300000 | 0.043134
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 455001.2793 | 1.7235 | 26400000 | 0.030546
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 441222.7393 | 0.96098 | 45914000 | 0.048824
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 424905.6752 | 0.3404 | 124824000 | 0.022382
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 422272.9772 | 0.25583 | 165062000 | 0.016177
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 406954.3166 | 0.86601 | 46992000 | 0.035251
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 401137.7846 | 1.5855 | 25300000 | 0.032639
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR SVC at JAY 4 138 kV | Current Study |  |  | 393584.2554 | 7.4261 | 5300000 | 0.041522
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 260671.5692 | 1.7317 | 15053000 | 0.023019
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510422 COFFEYT4 138 787350 G24-346-TAP 138 1 | Current Study | 6.1 | (525.00, 525.00) | 256019.5305 | 3.4975 | 7320000 | 0.036236
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 247098.8953 | 0.46221 | 53460000 | 0.016768
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 240801.4854 | 0.96098 | 25058000 | 0.048824
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 225420.6118 | 1.8297 | 12320000 | 0.039458
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at CENTRTN5 161 kV | Current Study |  |  | 218003.1808 | 6.7078 | 3250000 | 0.043134
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 215616.1058 | 1.7968 | 12000000 | 0.061109
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 212176.8517 | 1.7681 | 12000000 | 0.039458
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 212176.8517 | 1.7681 | 12000000 | 0.039458
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510422 COFFEYT4 138 533002 DEARING4 138 1 | Current Study | 5.02 | (717.00, 717.00) | 202570.6138 | 3.3627 | 6024000 | 0.029422
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 201947.9944 | 1.6829 | 12000000 | 0.022839
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 199918.1541 | 1.666 | 12000000 | 0.039458
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 197414.7646 | 1.6451 | 12000000 | 0.056373
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 189168.0015 | 1.5764 | 12000000 | 0.039458
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 174916.3433 | 1.4576 | 12000000 | 0.070495
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 172367.5627 | 1.4364 | 12000000 | 0.061109
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 165433.3391 | 1.3786 | 12000000 | 0.070495
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 152745.474 | 1.2729 | 12000000 | 0.056373
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 143866.4988 | 1.2338 | 11660000 | 0.070646
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 143738.6718 | 1.1978 | 12000000 | 0.039458
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 143738.6718 | 1.1978 | 12000000 | 0.039458
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 137562.6816 | 1.1464 | 12000000 | 0.03886
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 136319.354 | 1.136 | 12000000 | 0.039458
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 134004.1663 | 1.1167 | 12000000 | 0.039458
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 127751.1771 | 1.0646 | 12000000 | 0.039458
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 4.8 MVAR switched shunt at COWSKIN2 69 kV | Current Study |  |  | 122793.1267 | 8.8981 | 1380000 | 0.041522
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 121108.2485 | 2.2851 | 5300000 | 0.070646
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 117480.7174 | 1.78 | 6600000 | 0.070646
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 114723.1881 | 0.95603 | 12000000 | 0.026245
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 113360.5061 | 1.7176 | 6600000 | 0.070495
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 112365.9114 | 1.7025 | 6600000 | 0.056373
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 112365.9114 | 1.7025 | 6600000 | 0.056373
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 111367.3271 | 2.1013 | 5300000 | 0.061109
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 106780.8359 | 1.6179 | 6600000 | 0.056373
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 95786.436 | 2.9473 | 3250000 | 0.056373
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 95786.436 | 2.9473 | 3250000 | 0.056373
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 93862.3402 | 1.771 | 5300000 | 0.056373
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 91723.6352 | 1.7306 | 5300000 | 0.012929
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 83988.6971 | 0.69991 | 12000000 | 0.024659
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 81533.2497 | 1.5384 | 5300000 | 0.03886
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 78841.6367 | 1.4876 | 5300000 | 0.070646
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 78230.4747 | 1.476 | 5300000 | 0.03886
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 77857.3558 | 2.3956 | 3250000 | 0.056373
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 77525.5849 | 1.4627 | 5300000 | 0.070495
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 69622.5685 | 2.1422 | 3250000 | 0.056373
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 69202.7373 | 1.3057 | 5300000 | 0.070646
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 61053.0755 | 1.7345 | 3520000 | 0.070495
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 59626.6728 | 1.8347 | 3250000 | 0.056373
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 59100.6948 | 1.8185 | 3250000 | 0.056373
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 59097.035 | 1.8184 | 3250000 | 0.056373
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 57557.0954 | 1.771 | 3250000 | 0.056373
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 56369.9833 | 1.7345 | 3250000 | 0.070495
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 53963.8817 | 1.6604 | 3250000 | 0.056373
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 52560.7118 | 1.6173 | 3250000 | 0.056373
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 50533.5991 | 1.5549 | 3250000 | 0.070495
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 50432.0889 | 1.5518 | 3250000 | 0.070646
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 49513.465 | 1.5235 | 3250000 | 0.056373
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 45550.6708 | 1.8726 | 2432500 | 0.03886
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | Current Study | 0 | (424.00, 424.00) | 42856.1342 | 35.7134 | 120000 | 0.068284
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | Current Study | 0 | (275.00, 275.00) | 42856.1342 | 35.7134 | 120000 | 0.0455
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 42557.8792 | 0.80298 | 5300000 | 0.022957
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 42110.1839 | 0.26007 | 16192000 | 0.029306
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 41521.0023 | 0.27796 | 14938000 | 0.029754
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 40195.024 | 0.27796 | 14460953.1406 | 0.029754
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 37941.8559 | 1.5598 | 2432500 | 0.070646
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 37916.7733 | 1.7235 | 2200000 | 0.030546
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 37415.8632 | 1.5382 | 2432500 | 0.070646
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 32667.6082 | 2.3672 | 1380000 | 0.056373
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 26875.8986 | 1.9475 | 1380000 | 0.056373
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 25720.4273 | 0.86601 | 2970000 | 0.035251
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 24735.9238 | 1.7925 | 1380000 | 0.070646
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 24254.2624 | 1.8374 | 1320000 | 0.03886
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 19052.1684 | 0.86601 | 2200000 | 0.035251
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 18840.7855 | 1.3653 | 1380000 | 0.047926
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 18175.6367 | 1.3171 | 1380000 | 0.030281
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 14530.1406 | 0.27415 | 5300000 | 0.039458
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 11446.1065 | 0.49766 | 2300000 | 0.035251
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 4291.1193 | 0.26007 | 1650000 | 0.029306
GEN-2024-319 | 03 CENTRAL | TBD | ERIS | Rebuild line 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | Current Study | 17.54 | (1793.00, 1793.00) | 2324855.4617 | 6.0248 | 38588000 | 0.029094
GEN-2024-319 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 1952510.7724 | 0.20807 | 938400000 | 0.031392
GEN-2024-319 | 03 CENTRAL | TBD | ERIS | Rebuild line 645458 S3458 3 345 778170 G24-040-TAP 345 1 | Current Study | 13.15 | (1793.00, 1793.00) | 1254455.1694 | 4.3362 | 28930000 | 0.067577
GEN-2024-319 | 03 CENTRAL | TBD | ERIS | Rebuild line 640139 COOPER 3 345 778170 G24-040-TAP 345 1 | Current Study | 12.59 | (1793.00, 1793.00) | 1201033.5044 | 4.3362 | 27698000 | 0.067577
GEN-2024-319 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 1190757.5732 | 0.59984 | 198511000 | 0.020378
GEN-2024-319 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 823539.9713 | 0.87626 | 93984000 | 0.054646
GEN-2024-319 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 649411.2375 | 0.45162 | 143796000 | 0.02267
GEN-2024-319 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 244911.7567 | 0.53341 | 45914000 | 0.027101
GEN-2024-319 | 03 CENTRAL | TBD | ERIS | Rebuild line 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 | Current Study | 3.23 | (1793.00, 1793.00) | 241045.0028 | 3.3921 | 7106000 | 0.038429
GEN-2024-319 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 133662.9089 | 0.53341 | 25058000 | 0.027101
GEN-2024-319 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 111283.8089 | 0.95441 | 11660000 | 0.054646
GEN-2024-319 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 52953.0439 | 0.28469 | 18600000 | 0.050183
GEN-2024-319 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 52953.0439 | 0.28469 | 18600000 | 0.050183
GEN-2024-319 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 30538.492 | 0.20443 | 14938000 | 0.021884
GEN-2024-319 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 30173.934 | 0.16223 | 18600000 | 0.031392
GEN-2024-319 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 29563.2415 | 0.20443 | 14460953.1406 | 0.021884
GEN-2024-319 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 11140.9033 | 0.67521 | 1650000 | 0.041138
GEN-2024-320 | 03 CENTRAL | TBD | ERIS | Rebuild line 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | Current Study | 17.54 | (1793.00, 1793.00) | 2606649.1369 | 6.7551 | 38588000 | 0.032621
GEN-2024-320 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 2000036.2707 | 0.21313 | 938400000 | 0.032156
GEN-2024-320 | 03 CENTRAL | TBD | ERIS | Rebuild line 645458 S3458 3 345 778170 G24-040-TAP 345 1 | Current Study | 13.15 | (1793.00, 1793.00) | 1426707.1123 | 4.9316 | 28930000 | 0.076856
GEN-2024-320 | 03 CENTRAL | TBD | ERIS | Rebuild line 640139 COOPER 3 345 778170 G24-040-TAP 345 1 | Current Study | 12.59 | (1793.00, 1793.00) | 1365950.0033 | 4.9316 | 27698000 | 0.076856
GEN-2024-320 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 1280718.0836 | 0.64516 | 198511000 | 0.021917
GEN-2024-320 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 789166.8961 | 0.54881 | 143796000 | 0.027549
GEN-2024-320 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 783989.9347 | 0.83417 | 93984000 | 0.052022
GEN-2024-320 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 268318.0719 | 0.58439 | 45914000 | 0.029691
GEN-2024-320 | 03 CENTRAL | TBD | ERIS | Rebuild line 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 | Current Study | 3.23 | (1793.00, 1793.00) | 234964.4201 | 3.3066 | 7106000 | 0.037459
GEN-2024-320 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 146437.1269 | 0.58439 | 25058000 | 0.029691
GEN-2024-320 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 105939.4676 | 0.90857 | 11660000 | 0.052022
GEN-2024-320 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 55210.8484 | 0.29683 | 18600000 | 0.052323
GEN-2024-320 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 55210.8484 | 0.29683 | 18600000 | 0.052323
GEN-2024-320 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 32975.936 | 0.22075 | 14938000 | 0.023631
GEN-2024-320 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 31922.8455 | 0.22075 | 14460953.1406 | 0.023631
GEN-2024-320 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 30908.389 | 0.16617 | 18600000 | 0.032156
GEN-2024-320 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 12667.879 | 0.76775 | 1650000 | 0.046776
GEN-2024-321 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 515055 MAUD 4 138 787770 G24-360-TAP 138 1 | Current Study | 5.11 | (395.00, 395.00) | 810077.9982 | 13.2107 | 6132000 | 0.022865
GEN-2024-321 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 437419.974 | 2.4167 | 18100000 | 0.01502
GEN-2024-321 | 04 SOUTHEAST | TBD | ERIS | Add 10 MVAR switched shunt at G20-007-TAP 345 kV | Current Study |  |  | 265108.0538 | 5.002 | 5300000 | 0.039792
GEN-2024-321 | 04 SOUTHEAST | TBD | ERIS | Add 38 MVAR switched shunt at FRNT2WD7 345 kV | Current Study |  |  | 221348.1645 | 4.1764 | 5300000 | 0.049883
GEN-2024-321 | 04 SOUTHEAST | TBD | ERIS | Add 19 MVAR switched shunt at RANCHRD7 345 kV | Current Study |  |  | 202653.9651 | 3.8237 | 5300000 | 0.049883
GEN-2024-321 | 04 SOUTHEAST | TBD | ERIS | Add 0.42 MVAR switched shunt at TWNLKSW4 138 kV | Current Study |  |  | 162829.7724 | 6.6939 | 2432500 | 0.054136
GEN-2024-321 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 57945.6061 | 1.0933 | 5300000 | 0.04771
GEN-2024-321 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 38567.612 | 0.72769 | 5300000 | 0.050404
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Rebuild line 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Current Study | 75.83 | (1793.00, 1793.00) | 4617523.3693 | 2.7679 | 166826000 | 0.082753
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 2463541.8265 | 1.241 | 198511000 | 0.11186
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Rebuild line 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | Current Study | 84.86 | (1793.00, 1793.00) | 2043216.5243 | 1.0944 | 186692000 | 0.050898
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Rebuild line 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Current Study | 38.26 | (1793.00, 1793.00) | 1389062.9413 | 1.6503 | 84172000 | 0.10644
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Rebuild line 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Current Study | 37.4 | (1793.00, 1793.00) | 1372838.9006 | 1.6685 | 82280000 | 0.10644
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 1145039.4968 | 0.86128 | 132946000 | 0.071407
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 911391.3092 | 0.45911 | 198511000 | 0.065445
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | Current Study | 19.2 | (2390.00, 2390.00) | 773763.5297 | 1.8318 | 42240000 | 0.12482
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Current Study | 26.47 | (1793.00, 1793.00) | 764252.8078 | 1.3124 | 58234000 | 0.059922
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 741300.1641 | 0.37466 | 197860000 | 0.049377
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Rebuild line 530605 REDLIN 3 115 786630 G24-322-TAP 115 1 | Current Study | 0.86 | (115.00, 115.00) | 660203.4835 | 76.7678 | 860000 | 0.61163
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Rebuild line 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | Current Study | 10.74 | (394.00, 394.00) | 655345.1267 | 6.1019 | 10740000 | 0.014772
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Rebuild line 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | Current Study | 16.04 | (2390.00, 2390.00) | 646414.9488 | 1.8318 | 35288000 | 0.12482
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Rebuild line 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 | Current Study | 21.74 | (386.00, 386.00) | 615934.953 | 1.4912 | 41306000 | 0.021769
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Rebuild line 539650 BELOIT 3 115 539657 CONCORD3 115 1 | Current Study | 22.17 | (176.00, 176.00) | 590161.9812 | 2.662 | 22170000 | 0.040433
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 551599.957 | 0.3836 | 143796000 | 0.051092
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 535368.1385 | 0.32434 | 165062000 | 0.054419
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 500258.655 | 0.22914 | 218320000 | 0.018855
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Rebuild line 523961 POTTER_CO 7 345 784950 G24-266_TAP 345 1 | Current Study | 18.24 | (1793.00, 1793.00) | 433713.5603 | 1.0808 | 40128000 | 0.050898
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 427297.0325 | 0.045535 | 938400000 | 0.018229
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | Current Study | 13 | (2390.00, 2390.00) | 421423.6553 | 1.4735 | 28600000 | 0.12425
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR SVC at GEN-2021-076 345 kV | Current Study |  |  | 396963.5407 | 3.308 | 12000000 | 0.10644
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | Current Study | 16.71 | (1793.00, 1793.00) | 260813.2415 | 0.70946 | 36762000 | 0.052953
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 173413.0034 | 0.32438 | 53460000 | 0.031223
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 128602.5099 | 0.28009 | 45914000 | 0.037759
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Rebuild line 533413 CIRCLE 3 115 533416 RENO 3 115 2 | Current Study | 5.95 | (217.00, 217.00) | 124848.7218 | 2.0983 | 5950000 | 0.031957
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 114265.6863 | 0.95221 | 12000000 | 0.35327
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add 525 MVAR SVC at SD.LS-LR-MB3 345 kV | Current Study |  |  | 111830.9049 | 0.93192 | 12000000 | 0.098492
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 85493.6851 | 1.6131 | 5300000 | 0.14743
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 83979.0763 | 1.5845 | 5300000 | 0.14743
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 70186.0368 | 0.28009 | 25058000 | 0.037759
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 68513.6391 | 0.45865 | 14938000 | 0.13027
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MINGO 7 345 kV | Current Study |  |  | 68063.3992 | 1.2842 | 5300000 | 0.1317
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 66325.6476 | 0.45865 | 14460953.1406 | 0.13027
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add 7 MVAR switched shunt at G19-030-TAP 345 kV | Current Study |  |  | 63176.2414 | 1.192 | 5300000 | 0.12482
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 53339.4209 | 0.32942 | 16192000 | 0.098495
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add 66 MVAR switched shunt at GEN-2021-021 345 kV | Current Study |  |  | 47911.8273 | 0.904 | 5300000 | 0.0012496
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add 15 MVAR switched shunt at GEN-2022-075 345 kV | Current Study |  |  | 33757.3392 | 0.63693 | 5300000 | 0.054567
GEN-2024-322 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 32876.4162 | 0.62031 | 5300000 | 0.070339
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add 248 MVAR switched shunt at GEN-2022-015 345 kV | Current Study |  |  | 27368.9932 | 0.5164 | 5300000 | 0.098492
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 22286.683 | 0.4205 | 5300000 | 0.098492
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add 40 MVAR switched shunt at SEGNTP 3 115 kV | Current Study |  |  | 21618.4186 | 0.9771 | 2212500 | 0.21682
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 18243.8669 | 0.098085 | 18600000 | 0.045875
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 18243.8669 | 0.098085 | 18600000 | 0.045875
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add 12 MVAR switched shunt at BEELER 3 115 kV | Current Study |  |  | 16122.4509 | 0.7287 | 2212500 | 0.072123
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at IRS7 115 KV 115 kV | Current Study |  |  | 14092.0968 | 0.63693 | 2212500 | 0.054567
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add 0.8 MVAR switched shunt at HARBNGR7 345 kV | Current Study |  |  | 13812.1447 | 0.26061 | 5300000 | 0.072123
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 13156.6904 | 0.070735 | 18600000 | 0.036319
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add 20 MVAR switched shunt at MED-LDG3 115 kV | Current Study |  |  | 13145.3626 | 0.59414 | 2212500 | 0.054567
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 9817.9948 | 0.44375 | 2212500 | 0.038039
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 8958.6235 | 0.40491 | 2212500 | 0.054567
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 8685.8146 | 0.39258 | 2212500 | 0.054567
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add 24 MVAR switched shunt at NESSCTY3 115 kV | Current Study |  |  | 7908.879 | 0.35746 | 2212500 | 0.072123
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 7665.0746 | 0.34644 | 2212500 | 0.098492
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add 0.04 MVAR switched shunt at ELLIS 2 69 kV | Current Study |  |  | 5841.0364 | 0.42326 | 1380000 | 0.098492
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 5762.4059 | 0.26045 | 2212500 | 0.072123
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 5435.4029 | 0.32942 | 1650000 | 0.098495
GEN-2024-322 | 03 CENTRAL | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 3656.7517 | 0.26498 | 1380000 | 0.072123
GEN-2024-323 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2 | Current Study |  | (478.00, 478.00) | 6635683.5189 | 36.6612 | 18100000 | 0.078573
GEN-2024-323 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 4042993.0053 | 3.5844 | 112794000 | 0.17113
GEN-2024-323 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 514808 JOHNCO 4 138 514809 JOHNCO 7 345 514810 JOHNCO11 13 M2 | Current Study |  | (478.00, 478.00) | 796146.2828 | 4.3986 | 18100000 | 0.0078229
GEN-2024-323 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | Current Study | 13.16 | (395.00, 395.00) | 708431.22 | 4.486 | 15792000 | 0.024835
GEN-2024-323 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 521049 SCLMNJC4 138 784980 G24-267-TAP 138 1 | Current Study | 6.96 | (472.00, 472.00) | 525650.9484 | 6.2937 | 8352000 | 0.039779
GEN-2024-323 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1 | Current Study | 11.3 | (1793.00, 1793.00) | 451379.9434 | 1.8157 | 24860000 | 0.031393
GEN-2024-323 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 | Current Study | 6.08 | (395.00, 395.00) | 327299.5302 | 4.486 | 7296000 | 0.024835
GEN-2024-323 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | Current Study | 0.64 | (717.00, 717.00) | 281558.2841 | 36.6612 | 768000 | 0.15715
GEN-2024-323 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 240035.0563 | 4.529 | 5300000 | 0.27307
GEN-2024-323 | 04 SOUTHEAST | TBD | ERIS | Add 10 MVAR switched shunt at G20-007-TAP 345 kV | Current Study |  |  | 165662.8516 | 3.1257 | 5300000 | 0.034357
GEN-2024-323 | 04 SOUTHEAST | TBD | ERIS | Add 38 MVAR switched shunt at FRNT2WD7 345 kV | Current Study |  |  | 139683.917 | 2.6355 | 5300000 | 0.043495
GEN-2024-323 | 04 SOUTHEAST | TBD | ERIS | Add 19 MVAR switched shunt at RANCHRD7 345 kV | Current Study |  |  | 127886.7602 | 2.413 | 5300000 | 0.043495
GEN-2024-323 | 04 SOUTHEAST | TBD | ERIS | Add 0.42 MVAR switched shunt at TWNLKSW4 138 kV | Current Study |  |  | 88144.4412 | 3.6236 | 2432500 | 0.040492
GEN-2024-323 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 | Current Study | 0.55 | (395.00, 395.00) | 29607.6878 | 4.486 | 660000 | 0.024835
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 19801473.7707 | 1.3074 | 1514620000 | 0.050254
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 17292421.5358 | 1.6105 | 1073760000 | 0.17242
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 17080684.2471 | 1.3291 | 1285130000 | 0.26179
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 16906846.2788 | 1.3295 | 1271630000 | 0.17113
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1 | Current Study | 52.45 | (1046.00, 1046.00) | 12531839.694 | 12.5752 | 99655000 | 0.51873
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 10412349.7306 | 1.1096 | 938400000 | 0.11765
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 9188556.6338 | 0.97917 | 938400000 | 0.18374
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 8929599.5402 | 1.2321 | 724760000 | 0.18267
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527597 TWEEDY 3 115 527798 EDDY_NTH 3 115 1 | Current Study | 44.83 | (394.00, 394.00) | 8347684.9463 | 18.6208 | 44830000 | 0.2238
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 6286804.2026 | 1.302 | 482840000 | 0.20681
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 6255456.1467 | 1.7068 | 366500000 | 0.070116
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 6146407.935 | 1.3096 | 469340000 | 0.13979
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3 | Current Study | 39.39 | (478.00, 544.00) | 4254674.4294 | 4.0262 | 105675000 | 0.086
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528095 7-RIVERS 6 230 528179 PECOS 6 230 1 | Current Study | 20.61 | (386.00, 386.00) | 3945109.6356 | 10.0746 | 39159000 | 0.097298
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527799 EDDY_NORTH 6 230 528095 7-RIVERS 6 230 1 | Current Study | 24.1 | (386.00, 386.00) | 3855453.0569 | 8.4199 | 45790000 | 0.082031
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524875 OASIS 6 230 787680 G24-357-TAP 230 1 | Current Study | 26.02 | (901.00, 901.00) | 3710986.8469 | 7.5063 | 49438000 | 0.25639
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527482 CHAVES_CNTY3 115 527546 SAMSON 3 115 1 | Current Study | 7.78 | (217.00, 217.00) | 3325709.4888 | 42.7469 | 7780000 | 0.48835
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Current Study | 54.58 | (637.00, 637.00) | 3123315.7356 | 3.0118 | 103702000 | 0.043711
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524885 SN_JUAN_SS 6 230 787680 G24-357-TAP 230 1 | Current Study | 20.18 | (901.00, 901.00) | 2878082.8044 | 7.5063 | 38342000 | 0.25639
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 527796 EDDY_TR 1 13 527799 EDDY_NORTH 6 230 527802 EDDY_CNTY 7 345 M2 | Current Study |  | (516.00, 558.00) | 2594314.65 | 10.3773 | 25000000 | 0.21512
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1210416.3712 | 1.4324 | 84500000 | 0.054975
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 1044589.945 | 0.52794 | 197860000 | 0.032615
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1041104.8639 | 1.2321 | 84500000 | 0.18267
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 1035667.7434 | 1.2256 | 84500000 | 0.09739
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 988722.6109 | 0.79209 | 124824000 | 0.064776
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 936500.0481 | 0.47176 | 198511000 | 0.031522
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1 | Current Study | 9.6 | (901.00, 901.00) | 802687.5905 | 4.4007 | 18240000 | 0.18425
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 749815.3024 | 0.45426 | 165062000 | 0.035727
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527522 ROSWELL_CTY3 115 527534 SW4J795_W 3 115 1 | Current Study | 3.33 | (217.00, 217.00) | 746675.0359 | 22.4227 | 3330000 | 0.19891
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 524872 OASIS_TR1 1 13 524874 OASIS 3 115 524875 OASIS 6 230 M2 | Current Study |  | (239.00, 239.00) | 745754.2309 | 5.404 | 13800000 | 0.017467
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 693037.5862 | 1.255 | 55220000 | 0.076521
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 683930.836 | 0.8393 | 81488000 | 0.069661
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 559248.8062 | 2.1104 | 26500000 | 0.04146
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 532107.6459 | 1.224 | 43472000 | 0.046631
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528013 PHANTOM 3 115 528228 WOOD_DRAW 3 115 1 | Current Study | 7.71 | (260.00, 260.00) | 528494.1756 | 6.8547 | 7710000 | 0.012519
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1 | Current Study | 2.49 | (394.00, 394.00) | 463656.8262 | 18.6208 | 2490000 | 0.2238
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528016 SAND_DUNES 3 115 528018 RED_BLUFF 3 115 1 | Current Study | 7.69 | (394.00, 394.00) | 424349.6635 | 5.5182 | 7690000 | 0.03676
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 289440.6438 | 1.1578 | 25000000 | 0.021393
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 289440.6438 | 1.1578 | 25000000 | 0.024548
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1 | Current Study | 18.95 | (901.00, 901.00) | 277310.7214 | 0.7702 | 36005000 | 0.028119
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 247185.2017 | 1.329 | 18600000 | 0.17113
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 247056.7192 | 1.3283 | 18600000 | 0.26179
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 243754.012 | 1.3105 | 18600000 | 0.17113
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 243582.8772 | 1.3096 | 18600000 | 0.13979
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 243168.1954 | 1.3074 | 18600000 | 0.050254
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 229166.2777 | 1.2321 | 18600000 | 0.18267
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528018 RED_BLUFF 3 115 528235 WOLFCAMP_TP3 115 1 | Current Study | 7.81 | (598.00, 598.00) | 206443.9474 | 2.6433 | 7810000 | 0.044299
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 185158.5019 | 0.99548 | 18600000 | 0.23959
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 528184 SENDERO +3 115 528187 SENDERO_345 345 M2 | Current Study |  | (435.00, 435.00) | 182304.4526 | 1.0851 | 16800000 | 0.0053629
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 174693.9376 | 0.93921 | 18600000 | 0.11765
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 155887.657 | 0.83811 | 18600000 | 0.18374
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 155887.657 | 0.83811 | 18600000 | 0.18374
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 131769.6652 | 0.70844 | 18600000 | 0.11765
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | Current Study | 0.78 | (598.00, 598.00) | 106566.5763 | 2.0137 | 5292000 | 0.035556
GEN-2024-324 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 102708.1027 | 0.56745 | 18100000 | 0.010867
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | Current Study | 0.2 | (598.00, 598.00) | 90215.0911 | 2.0137 | 4480000 | 0.035556
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 73805.1236 | 0.45581 | 16192000 | 0.063884
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 67709.1803 | 0.45327 | 14938000 | 0.060348
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 65546.8794 | 0.45327 | 14460953.1406 | 0.060348
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 58112.923 | 0.88641 | 6556000 | 0.076521
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 57669.1162 | 1.0881 | 5300000 | 0.19478
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1 | Current Study | 2.13 | (598.00, 598.00) | 35653.4939 | 1.6739 | 2130000 | 0.022818
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 21155.9091 | 0.1763 | 12000000 | 0.030659
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 21058.6015 | 1.526 | 1380000 | 0.169
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 20616.4288 | 1.4939 | 1380000 | 0.19478
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 14040.5138 | 0.6346 | 2212500 | 0.032619
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 13709.2132 | 0.99342 | 1380000 | 0.19478
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 10606.3587 | 0.47938 | 2212500 | 0.063884
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 9596.7193 | 0.69541 | 1380000 | 0.0062192
GEN-2024-324 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 8211.8759 | 0.59506 | 1380000 | 0.047083
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 7520.9025 | 0.45581 | 1650000 | 0.063884
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 5225.7255 | 0.23619 | 2212500 | 0.030659
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528184 SENDERO +3 115 528193 BLACKRIVER 3 115 1 | Current Study | 0.25 | (598.00, 598.00) | 4184.6824 | 1.6739 | 250000 | 0.022818
GEN-2024-324 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 3316.181 | 0.2403 | 1380000 | 0.030659
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 18567549.8859 | 1.2259 | 1514620000 | 0.050264
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 16266991.124 | 1.515 | 1073760000 | 0.17301
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 16021736.0899 | 1.2467 | 1285130000 | 0.26193
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 15861006.7763 | 1.2473 | 1271630000 | 0.17125
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1 | Current Study | 52.45 | (1046.00, 1046.00) | 11404229.4005 | 11.4437 | 99655000 | 0.50353
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 9746867.4034 | 1.0387 | 938400000 | 0.11747
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 8604279.7997 | 0.91691 | 938400000 | 0.18353
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527597 TWEEDY 3 115 527798 EDDY_NTH 3 115 1 | Current Study | 44.83 | (394.00, 394.00) | 8517253.1562 | 18.999 | 44830000 | 0.24357
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 8371185.428 | 1.155 | 724760000 | 0.18267
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 5895755.669 | 1.2211 | 482840000 | 0.20688
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 5824138.3034 | 1.5891 | 366500000 | 0.069633
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 5764945.005 | 1.2283 | 469340000 | 0.13985
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3 | Current Study | 39.39 | (478.00, 544.00) | 3918550.5611 | 3.7081 | 105675000 | 0.084486
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528095 7-RIVERS 6 230 528179 PECOS 6 230 1 | Current Study | 20.61 | (386.00, 386.00) | 3713598.5696 | 9.4834 | 39159000 | 0.097694
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527799 EDDY_NORTH 6 230 528095 7-RIVERS 6 230 1 | Current Study | 24.1 | (386.00, 386.00) | 3554334.4402 | 7.7623 | 45790000 | 0.080666
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524875 OASIS 6 230 787680 G24-357-TAP 230 1 | Current Study | 26.02 | (901.00, 901.00) | 3417116.5593 | 6.9119 | 49438000 | 0.25182
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Current Study | 54.58 | (637.00, 637.00) | 2893523.9988 | 2.7902 | 103702000 | 0.043195
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524885 SN_JUAN_SS 6 230 787680 G24-357-TAP 230 1 | Current Study | 20.18 | (901.00, 901.00) | 2650169.5683 | 6.9119 | 38342000 | 0.25182
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 527796 EDDY_TR 1 13 527799 EDDY_NORTH 6 230 527802 EDDY_CNTY 7 345 M2 | Current Study |  | (516.00, 558.00) | 2435945.5177 | 9.7438 | 25000000 | 0.21545
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527482 CHAVES_CNTY3 115 527546 SAMSON 3 115 1 | Current Study | 7.78 | (217.00, 217.00) | 1914451.5091 | 24.6073 | 7780000 | 0.29986
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1136306.2984 | 1.3447 | 84500000 | 0.05505
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527522 ROSWELL_CTY3 115 527534 SW4J795_W 3 115 1 | Current Study | 3.33 | (217.00, 217.00) | 1110311.5892 | 33.3427 | 3330000 | 0.31551
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 978818.3784 | 0.4947 | 197860000 | 0.032599
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 975999.1841 | 1.155 | 84500000 | 0.18267
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 970750.4923 | 1.1488 | 84500000 | 0.097371
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 926825.2313 | 0.74251 | 124824000 | 0.064769
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 877815.6393 | 0.4422 | 198511000 | 0.031517
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1 | Current Study | 9.6 | (901.00, 901.00) | 739022.5346 | 4.0517 | 18240000 | 0.18094
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 702613.1219 | 0.42567 | 165062000 | 0.03571
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 524872 OASIS_TR1 1 13 524874 OASIS 3 115 524875 OASIS 6 230 M2 | Current Study |  | (239.00, 239.00) | 687115.47 | 4.9791 | 13800000 | 0.017166
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 646989.3732 | 1.1717 | 55220000 | 0.076199
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 641122.8532 | 0.78677 | 81488000 | 0.069654
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 526988.1228 | 1.9886 | 26500000 | 0.041672
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528013 PHANTOM 3 115 528228 WOOD_DRAW 3 115 1 | Current Study | 7.71 | (260.00, 260.00) | 498730.2568 | 6.4686 | 7710000 | 0.012601
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 498684.0029 | 1.1471 | 43472000 | 0.046615
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1 | Current Study | 2.49 | (394.00, 394.00) | 473075.1809 | 18.999 | 2490000 | 0.24357
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528016 SAND_DUNES 3 115 528018 RED_BLUFF 3 115 1 | Current Study | 7.69 | (394.00, 394.00) | 399874.8188 | 5.1999 | 7690000 | 0.03695
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 268814.7263 | 1.0753 | 25000000 | 0.021193
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 268814.7263 | 1.0753 | 25000000 | 0.024319
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1 | Current Study | 18.95 | (901.00, 901.00) | 257539.0342 | 0.71529 | 36005000 | 0.027855
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 231894.5884 | 1.2467 | 18600000 | 0.17125
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 231739.9875 | 1.2459 | 18600000 | 0.26193
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 228675.6485 | 1.2294 | 18600000 | 0.17125
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 228465.4559 | 1.2283 | 18600000 | 0.13985
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 228015.2301 | 1.2259 | 18600000 | 0.050264
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 214835.3234 | 1.155 | 18600000 | 0.18267
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528018 RED_BLUFF 3 115 528235 WOLFCAMP_TP3 115 1 | Current Study | 7.81 | (598.00, 598.00) | 194396.7813 | 2.4891 | 7810000 | 0.044495
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 528184 SENDERO +3 115 528187 SENDERO_345 345 M2 | Current Study |  | (435.00, 435.00) | 175880.2797 | 1.0469 | 16800000 | 0.0055188
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 174246.706 | 0.93681 | 18600000 | 0.2405
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 163528.7605 | 0.87919 | 18600000 | 0.11747
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 145975.1593 | 0.78481 | 18600000 | 0.18353
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 145975.1593 | 0.78481 | 18600000 | 0.18353
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 123347.8982 | 0.66316 | 18600000 | 0.11747
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | Current Study | 0.78 | (598.00, 598.00) | 100316.0441 | 1.8956 | 5292000 | 0.035702
GEN-2024-325 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 96315.8707 | 0.53213 | 18100000 | 0.01087
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | Current Study | 0.2 | (598.00, 598.00) | 84923.6352 | 1.8956 | 4480000 | 0.035702
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 69161.5643 | 0.42713 | 16192000 | 0.063856
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 63467.7519 | 0.42487 | 14938000 | 0.060339
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 61440.9014 | 0.42487 | 14460953.1406 | 0.060339
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 54251.6659 | 0.82751 | 6556000 | 0.076199
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 54054.327 | 1.0199 | 5300000 | 0.19474
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1 | Current Study | 2.13 | (598.00, 598.00) | 34004.4082 | 1.5965 | 2130000 | 0.023213
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 19828.5513 | 0.16524 | 12000000 | 0.030651
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 19754.4599 | 1.4315 | 1380000 | 0.16911
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 19324.1592 | 1.4003 | 1380000 | 0.19474
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 13161.3827 | 0.59486 | 2212500 | 0.032615
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 12849.8986 | 0.93115 | 1380000 | 0.19474
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 9939.0439 | 0.44922 | 2212500 | 0.063856
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 8981.9712 | 0.65087 | 1380000 | 0.0062089
GEN-2024-325 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 7691.9497 | 0.55739 | 1380000 | 0.047043
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 7047.7138 | 0.42713 | 1650000 | 0.063856
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 4897.8546 | 0.22137 | 2212500 | 0.030651
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528184 SENDERO +3 115 528193 BLACKRIVER 3 115 1 | Current Study | 0.25 | (598.00, 598.00) | 3991.1277 | 1.5965 | 250000 | 0.023213
GEN-2024-325 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 3108.1181 | 0.22523 | 1380000 | 0.030651
GEN-2024-326 | 01 NORTH | TBD | NRIS | Rebuild line 652216 WATFORD4 230 659302 CHARL_CK-BE4 230 1 | Current Study | 34.26 | (637.00, 637.00) | 27145464.7227 | 41.7019 | 65094000 | 0.021912
GEN-2024-326 | 01 NORTH | TBD | NRIS | Rebuild line 652424 BELFELD3 345 659183 CHARL_CK-BE3 345 1 | Current Study | 40.74 | (1793.00, 1793.00) | 24198297.3407 | 26.9986 | 89628000 | 0.244
GEN-2024-326 | 01 NORTH | TBD | ERIS | Rebuild line 640404 WAYSIDE 4 230 652484 NUNDRWD4 230 1 | Current Study | 80.12 | (519.00, 519.00) | 13867819.8552 | 9.1099 | 152228000 | 0.046471
GEN-2024-326 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 652220 BELFELD29 13 652424 BELFELD3 345 652425 BELFELD4 230 M2 | Current Study |  | (250.00, 312.00) | 12479329.9902 | 49.9173 | 25000000 | 0.19772
GEN-2024-326 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 652221 BELFELD9 13 652424 BELFELD3 345 652425 BELFELD4 230 M2 | Current Study |  | (312.00, 390.00) | 12479329.9902 | 49.9173 | 25000000 | 0.15676
GEN-2024-326 | 01 NORTH | TBD | NRIS | Rebuild line 652296 WARD 4 230 652426 BISMARK4 230 1 | Current Study | 7.74 | (519.00, 519.00) | 8723756.6355 | 59.3211 | 14706000 | 0.042655
GEN-2024-326 | 01 NORTH | TBD | ERIS | Rebuild line 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Current Study | 36.8 | (1793.00, 1793.00) | 6064443.4307 | 7.4907 | 80960000 | 0.093218
GEN-2024-326 | 01 NORTH | TBD | NRIS | Rebuild line 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 | Current Study | 13.41 | (217.00, 217.00) | 4595388.0381 | 34.2684 | 13410000 | 0.012396
GEN-2024-326 | 01 NORTH | TBD | ERIS | Rebuild line 652884 NUNDRWD-LNX3 230 785430 G24-282-TAP 230 1 | Current Study | 35.21 | (519.00, 519.00) | 3531329.8081 | 5.2786 | 66899000 | 0.068478
GEN-2024-326 | 01 NORTH | TBD | ERIS | Rebuild line 652529 WATERTN3 345 659165 CROCKER_-BE3 345 1 | Current Study | 44.23 | (1793.00, 1793.00) | 3206494.6198 | 3.2953 | 97306000 | 0.070231
GEN-2024-326 | 01 NORTH | TBD | NRIS | Rebuild line 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 | Current Study | 7.43 | (217.00, 217.00) | 2546139.6811 | 34.2684 | 7430000 | 0.012396
GEN-2024-326 | 01 NORTH | TBD | NRIS | Rebuild line 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 | Current Study | 5 | (217.00, 217.00) | 1713418.3587 | 34.2684 | 5000000 | 0.012396
GEN-2024-326 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 659120 BROADLND-BE3 345 659204 BD.KU2A_-BE9 13 659205 BROADLND-BE4 230 M2 | Current Study |  | (471.00, 478.00) | 1506842.8848 | 6.0274 | 25000000 | 0.0454
GEN-2024-326 | 01 NORTH | TBD | ERIS | Rebuild line 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | Current Study | 4.2 | (519.00, 519.00) | 907542.3226 | 11.3727 | 7980000 | 0.040613
GEN-2024-326 | 01 NORTH | TBD | ERIS | Add 24 MVAR switched shunt at DH_CS_EA-TS4 230 kV | Current Study |  |  | 485264.2248 | 12.6866 | 3825000 | 0.032047
GEN-2024-326 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 652237 WATERT19 13 652529 WATERTN3 345 652530 WATERTN4 230 M2 | Current Study |  | (400.00, 478.00) | 398864.2557 | 1.5955 | 25000000 | 0.0050894
GEN-2024-326 | 01 NORTH | TBD | ERIS | Add 60 MVAR switched shunt at WAYSIDE 4 230 kV | Current Study |  |  | 257475.395 | 6.7314 | 3825000 | 0.096405
GEN-2024-326 | 01 NORTH | TBD | ERIS | Add 24 MVAR switched shunt at DAYTON__-ER7 115 kV | Current Study |  |  | 165731.0955 | 7.4907 | 2212500 | 0.093218
GEN-2024-326 | 01 NORTH | TBD | ERIS | Add 0.4 MVAR switched shunt at SHINDLER-ER7 115 kV | Current Study |  |  | 159141.1417 | 7.1928 | 2212500 | 0.098447
GEN-2024-326 | 01 NORTH | TBD | ERIS | Add 0.5 MVAR switched shunt at ORLAND-ER8 69 kV | Current Study |  |  | 103371.2596 | 7.4907 | 1380000 | 0.093218
GEN-2024-326 | 01 NORTH | TBD | ERIS | Add 14.4 MVAR switched shunt at SW145-ER8 69 kV | Current Study |  |  | 103371.2596 | 7.4907 | 1380000 | 0.093218
GEN-2024-326 | 01 NORTH | TBD | ERIS | Add 4.4 MVAR switched shunt at DESMET-ER7 115 kV | Current Study |  |  | 83677.9078 | 3.7821 | 2212500 | 0.096405
GEN-2024-326 | 01 NORTH | TBD | ERIS | Add 10 MVAR switched shunt at REDFIELD 115 kV | Current Study |  |  | 72907.8433 | 3.2953 | 2212500 | 0.070231
GEN-2024-326 | 01 NORTH | TBD | ERIS | Add 54 MVAR switched shunt at REDFELD-ER7 115 kV | Current Study |  |  | 72907.8433 | 3.2953 | 2212500 | 0.070231
GEN-2024-326 | 01 NORTH | TBD | ERIS | Add line and rebuild line 652568 GROTONSOUTH7 115 659187 GROTON__-BE7 115 M2 | Current Study | 0.1 | (598.00, 598.00) | 62805.8773 | 1.4471 | 4340000 | 0.0042219
GEN-2024-326 | 01 NORTH | TBD | ERIS | Add 5.5 MVAR switched shunt at LOOMIS-ER8 69 kV | Current Study |  |  | 52133.4525 | 3.7778 | 1380000 | 0.098447
GEN-2024-326 | 01 NORTH | TBD | ERIS | Add 4 MVAR switched shunt at MOS-RDFL-ER8 69 kV | Current Study |  |  | 45474.7226 | 3.2953 | 1380000 | 0.070231
GEN-2024-326 | 01 NORTH | TBD | ERIS | Rebuild line 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Current Study | 0 | (880.00, 880.00) | 16479.4658 | 7.4907 | 220000 | 0.093218
GEN-2024-326 | 01 NORTH | TBD | ERIS | Rebuild line 652484 NUNDRWD4 230 652884 NUNDRWD-LNX3 230 Z | Current Study | 0.14514 | (519.00, 519.00) | 14556.5615 | 5.2786 | 275765.6361 | 0.068478
GEN-2024-326 | 01 NORTH | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 9541.8848 | 0.69144 | 1380000 | 0.096405
GEN-2024-327 | 01 NORTH | TBD | ERIS | Rebuild line 640404 WAYSIDE 4 230 652484 NUNDRWD4 230 1 | Current Study | 80.12 | (519.00, 519.00) | 9134799.0503 | 6.0007 | 152228000 | 0.034437
GEN-2024-327 | 01 NORTH | TBD | ERIS | Rebuild line 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Current Study | 36.8 | (1793.00, 1793.00) | 5567486.4601 | 6.8768 | 80960000 | 0.096277
GEN-2024-327 | 01 NORTH | TBD | ERIS | Rebuild line 652529 WATERTN3 345 659165 CROCKER_-BE3 345 1 | Current Study | 44.23 | (1793.00, 1793.00) | 3223220.9925 | 3.3125 | 97306000 | 0.079422
GEN-2024-327 | 01 NORTH | TBD | ERIS | Rebuild line 652884 NUNDRWD-LNX3 230 785430 G24-282-TAP 230 1 | Current Study | 35.21 | (519.00, 519.00) | 1959021.256 | 2.9283 | 66899000 | 0.042737
GEN-2024-327 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 659120 BROADLND-BE3 345 659204 BD.KU2A_-BE9 13 659205 BROADLND-BE4 230 M2 | Current Study |  | (471.00, 478.00) | 1322865.3486 | 5.2915 | 25000000 | 0.044839
GEN-2024-327 | 01 NORTH | TBD | ERIS | Rebuild line 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | Current Study | 4.2 | (519.00, 519.00) | 893149.4528 | 11.1923 | 7980000 | 0.044964
GEN-2024-327 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 659160 GROTON__-BE3 345 659161 GRT.KU2A-BE9 13 659187 GROTON__-BE7 115 M2 | Current Study |  | (400.00, 400.00) | 304630.2575 | 1.8133 | 16800000 | 0.0057809
GEN-2024-327 | 01 NORTH | TBD | ERIS | Add 60 MVAR switched shunt at WAYSIDE 4 230 kV | Current Study |  |  | 164174.2325 | 4.2921 | 3825000 | 0.069155
GEN-2024-327 | 01 NORTH | TBD | ERIS | Add 24 MVAR switched shunt at DAYTON__-ER7 115 kV | Current Study |  |  | 152150.0927 | 6.8768 | 2212500 | 0.096277
GEN-2024-327 | 01 NORTH | TBD | ERIS | Add 0.4 MVAR switched shunt at SHINDLER-ER7 115 kV | Current Study |  |  | 145853.6227 | 6.5923 | 2212500 | 0.10151
GEN-2024-327 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 652237 WATERT19 13 652529 WATERTN3 345 652530 WATERTN4 230 M2 | Current Study |  | (400.00, 478.00) | 135117.8583 | 0.54047 | 25000000 | 0.0019396
GEN-2024-327 | 01 NORTH | TBD | ERIS | Add 0.5 MVAR switched shunt at ORLAND-ER8 69 kV | Current Study |  |  | 94900.3968 | 6.8768 | 1380000 | 0.096277
GEN-2024-327 | 01 NORTH | TBD | ERIS | Add 14.4 MVAR switched shunt at SW145-ER8 69 kV | Current Study |  |  | 94900.3968 | 6.8768 | 1380000 | 0.096277
GEN-2024-327 | 01 NORTH | TBD | ERIS | Add line and rebuild line 652568 GROTONSOUTH7 115 659187 GROTON__-BE7 115 M2 | Current Study | 0.1 | (598.00, 598.00) | 76441.6462 | 1.7613 | 4340000 | 0.0057809
GEN-2024-327 | 01 NORTH | TBD | ERIS | Add 4.4 MVAR switched shunt at DESMET-ER7 115 kV | Current Study |  |  | 74281.0758 | 3.3573 | 2212500 | 0.096277
GEN-2024-327 | 01 NORTH | TBD | ERIS | Add 10 MVAR switched shunt at REDFIELD 115 kV | Current Study |  |  | 73288.1601 | 3.3125 | 2212500 | 0.079422
GEN-2024-327 | 01 NORTH | TBD | ERIS | Add 54 MVAR switched shunt at REDFELD-ER7 115 kV | Current Study |  |  | 73288.1601 | 3.3125 | 2212500 | 0.079422
GEN-2024-327 | 01 NORTH | TBD | ERIS | Add 5.5 MVAR switched shunt at LOOMIS-ER8 69 kV | Current Study |  |  | 47780.5603 | 3.4624 | 1380000 | 0.10151
GEN-2024-327 | 01 NORTH | TBD | ERIS | Add 4 MVAR switched shunt at MOS-RDFL-ER8 69 kV | Current Study |  |  | 45711.9372 | 3.3125 | 1380000 | 0.079422
GEN-2024-327 | 01 NORTH | TBD | ERIS | Rebuild line 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Current Study | 0 | (880.00, 880.00) | 15129.0393 | 6.8768 | 220000 | 0.096277
GEN-2024-327 | 01 NORTH | TBD | ERIS | Rebuild line 652484 NUNDRWD4 230 652884 NUNDRWD-LNX3 230 Z | Current Study | 0.14514 | (519.00, 519.00) | 8075.3187 | 2.9283 | 275765.6361 | 0.042737
GEN-2024-327 | 01 NORTH | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 6084.1993 | 0.44088 | 1380000 | 0.069155
GEN-2024-328 | 01 NORTH | TBD | ERIS | Rebuild line 652497 MAURINE4 230 659351 BISON___-GE4 230 1 | Current Study | 38.56 | (386.00, 386.00) | 47324452.3156 | 64.5944 | 73264000 | 0.21962
GEN-2024-328 | 01 NORTH | TBD | ERIS | Rebuild line 652403 DAWSONC4 230 652411 MI CTYE4 230 1 | Current Study | 70.4 | (386.00, 386.00) | 40456623.3008 | 30.2457 | 133760000 | 0.20269
GEN-2024-328 | 01 NORTH | TBD | ERIS | Rebuild line 659265 LITTL_MS-BE4 230 659266 RHAME___-BE4 230 1 | Current Study | 24.19 | (519.00, 519.00) | 31174339.1914 | 67.8278 | 45961000 | 0.66688
GEN-2024-328 | 01 NORTH | TBD | ERIS | Rebuild line 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1 | Current Study | 40.93 | (519.00, 519.00) | 22496856.2295 | 28.9285 | 77767000 | 0.069643
GEN-2024-328 | 01 NORTH | TBD | ERIS | Rebuild line 652404 DAWSONC7 115 661056 LEWIS 7 115 1 | Current Study | 51.58 | (176.00, 176.00) | 20962027.2282 | 40.6398 | 51580000 | 0.037676
GEN-2024-328 | 01 NORTH | TBD | ERIS | Rebuild line 640404 WAYSIDE 4 230 652484 NUNDRWD4 230 1 | Current Study | 80.12 | (519.00, 519.00) | 16987019.7552 | 11.1589 | 152228000 | 0.051231
GEN-2024-328 | 01 NORTH | TBD | ERIS | Rebuild line 652403 DAWSONC4 230 652616 MINGUSVILLE4 230 1 | Current Study | 30.68 | (386.00, 386.00) | 16863023.4332 | 28.9285 | 58292000 | 0.069643
GEN-2024-328 | 01 NORTH | TBD | NRIS | Rebuild line 652424 BELFELD3 345 659183 CHARL_CK-BE3 345 1 | Current Study | 40.74 | (1793.00, 1793.00) | 16341160.9285 | 18.2322 | 89628000 | 0.1483
GEN-2024-328 | 01 NORTH | TBD | ERIS | Rebuild line 652425 BELFELD4 230 659247 MEDORA__-UM4 230 1 | Current Study | 22.59 | (519.00, 519.00) | 12416417.8408 | 28.9285 | 42921000 | 0.069643
GEN-2024-328 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 652220 BELFELD29 13 652424 BELFELD3 345 652425 BELFELD4 230 M2 | Current Study |  | (250.00, 312.00) | 7401028.7652 | 29.6041 | 25000000 | 0.10554
GEN-2024-328 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 652221 BELFELD9 13 652424 BELFELD3 345 652425 BELFELD4 230 M2 | Current Study |  | (312.00, 390.00) | 7401028.7652 | 29.6041 | 25000000 | 0.083672
GEN-2024-328 | 01 NORTH | TBD | ERIS | Rebuild line 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Current Study | 36.8 | (1793.00, 1793.00) | 6659044.4682 | 8.2251 | 80960000 | 0.092122
GEN-2024-328 | 01 NORTH | TBD | ERIS | Rebuild line 652884 NUNDRWD-LNX3 230 785430 G24-282-TAP 230 1 | Current Study | 35.21 | (519.00, 519.00) | 5620318.2218 | 8.4012 | 66899000 | 0.098089
GEN-2024-328 | 01 NORTH | TBD | NRIS | Rebuild line 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 | Current Study | 13.41 | (217.00, 217.00) | 4041582.8575 | 30.1386 | 13410000 | 0.0098117
GEN-2024-328 | 01 NORTH | TBD | ERIS | Rebuild line 652529 WATERTN3 345 659165 CROCKER_-BE3 345 1 | Current Study | 44.23 | (1793.00, 1793.00) | 3427634.249 | 3.5225 | 97306000 | 0.067567
GEN-2024-328 | 01 NORTH | TBD | ERIS | Rebuild line 652200 GLENDIVE7 115 661032 GLENDCT7 115 1 | Current Study | 3.8 | (176.00, 176.00) | 3110337.1112 | 81.851 | 3800000 | 0.093551
GEN-2024-328 | 01 NORTH | TBD | NRIS | Rebuild line 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 | Current Study | 7.43 | (217.00, 217.00) | 2239296.0948 | 30.1386 | 7430000 | 0.0098117
GEN-2024-328 | 01 NORTH | TBD | ERIS | Rebuild line 652200 GLENDIVE7 115 652404 DAWSONC7 115 1 | Current Study | 2.73 | (176.00, 176.00) | 2234531.6615 | 81.851 | 2730000 | 0.093551
GEN-2024-328 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 659120 BROADLND-BE3 345 659204 BD.KU2A_-BE9 13 659205 BROADLND-BE4 230 M2 | Current Study |  | (471.00, 478.00) | 1577458.8878 | 6.3098 | 25000000 | 0.042775
GEN-2024-328 | 01 NORTH | TBD | NRIS | Rebuild line 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 | Current Study | 5 | (217.00, 217.00) | 1506928.7314 | 30.1386 | 5000000 | 0.0098117
GEN-2024-328 | 01 NORTH | TBD | ERIS | Rebuild line 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | Current Study | 4.2 | (519.00, 519.00) | 958678.9984 | 12.0135 | 7980000 | 0.038611
GEN-2024-328 | 01 NORTH | TBD | ERIS | Add 24 MVAR switched shunt at DH_CS_EA-TS4 230 kV | Current Study |  |  | 592702.2573 | 15.4955 | 3825000 | 0.035228
GEN-2024-328 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 652237 WATERT19 13 652529 WATERTN3 345 652530 WATERTN4 230 M2 | Current Study |  | (400.00, 478.00) | 468844.2321 | 1.8754 | 25000000 | 0.0053841
GEN-2024-328 | 01 NORTH | TBD | ERIS | Add 60 MVAR switched shunt at WAYSIDE 4 230 kV | Current Study |  |  | 302032.1187 | 7.8963 | 3825000 | 0.10178
GEN-2024-328 | 01 NORTH | TBD | ERIS | Add 24 MVAR switched shunt at DAYTON__-ER7 115 kV | Current Study |  |  | 181980.5474 | 8.2251 | 2212500 | 0.092122
GEN-2024-328 | 01 NORTH | TBD | ERIS | Add 0.4 MVAR switched shunt at SHINDLER-ER7 115 kV | Current Study |  |  | 174854.8997 | 7.903 | 2212500 | 0.097351
GEN-2024-328 | 01 NORTH | TBD | ERIS | Add 14.4 MVAR switched shunt at SW145-ER8 69 kV | Current Study |  |  | 113506.5109 | 8.2251 | 1380000 | 0.092122
GEN-2024-328 | 01 NORTH | TBD | ERIS | Add 0.5 MVAR switched shunt at ORLAND-ER8 69 kV | Current Study |  |  | 113506.5109 | 8.2251 | 1380000 | 0.092122
GEN-2024-328 | 01 NORTH | TBD | ERIS | Add 4.4 MVAR switched shunt at DESMET-ER7 115 kV | Current Study |  |  | 98158.5669 | 4.4365 | 2212500 | 0.10178
GEN-2024-328 | 01 NORTH | TBD | ERIS | Add 10 MVAR switched shunt at REDFIELD 115 kV | Current Study |  |  | 77936.0175 | 3.5225 | 2212500 | 0.067567
GEN-2024-328 | 01 NORTH | TBD | ERIS | Add 54 MVAR switched shunt at REDFELD-ER7 115 kV | Current Study |  |  | 77936.0175 | 3.5225 | 2212500 | 0.067567
GEN-2024-328 | 01 NORTH | TBD | ERIS | Add 5.5 MVAR switched shunt at LOOMIS-ER8 69 kV | Current Study |  |  | 59886.7759 | 4.3396 | 1380000 | 0.10178
GEN-2024-328 | 01 NORTH | TBD | ERIS | Add 4 MVAR switched shunt at MOS-RDFL-ER8 69 kV | Current Study |  |  | 48610.9397 | 3.5225 | 1380000 | 0.067567
GEN-2024-328 | 01 NORTH | TBD | ERIS | Rebuild line 652484 NUNDRWD4 230 652884 NUNDRWD-LNX3 230 Z | Current Study | 0.14514 | (519.00, 519.00) | 23167.6203 | 8.4012 | 275765.6361 | 0.098089
GEN-2024-328 | 01 NORTH | TBD | ERIS | Rebuild line 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Current Study | 0 | (880.00, 880.00) | 18095.2295 | 8.2251 | 220000 | 0.092122
GEN-2024-328 | 01 NORTH | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 11193.1304 | 0.8111 | 1380000 | 0.10178
GEN-2024-329 | 01 NORTH | TBD | ERIS | Rebuild line 640404 WAYSIDE 4 230 652484 NUNDRWD4 230 1 | Current Study | 80.12 | (519.00, 519.00) | 9645241.5871 | 6.336 | 152228000 | 0.036362
GEN-2024-329 | 01 NORTH | TBD | ERIS | Rebuild line 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Current Study | 36.8 | (1793.00, 1793.00) | 5550219.6029 | 6.8555 | 80960000 | 0.095978
GEN-2024-329 | 01 NORTH | TBD | ERIS | Rebuild line 652529 WATERTN3 345 659165 CROCKER_-BE3 345 1 | Current Study | 44.23 | (1793.00, 1793.00) | 3192490.01 | 3.2809 | 97306000 | 0.078665
GEN-2024-329 | 01 NORTH | TBD | ERIS | Rebuild line 652884 NUNDRWD-LNX3 230 785430 G24-282-TAP 230 1 | Current Study | 35.21 | (519.00, 519.00) | 2153914.8136 | 3.2197 | 66899000 | 0.046989
GEN-2024-329 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 659120 BROADLND-BE3 345 659204 BD.KU2A_-BE9 13 659205 BROADLND-BE4 230 M2 | Current Study |  | (471.00, 478.00) | 1385250.1104 | 5.541 | 25000000 | 0.046954
GEN-2024-329 | 01 NORTH | TBD | ERIS | Rebuild line 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | Current Study | 4.2 | (519.00, 519.00) | 818219.0112 | 10.2534 | 7980000 | 0.041192
GEN-2024-329 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 659160 GROTON__-BE3 345 659161 GRT.KU2A-BE9 13 659187 GROTON__-BE7 115 M2 | Current Study |  | (400.00, 400.00) | 333938.0624 | 1.9877 | 16800000 | 0.006337
GEN-2024-329 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 652237 WATERT19 13 652529 WATERTN3 345 652530 WATERTN4 230 M2 | Current Study |  | (400.00, 478.00) | 177140.4124 | 0.70856 | 25000000 | 0.0025428
GEN-2024-329 | 01 NORTH | TBD | ERIS | Add 60 MVAR switched shunt at WAYSIDE 4 230 kV | Current Study |  |  | 174525.4287 | 4.5628 | 3825000 | 0.073515
GEN-2024-329 | 01 NORTH | TBD | ERIS | Add 24 MVAR switched shunt at DAYTON__-ER7 115 kV | Current Study |  |  | 151678.2184 | 6.8555 | 2212500 | 0.095978
GEN-2024-329 | 01 NORTH | TBD | ERIS | Add 0.4 MVAR switched shunt at SHINDLER-ER7 115 kV | Current Study |  |  | 145424.5795 | 6.5729 | 2212500 | 0.10121
GEN-2024-329 | 01 NORTH | TBD | ERIS | Add 14.4 MVAR switched shunt at SW145-ER8 69 kV | Current Study |  |  | 94606.0752 | 6.8555 | 1380000 | 0.095978
GEN-2024-329 | 01 NORTH | TBD | ERIS | Add 0.5 MVAR switched shunt at ORLAND-ER8 69 kV | Current Study |  |  | 94606.0752 | 6.8555 | 1380000 | 0.095978
GEN-2024-329 | 01 NORTH | TBD | ERIS | Add line and rebuild line 652568 GROTONSOUTH7 115 659187 GROTON__-BE7 115 M2 | Current Study | 0.1 | (598.00, 598.00) | 83795.9283 | 1.9308 | 4340000 | 0.006337
GEN-2024-329 | 01 NORTH | TBD | ERIS | Add 4.4 MVAR switched shunt at DESMET-ER7 115 kV | Current Study |  |  | 74050.7024 | 3.3469 | 2212500 | 0.095978
GEN-2024-329 | 01 NORTH | TBD | ERIS | Add 10 MVAR switched shunt at REDFIELD 115 kV | Current Study |  |  | 72589.4128 | 3.2809 | 2212500 | 0.078665
GEN-2024-329 | 01 NORTH | TBD | ERIS | Add 54 MVAR switched shunt at REDFELD-ER7 115 kV | Current Study |  |  | 72589.4128 | 3.2809 | 2212500 | 0.078665
GEN-2024-329 | 01 NORTH | TBD | ERIS | Add 5.5 MVAR switched shunt at LOOMIS-ER8 69 kV | Current Study |  |  | 47640.0089 | 3.4522 | 1380000 | 0.10121
GEN-2024-329 | 01 NORTH | TBD | ERIS | Add 4 MVAR switched shunt at MOS-RDFL-ER8 69 kV | Current Study |  |  | 45276.1083 | 3.2809 | 1380000 | 0.078665
GEN-2024-329 | 01 NORTH | TBD | ERIS | Rebuild line 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Current Study | 0 | (880.00, 880.00) | 15082.1185 | 6.8555 | 220000 | 0.095978
GEN-2024-329 | 01 NORTH | TBD | ERIS | Rebuild line 652484 NUNDRWD4 230 652884 NUNDRWD-LNX3 230 Z | Current Study | 0.14514 | (519.00, 519.00) | 8878.6931 | 3.2197 | 275765.6361 | 0.046989
GEN-2024-329 | 01 NORTH | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 6467.8084 | 0.46868 | 1380000 | 0.073515
GEN-2024-330 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 4279068.2296 | 0.456 | 938400000 | 0.034382
GEN-2024-330 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 3475334.1763 | 0.37035 | 938400000 | 0.049419
GEN-2024-330 | 03 CENTRAL | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 2309822.7402 | 1.058 | 218320000 | 0.029019
GEN-2024-330 | 03 CENTRAL | TBD | ERIS | Rebuild line 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 | Current Study | 9.08 | (395.00, 395.00) | 690246.1069 | 6.3349 | 10896000 | 0.030415
GEN-2024-330 | 03 CENTRAL | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 687338.1995 | 1.2857 | 53460000 | 0.041252
GEN-2024-330 | 03 CENTRAL | TBD | ERIS | Rebuild line 645458 S3458 3 345 778170 G24-040-TAP 345 1 | Current Study | 13.15 | (1793.00, 1793.00) | 661373.9368 | 2.2861 | 28930000 | 0.031511
GEN-2024-330 | 03 CENTRAL | TBD | ERIS | Rebuild line 640139 COOPER 3 345 778170 G24-040-TAP 345 1 | Current Study | 12.59 | (1793.00, 1793.00) | 633208.9631 | 2.2861 | 27698000 | 0.031511
GEN-2024-330 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 577668.4554 | 0.291 | 198511000 | 0.0087433
GEN-2024-330 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 513212.1877 | 1.1178 | 45914000 | 0.050228
GEN-2024-330 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 505896.4362 | 0.53828 | 93984000 | 0.02969
GEN-2024-330 | 03 CENTRAL | TBD | ERIS | Rebuild line 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Current Study | 3.89 | (395.00, 395.00) | 295711.1625 | 6.3349 | 4668000 | 0.030415
GEN-2024-330 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 280090.4081 | 1.1178 | 25058000 | 0.050228
GEN-2024-330 | 03 CENTRAL | TBD | ERIS | Rebuild line 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 | Current Study | 3.49 | (395.00, 395.00) | 265303.845 | 6.3349 | 4188000 | 0.030415
GEN-2024-330 | 03 CENTRAL | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 239502.9416 | 1.2877 | 18600000 | 0.1147
GEN-2024-330 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | Current Study |  |  | 168288.6812 | 3.1753 | 5300000 | 0.12002
GEN-2024-330 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 122796.6636 | 0.6602 | 18600000 | 0.10293
GEN-2024-330 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 122796.6636 | 0.6602 | 18600000 | 0.10293
GEN-2024-330 | 03 CENTRAL | TBD | ERIS | Rebuild line 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Current Study | 1.46 | (395.00, 395.00) | 110986.7088 | 6.3349 | 1752000 | 0.030415
GEN-2024-330 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 68361.0806 | 0.58629 | 11660000 | 0.02969
GEN-2024-330 | 03 CENTRAL | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 54152.1753 | 0.29114 | 18600000 | 0.034382
GEN-2024-330 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 53707.5163 | 0.28875 | 18600000 | 0.049419
GEN-2024-330 | 03 CENTRAL | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 45069.2192 | 0.85036 | 5300000 | 0.026374
GEN-2024-330 | 03 CENTRAL | TBD | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 44583.4962 | 2.0151 | 2212500 | 0.057578
GEN-2024-330 | 03 CENTRAL | TBD | ERIS | Rebuild line 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Current Study | 0.58 | (395.00, 395.00) | 44090.6104 | 6.3349 | 696000 | 0.030415
GEN-2024-330 | 03 CENTRAL | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 29235.4813 | 0.55161 | 5300000 | 0.016805
GEN-2024-330 | 03 CENTRAL | TBD | ERIS | Add 248 MVAR switched shunt at GEN-2022-015 345 kV | Current Study |  |  | 25916.2673 | 0.48899 | 5300000 | 0.031088
GEN-2024-330 | 03 CENTRAL | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 21103.7223 | 0.39818 | 5300000 | 0.031088
GEN-2024-330 | 03 CENTRAL | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 14718.4068 | 0.12265 | 12000000 | 0.015168
GEN-2024-330 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 6620.8498 | 0.40126 | 1650000 | 0.021622
GEN-2024-331 | 01 NORTH | TBD | ERIS | Rebuild line 640404 WAYSIDE 4 230 652484 NUNDRWD4 230 1 | Current Study | 80.12 | (519.00, 519.00) | 16042911.2571 | 10.5387 | 152228000 | 0.04032
GEN-2024-331 | 01 NORTH | TBD | ERIS | Rebuild line 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Current Study | 36.8 | (1793.00, 1793.00) | 8539851.6333 | 10.5482 | 80960000 | 0.098451
GEN-2024-331 | 01 NORTH | TBD | ERIS | Rebuild line 652529 WATERTN3 345 659165 CROCKER_-BE3 345 1 | Current Study | 44.23 | (1793.00, 1793.00) | 4861505.809 | 4.9961 | 97306000 | 0.079861
GEN-2024-331 | 01 NORTH | TBD | ERIS | Rebuild line 652884 NUNDRWD-LNX3 230 785430 G24-282-TAP 230 1 | Current Study | 35.21 | (519.00, 519.00) | 3707602.5879 | 5.5421 | 66899000 | 0.053922
GEN-2024-331 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 659120 BROADLND-BE3 345 659204 BD.KU2A_-BE9 13 659205 BROADLND-BE4 230 M2 | Current Study |  | (471.00, 478.00) | 2467768.8262 | 9.8711 | 25000000 | 0.055764
GEN-2024-331 | 01 NORTH | TBD | ERIS | Rebuild line 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | Current Study | 4.2 | (519.00, 519.00) | 1244640.7568 | 15.597 | 7980000 | 0.041773
GEN-2024-331 | 01 NORTH | TBD | ERIS | Add 24 MVAR switched shunt at DH_CS_EA-TS4 230 kV | Current Study |  |  | 577988.7565 | 15.1108 | 3825000 | 0.028628
GEN-2024-331 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 659160 GROTON__-BE3 345 659161 GRT.KU2A-BE9 13 659187 GROTON__-BE7 115 M2 | Current Study |  | (400.00, 400.00) | 497549.1145 | 2.9616 | 16800000 | 0.0062946
GEN-2024-331 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 652237 WATERT19 13 652529 WATERTN3 345 652530 WATERTN4 230 M2 | Current Study |  | (400.00, 478.00) | 495127.8587 | 1.9805 | 25000000 | 0.0047382
GEN-2024-331 | 01 NORTH | TBD | ERIS | Add 60 MVAR switched shunt at WAYSIDE 4 230 kV | Current Study |  |  | 294116.701 | 7.6893 | 3825000 | 0.082594
GEN-2024-331 | 01 NORTH | TBD | ERIS | Add 24 MVAR switched shunt at DAYTON__-ER7 115 kV | Current Study |  |  | 233379.8613 | 10.5482 | 2212500 | 0.098451
GEN-2024-331 | 01 NORTH | TBD | ERIS | Add 0.4 MVAR switched shunt at SHINDLER-ER7 115 kV | Current Study |  |  | 223467.2719 | 10.1002 | 2212500 | 0.10368
GEN-2024-331 | 01 NORTH | TBD | ERIS | Add 0.5 MVAR switched shunt at ORLAND-ER8 69 kV | Current Study |  |  | 145565.744 | 10.5482 | 1380000 | 0.098451
GEN-2024-331 | 01 NORTH | TBD | ERIS | Add 14.4 MVAR switched shunt at SW145-ER8 69 kV | Current Study |  |  | 145565.744 | 10.5482 | 1380000 | 0.098451
GEN-2024-331 | 01 NORTH | TBD | ERIS | Add line and rebuild line 652568 GROTONSOUTH7 115 659187 GROTON__-BE7 115 M2 | Current Study | 0.1 | (598.00, 598.00) | 124851.2662 | 2.8768 | 4340000 | 0.0062946
GEN-2024-331 | 01 NORTH | TBD | ERIS | Add 4.4 MVAR switched shunt at DESMET-ER7 115 kV | Current Study |  |  | 113938.1966 | 5.1497 | 2212500 | 0.098451
GEN-2024-331 | 01 NORTH | TBD | ERIS | Add 10 MVAR switched shunt at REDFIELD 115 kV | Current Study |  |  | 110538.749 | 4.9961 | 2212500 | 0.079861
GEN-2024-331 | 01 NORTH | TBD | ERIS | Add 54 MVAR switched shunt at REDFELD-ER7 115 kV | Current Study |  |  | 110538.749 | 4.9961 | 2212500 | 0.079861
GEN-2024-331 | 01 NORTH | TBD | ERIS | Add 5.5 MVAR switched shunt at LOOMIS-ER8 69 kV | Current Study |  |  | 73206.2136 | 5.3048 | 1380000 | 0.10368
GEN-2024-331 | 01 NORTH | TBD | ERIS | Add 4 MVAR switched shunt at MOS-RDFL-ER8 69 kV | Current Study |  |  | 68946.2027 | 4.9961 | 1380000 | 0.079861
GEN-2024-331 | 01 NORTH | TBD | ERIS | Rebuild line 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Current Study | 0 | (880.00, 880.00) | 23206.1186 | 10.5482 | 220000 | 0.098451
GEN-2024-331 | 01 NORTH | TBD | ERIS | Rebuild line 652484 NUNDRWD4 230 652884 NUNDRWD-LNX3 230 Z | Current Study | 0.14514 | (519.00, 519.00) | 15283.1789 | 5.5421 | 275765.6361 | 0.053922
GEN-2024-331 | 01 NORTH | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 10899.7897 | 0.78984 | 1380000 | 0.082594
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 8974293.1245 | 0.95471 | 940000000 | 0.017986
GEN-2024-332 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 514889 WRAIRPT4 138 514925 PENN 4 138 1 | Current Study | 3.22 | (281.00, 281.00) | 3864000 | 100 | 3864000 | 0.055441
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 532803 BURNS 7 345 1 | Current Study | 50.03 | (1793.00, 1793.00) | 3312634.9256 | 3.0097 | 110066000 | 0.041882
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532803 BURNS 7 345 1 | Current Study | 45.5 | (1793.00, 1793.00) | 3012690.1682 | 3.0097 | 100100000 | 0.041882
GEN-2024-332 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 514925 PENN 4 138 514926 SANTAFE4 138 1 | Current Study | 2.02 | (265.00, 265.00) | 2424000 | 100 | 2424000 | 0.19678
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 1778020.1618 | 1.516 | 117282000 | 0.042536
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 1705528.75 | 1.1352 | 150244000 | 0.0343
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 1 | Current Study |  | (1868.00, 1868.00) | 1704448.1513 | 2.7715 | 61500000 | 0.090002
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 2 | Current Study |  | (1868.00, 1868.00) | 1704448.1513 | 2.7715 | 61500000 | 0.090002
GEN-2024-332 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 514959 FOSTER 4 138 515387 NEWDOMI4 138 1 | Current Study | 1.44 | (281.00, 281.00) | 1267272.9287 | 73.3376 | 1728000 | 0.47996
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 1075434.407 | 1.9329 | 55638000 | 0.058126
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1051025.9273 | 1.0466 | 100427000 | 0.017921
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1024737.9187 | 0.46937 | 218320000 | 0.019311
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 940234.5634 | 1.0454 | 89936000 | 0.016282
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 903419.4756 | 2.0149 | 44836000 | 0.063073
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 897702.1223 | 0.9402 | 95480000 | 0.050696
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 841052.2819 | 0.58489 | 143796000 | 0.038951
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 838106.1758 | 1.5196 | 55154000 | 0.035729
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 834423.8371 | 1.2643 | 66000000 | 0.038746
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 796348.6569 | 0.9402 | 84700000 | 0.050696
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 731174.4917 | 0.36833 | 198511000 | 0.026252
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 657846.3024 | 0.52702 | 124824000 | 0.045972
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 610987.1972 | 0.3088 | 197860000 | 0.020348
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 544040.5836 | 1.1577 | 46992000 | 0.062519
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 466431.9788 | 0.49629 | 93984000 | 0.041061
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 440334.6421 | 0.26677 | 165062000 | 0.02238
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 434266.225 | 0.53292 | 81488000 | 0.047181
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 427223.2746 | 0.93049 | 45914000 | 0.062718
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 424216.3466 | 0.31909 | 132946000 | 0.013227
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 401167.6949 | 1.5196 | 26400000 | 0.035729
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 369726.7766 | 1.1006 | 33594000 | 0.059877
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 330207.812 | 1.2613 | 26180000 | 0.019002
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 260206.305 | 1.0285 | 25300000 | 0.028088
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 242461.1609 | 0.45354 | 53460000 | 0.021828
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 233161.1451 | 0.93049 | 25058000 | 0.062718
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514959 FOSTER 4 138 514962 DISCVRY4 138 1 | Current Study | 0.18 | (281.00, 281.00) | 216000 | 100 | 216000 | 0.47744
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 122 MVAR switched shunt at HOYT 7 345 kV | Current Study |  |  | 212433.5908 | 4.0082 | 5300000 | 0.039455
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 201081.9763 | 0.78321 | 25674000 | 0.03666
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR SVC at JAY 4 138 kV | Current Study |  |  | 189184.8158 | 3.5695 | 5300000 | 0.026478
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 185744.33 | 1.5077 | 12320000 | 0.043134
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 138 MVAR switched shunt at GEN-2024-016 345 kV | Current Study |  |  | 182456.2502 | 3.4426 | 5300000 | 0.028737
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 174831.4096 | 1.4569 | 12000000 | 0.043134
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 174831.4096 | 1.4569 | 12000000 | 0.043134
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 0.06 MVAR switched shunt at G24-125-TAP 345 kV | Current Study |  |  | 168711.2199 | 3.1832 | 5300000 | 0.030313
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 155872.3682 | 1.2989 | 12000000 | 0.043134
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 155657.9142 | 1.0341 | 15053000 | 0.018236
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 154591.3075 | 1.2883 | 12000000 | 0.058126
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 142855.5338 | 0.79772 | 17908000 | 0.037957
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 130155.1059 | 1.0846 | 12000000 | 0.050696
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 123583.1934 | 1.0299 | 12000000 | 0.058126
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 123245.6726 | 1.027 | 12000000 | 0.032271
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 121806.1393 | 1.0151 | 12000000 | 0.06886
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 118439.0965 | 0.98699 | 12000000 | 0.043134
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 118439.0965 | 0.98699 | 12000000 | 0.043134
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 113498.8128 | 0.94582 | 12000000 | 0.042536
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 112325.6596 | 0.93605 | 12000000 | 0.043134
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 110417.9702 | 0.92015 | 12000000 | 0.043134
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 108520.7602 | 0.90434 | 12000000 | 0.016282
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 106328.9388 | 0.88607 | 12000000 | 0.032271
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 105265.5754 | 0.87721 | 12000000 | 0.043134
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at CENTRTN5 161 kV | Current Study |  |  | 104419.4984 | 3.2129 | 3250000 | 0.027409
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 102921.3843 | 1.9419 | 5300000 | 0.032271
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 97550.2911 | 1.8406 | 5300000 | 0.032585
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 94816.9494 | 0.79014 | 12000000 | 0.050696
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 88540.4976 | 0.73784 | 12000000 | 0.033542
GEN-2024-332 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 86765.2486 | 0.47937 | 18100000 | 0.009792
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 79847.5636 | 1.5066 | 5300000 | 0.058126
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 68506.3262 | 0.57089 | 12000000 | 0.033542
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 67270.6212 | 1.2693 | 5300000 | 0.042536
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 64545.6013 | 1.2178 | 5300000 | 0.042536
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 63028.3034 | 0.54055 | 11660000 | 0.041061
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 61449.3601 | 0.93105 | 6600000 | 0.050696
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 57080.9502 | 1.077 | 5300000 | 0.06886
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 54707.2856 | 0.36623 | 14938000 | 0.05201
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 53058.0353 | 1.0011 | 5300000 | 0.041061
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 52960.2018 | 0.36623 | 14460953.1406 | 0.05201
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 51468.7986 | 0.77983 | 6600000 | 0.041061
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 50396.0974 | 0.76358 | 6600000 | 0.033542
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 50396.0974 | 0.76358 | 6600000 | 0.033542
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 47891.1917 | 0.72562 | 6600000 | 0.033542
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 43794.4607 | 0.27047 | 16192000 | 0.040435
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 42960.2047 | 1.3219 | 3250000 | 0.033542
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 42960.2047 | 1.3219 | 3250000 | 0.033542
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 42358.1937 | 0.79921 | 5300000 | 0.030313
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 42097.248 | 0.79429 | 5300000 | 0.033542
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 37582.4824 | 1.545 | 2432500 | 0.042536
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 37428.2274 | 0.70619 | 5300000 | 0.032271
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 36765.1477 | 0.69368 | 5300000 | 0.032271
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 34919.0145 | 1.0744 | 3250000 | 0.033542
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 34673.5852 | 0.65422 | 5300000 | 0.032271
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 34540.8541 | 0.65171 | 5300000 | 0.041061
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 34384.5874 | 1.1577 | 2970000 | 0.062519
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 33430.6412 | 1.5196 | 2200000 | 0.035729
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 33095.0091 | 0.9402 | 3520000 | 0.050696
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 31848.7848 | 0.60092 | 5300000 | 0.043134
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 31225.7134 | 0.96079 | 3250000 | 0.033542
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 30556.4921 | 0.9402 | 3250000 | 0.050696
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 27392.7617 | 0.84285 | 3250000 | 0.050696
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 26742.5554 | 0.82285 | 3250000 | 0.033542
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 26506.6543 | 0.81559 | 3250000 | 0.033542
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 26505.0129 | 0.81554 | 3250000 | 0.033542
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 25814.3502 | 0.79429 | 3250000 | 0.033542
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 25470.0648 | 1.1577 | 2200000 | 0.062519
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 24683.1937 | 0.46572 | 5300000 | 0.0046159
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 24202.7943 | 0.7447 | 3250000 | 0.033542
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 23573.4728 | 0.72534 | 3250000 | 0.033542
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 22206.7829 | 0.68329 | 3250000 | 0.033542
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 22094.5112 | 0.67983 | 3250000 | 0.041061
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 20011.4818 | 1.516 | 1320000 | 0.042536
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 18299.0717 | 0.34527 | 5300000 | 0.040435
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 17028.7053 | 0.14191 | 12000000 | 0.026323
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 16622.4874 | 0.68335 | 2432500 | 0.041061
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 16392.0477 | 0.67388 | 2432500 | 0.041061
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 15554.3618 | 0.63944 | 2432500 | 0.038669
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 15301.8023 | 0.6653 | 2300000 | 0.062519
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 14651.4182 | 1.0617 | 1380000 | 0.033542
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 13099.1021 | 0.94921 | 1380000 | 0.028953
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 12410.7416 | 0.89933 | 1380000 | 0.041883
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 12053.8372 | 0.87347 | 1380000 | 0.033542
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 11972.6773 | 0.2259 | 5300000 | 0.043134
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 10836.9127 | 0.78528 | 1380000 | 0.041061
GEN-2024-332 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 7632.1307 | 0.144 | 5300000 | 0.032783
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 6293.6126 | 0.28446 | 2212500 | 0.040435
GEN-2024-332 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 4462.7507 | 0.27047 | 1650000 | 0.040435
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 5991778.7017 | 0.63742 | 940000000 | 0.018013
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 532803 BURNS 7 345 1 | Current Study | 50.03 | (1793.00, 1793.00) | 2229350.279 | 2.0255 | 110066000 | 0.042279
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532803 BURNS 7 345 1 | Current Study | 45.5 | (1793.00, 1793.00) | 2027492.2585 | 2.0255 | 100100000 | 0.042279
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 1200741.9816 | 1.0238 | 117282000 | 0.043088
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 1148860.3958 | 0.76466 | 150244000 | 0.034657
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 1 | Current Study |  | (1868.00, 1868.00) | 996287.7413 | 1.62 | 61500000 | 0.078913
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 2 | Current Study |  | (1868.00, 1868.00) | 996287.7413 | 1.62 | 61500000 | 0.078913
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 760008.317 | 1.366 | 55638000 | 0.061616
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 712891.6606 | 0.70986 | 100427000 | 0.018233
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 690900.6807 | 0.31646 | 218320000 | 0.01953
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 649978.7739 | 1.4497 | 44836000 | 0.068068
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 630556.0657 | 0.70112 | 89936000 | 0.016379
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 600517.2443 | 0.62895 | 95480000 | 0.05087
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 566616.6019 | 0.39404 | 143796000 | 0.039362
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 566184.8489 | 1.0266 | 55154000 | 0.036206
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 560810.8737 | 0.84971 | 66000000 | 0.039061
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 532716.9103 | 0.62895 | 84700000 | 0.05087
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 486889.6625 | 0.24527 | 198511000 | 0.026222
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 441357.8555 | 0.35358 | 124824000 | 0.046265
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 403111.876 | 0.20374 | 197860000 | 0.020138
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 346045.6658 | 0.73639 | 46992000 | 0.059649
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 313404.2044 | 0.33347 | 93984000 | 0.041384
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 309238.7514 | 0.67352 | 45914000 | 0.068096
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 290545.0172 | 0.17602 | 165062000 | 0.02215
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 290423.1963 | 0.3564 | 81488000 | 0.047329
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 282673.6853 | 0.21262 | 132946000 | 0.013221
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 271009.8998 | 1.0266 | 26400000 | 0.036206
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 249218.3995 | 0.74185 | 33594000 | 0.060541
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 222629.3725 | 0.85038 | 26180000 | 0.019217
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 174251.2845 | 0.68874 | 25300000 | 0.028214
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 168769.975 | 0.67352 | 25058000 | 0.068096
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 164788.0016 | 0.30825 | 53460000 | 0.022253
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 122 MVAR switched shunt at HOYT 7 345 kV | Current Study |  |  | 143101.2297 | 2.7 | 5300000 | 0.039866
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 125415.5441 | 1.018 | 12320000 | 0.043686
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 138 MVAR switched shunt at GEN-2024-016 345 kV | Current Study |  |  | 121819.7889 | 2.2985 | 5300000 | 0.02878
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 118047.099 | 0.98373 | 12000000 | 0.043686
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 118047.099 | 0.98373 | 12000000 | 0.043686
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 0.06 MVAR switched shunt at G24-125-TAP 345 kV | Current Study |  |  | 115457.9846 | 2.1785 | 5300000 | 0.031118
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 114060.4924 | 0.44426 | 25674000 | 0.031192
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 109249.504 | 0.91041 | 12000000 | 0.061616
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 105561.837 | 0.70127 | 15053000 | 0.01855
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 105245.8532 | 0.87705 | 12000000 | 0.043686
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 87336.1044 | 0.7278 | 12000000 | 0.061616
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 87067.1824 | 0.72556 | 12000000 | 0.05087
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 82608.3009 | 0.6884 | 12000000 | 0.032446
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 82004.5066 | 0.68337 | 12000000 | 0.069539
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 81093.0417 | 0.45283 | 17908000 | 0.03232
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 79970.7088 | 0.66642 | 12000000 | 0.043686
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 79970.7088 | 0.66642 | 12000000 | 0.043686
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 76648.6292 | 0.63874 | 12000000 | 0.043088
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 75842.8836 | 0.63202 | 12000000 | 0.043686
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 74554.8016 | 0.62129 | 12000000 | 0.043686
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 72778.0548 | 0.60648 | 12000000 | 0.016379
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 71269.4635 | 0.59391 | 12000000 | 0.032446
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 71075.8772 | 0.5923 | 12000000 | 0.043686
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 68985.4703 | 1.3016 | 5300000 | 0.032446
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 65209.1065 | 1.2304 | 5300000 | 0.032673
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 63427.7431 | 0.52856 | 12000000 | 0.05087
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 57543.3352 | 0.47953 | 12000000 | 0.032699
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 56428.1838 | 1.0647 | 5300000 | 0.061616
GEN-2024-333 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 50894.2162 | 0.28118 | 18100000 | 0.0086156
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 45429.558 | 0.85716 | 5300000 | 0.043088
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 44522.9314 | 0.37102 | 12000000 | 0.032699
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 43589.2829 | 0.82244 | 5300000 | 0.043088
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 42349.8735 | 0.36321 | 11660000 | 0.041384
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 41106.5137 | 0.62283 | 6600000 | 0.05087
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 38429.0577 | 0.72508 | 5300000 | 0.069539
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 36474.5811 | 0.24417 | 14938000 | 0.052014
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at TXPLSTP2 69 kV | Current Study |  |  | 35788.1438 | 2.5933 | 1380000 | 0.05502
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 35650.6648 | 0.67265 | 5300000 | 0.041384
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 35309.7609 | 0.24417 | 14460953.1406 | 0.052014
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 34582.8276 | 0.52398 | 6600000 | 0.041384
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 32752.9165 | 0.49626 | 6600000 | 0.032699
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 32752.9165 | 0.49626 | 6600000 | 0.032699
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 31124.9538 | 0.47159 | 6600000 | 0.032699
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 28987.9456 | 0.54694 | 5300000 | 0.031118
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 28906.6147 | 0.17852 | 16192000 | 0.040033
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 27920.2572 | 0.85908 | 3250000 | 0.032699
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 27920.2572 | 0.85908 | 3250000 | 0.032699
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 27359.4132 | 0.51622 | 5300000 | 0.032699
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 25380.4043 | 1.0434 | 2432500 | 0.043088
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 25087.1467 | 0.47334 | 5300000 | 0.032446
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 24642.702 | 0.46496 | 5300000 | 0.032446
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 23240.7832 | 0.43851 | 5300000 | 0.032446
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 23208.6319 | 0.4379 | 5300000 | 0.041384
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 22694.209 | 0.69828 | 3250000 | 0.032699
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 22584.1583 | 1.0266 | 2200000 | 0.036206
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 22138.8846 | 0.62895 | 3520000 | 0.05087
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 21870.8637 | 0.73639 | 2970000 | 0.059649
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 21504.4691 | 0.40574 | 5300000 | 0.043686
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 20440.7476 | 0.62895 | 3250000 | 0.05087
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 20293.8965 | 0.62443 | 3250000 | 0.032699
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 18324.372 | 0.56383 | 3250000 | 0.05087
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 17380.2483 | 0.53478 | 3250000 | 0.032699
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 17226.9339 | 0.53006 | 3250000 | 0.032699
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 17225.8671 | 0.53003 | 3250000 | 0.032699
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 16783.7262 | 0.31667 | 5300000 | 0.0047079
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 16776.9986 | 0.51622 | 3250000 | 0.032699
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 16200.6398 | 0.73639 | 2200000 | 0.059649
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 15729.6327 | 0.48399 | 3250000 | 0.032699
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 15320.6305 | 0.4714 | 3250000 | 0.032699
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 14845.7064 | 0.45679 | 3250000 | 0.041384
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 14432.4054 | 0.44407 | 3250000 | 0.032699
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 13514.2598 | 1.0238 | 1320000 | 0.043088
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 12078.3374 | 0.22789 | 5300000 | 0.040034
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 11355.478 | 0.094629 | 12000000 | 0.02633
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 11168.9534 | 0.45916 | 2432500 | 0.041384
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 11014.1168 | 0.45279 | 2432500 | 0.041384
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 9732.9562 | 0.42317 | 2300000 | 0.05965
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 9522.1 | 0.69001 | 1380000 | 0.032699
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 9214.8157 | 0.37882 | 2432500 | 0.034363
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 8352.2306 | 0.60523 | 1380000 | 0.04228
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 8084.0155 | 0.15253 | 5300000 | 0.043686
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 7833.9067 | 0.56767 | 1380000 | 0.032699
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 7281.52 | 0.52765 | 1380000 | 0.041384
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 4186.9549 | 0.18924 | 2212500 | 0.04035
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 2945.6469 | 0.17852 | 1650000 | 0.040033
GEN-2024-334 | 04 SOUTHEAST | TBD | ERIS | Add 19 MVAR switched shunt at RANCHRD7 345 kV | Current Study |  |  | 1021836.0829 | 19.2799 | 5300000 | 1
GEN-2024-334 | 04 SOUTHEAST | TBD | ERIS | Add 38 MVAR switched shunt at FRNT2WD7 345 kV | Current Study |  |  | 558048.6455 | 10.5292 | 5300000 | 1
GEN-2024-334 | 04 SOUTHEAST | TBD | ERIS | Add 10 MVAR switched shunt at G20-007-TAP 345 kV | Current Study |  |  | 109024.6701 | 2.0571 | 5300000 | 0.065061
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 37501074.3316 | 2.4759 | 1514620000 | 0.050759
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 32860295.4902 | 2.557 | 1285130000 | 0.2686
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 32718630.9514 | 2.573 | 1271630000 | 0.17663
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 26770894.0933 | 2.4932 | 1073760000 | 0.14236
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 17423895.6148 | 1.8568 | 938400000 | 0.105
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 16574346.4168 | 2.2869 | 724760000 | 0.18083
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 15580138.6701 | 1.6603 | 938400000 | 0.16616
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 11990473.2116 | 2.4833 | 482840000 | 0.21037
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 11796329.6841 | 2.5134 | 469340000 | 0.14309
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 9396213.7123 | 2.5638 | 366500000 | 0.056171
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526460 AMOCO_SS 6 230 777420 G24-015-TAP 230 1 | Current Study | 25.97 | (519.00, 519.00) | 7141453.337 | 14.4731 | 49343000 | 0.11
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 2404143.275 | 2.8451 | 84500000 | 0.058236
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 2180965.748 | 3.9496 | 55220000 | 0.12843
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1932408.3451 | 2.2869 | 84500000 | 0.18083
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 1909995.3549 | 0.96533 | 197860000 | 0.031805
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 1901597.5453 | 2.2504 | 84500000 | 0.095369
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1830659.252 | 1.4666 | 124824000 | 0.063965
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1740431.7862 | 0.87674 | 198511000 | 0.031244
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 1371457.5102 | 0.83087 | 165062000 | 0.034852
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 1265934.9828 | 1.5535 | 81488000 | 0.068768
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 972899.5483 | 2.238 | 43472000 | 0.045472
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 966555.2653 | 3.6474 | 26500000 | 0.038216
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 572423.6379 | 2.2897 | 25000000 | 0.025892
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 572423.6379 | 2.2897 | 25000000 | 0.022564
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 478360.1422 | 2.5718 | 18600000 | 0.17663
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 475294.5888 | 2.5553 | 18600000 | 0.2686
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 471720.0021 | 2.5361 | 18600000 | 0.17663
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 467489.9479 | 2.5134 | 18600000 | 0.14309
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 460524.7406 | 2.4759 | 18600000 | 0.050759
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 425358.5233 | 2.2869 | 18600000 | 0.18083
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528018 RED_BLUFF 3 115 528235 WOLFCAMP_TP3 115 1 | Current Study | 7.81 | (598.00, 598.00) | 373481.9416 | 4.7821 | 7810000 | 0.042742
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 330905.7113 | 1.7791 | 18600000 | 0.22836
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 292330.6469 | 1.5717 | 18600000 | 0.105
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 287660.6646 | 1.5466 | 18600000 | 0.18083
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 287660.6646 | 1.5466 | 18600000 | 0.18083
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 220501.7073 | 1.1855 | 18600000 | 0.105
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | Current Study | 0.78 | (598.00, 598.00) | 216417.6086 | 4.0895 | 5292000 | 0.038511
GEN-2024-336 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 195847.3017 | 1.082 | 18100000 | 0.011051
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | Current Study | 0.2 | (598.00, 598.00) | 183210.674 | 4.0895 | 4480000 | 0.038511
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 182879.3951 | 2.7895 | 6556000 | 0.12843
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 135307.8957 | 0.83565 | 16192000 | 0.062464
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 126020.4362 | 0.84362 | 14938000 | 0.059904
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 121995.9582 | 0.84362 | 14460953.1406 | 0.059904
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 105886.7056 | 1.9979 | 5300000 | 0.19074
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 40639.4724 | 2.9449 | 1380000 | 0.17395
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 39137.5115 | 0.32615 | 12000000 | 0.030249
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 37853.9827 | 2.743 | 1380000 | 0.19074
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 26138.6429 | 1.1814 | 2212500 | 0.032387
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 25171.5913 | 1.824 | 1380000 | 0.19074
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1 | Current Study | 2.13 | (598.00, 598.00) | 21694.3215 | 1.0185 | 2130000 | 0.0074048
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 19444.7764 | 0.87886 | 2212500 | 0.062464
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 17344.6155 | 1.2569 | 1380000 | 0.0059948
GEN-2024-336 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 14888.2092 | 1.0789 | 1380000 | 0.045527
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 13788.1687 | 0.83565 | 1650000 | 0.062464
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 9667.3648 | 0.43694 | 2212500 | 0.030249
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 6134.7905 | 0.44455 | 1380000 | 0.030249
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 528184 SENDERO +3 115 528187 SENDERO_345 345 M2 | Current Study |  | (435.00, 435.00) | 4050.6301 | 0.024111 | 16800000 | 6.3551e-05
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528184 SENDERO +3 115 528193 BLACKRIVER 3 115 1 | Current Study | 0.25 | (598.00, 598.00) | 2546.2819 | 1.0185 | 250000 | 0.0074048
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515134 PRARPNT4 138 515570 MAYSVLT4 138 1 | Current Study | 13.55 | (211.00, 211.00) | 13490000.9786 | 82.9643 | 16260000 | 0.21088
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515100 PAOLI- 4 138 515124 MAYSVIL4 138 1 | Current Study | 11.4 | (211.00, 211.00) | 11349521.1185 | 82.9643 | 13680000 | 0.21088
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515129 RATLIFF4 138 515134 PRARPNT4 138 1 | Current Study | 10.62 | (265.00, 265.00) | 10572974.9367 | 82.9643 | 12744000 | 0.21088
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515129 RATLIFF4 138 515561 CARTRCO4 138 1 | Current Study | 7.22 | (265.00, 265.00) | 7356590.3062 | 84.9099 | 8664000 | 0.22481
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515097 WLNUTCK4 138 515100 PAOLI- 4 138 1 | Current Study | 15.55 | (265.00, 265.00) | 6006483.9216 | 32.1891 | 18660000 | 0.095982
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1 | Current Study | 56.1 | (1793.00, 1793.00) | 3181753.4213 | 2.578 | 123420000 | 0.02958
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 1 | Current Study |  | (1868.00, 1868.00) | 3024687.5661 | 4.9182 | 61500000 | 0.09583
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 2 | Current Study |  | (1868.00, 1868.00) | 3024687.5661 | 4.9182 | 61500000 | 0.09583
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515124 MAYSVIL4 138 515570 MAYSVLT4 138 1 | Current Study | 3.01 | (211.00, 211.00) | 2996671.8041 | 82.9643 | 3612000 | 0.21088
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505600 TUPELO 4 138 505602 S BROWN4 138 1 | Current Study | 36.9 | (281.00, 281.00) | 2960913.8052 | 6.6868 | 44280000 | 0.034578
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 2714819.9779 | 2.3148 | 117282000 | 0.038968
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 2636368.6269 | 1.7547 | 150244000 | 0.031812
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515044 SEMINOL4 138 515531 VANOSTP4 138 1 | Current Study | 21.55 | (395.00, 395.00) | 2228722.8977 | 8.6184 | 25860000 | 0.057146
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515117 ARBUCKL4 138 515531 VANOSTP4 138 1 | Current Study | 18.2 | (472.00, 472.00) | 2146133.0221 | 9.8266 | 21840000 | 0.077517
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 1729574.798 | 1.5334 | 112794000 | 0.10449
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 764550 G20-087-TAP 345 1 | Current Study | 14.38 | (1793.00, 1793.00) | 1607319.3313 | 5.0807 | 31636000 | 0.13861
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515133 BLUERIV4 138 515178 PARKLN 4 138 1 | Current Study | 12.7 | (395.00, 395.00) | 1590305.1748 | 10.4351 | 15240000 | 0.055581
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1576401.9666 | 0.72206 | 218320000 | 0.017824
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1558894.1449 | 1.5523 | 100427000 | 0.015948
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 1534889.6634 | 1.7066 | 89936000 | 0.015948
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 1500515.3324 | 2.3724 | 63250000 | 0.10305
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1474480.7995 | 1.5443 | 95480000 | 0.049961
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1 | Current Study | 30.63 | (1793.00, 1793.00) | 1463891.9187 | 2.1724 | 67386000 | 0.028456
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 1457560.3823 | 2.6197 | 55638000 | 0.047268
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 1356562.1764 | 2.0554 | 66000000 | 0.037794
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 1308007.1609 | 1.5443 | 84700000 | 0.049961
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1306444.1282 | 0.90854 | 143796000 | 0.036303
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515117 ARBUCKL4 138 515133 BLUERIV4 138 1 | Current Study | 10.35 | (395.00, 395.00) | 1296036.107 | 10.4351 | 12420000 | 0.055581
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 1264847.2167 | 2.2933 | 55154000 | 0.032353
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at WILDHRS2 69 kV | Current Study |  |  | 1171756.0777 | 84.9099 | 1380000 | 0.22481
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1130145.1259 | 0.56931 | 198511000 | 0.024346
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515178 PARKLN 4 138 515977 LKKONWA4 138 1 | Current Study | 13.56 | (472.00, 472.00) | 1125566.8272 | 6.9172 | 16272000 | 0.066938
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 1063133.0597 | 2.3712 | 44836000 | 0.044534
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | Current Study | 13.6 | (1793.00, 1793.00) | 1026884.4786 | 3.4321 | 29920000 | 0.051845
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 1000936.869 | 0.50588 | 197860000 | 0.020001
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 999390.9976 | 0.80064 | 124824000 | 0.041904
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | Current Study | 8.91 | (2390.00, 2390.00) | 982886.8638 | 5.0142 | 19602000 | 0.13861
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 776060 G23-204-TAP 345 1 | Current Study | 17.82 | (1793.00, 1793.00) | 915638.6426 | 2.3356 | 39204000 | 0.070383
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 893696.459 | 1.9018 | 46992000 | 0.06162
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2 | Current Study |  | (484.00, 515.00) | 871896.5541 | 4.8171 | 18100000 | 0.01868
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520400 NOBLE4 138 520975 LIDDELL4 138 1 | Current Study | 5.73 | (265.00, 265.00) | 824540.3816 | 11.9916 | 6876000 | 0.030766
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 769870.6621 | 0.81915 | 93984000 | 0.040664
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 721797.5305 | 0.43729 | 165062000 | 0.022011
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 672964.9034 | 0.50619 | 132946000 | 0.01259
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 665790.0667 | 0.81704 | 81488000 | 0.043401
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | Current Study | 5.97 | (2390.00, 2390.00) | 658567.2926 | 5.0142 | 13134000 | 0.13861
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 640986.212 | 2.4966 | 25674000 | 0.070117
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 617325.7651 | 1.8376 | 33594000 | 0.059985
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 605431.456 | 2.2933 | 26400000 | 0.032353
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | Current Study | 7.74 | (1793.00, 1793.00) | 534439.3521 | 3.1386 | 17028000 | 0.070383
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 512022.3307 | 1.9558 | 26180000 | 0.017679
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 496026.1631 | 1.0803 | 45914000 | 0.043691
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 455695.2374 | 2.5446 | 17908000 | 0.072647
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 424854.3735 | 1.6793 | 25300000 | 0.027517
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | Current Study | 6.93 | (1793.00, 1793.00) | 356081.6943 | 2.3356 | 15246000 | 0.070383
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 343436.5205 | 0.64242 | 53460000 | 0.018551
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514948 CEDARLN4 138 766111 G21-088-TAP 138 1 | Current Study | 2.86 | (395.00, 395.00) | 297289.4561 | 8.6623 | 3432000 | 0.059394
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 295089.4603 | 5.5677 | 5300000 | 0.043691
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 283968.9552 | 2.3049 | 12320000 | 0.039566
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 270710.9726 | 1.0803 | 25058000 | 0.043691
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 267285.0088 | 2.2274 | 12000000 | 0.039566
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 267285.0088 | 2.2274 | 12000000 | 0.039566
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 238300.128 | 1.9858 | 12000000 | 0.039566
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 231202.3011 | 1.5359 | 15053000 | 0.016251
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2 | Current Study |  | (478.00, 478.00) | 214643.186 | 1.1859 | 18100000 | 0.0079382
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 213780.4044 | 1.7815 | 12000000 | 0.049961
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 209520.9152 | 1.746 | 12000000 | 0.047267
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 191879.6959 | 1.599 | 12000000 | 0.030146
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 188628.5777 | 1.5719 | 12000000 | 0.063982
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 181071.5535 | 1.5089 | 12000000 | 0.039566
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 181071.5535 | 1.5089 | 12000000 | 0.039566
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 177154.9402 | 1.4763 | 12000000 | 0.015948
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 173298.7847 | 1.4442 | 12000000 | 0.038968
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 171725.235 | 1.431 | 12000000 | 0.039566
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 168808.7295 | 1.4067 | 12000000 | 0.039566
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 167494.9529 | 1.3958 | 12000000 | 0.047267
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 165542.2378 | 1.3795 | 12000000 | 0.030146
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 160931.6673 | 1.3411 | 12000000 | 0.039566
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 160237.0575 | 3.0233 | 5300000 | 0.030146
GEN-2024-337 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 157692.8276 | 0.87123 | 18100000 | 0.010678
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 156410.8289 | 1.3034 | 12000000 | 0.035553
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 155737.3078 | 1.2978 | 12000000 | 0.049961
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 151508.8901 | 2.8587 | 5300000 | 0.030365
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 130296.9218 | 1.9742 | 6600000 | 0.032837
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 121019.5511 | 1.0085 | 12000000 | 0.035553
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 108219.1157 | 2.0419 | 5300000 | 0.047267
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 104031.55 | 0.89221 | 11660000 | 0.040664
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 102713.9986 | 1.938 | 5300000 | 0.038968
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 100930.8776 | 1.5293 | 6600000 | 0.049961
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 98553.227 | 1.8595 | 5300000 | 0.038968
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 89027.0055 | 1.3489 | 6600000 | 0.035553
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 89027.0055 | 1.3489 | 6600000 | 0.035553
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 88395.3675 | 1.6678 | 5300000 | 0.063982
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 87575.0664 | 1.6524 | 5300000 | 0.040664
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 84951.9481 | 1.2872 | 6600000 | 0.040664
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 84601.9754 | 1.2818 | 6600000 | 0.035553
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 84237.3894 | 0.56391 | 14938000 | 0.048051
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CHILD4WT 138 kV | Current Study |  |  | 81706.4204 | 3.3589 | 2432500 | 0.13861
GEN-2024-337 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 81656.7916 | 1.5407 | 5300000 | 0.21045
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 81547.258 | 0.56391 | 14460953.1406 | 0.048051
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 75891.1618 | 2.3351 | 3250000 | 0.035553
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 75891.1618 | 2.3351 | 3250000 | 0.035553
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 74366.7094 | 1.4031 | 5300000 | 0.035553
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 71685.568 | 0.44272 | 16192000 | 0.039712
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 65247.2858 | 2.0076 | 3250000 | 0.032837
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 65247.2858 | 2.0076 | 3250000 | 0.032837
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 64980.2077 | 2.6713 | 2432500 | 0.096926
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 61686.0323 | 1.898 | 3250000 | 0.035553
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 61380.059 | 1.1581 | 5300000 | 0.026356
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 58271.5542 | 1.0995 | 5300000 | 0.030146
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 57383.8472 | 2.359 | 2432500 | 0.038968
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 57239.2134 | 1.08 | 5300000 | 0.030146
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 57011.489 | 1.0757 | 5300000 | 0.040664
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 56483.6245 | 1.9018 | 2970000 | 0.06162
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 55161.6475 | 1.6973 | 3250000 | 0.035553
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 54358.7392 | 1.5443 | 3520000 | 0.049961
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 53982.8851 | 1.0185 | 5300000 | 0.030146
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 50452.6213 | 2.2933 | 2200000 | 0.032353
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 50189.1892 | 1.5443 | 3250000 | 0.049961
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 50041.4661 | 0.94418 | 5300000 | 0.040664
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 47241.9443 | 1.4536 | 3250000 | 0.035553
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 46825.2143 | 1.4408 | 3250000 | 0.035553
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 46822.3147 | 1.4407 | 3250000 | 0.035553
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 45602.2275 | 1.4031 | 3250000 | 0.035553
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 44992.7464 | 1.3844 | 3250000 | 0.049961
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 42755.3404 | 1.3155 | 3250000 | 0.035553
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 41839.7219 | 1.9018 | 2200000 | 0.06162
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 41643.6152 | 1.2813 | 3250000 | 0.035553
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 39229.2953 | 1.2071 | 3250000 | 0.035553
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 38497.0626 | 0.72636 | 5300000 | 0.0043195
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 37615.6595 | 2.7258 | 1380000 | 0.10623
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 36468.1481 | 1.1221 | 3250000 | 0.040664
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 33105.0203 | 1.4393 | 2300000 | 0.081155
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514947 CANADN-4 138 766111 G21-088-TAP 138 1 | Current Study | 0.3 | (395.00, 395.00) | 31184.2087 | 8.6623 | 360000 | 0.059394
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 30555.0926 | 2.3148 | 1320000 | 0.038968
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 29953.0798 | 0.56515 | 5300000 | 0.039712
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 27436.2861 | 1.1279 | 2432500 | 0.040664
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 27055.9334 | 1.1123 | 2432500 | 0.040664
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 26945.0964 | 0.22454 | 12000000 | 0.024991
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520400 NOBLE4 138 520842 CANADNS4 138 1 | Current Study | 0.18 | (265.00, 265.00) | 25901.7921 | 11.9916 | 216000 | 0.030766
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 25882.3988 | 1.8755 | 1380000 | 0.035553
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 24761.0342 | 1.7943 | 1380000 | 0.032837
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 21293.6534 | 1.543 | 1380000 | 0.035553
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 18923.0241 | 1.3712 | 1380000 | 0.038316
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 18304.0173 | 0.34536 | 5300000 | 0.039566
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 17886.8921 | 1.2962 | 1380000 | 0.040664
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 12231.667 | 0.55284 | 2212500 | 0.022351
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 11859.1871 | 0.53601 | 2212500 | 0.022351
GEN-2024-337 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 7304.9152 | 0.44272 | 1650000 | 0.039712
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 5267921.8955 | 4.6704 | 112794000 | 0.22732
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1 | Current Study | 56.1 | (1793.00, 1793.00) | 5060528.1006 | 4.1002 | 123420000 | 0.033605
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 1 | Current Study |  | (1868.00, 1868.00) | 4427910.7865 | 7.1999 | 61500000 | 0.10021
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 2 | Current Study |  | (1868.00, 1868.00) | 4427910.7865 | 7.1999 | 61500000 | 0.10021
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505600 TUPELO 4 138 505602 S BROWN4 138 1 | Current Study | 36.9 | (281.00, 281.00) | 4322106.0782 | 9.7609 | 44280000 | 0.036053
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 3705998.5181 | 3.1599 | 117282000 | 0.037997
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 3602746.7286 | 2.3979 | 150244000 | 0.031052
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 3297982.9068 | 5.2142 | 63250000 | 0.16179
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1 | Current Study | 30.63 | (1793.00, 1793.00) | 2419163.3371 | 3.59 | 67386000 | 0.033589
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | Current Study | 13.16 | (395.00, 395.00) | 2344509.2164 | 14.8462 | 15792000 | 0.083786
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515044 SEMINOL4 138 515531 VANOSTP4 138 1 | Current Study | 21.55 | (395.00, 395.00) | 2269495.3094 | 8.7761 | 25860000 | 0.041565
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 2174431.8269 | 2.4178 | 89936000 | 0.016138
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 2157998.7836 | 0.98846 | 218320000 | 0.017429
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 2139207.1559 | 2.1301 | 100427000 | 0.015632
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515117 ARBUCKL4 138 515531 VANOSTP4 138 1 | Current Study | 18.2 | (472.00, 472.00) | 2104512.2189 | 9.636 | 21840000 | 0.054295
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 2085970.8782 | 2.1847 | 95480000 | 0.050487
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 2014393.9968 | 3.6205 | 55638000 | 0.046661
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 764550 G20-087-TAP 345 1 | Current Study | 14.38 | (1793.00, 1793.00) | 1927444.3276 | 6.0926 | 31636000 | 0.11872
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 1913323.0286 | 2.899 | 66000000 | 0.038076
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 1850458.0372 | 2.1847 | 84700000 | 0.050487
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1791395.282 | 1.2458 | 143796000 | 0.035556
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 1713781.6108 | 3.1073 | 55154000 | 0.031312
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515133 BLUERIV4 138 515178 PARKLN 4 138 1 | Current Study | 12.7 | (395.00, 395.00) | 1527489.7124 | 10.0229 | 15240000 | 0.038133
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1509504.2092 | 0.76041 | 198511000 | 0.023227
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 1452115.979 | 3.2387 | 44836000 | 0.043449
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 776060 G23-204-TAP 345 1 | Current Study | 17.82 | (1793.00, 1793.00) | 1451951.1577 | 3.7036 | 39204000 | 0.079721
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 1352594.1395 | 0.68361 | 197860000 | 0.019306
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1326598.7695 | 1.0628 | 124824000 | 0.039731
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | Current Study | 13.6 | (1793.00, 1793.00) | 1249920.5518 | 4.1775 | 29920000 | 0.045076
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515117 ARBUCKL4 138 515133 BLUERIV4 138 1 | Current Study | 10.35 | (395.00, 395.00) | 1244843.9782 | 10.0229 | 12420000 | 0.038133
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515178 PARKLN 4 138 515977 LKKONWA4 138 1 | Current Study | 13.56 | (472.00, 472.00) | 1206846.8497 | 7.4167 | 16272000 | 0.051266
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 1191600.8682 | 2.5358 | 46992000 | 0.058686
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 1183777.4496 | 4.6108 | 25674000 | 0.092494
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | Current Study | 8.91 | (2390.00, 2390.00) | 1178645.5083 | 6.0129 | 19602000 | 0.11872
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2 | Current Study |  | (484.00, 515.00) | 1154468.8966 | 6.3783 | 18100000 | 0.017667
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1105075.5579 | 1.1758 | 93984000 | 0.041692
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 | Current Study | 6.08 | (395.00, 395.00) | 1083177.5103 | 14.8462 | 7296000 | 0.083786
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 976027.9661 | 0.59131 | 165062000 | 0.02126
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 912801.6547 | 0.6866 | 132946000 | 0.012198
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 902050.9783 | 2.6852 | 33594000 | 0.062608
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 883232.9107 | 1.0839 | 81488000 | 0.041125
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | Current Study | 7.74 | (1793.00, 1793.00) | 847473.8832 | 4.9769 | 17028000 | 0.079721
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 842922.2293 | 4.707 | 17908000 | 0.095985
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 820318.282 | 3.1073 | 26400000 | 0.031312
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | Current Study | 5.97 | (2390.00, 2390.00) | 789732.1756 | 6.0129 | 13134000 | 0.11872
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 709636.6394 | 2.7106 | 26180000 | 0.017502
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 677470.2771 | 1.4755 | 45914000 | 0.042624
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 596177.56 | 2.3564 | 25300000 | 0.027581
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 2.3 MVAR switched shunt at MON152 2 69 kV | Current Study |  |  | 577206.3108 | 41.8265 | 1380000 | 1
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | Current Study | 6.93 | (1793.00, 1793.00) | 564647.6724 | 3.7036 | 15246000 | 0.079721
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 467025.6878 | 3.8919 | 12000000 | 0.033078
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 453657.4223 | 0.84859 | 53460000 | 0.017503
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1 | Current Study | 11.3 | (1793.00, 1793.00) | 437915.9997 | 1.7615 | 24860000 | 0.031048
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 403031.9001 | 7.6044 | 5300000 | 0.042624
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 387795.5935 | 3.1477 | 12320000 | 0.038595
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 369735.8148 | 1.4755 | 25058000 | 0.042624
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 365011.5569 | 3.0418 | 12000000 | 0.038595
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 365011.5569 | 3.0418 | 12000000 | 0.038595
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 325429.0285 | 2.7119 | 12000000 | 0.038595
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 317347.7591 | 2.1082 | 15053000 | 0.015933
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 302438.4184 | 2.5203 | 12000000 | 0.050487
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 289564.271 | 2.413 | 12000000 | 0.046661
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 260933.9442 | 2.1744 | 12000000 | 0.029282
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 257748.9812 | 2.1479 | 12000000 | 0.062448
GEN-2024-338 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 255921.5475 | 4.8287 | 5300000 | 0.47112
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 250969.9831 | 2.0914 | 12000000 | 0.016138
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 247276.1564 | 2.0606 | 12000000 | 0.038595
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 247276.1564 | 2.0606 | 12000000 | 0.038595
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 236570.0328 | 1.9714 | 12000000 | 0.037997
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 234512.5739 | 1.9543 | 12000000 | 0.038595
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 231483.1142 | 1.929 | 12000000 | 0.046661
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 230529.716 | 1.9211 | 12000000 | 0.038595
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 225411.8699 | 1.8784 | 12000000 | 0.036598
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 225118.0816 | 1.876 | 12000000 | 0.029282
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 220323.959 | 1.836 | 12000000 | 0.050487
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 219772.5891 | 1.8314 | 12000000 | 0.038595
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 217903.6568 | 4.1114 | 5300000 | 0.029282
GEN-2024-338 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 204621.9727 | 1.1305 | 18100000 | 0.009897
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 204396.0103 | 3.8565 | 5300000 | 0.02926
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 195559.1273 | 2.963 | 6600000 | 0.035203
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 188144.8062 | 3.5499 | 5300000 | 0.033078
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 174407.6385 | 1.4534 | 12000000 | 0.036598
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 149562.1061 | 2.8219 | 5300000 | 0.046661
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 149327.3205 | 1.2807 | 11660000 | 0.041692
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 142788.4612 | 2.1635 | 6600000 | 0.050487
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 140214.7976 | 2.6456 | 5300000 | 0.037997
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2 | Current Study |  | (478.00, 478.00) | 137080.6399 | 0.75735 | 18100000 | 0.0036212
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 134534.9316 | 2.5384 | 5300000 | 0.037997
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 128301.4988 | 1.944 | 6600000 | 0.036598
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 128301.4988 | 1.944 | 6600000 | 0.036598
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 125705.5763 | 2.3718 | 5300000 | 0.041692
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 121940.3424 | 1.8476 | 6600000 | 0.041692
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 121924.3553 | 1.8473 | 6600000 | 0.036598
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 120786.6603 | 2.279 | 5300000 | 0.062448
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 112687.3406 | 8.1657 | 1380000 | 0.22732
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 112582.0214 | 0.75366 | 14938000 | 0.045871
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 109370.7438 | 3.3653 | 3250000 | 0.036598
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 109370.7438 | 3.3653 | 3250000 | 0.036598
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 108986.7008 | 0.75366 | 14460953.1406 | 0.045871
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 107173.7753 | 2.0221 | 5300000 | 0.036598
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 | Current Study | 0.55 | (395.00, 395.00) | 97984.8077 | 14.8462 | 660000 | 0.083786
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CHILD4WT 138 kV | Current Study |  |  | 97979.6431 | 4.0279 | 2432500 | 0.11872
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 97927.8872 | 3.0132 | 3250000 | 0.035203
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 97927.8872 | 3.0132 | 3250000 | 0.035203
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 96923.1655 | 0.59859 | 16192000 | 0.038352
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 88898.9848 | 2.7354 | 3250000 | 0.036598
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 82582.0272 | 1.5582 | 5300000 | 0.025328
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 81834.5034 | 1.544 | 5300000 | 0.041692
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 79496.3507 | 2.446 | 3250000 | 0.036598
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 79242.4982 | 1.4951 | 5300000 | 0.029282
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 78334.644 | 3.2203 | 2432500 | 0.037997
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 77838.6356 | 1.4687 | 5300000 | 0.029282
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 76902.1522 | 2.1847 | 3520000 | 0.050487
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 75311.8526 | 2.5358 | 2970000 | 0.058686
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 73410.4099 | 1.3851 | 5300000 | 0.029282
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 71829.7067 | 1.3553 | 5300000 | 0.041692
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 71003.416 | 2.1847 | 3250000 | 0.050487
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 69427.269 | 2.8542 | 2432500 | 0.073971
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 68359.8568 | 3.1073 | 2200000 | 0.031312
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 68082.85 | 2.0949 | 3250000 | 0.036598
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 67482.2785 | 2.0764 | 3250000 | 0.036598
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 67478.0997 | 2.0762 | 3250000 | 0.036598
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 65719.7679 | 2.0221 | 3250000 | 0.036598
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 63651.9287 | 1.9585 | 3250000 | 0.050487
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 61616.9693 | 1.8959 | 3250000 | 0.036598
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 60014.8036 | 1.8466 | 3250000 | 0.036598
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 56535.4002 | 1.7396 | 3250000 | 0.036598
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 55786.5575 | 2.5358 | 2200000 | 0.058686
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 54331.1923 | 1.0251 | 5300000 | 0.0043544
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 53707.9541 | 3.8919 | 1380000 | 0.033078
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 52396.7656 | 2.2781 | 2300000 | 0.091749
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 52346.5155 | 1.6107 | 3250000 | 0.041692
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 41710.7318 | 3.1599 | 1320000 | 0.037997
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 40498.352 | 0.76412 | 5300000 | 0.038352
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 39382.1471 | 1.619 | 2432500 | 0.041692
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 38836.1875 | 1.5966 | 2432500 | 0.041692
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 37300.4859 | 2.7029 | 1380000 | 0.036598
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 37163.1667 | 2.693 | 1380000 | 0.035203
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 36554.6503 | 0.30462 | 12000000 | 0.024217
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 30687.4036 | 2.2237 | 1380000 | 0.036598
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 26326.4884 | 1.9077 | 1380000 | 0.038076
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 25674.9114 | 1.8605 | 1380000 | 0.041692
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 24996.4556 | 0.47163 | 5300000 | 0.038595
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 17644.4324 | 0.79749 | 2212500 | 0.02303
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 17107.1225 | 0.7732 | 2212500 | 0.02303
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 9876.6813 | 0.59859 | 1650000 | 0.038352
GEN-2024-339 | 03 CENTRAL | TBD | ERIS | Rebuild line 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | Current Study | 17.54 | (1793.00, 1793.00) | 4559392.2919 | 11.8156 | 38588000 | 0.037849
GEN-2024-339 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 2995163.1679 | 0.31918 | 938400000 | 0.031944
GEN-2024-339 | 03 CENTRAL | TBD | ERIS | Rebuild line 645458 S3458 3 345 778170 G24-040-TAP 345 1 | Current Study | 13.15 | (1793.00, 1793.00) | 2502420.961 | 8.6499 | 28930000 | 0.08942
GEN-2024-339 | 03 CENTRAL | TBD | ERIS | Rebuild line 640139 COOPER 3 345 778170 G24-040-TAP 345 1 | Current Study | 12.59 | (1793.00, 1793.00) | 2395853.9847 | 8.6499 | 27698000 | 0.08942
GEN-2024-339 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 2075485.9447 | 1.0455 | 198511000 | 0.02356
GEN-2024-339 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1395371.7705 | 0.97038 | 143796000 | 0.032311
GEN-2024-339 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1105114.766 | 1.1759 | 93984000 | 0.048642
GEN-2024-339 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 731487.4374 | 0.36849 | 198511000 | 0.013132
GEN-2024-339 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 414593.3265 | 0.90298 | 45914000 | 0.030432
GEN-2024-339 | 03 CENTRAL | TBD | ERIS | Rebuild line 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 | Current Study | 3.23 | (1793.00, 1793.00) | 339976.7603 | 4.7844 | 7106000 | 0.035953
GEN-2024-339 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 226268.2314 | 0.90298 | 25058000 | 0.030432
GEN-2024-339 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 149332.6187 | 1.2807 | 11660000 | 0.048642
GEN-2024-339 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 82422.2362 | 0.44313 | 18600000 | 0.051813
GEN-2024-339 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 82422.2362 | 0.44313 | 18600000 | 0.051813
GEN-2024-339 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 53550.7514 | 0.35849 | 14938000 | 0.025455
GEN-2024-339 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 51840.6016 | 0.35849 | 14460953.1406 | 0.025455
GEN-2024-339 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 46286.9947 | 0.24885 | 18600000 | 0.031944
GEN-2024-339 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 21417.352 | 1.298 | 1650000 | 0.052459
GEN-2024-340 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | Current Study | 44.59 | (1793.00, 1793.00) | 98098000 | 100 | 98098000 | 0.46468
GEN-2024-340 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514909 REDBUD 7 345 787290 G24-344-TAP 345 1 | Current Study | 26.49 | (1793.00, 1793.00) | 58278000 | 100 | 58278000 | 0.53532
GEN-2024-340 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1 | Current Study | 8.4 | (1793.00, 1793.00) | 18480000 | 100 | 18480000 | 0.53532
GEN-2024-340 | 04 SOUTHEAST | TBD | ERIS | Add 38 MVAR switched shunt at FRNT2WD7 345 kV | Current Study |  |  | 783464.805 | 14.7824 | 5300000 | 0.062174
GEN-2024-340 | 04 SOUTHEAST | TBD | ERIS | Add 10 MVAR switched shunt at G20-007-TAP 345 kV | Current Study |  |  | 773017.8247 | 14.5852 | 5300000 | 0.040858
GEN-2024-340 | 04 SOUTHEAST | TBD | ERIS | Add 19 MVAR switched shunt at RANCHRD7 345 kV | Current Study |  |  | 717296.4346 | 13.5339 | 5300000 | 0.062174
GEN-2024-340 | 04 SOUTHEAST | TBD | ERIS | Add 0.42 MVAR switched shunt at TWNLKSW4 138 kV | Current Study |  |  | 461507.7019 | 18.9726 | 2432500 | 0.054032
GEN-2024-341 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 26251734.6393 | 23.2741 | 112794000 | 0.3794
GEN-2024-341 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 514808 JOHNCO 4 138 514809 JOHNCO 7 345 514810 JOHNCO11 13 M2 | Current Study |  | (478.00, 478.00) | 8228547.635 | 45.4616 | 18100000 | 0.027606
GEN-2024-341 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 2574452.8689 | 48.5746 | 5300000 | 1
GEN-2024-341 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | Current Study | 13.16 | (395.00, 395.00) | 2353666.1566 | 14.9042 | 15792000 | 0.028172
GEN-2024-341 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1 | Current Study | 11.3 | (1793.00, 1793.00) | 1955130.718 | 7.8646 | 24860000 | 0.046427
GEN-2024-341 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 1621899.5662 | 30.6019 | 5300000 | 1
GEN-2024-341 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 | Current Study | 6.08 | (395.00, 395.00) | 1087408.0723 | 14.9042 | 7296000 | 0.028172
GEN-2024-341 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 559339.9097 | 3.0903 | 18100000 | 0.009061
GEN-2024-341 | 04 SOUTHEAST | TBD | ERIS | Add 10 MVAR switched shunt at G20-007-TAP 345 kV | Current Study |  |  | 523752.9713 | 9.8821 | 5300000 | 0.037088
GEN-2024-341 | 04 SOUTHEAST | TBD | ERIS | Add 38 MVAR switched shunt at FRNT2WD7 345 kV | Current Study |  |  | 446033.1178 | 8.4157 | 5300000 | 0.047421
GEN-2024-341 | 04 SOUTHEAST | TBD | ERIS | Add 19 MVAR switched shunt at RANCHRD7 345 kV | Current Study |  |  | 408362.9067 | 7.705 | 5300000 | 0.047421
GEN-2024-341 | 04 SOUTHEAST | TBD | ERIS | Add 0.42 MVAR switched shunt at TWNLKSW4 138 kV | Current Study |  |  | 269545.6191 | 11.081 | 2432500 | 0.042278
GEN-2024-341 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 | Current Study | 0.55 | (395.00, 395.00) | 98367.5065 | 14.9042 | 660000 | 0.028172
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509049 MURVAUL4 138 712002 TENASK4 138 P | Current Study | 10 | (265.00, 265.00) | 3436889.1001 | 28.6407 | 12000000 | 0.056631
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509048 MURVAULTP 138 509049 MURVAUL4 138 P | Current Study | 9 | (265.00, 265.00) | 3093200.1901 | 28.6407 | 10800000 | 0.056631
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 1748195.3177 | 1.5499 | 112794000 | 0.056116
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | Current Study | 7.6 | (211.00, 211.00) | 834614.9255 | 9.1515 | 9120000 | 0.037164
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | Current Study | 10.42 | (395.00, 395.00) | 770743.2116 | 6.164 | 12504000 | 0.010582
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507732 GENMOTR4 138 507759 SW SHV 4 138 1 | Current Study | 4.34 | (395.00, 395.00) | 542836.1875 | 10.4231 | 5208000 | 0.01514
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1 | Current Study | 11.3 | (1793.00, 1793.00) | 489805.7015 | 1.9703 | 24860000 | 0.025833
GEN-2024-343 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 317476.5668 | 1.754 | 18100000 | 0.011423
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507727 FLOURNY4 138 507732 GENMOTR4 138 1 | Current Study | 1.56 | (395.00, 395.00) | 195120.8416 | 10.4231 | 1872000 | 0.01514
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Add 10 MVAR switched shunt at G20-007-TAP 345 kV | Current Study |  |  | 183426.3501 | 3.4609 | 5300000 | 0.028848
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Add 38 MVAR switched shunt at FRNT2WD7 345 kV | Current Study |  |  | 158776.2409 | 2.9958 | 5300000 | 0.037493
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Add 19 MVAR switched shunt at RANCHRD7 345 kV | Current Study |  |  | 145366.6212 | 2.7428 | 5300000 | 0.037493
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 137793.6185 | 2.5999 | 5300000 | 0.11888
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | Current Study | 1.8 | (395.00, 395.00) | 133141.8216 | 6.164 | 2160000 | 0.010582
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Add 0.42 MVAR switched shunt at TWNLKSW4 138 kV | Current Study |  |  | 97658.037 | 4.0147 | 2432500 | 0.034021
GEN-2024-343 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 43162.9841 | 0.8144 | 5300000 | 0.059108
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 1588468.5491 | 1.0573 | 150244000 | 0.023959
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 1257081.7249 | 2.8037 | 44836000 | 0.065823
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 1256684.9371 | 1.3973 | 89936000 | 0.016321
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1213158.9586 | 1.208 | 100427000 | 0.015514
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1107588.5052 | 0.50732 | 218320000 | 0.015654
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 926061.5178 | 1.6644 | 55638000 | 0.037539
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 922860.8945 | 1.3983 | 66000000 | 0.032139
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 882479.0198 | 0.6137 | 143796000 | 0.030652
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 847161.1767 | 0.72233 | 117282000 | 0.0152
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 771833.376 | 0.80837 | 95480000 | 0.032691
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 739864.7901 | 0.37393 | 197860000 | 0.01848
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 736836.5049 | 0.37118 | 198511000 | 0.019841
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 684690.898 | 0.80837 | 84700000 | 0.032691
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 543635.8417 | 0.57843 | 93984000 | 0.035893
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 536515.5528 | 0.32504 | 165062000 | 0.020451
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 532647.3349 | 1.5855 | 33594000 | 0.064696
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 439126.7248 | 0.3303 | 132946000 | 0.010269
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 404054.1675 | 0.3237 | 124824000 | 0.021177
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 396602.8886 | 0.71908 | 55154000 | 0.012681
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 378048.5583 | 1.444 | 26180000 | 0.016317
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 284300.6313 | 0.605 | 46992000 | 0.024503
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 274669.0818 | 0.59823 | 45914000 | 0.030242
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 266451.8296 | 0.32698 | 81488000 | 0.021711
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 245227.1703 | 0.96928 | 25300000 | 0.019853
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 68 MVAR SVC at TONTITN7 345 kV | Current Study |  |  | 244292.1782 | 2.0358 | 12000000 | 0.013888
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 189837.8406 | 0.71908 | 26400000 | 0.012681
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 179650.8669 | 1.1935 | 15053000 | 0.015785
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 149903.2507 | 0.59823 | 25058000 | 0.030242
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 145043.5857 | 1.2087 | 12000000 | 0.016321
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 133119.7097 | 1.1093 | 12000000 | 0.037539
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 126365.9674 | 1.053 | 12000000 | 0.037023
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 119686.2355 | 0.99739 | 12000000 | 0.032691
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 119686.2355 | 0.99739 | 12000000 | 0.032691
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 116306.5571 | 0.96922 | 12000000 | 0.032691
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 113250.1751 | 0.94375 | 12000000 | 0.048017
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 107070.272 | 2.0202 | 5300000 | 0.026823
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 106418.3949 | 0.88682 | 12000000 | 0.037539
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 102525.2719 | 0.85438 | 12000000 | 0.020134
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 101560.0934 | 0.84633 | 12000000 | 0.028856
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 0.06 MVAR switched shunt at G24-125-TAP 345 kV | Current Study |  |  | 98192.6474 | 1.8527 | 5300000 | 0.013232
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 92387.4454 | 0.7499 | 12320000 | 0.016091
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 92324.7592 | 0.76937 | 12000000 | 0.037023
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 88452.6258 | 0.73711 | 12000000 | 0.020134
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 86959.2531 | 0.72466 | 12000000 | 0.016091
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 86959.2531 | 0.72466 | 12000000 | 0.016091
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 85617.9588 | 1.6154 | 5300000 | 0.020134
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 83036.51 | 1.5667 | 5300000 | 0.041041
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 78579.9615 | 0.65483 | 12000000 | 0.028856
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 77529.2308 | 0.64608 | 12000000 | 0.016091
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 73460.7539 | 0.63002 | 11660000 | 0.035893
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 71414.3212 | 0.59512 | 12000000 | 0.021947
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 69668.668 | 1.0556 | 6600000 | 0.021947
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 68978.213 | 1.3015 | 5300000 | 0.037023
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 68934.7682 | 1.3007 | 5300000 | 0.032691
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 68757.3231 | 1.2973 | 5300000 | 0.037539
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 65339.087 | 0.54449 | 12000000 | 0.018818
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 61741.0692 | 0.51451 | 12000000 | 0.018036
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 59987.7494 | 0.90891 | 6600000 | 0.035893
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 57806.6817 | 0.87586 | 6600000 | 0.028856
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 57806.6817 | 0.87586 | 6600000 | 0.028856
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 55029.3743 | 0.36839 | 14938000 | 0.039237
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 54933.4377 | 0.83232 | 6600000 | 0.028856
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 53465.5538 | 0.3302 | 16192000 | 0.037023
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 53272.0045 | 0.36839 | 14460953.1406 | 0.039237
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 52833.3714 | 0.80051 | 6600000 | 0.032691
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 49277.3649 | 1.5162 | 3250000 | 0.028856
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 49277.3649 | 1.5162 | 3250000 | 0.028856
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 48287.5131 | 0.91109 | 5300000 | 0.028856
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at SLKHILLS 4 138 kV | Current Study |  |  | 42477.5206 | 1.7462 | 2432500 | 0.065652
GEN-2024-344 | 04 SOUTHEAST | TBD | NRIS | Add 0.09 MVAR switched shunt at GRAY CO3 115 kV | Current Study |  |  | 40698.1128 | 1.8395 | 2212500 | 0.033396
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 40257.9457 | 0.75958 | 5300000 | 0.035893
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 40053.7434 | 1.2324 | 3250000 | 0.028856
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 36131.9666 | 0.68174 | 5300000 | 0.032691
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 35817.3543 | 1.1021 | 3250000 | 0.028856
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 35336.1518 | 0.66672 | 5300000 | 0.035893
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 34887.1748 | 1.0735 | 3250000 | 0.021947
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 34887.1748 | 1.0735 | 3250000 | 0.021947
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 30674.9623 | 0.94384 | 3250000 | 0.028856
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 30584.0902 | 0.57706 | 5300000 | 0.020134
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 30404.3727 | 0.93552 | 3250000 | 0.028856
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 30402.49 | 0.93546 | 3250000 | 0.028856
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 29610.2675 | 0.91109 | 3250000 | 0.028856
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 28844.1669 | 0.54423 | 5300000 | 0.020134
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 28454.6867 | 0.80837 | 3520000 | 0.032691
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 27876.7647 | 0.52598 | 5300000 | 0.0039098
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 27761.7375 | 0.85421 | 3250000 | 0.028856
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 27039.8762 | 0.832 | 3250000 | 0.028856
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 26272.0798 | 0.80837 | 3250000 | 0.032691
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 25751.524 | 0.79235 | 3250000 | 0.035893
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 25472.2191 | 0.78376 | 3250000 | 0.028856
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 23604.1211 | 1.0669 | 2212500 | 0.11374
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 23551.945 | 0.72468 | 3250000 | 0.032691
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 23380.2428 | 0.44114 | 5300000 | 0.015119
GEN-2024-344 | 04 SOUTHEAST | TBD | NRIS | Add 16 MVAR switched shunt at UNDERWOOD 2 345 kV | Current Study |  |  | 22550.5268 | 0.42548 | 5300000 | 0.033396
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 22339.9597 | 0.42151 | 5300000 | 0.037023
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 19373.7883 | 0.79646 | 2432500 | 0.035893
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 19105.207 | 0.78541 | 2432500 | 0.035893
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 17968.4388 | 0.605 | 2970000 | 0.024503
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 17011.0545 | 0.14176 | 12000000 | 0.019722
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 16805.8622 | 1.2178 | 1380000 | 0.028856
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 15819.82 | 0.71908 | 2200000 | 0.012681
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 14269.5069 | 0.58662 | 2432500 | 0.026606
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 13893.0923 | 0.26213 | 5300000 | 0.037539
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 13826.3153 | 1.0019 | 1380000 | 0.028856
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 13309.9546 | 0.605 | 2200000 | 0.024503
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 13239.5167 | 0.95939 | 1380000 | 0.021947
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 12697.9255 | 0.92014 | 1380000 | 0.032139
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 12630.6038 | 0.91526 | 1380000 | 0.035893
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 11563.231 | 0.02163 | 53460000 | 0.00078074
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 9534.7347 | 0.72233 | 1320000 | 0.0152
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 9315.8895 | 0.42106 | 2212500 | 0.021947
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 8240.2207 | 0.15548 | 5300000 | 0.0047827
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 7996.283 | 0.34766 | 2300000 | 0.024503
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 5448.2562 | 0.3302 | 1650000 | 0.037023
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 4378.149 | 0.19788 | 2212500 | 0.01
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 1746.6004 | 0.071803 | 2432500 | 0.0014826
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 13035874.312 | 13.8703 | 93984000 | 0.28689
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 7317039.8415 | 8.1358 | 89936000 | 0.031677
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 7174205.2839 | 7.1437 | 100427000 | 0.030582
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 6300828.4291 | 6.5991 | 95480000 | 0.088957
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 5589444.5742 | 6.5991 | 84700000 | 0.088957
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 4069894.7806 | 2.7089 | 150244000 | 0.020462
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 3748349.6099 | 5.6793 | 66000000 | 0.043512
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 3359716.2837 | 1.5389 | 218320000 | 0.015828
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 2459749.3753 | 1.7106 | 143796000 | 0.028479
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 2343754.6059 | 19.5313 | 12000000 | 0.28689
GEN-2024-345 | 04 SOUTHEAST | TBD | NRIS | Add 16 MVAR switched shunt at UNDERWOOD 2 345 kV | Current Study |  |  | 2025718.8678 | 38.2211 | 5300000 | 1
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 1811013.4541 | 6.9175 | 26180000 | 0.026054
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 1761519.5338 | 15.1074 | 11660000 | 0.28689
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512734 FARML 4 138 778710 G24-058-TAP 138 1 | Current Study | 6.69 | (395.00, 395.00) | 1656401.194 | 20.6328 | 8028000 | 0.040901
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 1552040.8146 | 12.9337 | 12000000 | 0.149
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 1438449.6125 | 21.7947 | 6600000 | 0.28689
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 1416318.195 | 11.8027 | 12000000 | 0.13414
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 1172402.3982 | 9.77 | 12000000 | 0.088957
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 1098832.3661 | 4.3432 | 25300000 | 0.029653
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 1060141.6602 | 7.0427 | 15053000 | 0.031049
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 977053.3815 | 8.1421 | 12000000 | 0.088957
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 977053.3815 | 8.1421 | 12000000 | 0.088957
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 965347.5414 | 18.2141 | 5300000 | 0.28689
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 949463.5242 | 7.9122 | 12000000 | 0.088957
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 913537.2366 | 7.6128 | 12000000 | 0.088957
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 910883.774 | 7.5907 | 12000000 | 0.088957
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 847327.5683 | 15.9873 | 5300000 | 0.28689
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 844515.3005 | 7.0376 | 12000000 | 0.031677
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 805680.7584 | 0.68696 | 117282000 | 0.0048186
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 756540.6448 | 6.3045 | 12000000 | 0.088957
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 665504.5405 | 5.5459 | 12000000 | 0.088957
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 630666.2202 | 5.2556 | 12000000 | 0.064606
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 629424.5368 | 5.2452 | 12000000 | 0.088957
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 617497.2404 | 18.9999 | 3250000 | 0.28689
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 568200.8994 | 8.6091 | 6600000 | 0.094545
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 568200.8994 | 8.6091 | 6600000 | 0.094545
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 541521.204 | 0.98183 | 55154000 | 0.0057714
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 513576.4079 | 4.2798 | 12000000 | 0.031677
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 513576.4079 | 4.2798 | 12000000 | 0.031677
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 483904.0952 | 4.0325 | 12000000 | 0.031677
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 474633.8591 | 8.9554 | 5300000 | 0.094545
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 464565.1566 | 19.0983 | 2432500 | 0.28689
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 458124.8315 | 18.8335 | 2432500 | 0.28689
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 457883.2322 | 3.8157 | 12000000 | 0.031677
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 431302.9308 | 6.5349 | 6600000 | 0.088957
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 393701.4264 | 12.1139 | 3250000 | 0.094545
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 372738.0273 | 7.0328 | 5300000 | 1
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 302869.9584 | 21.9471 | 1380000 | 0.28689
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 301514.2999 | 9.2774 | 3250000 | 0.094545
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 298854.5861 | 9.1955 | 3250000 | 0.094545
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 298836.0798 | 9.195 | 3250000 | 0.094545
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 294961.7389 | 5.5653 | 5300000 | 0.088957
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 291049.0646 | 8.9554 | 3250000 | 0.094545
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510422 COFFEYT4 138 533002 DEARING4 138 1 | Current Study | 5.02 | (717.00, 717.00) | 288151.1957 | 4.7834 | 6024000 | 0.013881
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 265783.8429 | 8.178 | 3250000 | 0.094545
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 259204.4056 | 0.98183 | 26400000 | 0.0057714
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 251049.8 | 3.8038 | 6600000 | 0.043958
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 250374.8245 | 7.7038 | 3250000 | 0.094545
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 249109.9451 | 4.7002 | 5300000 | 0.041041
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 243950.0632 | 4.6028 | 5300000 | 0.043645
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 235724.5207 | 4.4476 | 5300000 | 0.01102
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 232288.6057 | 6.5991 | 3520000 | 0.088957
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 214470.9815 | 6.5991 | 3250000 | 0.088957
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 192265.2796 | 5.9159 | 3250000 | 0.088957
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 181031.0791 | 0.33863 | 53460000 | 0.0040744
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 168748.5223 | 1.4062 | 12000000 | 0.015862
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 165190.351 | 11.9703 | 1380000 | 0.094545
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 136492.5046 | 4.1998 | 3250000 | 0.026643
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 136492.5046 | 4.1998 | 3250000 | 0.026643
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 135903.4033 | 9.8481 | 1380000 | 0.094545
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 99209.8584 | 3.0526 | 3250000 | 0.026643
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 98342.6101 | 0.79824 | 12320000 | 0.0057093
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 76896.7474 | 2.3661 | 3250000 | 0.026643
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 51574.6877 | 3.7373 | 1380000 | 0.043512
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 47677.489 | 0.89958 | 5300000 | 0.0092242
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 21600.3671 | 0.98183 | 2200000 | 0.0057714
GEN-2024-345 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 9067.8757 | 0.68696 | 1320000 | 0.0048186
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 533008 TV1MNDV4 138 533020 NEOSHOS4 138 1 | Current Study | 22.77 | (265.00, 265.00) | 12369542.2473 | 45.2699 | 27324000 | 0.15652
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532996 TIOGA 4 138 533001 ALTOONA4 138 1 | Current Study | 16.38 | (134.00, 134.00) | 11909264.3202 | 60.5884 | 19656000 | 0.033758
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 533001 ALTOONA4 138 533006 TAYLOR 4 138 1 | Current Study | 21.66 | (265.00, 265.00) | 11671614.4152 | 44.9046 | 25992000 | 0.14495
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 533002 DEARING4 138 533004 MONTGOM4 138 1 | Current Study | 11.45 | (265.00, 265.00) | 6175453.5014 | 44.9451 | 13740000 | 0.1383
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 533002 DEARING4 138 533003 LIBERTY4 138 1 | Current Study | 10.03 | (395.00, 395.00) | 5443762.8429 | 45.229 | 12036000 | 0.1526
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 533003 LIBERTY4 138 533008 TV1MNDV4 138 1 | Current Study | 8.36 | (265.00, 265.00) | 4541474.4483 | 45.2699 | 10032000 | 0.15652
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510422 COFFEYT4 138 787350 G24-346-TAP 138 1 | Current Study | 6.1 | (525.00, 525.00) | 4206687.2416 | 57.4684 | 7320000 | 0.53857
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510379 DELWARE4 138 763113 G18-079-TAP 138 1 | Current Study | 12.23 | (395.00, 395.00) | 3552251.651 | 24.2045 | 14676000 | 0.21077
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 2573970.9083 | 2.862 | 89936000 | 0.030391
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 2569812.5765 | 2.5589 | 100427000 | 0.029876
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510422 COFFEYT4 138 533002 DEARING4 138 1 | Current Study | 5.02 | (717.00, 717.00) | 2495018.8021 | 41.418 | 6024000 | 0.3278
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 2150505.8498 | 2.2523 | 95480000 | 0.082804
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 533680 CHRYJCT2 69 533697 LIBERT-2 69 1 | Current Study | 3.84 | (106.00, 106.00) | 2014388.5852 | 61.7153 | 3264000 | 0.019312
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 1907706.8023 | 2.2523 | 84700000 | 0.082804
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 1393852.5211 | 2.1119 | 66000000 | 0.044129
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 1367534.6853 | 0.91021 | 150244000 | 0.018752
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 1227610.6344 | 23.1625 | 5300000 | 0.15652
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1215451.6189 | 0.55673 | 218320000 | 0.015617
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 533004 MONTGOM4 138 533006 TAYLOR 4 138 1 | Current Study | 1.88 | (265.00, 265.00) | 1013048.7119 | 44.9046 | 2256000 | 0.14495
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 816861.1993 | 0.56807 | 143796000 | 0.025794
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 673132.1967 | 2.5712 | 26180000 | 0.026411
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 526889.4282 | 0.44925 | 117282000 | 0.0085942
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 401162.8888 | 1.5856 | 25300000 | 0.029525
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 400147.1017 | 3.3346 | 12000000 | 0.082804
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 381888.9252 | 2.537 | 15053000 | 0.030504
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 335019.3305 | 2.7918 | 12000000 | 0.086535
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 333473.4554 | 2.7789 | 12000000 | 0.082804
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 333473.4554 | 2.7789 | 12000000 | 0.082804
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 329739.3231 | 0.35085 | 93984000 | 0.019791
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 324056.892 | 2.7005 | 12000000 | 0.082804
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 310889.4205 | 2.5907 | 12000000 | 0.082804
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 533683 COFFSUB2 69 533685 CRA S 2 69 1 | Current Study | 0.58 | (140.00, 140.00) | 302628.7625 | 61.3851 | 493000 | 0.023236
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 297081.5906 | 2.4757 | 12000000 | 0.030391
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 274718.27 | 5.1834 | 5300000 | 0.14495
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 269504.2974 | 0.48864 | 55154000 | 0.0078336
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 259214.0792 | 2.1601 | 12000000 | 0.086535
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 258211.2991 | 2.1518 | 12000000 | 0.082804
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 236809.5865 | 1.9734 | 12000000 | 0.062002
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 227140.1982 | 1.8928 | 12000000 | 0.082804
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 214825.9032 | 1.7902 | 12000000 | 0.082804
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 203730.6159 | 1.6978 | 12000000 | 0.056919
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 193116.1372 | 3.6437 | 5300000 | 0.15652
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 192068.1626 | 3.6239 | 5300000 | 0.082804
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 190688.637 | 2.8892 | 6600000 | 0.086535
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 190688.637 | 2.8892 | 6600000 | 0.086535
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 180664.6914 | 1.5055 | 12000000 | 0.030391
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 180664.6914 | 1.5055 | 12000000 | 0.030391
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 170226.6356 | 1.4186 | 12000000 | 0.030391
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 165771.1233 | 1.3814 | 12000000 | 0.044024
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 161073.0781 | 1.3423 | 12000000 | 0.030391
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 159287.4699 | 3.0054 | 5300000 | 0.086535
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 147205.9576 | 2.2304 | 6600000 | 0.082804
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 132126.4864 | 4.0654 | 3250000 | 0.086535
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 129000.8604 | 0.48864 | 26400000 | 0.0078336
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 101188.4194 | 3.1135 | 3250000 | 0.086535
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 100671.9921 | 1.8995 | 5300000 | 0.082804
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 100295.8175 | 3.086 | 3250000 | 0.086535
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 100289.6068 | 3.0858 | 3250000 | 0.086535
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 97676.2787 | 3.0054 | 3250000 | 0.086535
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 93712.5563 | 1.7682 | 5300000 | 0.086535
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 91647.095 | 3.7676 | 2432500 | 0.15652
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 91340.161 | 1.7234 | 5300000 | 0.041041
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 90225.1067 | 1.7024 | 5300000 | 0.044024
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 89197.2519 | 2.7445 | 3250000 | 0.086535
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 86066.1527 | 3.5382 | 2432500 | 0.14495
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 84025.9741 | 2.5854 | 3250000 | 0.086535
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 81238.7507 | 1.2309 | 6600000 | 0.038795
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 79281.3217 | 2.2523 | 3520000 | 0.082804
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 73200.0734 | 2.2523 | 3250000 | 0.082804
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 72874.2225 | 2.2423 | 3250000 | 0.038795
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 72874.2225 | 2.2423 | 3250000 | 0.038795
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 65621.1506 | 2.0191 | 3250000 | 0.082804
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 59904.9582 | 0.48624 | 12320000 | 0.0094849
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 55438.0025 | 4.0172 | 1380000 | 0.086535
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 55326.239 | 0.10349 | 53460000 | 0.003396
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 52968.7789 | 1.6298 | 3250000 | 0.038795
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 45609.2814 | 3.305 | 1380000 | 0.086535
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 44557.2153 | 0.38214 | 11660000 | 0.019791
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 41055.666 | 1.2633 | 3250000 | 0.038795
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 36385.2398 | 0.55129 | 6600000 | 0.019791
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 30616.8956 | 0.94206 | 3250000 | 0.038795
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 26960.9573 | 0.22467 | 12000000 | 0.0069117
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 19178.443 | 1.3897 | 1380000 | 0.044129
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 10750.0717 | 0.48864 | 2200000 | 0.0078336
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 7661.0233 | 0.55515 | 1380000 | 0.019791
GEN-2024-346 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 5930.1005 | 0.44925 | 1320000 | 0.0085942
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 24909916.502 | 1.6446 | 1514620000 | 0.050829
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 23992015.8582 | 2.2344 | 1073760000 | 0.19233
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 21903910.6658 | 1.7044 | 1285130000 | 0.26992
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 21846903.0767 | 1.718 | 1271630000 | 0.1778
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 11709407.9207 | 1.2478 | 938400000 | 0.10638
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 11056536.1278 | 1.5255 | 724760000 | 0.18186
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 10536252.4731 | 1.1228 | 938400000 | 0.1694
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 7966733.6285 | 1.65 | 482840000 | 0.21071
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 7850883.7893 | 1.6727 | 469340000 | 0.14356
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 5117525.8646 | 1.3963 | 366500000 | 0.046119
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1 | Current Study | 4.86 | (217.00, 217.00) | 4860000 | 100 | 4860000 | 0.47475
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527956 SBCRDWRDLEA 115 528505 LEA_ROAD 3 115 1 | Current Study | 4 | (217.00, 217.00) | 2892631.1744 | 72.3158 | 4000000 | 0.52525
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1 | Current Study | 3.54 | (217.00, 217.00) | 2559978.5893 | 72.3158 | 3540000 | 0.52525
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1 | Current Study | 3.11 | (217.00, 217.00) | 2249020.7381 | 72.3158 | 3110000 | 0.52525
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526460 AMOCO_SS 6 230 777420 G24-015-TAP 230 1 | Current Study | 25.97 | (519.00, 519.00) | 2039616.2205 | 4.1335 | 49343000 | 0.047361
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1621259.917 | 1.9187 | 84500000 | 0.059204
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1289085.0803 | 1.5255 | 84500000 | 0.18186
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 1269345.839 | 1.5022 | 84500000 | 0.095971
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 1262671.069 | 0.63816 | 197860000 | 0.031698
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1219476.063 | 0.97696 | 124824000 | 0.064236
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1153056.3597 | 0.58085 | 198511000 | 0.031205
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 1004542.691 | 3.7907 | 26500000 | 0.059876
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 906951.3518 | 0.54946 | 165062000 | 0.034745
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528547 S_JAL 3 115 785400 G24-281-TAP 115 1 | Current Study | 10.82 | (260.00, 260.00) | 880267.0382 | 8.1356 | 10820000 | 0.050879
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 844147.2704 | 1.5287 | 55220000 | 0.074939
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 843763.468 | 1.0354 | 81488000 | 0.069098
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 647418.4533 | 1.4893 | 43472000 | 0.045617
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528016 SAND_DUNES 3 115 528018 RED_BLUFF 3 115 1 | Current Study | 7.69 | (394.00, 394.00) | 460681.0785 | 5.9907 | 7690000 | 0.032087
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528018 RED_BLUFF 3 115 528235 WOLFCAMP_TP3 115 1 | Current Study | 7.81 | (598.00, 598.00) | 365190.981 | 4.6759 | 7810000 | 0.063005
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 358991.6123 | 1.9301 | 18600000 | 0.25771
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 319410.9093 | 1.7173 | 18600000 | 0.1778
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 316820.3468 | 1.7033 | 18600000 | 0.26992
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 314977.1511 | 1.6934 | 18600000 | 0.1778
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 311131.458 | 1.6727 | 18600000 | 0.14356
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 305901.4452 | 1.6446 | 18600000 | 0.050829
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 283751.2721 | 1.5255 | 18600000 | 0.18186
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 262889.5915 | 1.4134 | 18600000 | 0.27351
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | Current Study | 0.78 | (598.00, 598.00) | 236145.0414 | 4.4623 | 5292000 | 0.063349
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 220410.3009 | 0.88164 | 25000000 | 0.013098
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 220410.3009 | 0.88164 | 25000000 | 0.01503
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | Current Study | 0.2 | (598.00, 598.00) | 199911.1462 | 4.4623 | 4480000 | 0.063349
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 196455.4235 | 1.0562 | 18600000 | 0.10638
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 191894.7783 | 1.0317 | 18600000 | 0.18186
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 191894.7783 | 1.0317 | 18600000 | 0.18186
GEN-2024-351 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 129936.1201 | 0.71788 | 18100000 | 0.011053
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 89480.6967 | 0.55262 | 16192000 | 0.062273
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 83481.9154 | 0.55886 | 14938000 | 0.059824
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 80815.9102 | 0.55886 | 14460953.1406 | 0.059824
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 70783.8453 | 1.0797 | 6556000 | 0.074939
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 70681.018 | 1.3336 | 5300000 | 0.19194
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 27112.1301 | 1.9646 | 1380000 | 0.17494
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 25922.6016 | 0.21602 | 12000000 | 0.030205
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 25268.1204 | 1.831 | 1380000 | 0.19194
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 17335.5206 | 0.78353 | 2212500 | 0.032381
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1 | Current Study | 2.13 | (598.00, 598.00) | 17331.3116 | 0.81368 | 2130000 | 0.008918
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 16802.4275 | 1.2176 | 1380000 | 0.19194
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 12859.0585 | 0.5812 | 2212500 | 0.062273
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 10999.7827 | 0.79709 | 1380000 | 0.0057315
GEN-2024-351 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 9726.3338 | 0.70481 | 1380000 | 0.044838
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 9118.2775 | 0.55262 | 1650000 | 0.062273
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 528184 SENDERO +3 115 528187 SENDERO_345 345 M2 | Current Study |  | (435.00, 435.00) | 7974.9683 | 0.04747 | 16800000 | 0.00018862
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 6403.1472 | 0.28941 | 2212500 | 0.030205
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 4063.3582 | 0.29445 | 1380000 | 0.030205
GEN-2024-351 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528184 SENDERO +3 115 528193 BLACKRIVER 3 115 1 | Current Study | 0.25 | (598.00, 598.00) | 2034.1915 | 0.81368 | 250000 | 0.008918
GEN-2024-352 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 1872992.9075 | 0.19959 | 938400000 | 0.030114
GEN-2024-352 | 03 CENTRAL | TBD | ERIS | Rebuild line 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | Current Study | 17.54 | (1793.00, 1793.00) | 1867793.3721 | 4.8403 | 38588000 | 0.023375
GEN-2024-352 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 1171775.6961 | 0.59028 | 198511000 | 0.020053
GEN-2024-352 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 776821.1079 | 0.82655 | 93984000 | 0.051546
GEN-2024-352 | 03 CENTRAL | TBD | ERIS | Rebuild line 645458 S3458 3 345 778170 G24-040-TAP 345 1 | Current Study | 13.15 | (1793.00, 1793.00) | 625503.6198 | 2.1621 | 28930000 | 0.033695
GEN-2024-352 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 606523.0318 | 0.42179 | 143796000 | 0.021173
GEN-2024-352 | 03 CENTRAL | TBD | ERIS | Rebuild line 640139 COOPER 3 345 778170 G24-040-TAP 345 1 | Current Study | 12.59 | (1793.00, 1793.00) | 598866.2033 | 2.1621 | 27698000 | 0.033695
GEN-2024-352 | 03 CENTRAL | TBD | ERIS | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | Current Study | 6.07 | (364.00, 364.00) | 371094.3592 | 4.0757 | 9105000 | 0.032909
GEN-2024-352 | 03 CENTRAL | TBD | ERIS | Rebuild line 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 | Current Study | 3.23 | (1793.00, 1793.00) | 232929.3407 | 3.2779 | 7106000 | 0.037135
GEN-2024-352 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 222046.1907 | 0.48361 | 45914000 | 0.024571
GEN-2024-352 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 121183.8099 | 0.48361 | 25058000 | 0.024571
GEN-2024-352 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 104970.754 | 0.90026 | 11660000 | 0.051546
GEN-2024-352 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 49288.9128 | 0.26499 | 18600000 | 0.046711
GEN-2024-352 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 49288.9128 | 0.26499 | 18600000 | 0.046711
GEN-2024-352 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 29984.6794 | 0.20073 | 14938000 | 0.021487
GEN-2024-352 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 29027.115 | 0.20073 | 14460953.1406 | 0.021487
GEN-2024-352 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 28945.0717 | 0.15562 | 18600000 | 0.030114
GEN-2024-352 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 8353.1952 | 0.50625 | 1650000 | 0.030844
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 25049889.2053 | 1.6539 | 1514620000 | 0.051115
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 22124606.6906 | 1.7216 | 1285130000 | 0.27264
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 22094436.8809 | 1.7375 | 1271630000 | 0.17981
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 10766610.1514 | 1.4855 | 724760000 | 0.17709
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 9889479.306 | 1.0539 | 938400000 | 0.089844
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 8898006.0822 | 0.94821 | 938400000 | 0.14306
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 8055181.0248 | 1.6683 | 482840000 | 0.21305
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 7950545.3731 | 1.694 | 469340000 | 0.14538
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 6110067.1552 | 1.6671 | 366500000 | 0.055064
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 4236991.2769 | 0.39459 | 1073760000 | 0.033966
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 3087464.0222 | 5.5912 | 55220000 | 0.27409
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 2220254.7853 | 8.881 | 25000000 | 0.1514
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 2220254.7853 | 8.881 | 25000000 | 0.13194
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1631672.3888 | 1.931 | 84500000 | 0.059585
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1255282.5181 | 1.4855 | 84500000 | 0.17709
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 1248921.7047 | 0.63121 | 197860000 | 0.031352
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 1209437.9735 | 1.4313 | 84500000 | 0.091441
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1188594.8061 | 0.95222 | 124824000 | 0.062609
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1147493.1312 | 0.57805 | 198511000 | 0.031055
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 896202.7187 | 0.54295 | 165062000 | 0.034333
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 817121.6923 | 1.0028 | 81488000 | 0.066916
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 618204.1284 | 1.4221 | 43472000 | 0.043559
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1 | Current Study | 18.95 | (901.00, 901.00) | 357400.7822 | 0.99264 | 36005000 | 0.029138
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 323029.9576 | 1.7367 | 18600000 | 0.17981
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 320012.5161 | 1.7205 | 18600000 | 0.27264
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 318545.9632 | 1.7126 | 18600000 | 0.17981
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 315081.0584 | 1.694 | 18600000 | 0.14538
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 307620.3531 | 1.6539 | 18600000 | 0.051115
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 276310.7081 | 1.4855 | 18600000 | 0.17709
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 258891.5269 | 3.9489 | 6556000 | 0.27409
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 186862.8876 | 1.0046 | 18600000 | 0.17709
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 186862.8876 | 1.0046 | 18600000 | 0.17709
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 165921.4419 | 0.89205 | 18600000 | 0.089844
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 137509.0228 | 0.7393 | 18600000 | 0.14306
GEN-2024-355 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 133047.474 | 0.73507 | 18100000 | 0.011318
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 125152.6707 | 0.67286 | 18600000 | 0.089844
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 87419.0891 | 0.53989 | 16192000 | 0.060839
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 82865.4087 | 0.55473 | 14938000 | 0.059382
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 80219.0917 | 0.55473 | 14460953.1406 | 0.059382
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 67345.1612 | 1.2707 | 5300000 | 0.18288
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 27862.9675 | 2.0191 | 1380000 | 0.17979
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 25537.6953 | 0.21281 | 12000000 | 0.029756
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 24075.5678 | 1.7446 | 1380000 | 0.18288
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 17165.815 | 0.77586 | 2212500 | 0.032064
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 16009.4212 | 1.1601 | 1380000 | 0.18288
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 12562.79 | 0.56781 | 2212500 | 0.060839
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 11999.1672 | 0.8695 | 1380000 | 0.0062522
GEN-2024-355 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 9592.6562 | 0.69512 | 1380000 | 0.044221
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 8908.1952 | 0.53989 | 1650000 | 0.060839
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 6308.0714 | 0.28511 | 2212500 | 0.029756
GEN-2024-355 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 4003.0243 | 0.29007 | 1380000 | 0.029756
GEN-2024-359 | 01 NORTH | TBD | NRIS | Rebuild line 652216 WATFORD4 230 659302 CHARL_CK-BE4 230 1 | Current Study | 34.26 | (637.00, 637.00) | 15637574.925 | 24.0231 | 65094000 | 0.028402
GEN-2024-359 | 01 NORTH | TBD | NRIS | Rebuild line 652424 BELFELD3 345 659183 CHARL_CK-BE3 345 1 | Current Study | 40.74 | (1793.00, 1793.00) | 11998326.5348 | 13.3868 | 89628000 | 0.27221
GEN-2024-359 | 01 NORTH | TBD | ERIS | Rebuild line 640404 WAYSIDE 4 230 652484 NUNDRWD4 230 1 | Current Study | 80.12 | (519.00, 519.00) | 6217263.9642 | 4.0842 | 152228000 | 0.046877
GEN-2024-359 | 01 NORTH | TBD | ERIS | Rebuild line 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Current Study | 36.8 | (1793.00, 1793.00) | 2697707.5128 | 3.3321 | 80960000 | 0.093301
GEN-2024-359 | 01 NORTH | TBD | NRIS | Rebuild line 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 | Current Study | 13.41 | (217.00, 217.00) | 1650952.5509 | 12.3114 | 13410000 | 0.01002
GEN-2024-359 | 01 NORTH | TBD | ERIS | Rebuild line 652884 NUNDRWD-LNX3 230 785430 G24-282-TAP 230 1 | Current Study | 35.21 | (519.00, 519.00) | 1543217.9005 | 2.3068 | 66899000 | 0.067333
GEN-2024-359 | 01 NORTH | TBD | ERIS | Rebuild line 652529 WATERTN3 345 659165 CROCKER_-BE3 345 1 | Current Study | 44.23 | (1793.00, 1793.00) | 1436378.0571 | 1.4761 | 97306000 | 0.070787
GEN-2024-359 | 01 NORTH | TBD | NRIS | Rebuild line 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 | Current Study | 7.43 | (217.00, 217.00) | 914733.5909 | 12.3114 | 7430000 | 0.01002
GEN-2024-359 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 659120 BROADLND-BE3 345 659204 BD.KU2A_-BE9 13 659205 BROADLND-BE4 230 M2 | Current Study |  | (471.00, 478.00) | 684505.7767 | 2.738 | 25000000 | 0.046403
GEN-2024-359 | 01 NORTH | TBD | NRIS | Rebuild line 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 | Current Study | 5 | (217.00, 217.00) | 615567.6924 | 12.3114 | 5000000 | 0.01002
GEN-2024-359 | 01 NORTH | TBD | ERIS | Rebuild line 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | Current Study | 4.2 | (519.00, 519.00) | 396201.7994 | 4.9649 | 7980000 | 0.039893
GEN-2024-359 | 01 NORTH | TBD | ERIS | Add 24 MVAR switched shunt at DH_CS_EA-TS4 230 kV | Current Study |  |  | 216861.9646 | 5.6696 | 3825000 | 0.032224
GEN-2024-359 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 652237 WATERT19 13 652529 WATERTN3 345 652530 WATERTN4 230 M2 | Current Study |  | (400.00, 478.00) | 181071.1828 | 0.72428 | 25000000 | 0.0051984
GEN-2024-359 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 659160 GROTON__-BE3 345 659161 GRT.KU2A-BE9 13 659187 GROTON__-BE7 115 M2 | Current Study |  | (400.00, 400.00) | 121119.4224 | 0.72095 | 16800000 | 0.0045969
GEN-2024-359 | 01 NORTH | TBD | ERIS | Add 60 MVAR switched shunt at WAYSIDE 4 230 kV | Current Study |  |  | 116215.1595 | 3.0383 | 3825000 | 0.097906
GEN-2024-359 | 01 NORTH | TBD | ERIS | Add 24 MVAR switched shunt at DAYTON__-ER7 115 kV | Current Study |  |  | 73723.8341 | 3.3322 | 2212500 | 0.093301
GEN-2024-359 | 01 NORTH | TBD | ERIS | Add 0.4 MVAR switched shunt at SHINDLER-ER7 115 kV | Current Study |  |  | 70789.0141 | 3.1995 | 2212500 | 0.09853
GEN-2024-359 | 01 NORTH | TBD | ERIS | Add 14.4 MVAR switched shunt at SW145-ER8 69 kV | Current Study |  |  | 45983.6796 | 3.3322 | 1380000 | 0.093301
GEN-2024-359 | 01 NORTH | TBD | ERIS | Add 0.5 MVAR switched shunt at ORLAND-ER8 69 kV | Current Study |  |  | 45983.6796 | 3.3322 | 1380000 | 0.093301
GEN-2024-359 | 01 NORTH | TBD | ERIS | Add 4.4 MVAR switched shunt at DESMET-ER7 115 kV | Current Study |  |  | 37769.2066 | 1.7071 | 2212500 | 0.097906
GEN-2024-359 | 01 NORTH | TBD | ERIS | Add 10 MVAR switched shunt at REDFIELD 115 kV | Current Study |  |  | 32659.7231 | 1.4761 | 2212500 | 0.070787
GEN-2024-359 | 01 NORTH | TBD | ERIS | Add 54 MVAR switched shunt at REDFELD-ER7 115 kV | Current Study |  |  | 32659.7231 | 1.4761 | 2212500 | 0.070787
GEN-2024-359 | 01 NORTH | TBD | ERIS | Add line and rebuild line 652568 GROTONSOUTH7 115 659187 GROTON__-BE7 115 M2 | Current Study | 0.1 | (598.00, 598.00) | 30392.8051 | 0.7003 | 4340000 | 0.0045969
GEN-2024-359 | 01 NORTH | TBD | ERIS | Add 5.5 MVAR switched shunt at LOOMIS-ER8 69 kV | Current Study |  |  | 23189.9537 | 1.6804 | 1380000 | 0.09853
GEN-2024-359 | 01 NORTH | TBD | ERIS | Add 4 MVAR switched shunt at MOS-RDFL-ER8 69 kV | Current Study |  |  | 20370.8103 | 1.4761 | 1380000 | 0.070787
GEN-2024-359 | 01 NORTH | TBD | ERIS | Rebuild line 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Current Study | 0 | (880.00, 880.00) | 7330.7269 | 3.3321 | 220000 | 0.093301
GEN-2024-359 | 01 NORTH | TBD | ERIS | Rebuild line 652484 NUNDRWD4 230 652884 NUNDRWD-LNX3 230 Z | Current Study | 0.14514 | (519.00, 519.00) | 6361.3278 | 2.3068 | 275765.6361 | 0.067333
GEN-2024-359 | 01 NORTH | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 4306.8646 | 0.31209 | 1380000 | 0.097906
GEN-2024-360 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 515055 MAUD 4 138 787770 G24-360-TAP 138 1 | Current Study | 5.11 | (395.00, 395.00) | 4555411.5174 | 74.2892 | 6132000 | 0.39619
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 1 | Current Study |  | (1868.00, 1868.00) | 3551066.8756 | 5.7741 | 61500000 | 0.17579
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 2 | Current Study |  | (1868.00, 1868.00) | 3551066.8756 | 5.7741 | 61500000 | 0.17579
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 1784619.6036 | 1.5216 | 117282000 | 0.040025
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 1717611.9365 | 1.1432 | 150244000 | 0.032384
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1070185.0962 | 1.0656 | 100427000 | 0.017107
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1035793.2122 | 0.47444 | 218320000 | 0.0183
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 1027071.807 | 1.142 | 89936000 | 0.016674
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 1017883.0388 | 1.8295 | 55638000 | 0.051577
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 981160.7517 | 1.0276 | 95480000 | 0.051946
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 897656.2284 | 1.3601 | 66000000 | 0.039077
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 870384.5378 | 1.0276 | 84700000 | 0.051946
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 852180.4625 | 0.59263 | 143796000 | 0.037
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 829106.1727 | 1.5033 | 55154000 | 0.033137
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 765662.9533 | 1.7077 | 44836000 | 0.050114
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 710065.0594 | 0.3577 | 198511000 | 0.023901
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 636047.2514 | 1.3535 | 46992000 | 0.068524
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 635110.9415 | 0.50881 | 124824000 | 0.041609
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 627551.6162 | 0.31717 | 197860000 | 0.019594
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 518161.9536 | 0.55133 | 93984000 | 0.042764
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 452599.1008 | 0.2742 | 165062000 | 0.021565
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 428431.3487 | 0.32226 | 132946000 | 0.012524
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 425443.8096 | 1.2664 | 33594000 | 0.064594
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 421137.5742 | 0.51681 | 81488000 | 0.042895
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 396859.7556 | 1.5033 | 26400000 | 0.033137
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 388986.8949 | 0.615 | 63250000 | 0.041742
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 360292.3255 | 0.78471 | 45914000 | 0.049587
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 343270.3091 | 1.3112 | 26180000 | 0.018519
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 320204.2367 | 1.2472 | 25674000 | 0.054729
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 278269.3819 | 1.0999 | 25300000 | 0.028161
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 228643.0813 | 0.42769 | 53460000 | 0.019297
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 226533.8839 | 1.265 | 17908000 | 0.056429
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR SVC at JAY 4 138 kV | Current Study |  |  | 212428.586 | 4.0081 | 5300000 | 0.027873
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 196632.9462 | 0.78471 | 25058000 | 0.049587
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 186595.8883 | 1.5146 | 12320000 | 0.040623
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 175632.9071 | 1.4636 | 12000000 | 0.040623
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 175632.9071 | 1.4636 | 12000000 | 0.040623
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 158512.0594 | 1.053 | 15053000 | 0.017409
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 156586.9498 | 1.3049 | 12000000 | 0.040623
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 146318.2727 | 1.2193 | 12000000 | 0.051577
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 142255.4537 | 1.1855 | 12000000 | 0.051946
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 123581.3192 | 1.0298 | 12000000 | 0.030337
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 122728.9287 | 1.0227 | 12000000 | 0.065045
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 118982.0689 | 0.99152 | 12000000 | 0.040623
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 118982.0689 | 0.99152 | 12000000 | 0.040623
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 118543.2922 | 0.98786 | 12000000 | 0.016674
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at CENTRTN5 161 kV | Current Study |  |  | 118268.5997 | 3.639 | 3250000 | 0.029104
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 116969.574 | 0.97475 | 12000000 | 0.051577
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 113920.0648 | 0.94933 | 12000000 | 0.040025
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 112840.6055 | 0.94034 | 12000000 | 0.040623
GEN-2024-360 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 112617.7542 | 0.6222 | 18100000 | 0.011915
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 110924.1706 | 0.92437 | 12000000 | 0.040623
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 108295.7293 | 0.90246 | 12000000 | 0.038462
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 106618.5144 | 0.88849 | 12000000 | 0.030337
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 105748.1551 | 0.88123 | 12000000 | 0.040623
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 103631.9556 | 0.8636 | 12000000 | 0.051946
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 103201.6798 | 1.9472 | 5300000 | 0.030337
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at TXPLSTP2 69 kV | Current Study |  |  | 99191.5707 | 7.1878 | 1380000 | 0.09531
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 96553.9426 | 1.8218 | 5300000 | 0.030236
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 83791.5165 | 0.69826 | 12000000 | 0.038462
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 82393.5456 | 1.2484 | 6600000 | 0.032445
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 75574.4794 | 1.4259 | 5300000 | 0.051577
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 70018.5029 | 0.6005 | 11660000 | 0.042764
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 67520.2968 | 1.274 | 5300000 | 0.040025
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 67162.2258 | 1.0176 | 6600000 | 0.051946
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 4.8 MVAR switched shunt at COWSKIN2 69 kV | Current Study |  |  | 66274.9333 | 4.8025 | 1380000 | 0.027873
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 64785.163 | 1.2224 | 5300000 | 0.040025
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 61640.5178 | 0.93395 | 6600000 | 0.038462
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 61640.5178 | 0.93395 | 6600000 | 0.038462
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 58942.4459 | 1.1121 | 5300000 | 0.042764
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 58576.7155 | 0.88753 | 6600000 | 0.038462
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 57513.389 | 1.0852 | 5300000 | 0.065045
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 57176.9547 | 0.86632 | 6600000 | 0.042764
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 52991.1227 | 0.35474 | 14938000 | 0.04723
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 52545.5224 | 1.6168 | 3250000 | 0.038462
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 52545.5224 | 1.6168 | 3250000 | 0.038462
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 51490.0221 | 0.97151 | 5300000 | 0.038462
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 51298.8447 | 0.35474 | 14460953.1406 | 0.04723
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 44975.0624 | 0.27776 | 16192000 | 0.038929
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 42710.1749 | 1.3142 | 3250000 | 0.038462
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 41259.2649 | 1.2695 | 3250000 | 0.032445
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 41259.2649 | 1.2695 | 3250000 | 0.032445
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 40381.4555 | 0.76191 | 5300000 | 0.027093
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 40199.6156 | 1.3535 | 2970000 | 0.068524
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 38371.6135 | 0.72399 | 5300000 | 0.042764
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 38192.8213 | 1.1752 | 3250000 | 0.038462
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 37721.9702 | 1.5507 | 2432500 | 0.040025
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 37530.1592 | 0.70812 | 5300000 | 0.030337
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 36865.2737 | 0.69557 | 5300000 | 0.030337
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 36171.8249 | 1.0276 | 3520000 | 0.051946
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 34768.015 | 0.656 | 5300000 | 0.030337
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 33680.4359 | 0.63548 | 5300000 | 0.042764
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 33397.2887 | 1.0276 | 3250000 | 0.051946
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 33071.6463 | 1.5033 | 2200000 | 0.033137
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 32709.3773 | 1.0064 | 3250000 | 0.038462
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 32420.8417 | 0.99756 | 3250000 | 0.038462
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 32418.8341 | 0.9975 | 3250000 | 0.038462
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 31574.0701 | 0.97151 | 3250000 | 0.038462
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 29939.4305 | 0.92121 | 3250000 | 0.051946
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 29777.493 | 1.3535 | 2200000 | 0.068524
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 29602.9425 | 0.91086 | 3250000 | 0.038462
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 28833.2062 | 0.88718 | 3250000 | 0.038462
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 27161.5794 | 0.83574 | 3250000 | 0.038462
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 26677.9916 | 0.50336 | 5300000 | 0.0046771
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 24544.9068 | 0.75523 | 3250000 | 0.042764
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 20085.7581 | 1.5216 | 1320000 | 0.040025
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 18792.3715 | 0.35457 | 5300000 | 0.03893
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 18466.0072 | 0.75914 | 2432500 | 0.042764
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 18210.0106 | 0.74861 | 2432500 | 0.042764
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 17920.4552 | 1.2986 | 1380000 | 0.038462
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 17889.5938 | 0.77781 | 2300000 | 0.068524
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 17176.8434 | 0.14314 | 12000000 | 0.024893
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 16392.2271 | 0.67388 | 2432500 | 0.038205
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 15657.6945 | 1.1346 | 1380000 | 0.032445
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 14743.2997 | 1.0684 | 1380000 | 0.038462
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 12351.3629 | 0.89503 | 1380000 | 0.039077
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 12038.7824 | 0.87238 | 1380000 | 0.042764
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 12027.5648 | 0.22694 | 5300000 | 0.040623
GEN-2024-360 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 11740.5232 | 0.22152 | 5300000 | 0.047278
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 6686.9257 | 0.30223 | 2212500 | 0.019092
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 6483.2948 | 0.29303 | 2212500 | 0.019092
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 4583.0566 | 0.27776 | 1650000 | 0.038929
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 946974.9527 | 0.80743 | 117282000 | 0.042477
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 892331.2159 | 0.59392 | 150244000 | 0.033648
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 710075.3353 | 1.2762 | 55638000 | 0.07196
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 612147.7242 | 0.60954 | 100427000 | 0.019571
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 564391.5143 | 0.62755 | 89936000 | 0.018325
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 546585.8928 | 0.25036 | 218320000 | 0.019313
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 529944.8218 | 0.55503 | 95480000 | 0.056115
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 489124.2615 | 0.7411 | 66000000 | 0.042585
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 476467.1697 | 1.0627 | 44836000 | 0.062372
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 470112.3419 | 0.55503 | 84700000 | 0.056115
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 445639.272 | 0.30991 | 143796000 | 0.038697
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 435936.5078 | 0.7904 | 55154000 | 0.034846
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 306851.7508 | 0.15458 | 198511000 | 0.020657
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 302089.4312 | 0.32143 | 93984000 | 0.049862
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 297615.886 | 0.23843 | 124824000 | 0.038996
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 281678.2315 | 0.14236 | 197860000 | 0.017589
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 263437.8899 | 0.78418 | 33594000 | 0.079994
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 260216.9651 | 0.56675 | 45914000 | 0.071627
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 209087.3121 | 0.44494 | 46992000 | 0.045052
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 208665.261 | 0.7904 | 26400000 | 0.034846
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 203313.5337 | 0.12317 | 165062000 | 0.019375
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 202732.1848 | 0.15249 | 132946000 | 0.011853
GEN-2024-361 | 04 SOUTHEAST | TBD | NRIS | Add 5 MVAR switched shunt at CTNWOOD4 138 kV | Current Study |  |  | 194833.83 | 8.0096 | 2432500 | 0.19781
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 193131.7806 | 0.23701 | 81488000 | 0.039343
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 188242.8699 | 0.71903 | 26180000 | 0.020311
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 146487.066 | 0.579 | 25300000 | 0.029649
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 142015.8712 | 0.56675 | 25058000 | 0.071627
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 122445.7606 | 0.22904 | 53460000 | 0.020669
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at TXPLSTP2 69 kV | Current Study |  |  | 118928.306 | 8.618 | 1380000 | 0.22855
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 102071.6079 | 0.8506 | 12000000 | 0.07196
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 98929.4645 | 0.803 | 12320000 | 0.043075
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 93117.1975 | 0.77598 | 12000000 | 0.043075
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 93117.1975 | 0.77598 | 12000000 | 0.043075
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 0.06 MVAR switched shunt at G24-125-TAP 345 kV | Current Study |  |  | 90942.8151 | 1.7159 | 5300000 | 0.030638
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 90566.7301 | 0.60165 | 15053000 | 0.019894
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 83019.3964 | 0.69183 | 12000000 | 0.043075
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 81597.9595 | 0.67998 | 12000000 | 0.07196
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 76835.0797 | 0.64029 | 12000000 | 0.056115
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 65141.3996 | 0.54284 | 12000000 | 0.018325
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 63523.7496 | 0.52936 | 12000000 | 0.067334
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 63082.01 | 0.52568 | 12000000 | 0.043075
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 63082.01 | 0.52568 | 12000000 | 0.043075
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 60942.3476 | 0.50785 | 12000000 | 0.02992
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 60449.6067 | 0.50375 | 12000000 | 0.042477
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 59825.924 | 0.49855 | 12000000 | 0.043075
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 58809.867 | 0.49008 | 12000000 | 0.043075
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 56065.6429 | 0.46721 | 12000000 | 0.043075
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 55973.7386 | 0.46645 | 12000000 | 0.056115
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 52720.7469 | 0.99473 | 5300000 | 0.07196
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 52577.3848 | 0.43814 | 12000000 | 0.02992
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 51489.474 | 0.42908 | 12000000 | 0.036574
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 50892.422 | 0.96023 | 5300000 | 0.02992
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 45531.5644 | 0.85909 | 5300000 | 0.028517
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 41363.4549 | 0.62672 | 6600000 | 0.032576
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 40820.924 | 0.35009 | 11660000 | 0.049862
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 39838.885 | 0.33199 | 12000000 | 0.036574
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 36275.6916 | 0.54963 | 6600000 | 0.056115
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 35828.4152 | 0.67601 | 5300000 | 0.042477
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 34377.0663 | 0.64862 | 5300000 | 0.042477
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 34363.5296 | 0.64837 | 5300000 | 0.049862
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 33334.2457 | 0.50506 | 6600000 | 0.049862
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 29768.5815 | 0.56167 | 5300000 | 0.067334
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 29307.1376 | 0.44405 | 6600000 | 0.036574
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 29307.1376 | 0.44405 | 6600000 | 0.036574
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 27850.4451 | 0.42198 | 6600000 | 0.036574
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 24982.8994 | 0.7687 | 3250000 | 0.036574
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 24982.8994 | 0.7687 | 3250000 | 0.036574
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 24481.0591 | 0.46191 | 5300000 | 0.036574
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 23117.2933 | 0.15475 | 14938000 | 0.041208
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 22832.9412 | 0.43081 | 5300000 | 0.030638
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 22379.0397 | 0.15475 | 14460953.1406 | 0.041208
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 22370.7052 | 0.42209 | 5300000 | 0.049862
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 20713.0999 | 0.63733 | 3250000 | 0.032576
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 20713.0999 | 0.63733 | 3250000 | 0.032576
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 20306.6589 | 0.62482 | 3250000 | 0.036574
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 20286.0848 | 0.12528 | 16192000 | 0.035118
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 20016.4762 | 0.82288 | 2432500 | 0.042477
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 19635.7419 | 0.37049 | 5300000 | 0.049862
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 19537.1363 | 0.55503 | 3520000 | 0.056115
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 18507.4575 | 0.3492 | 5300000 | 0.02992
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 18179.5788 | 0.34301 | 5300000 | 0.02992
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 18158.872 | 0.55873 | 3250000 | 0.036574
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 18149.5503 | 0.34244 | 5300000 | 0.0063638
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 18038.5586 | 0.55503 | 3250000 | 0.056115
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 17388.7717 | 0.7904 | 2200000 | 0.034846
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 17145.3459 | 0.3235 | 5300000 | 0.02992
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 16170.8987 | 0.49757 | 3250000 | 0.056115
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 15551.7548 | 0.47852 | 3250000 | 0.036574
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 15414.5699 | 0.47429 | 3250000 | 0.036574
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 15413.6154 | 0.47427 | 3250000 | 0.036574
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 15011.9702 | 0.46191 | 3250000 | 0.036574
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 14309.7155 | 0.4403 | 3250000 | 0.049862
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 14074.7927 | 0.43307 | 3250000 | 0.036574
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 13708.8196 | 0.42181 | 3250000 | 0.036574
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 13214.788 | 0.44494 | 2970000 | 0.045052
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 12914.0405 | 0.39736 | 3250000 | 0.036574
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 10765.7084 | 0.44258 | 2432500 | 0.049862
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 10658.1311 | 0.80743 | 1320000 | 0.042477
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 10616.462 | 0.43644 | 2432500 | 0.049862
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 9788.7318 | 0.44494 | 2200000 | 0.045052
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 8520.325 | 0.61741 | 1380000 | 0.036574
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 8476.3407 | 0.15993 | 5300000 | 0.035119
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 8179.9151 | 0.068166 | 12000000 | 0.023709
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 7860.5228 | 0.5696 | 1380000 | 0.032576
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 7018.6272 | 0.5086 | 1380000 | 0.049862
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 7009.7385 | 0.50795 | 1380000 | 0.036574
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 6730.1494 | 0.48769 | 1380000 | 0.042586
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 6376.7841 | 0.12032 | 5300000 | 0.043075
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 5880.8398 | 0.25569 | 2300000 | 0.045052
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 5734.8939 | 0.23576 | 2432500 | 0.026732
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 5530.9996 | 0.24999 | 2212500 | 0.032576
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 4157.0132 | 0.18789 | 2212500 | 0.050077
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 2255.4605 | 0.10194 | 2212500 | 0.012879
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 2067.1961 | 0.12528 | 1650000 | 0.035118
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 8636072.0791 | 0.91873 | 940000000 | 0.018545
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511425 TUTCONT4 138 514898 CIMARON4 138 1 | Current Study | 14.65 | (395.00, 395.00) | 7751252.7597 | 44.0913 | 17580000 | 0.55034
GEN-2024-362 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1 | Current Study | 5.63 | (525.00, 525.00) | 4313595.9698 | 63.8484 | 6756000 | 0.068774
GEN-2024-362 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | Current Study | 4.8 | (395.00, 395.00) | 3422741.7913 | 59.4226 | 5760000 | 0.070138
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 532803 BURNS 7 345 1 | Current Study | 50.03 | (1793.00, 1793.00) | 3181538.1109 | 2.8906 | 110066000 | 0.043098
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532803 BURNS 7 345 1 | Current Study | 45.5 | (1793.00, 1793.00) | 2893463.6028 | 2.8906 | 100100000 | 0.043098
GEN-2024-362 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 514853 DVISION4 138 514863 HAYMAKR4 138 1 | Current Study | 3.36 | (395.00, 395.00) | 2395919.2539 | 59.4226 | 4032000 | 0.070138
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 1668496.0045 | 1.4226 | 117282000 | 0.042767
GEN-2024-362 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 514893 XEROX 4 138 514896 MORGAN 4 138 1 | Current Study | 1.37 | (472.00, 472.00) | 1644000 | 100 | 1644000 | 0.068774
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 1607732.5515 | 1.0701 | 150244000 | 0.034642
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511501 TUTTLE4 138 511575 LEONARD4 138 1 | Current Study | 2.12 | (395.00, 395.00) | 1222519.8602 | 48.055 | 2544000 | 0.55034
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2 | Current Study |  | (478.00, 478.00) | 1108210.6047 | 6.1227 | 18100000 | 0.073188
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 965705.4391 | 0.9616 | 100427000 | 0.017642
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 961405.8071 | 0.44037 | 218320000 | 0.019412
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 928034.6796 | 1.668 | 55638000 | 0.053742
GEN-2024-362 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 514893 XEROX 4 138 514894 CZECHAL4 138 1 | Current Study | 1.17 | (472.00, 472.00) | 896431.134 | 63.8484 | 1404000 | 0.068774
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 848621.8969 | 0.94358 | 89936000 | 0.015745
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 815716.9321 | 0.85433 | 95480000 | 0.049357
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 793087.5363 | 1.438 | 55154000 | 0.036225
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 789383.8746 | 0.54896 | 143796000 | 0.03917
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 764097.7726 | 1.7042 | 44836000 | 0.057156
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 757199.7463 | 1.1473 | 66000000 | 0.037671
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 723619.8591 | 0.85433 | 84700000 | 0.049357
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 723483.9322 | 0.36446 | 198511000 | 0.027831
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 638970.2207 | 0.5119 | 124824000 | 0.047842
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | Current Study | 1.06 | (395.00, 395.00) | 611259.9301 | 48.055 | 1272000 | 0.55034
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 601582.899 | 0.30404 | 197860000 | 0.021466
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511477 S.W.S.-4 138 520814 ANADARK4 138 1 | Current Study | 7.37 | (395.00, 395.00) | 567236.4441 | 6.4138 | 8844000 | 0.027278
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 502491.6641 | 1.0693 | 46992000 | 0.061869
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 433206.5072 | 0.26245 | 165062000 | 0.02359
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 424781.7909 | 0.52128 | 81488000 | 0.049447
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 416536.5098 | 0.4432 | 93984000 | 0.039287
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 410967.2291 | 0.30912 | 132946000 | 0.01373
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 379619.084 | 1.438 | 26400000 | 0.036225
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | Current Study | 13.6 | (1793.00, 1793.00) | 372941.3908 | 1.2465 | 29920000 | 0.033623
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 360079.3645 | 0.78425 | 45914000 | 0.056637
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 319082.0455 | 0.94982 | 33594000 | 0.055366
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 304055.8289 | 1.1614 | 26180000 | 0.018747
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 239424.71 | 0.94634 | 25300000 | 0.027691
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 232389.1828 | 0.4347 | 53460000 | 0.022415
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511477 S.W.S.-4 138 521089 WASHITA4 138 1 | Current Study | 2.05 | (717.00, 717.00) | 216467.4907 | 8.7995 | 2460000 | 0.080038
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 214213.8723 | 4.0418 | 5300000 | 0.056637
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 122 MVAR switched shunt at HOYT 7 345 kV | Current Study |  |  | 199823.1111 | 3.7702 | 5300000 | 0.039763
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 196516.7207 | 0.78425 | 25058000 | 0.056637
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 194611.3206 | 0.75801 | 25674000 | 0.038015
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 138 MVAR switched shunt at GEN-2024-016 345 kV | Current Study |  |  | 175807.5611 | 3.3171 | 5300000 | 0.029667
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 174289.6247 | 1.4147 | 12320000 | 0.043365
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 164049.6569 | 1.3671 | 12000000 | 0.043365
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 164049.6569 | 1.3671 | 12000000 | 0.043365
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 0.06 MVAR switched shunt at G24-125-TAP 345 kV | Current Study |  |  | 158177.7402 | 2.9845 | 5300000 | 0.030451
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 146259.8086 | 1.2188 | 12000000 | 0.043365
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 143002.9622 | 0.95 | 15053000 | 0.01795
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 138265.6206 | 0.77209 | 17908000 | 0.039361
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 133403.0279 | 1.1117 | 12000000 | 0.053742
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 118268.3266 | 0.98557 | 12000000 | 0.049357
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 118084.2101 | 0.98404 | 12000000 | 0.033128
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 114952.459 | 0.95794 | 12000000 | 0.069627
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 111135.0253 | 0.92613 | 12000000 | 0.043365
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 111135.0253 | 0.92613 | 12000000 | 0.043365
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 106644.8849 | 0.88871 | 12000000 | 0.053742
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 106507.3809 | 0.88756 | 12000000 | 0.042767
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 105398.6006 | 0.87832 | 12000000 | 0.043365
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 103608.5573 | 0.8634 | 12000000 | 0.043365
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 101875.94 | 0.84897 | 12000000 | 0.033128
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 98773.9077 | 0.82312 | 12000000 | 0.043365
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 98611.0921 | 1.8606 | 5300000 | 0.033128
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 97946.9339 | 0.81622 | 12000000 | 0.015745
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at CENTRTN5 161 kV | Current Study |  |  | 95374.3497 | 2.9346 | 3250000 | 0.026823
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 94905.0317 | 1.7907 | 5300000 | 0.033965
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 86314.2829 | 0.71929 | 12000000 | 0.049447
GEN-2024-362 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 83910.5148 | 0.46359 | 18100000 | 0.010146
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 78350.3561 | 0.65292 | 12000000 | 0.031802
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 68903.6591 | 1.3001 | 5300000 | 0.053742
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 63126.8072 | 1.1911 | 5300000 | 0.042767
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 60621.9211 | 0.50518 | 12000000 | 0.031802
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 60569.6463 | 1.1428 | 5300000 | 0.042767
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 56285.9982 | 0.48273 | 11660000 | 0.039287
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 55837.3253 | 0.84602 | 6600000 | 0.049357
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 54130.1106 | 0.36237 | 14938000 | 0.055137
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 53869.1697 | 1.0164 | 5300000 | 0.069627
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 52401.4589 | 0.36237 | 14460953.1406 | 0.055137
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 47382.3008 | 0.89401 | 5300000 | 0.039287
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 45963.0682 | 0.69641 | 6600000 | 0.039287
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 44596.0016 | 0.6757 | 6600000 | 0.031802
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 44596.0016 | 0.6757 | 6600000 | 0.031802
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 43165.7833 | 0.26659 | 16192000 | 0.042701
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 42379.386 | 0.64211 | 6600000 | 0.031802
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 39713.5612 | 0.74931 | 5300000 | 0.030451
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 37252.2683 | 0.70287 | 5300000 | 0.031802
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 36764.5158 | 1.5114 | 2432500 | 0.097927
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 35860.7533 | 0.67662 | 5300000 | 0.033128
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 35267.4329 | 1.4498 | 2432500 | 0.042767
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 35225.4431 | 0.66463 | 5300000 | 0.033128
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 33221.4741 | 0.62682 | 5300000 | 0.033128
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CHILD4WT 138 kV | Current Study |  |  | 32326.3449 | 1.3289 | 2432500 | 0.097927
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 31758.6024 | 1.0693 | 2970000 | 0.061869
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 31634.9237 | 1.438 | 2200000 | 0.036225
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 30845.9431 | 0.582 | 5300000 | 0.039287
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 30072.5136 | 0.85433 | 3520000 | 0.049357
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 29884.6885 | 0.56386 | 5300000 | 0.043365
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 27765.8349 | 0.85433 | 3250000 | 0.049357
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 27631.9405 | 0.85021 | 3250000 | 0.031802
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 24891.0411 | 0.76588 | 3250000 | 0.049357
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 23664.75 | 0.72815 | 3250000 | 0.031802
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 23524.8906 | 1.0693 | 2200000 | 0.061869
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 23455.9988 | 0.72172 | 3250000 | 0.031802
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 23454.5463 | 0.72168 | 3250000 | 0.031802
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 22843.3721 | 0.70287 | 3250000 | 0.031802
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 21738.1031 | 0.41015 | 5300000 | 0.0043555
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 21417.2904 | 0.65899 | 3250000 | 0.031802
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 19731.0128 | 0.60711 | 3250000 | 0.039287
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 19651.0004 | 0.60465 | 3250000 | 0.031802
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 18778.7958 | 1.4226 | 1320000 | 0.042767
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 18036.3818 | 0.34031 | 5300000 | 0.042701
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 16492.2265 | 0.13744 | 12000000 | 0.027315
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 14844.3434 | 0.61025 | 2432500 | 0.039287
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 14638.5544 | 0.60179 | 2432500 | 0.039287
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 14133.1895 | 0.61449 | 2300000 | 0.061869
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 11919.588 | 0.86374 | 1380000 | 0.043099
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 11234.3291 | 0.21197 | 5300000 | 0.043365
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 9677.6644 | 0.70128 | 1380000 | 0.039287
GEN-2024-362 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 7205.175 | 0.13595 | 5300000 | 0.03316
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 6203.2655 | 0.28037 | 2212500 | 0.042701
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 4398.6872 | 0.26659 | 1650000 | 0.042701
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 34638096.8292 | 2.2869 | 1514620000 | 0.046884
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 28415949.5817 | 3.0281 | 938400000 | 0.17124
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 25562473.3478 | 2.724 | 938400000 | 0.27262
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 24930890.0518 | 1.94 | 1285130000 | 0.20379
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 24522333.6402 | 1.9284 | 1271630000 | 0.13238
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 17004540.2762 | 2.3462 | 724760000 | 0.18553
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 14774063.9345 | 1.3759 | 1073760000 | 0.078564
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1 | Current Study | 18.95 | (901.00, 901.00) | 11880753.1158 | 32.9975 | 36005000 | 0.64251
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 10194958.058 | 2.1115 | 482840000 | 0.17887
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Rebuild 3-winding transformer and add 3-winding transformer 524263 BSHLND_TR1 1 13 524266 BUSHLAND 3 115 524267 BUSHLAND 6 230 1 | Current Study |  | (323.00, 323.00) | 9974898.1332 | 45.5475 | 21900000 | 0.077177
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 9720554.287 | 2.0711 | 469340000 | 0.11791
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 524243 OUTPOST 3 115 524266 BUSHLAND 3 115 M2 | Current Study | 1.93 | (598.00, 598.00) | 3143687.0738 | 45.5475 | 6902000 | 0.077177
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 2380650.9334 | 1.2032 | 197860000 | 0.039643
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | Current Study | 13.92 | (519.00, 519.00) | 2207218.8416 | 8.3455 | 26448000 | 0.04568
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523095 HITCHLAND 6 230 778320 G24-045-TAP 230 1 | Current Study | 37.8 | (772.00, 772.00) | 2105096.3428 | 2.9311 | 71820000 | 0.050542
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 2058046.6427 | 2.4356 | 84500000 | 0.10322
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1982564.7847 | 2.3462 | 84500000 | 0.18553
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1893490.2011 | 1.5169 | 124824000 | 0.066161
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1862858.4649 | 0.93842 | 198511000 | 0.033442
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | Current Study | 11.15 | (519.00, 519.00) | 1747289.7097 | 8.2478 | 21185000 | 0.044511
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 1696470.6902 | 1.0278 | 165062000 | 0.043111
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524243 OUTPOST 3 115 524560 ARNOT 3 115 1 | Current Study | 3.43 | (598.00, 598.00) | 1562278.5661 | 45.5475 | 3430000 | 0.15435
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 1451427.3603 | 4.0742 | 35625000 | 0.028328
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524300 HILLSIDE 3 115 524560 ARNOT 3 115 1 | Current Study | 3.17 | (598.00, 598.00) | 1443855.1179 | 45.5475 | 3170000 | 0.15435
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 1310171.2583 | 1.6078 | 81488000 | 0.071171
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 1130335.25 | 2.6001 | 43472000 | 0.05283
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 1111244.6456 | 2.0124 | 55220000 | 0.065438
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1028842.4366 | 1.2176 | 84500000 | 0.024922
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524300 HILLSIDE 3 115 524306 COULTER 3 115 1 | Current Study | 2.11 | (598.00, 598.00) | 961051.8293 | 45.5475 | 2110000 | 0.15435
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523094 HITCHLD_TR21 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2 | Current Study |  | (560.00, 644.00) | 797023.6047 | 3.1881 | 25000000 | 0.023569
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523091 HITCHLD_TR01 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2 | Current Study |  | (560.00, 644.00) | 797023.6047 | 3.1881 | 25000000 | 0.020503
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 732936.4595 | 2.9317 | 25000000 | 0.028891
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 732936.4595 | 2.9317 | 25000000 | 0.033153
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 586369.6535 | 4.1884 | 14000000 | 0.014164
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524281 34TH_ST_TP 3 115 524325 WESTERN 3 115 1 | Current Study | 1.11 | (217.00, 217.00) | 524805.1347 | 47.2797 | 1110000 | 0.076597
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 476750.6135 | 2.5632 | 18600000 | 0.17124
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524281 34TH_ST_TP 3 115 524306 COULTER 3 115 1 | Current Study | 0.96 | (217.00, 217.00) | 453885.5219 | 47.2797 | 960000 | 0.076597
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 436398.8757 | 2.3462 | 18600000 | 0.18553
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 433677.9144 | 2.3316 | 18600000 | 0.27262
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 433677.9144 | 2.3316 | 18600000 | 0.27262
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 425366.4952 | 2.2869 | 18600000 | 0.046884
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 395040.2706 | 2.1239 | 18600000 | 0.27262
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 385226.7221 | 2.0711 | 18600000 | 0.11791
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 360602.8783 | 1.9387 | 18600000 | 0.20379
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 359607.6064 | 1.9334 | 18600000 | 0.17124
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 358526.8291 | 1.9276 | 18600000 | 0.13238
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 353550.101 | 1.9008 | 18600000 | 0.13238
GEN-2024-364 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 170706.2043 | 0.94313 | 18100000 | 0.0096327
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 170639.998 | 1.0539 | 16192000 | 0.078774
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 135075.1972 | 0.90424 | 14938000 | 0.064208
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 130761.5542 | 0.90424 | 14460953.1406 | 0.064208
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 114598.2878 | 2.1622 | 5300000 | 0.20643
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 93180.6236 | 1.4213 | 6556000 | 0.065438
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 63577.3432 | 2.8736 | 2212500 | 0.078775
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 44804.0109 | 0.37337 | 12000000 | 0.034629
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 40968.3309 | 2.9687 | 1380000 | 0.20643
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 39685.5309 | 2.8758 | 1380000 | 0.013717
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 30125.967 | 2.183 | 1380000 | 0.12895
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 27242.5254 | 1.9741 | 1380000 | 0.20643
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 24522.2614 | 1.1084 | 2212500 | 0.078775
GEN-2024-364 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 20390.3062 | 1.4776 | 1380000 | 0.062352
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 17388.5868 | 1.0539 | 1650000 | 0.078774
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 11067.048 | 0.50021 | 2212500 | 0.034629
GEN-2024-364 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 7023.0122 | 0.50891 | 1380000 | 0.034629
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 19582831.0759 | 1.5238 | 1285130000 | 0.24011
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 19380947.4822 | 1.5241 | 1271630000 | 0.15694
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 18343064.1571 | 1.7083 | 1073760000 | 0.14631
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 16277772.5892 | 1.0747 | 1514620000 | 0.033049
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 10453665.238 | 1.114 | 938400000 | 0.094495
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 10081442.4412 | 1.391 | 724760000 | 0.16499
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 9371060.6043 | 0.99862 | 938400000 | 0.14991
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 6486852.3351 | 1.3435 | 482840000 | 0.17071
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 6421402.7642 | 1.3682 | 469340000 | 0.11683
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 5603862.7069 | 1.529 | 366500000 | 0.05025
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526460 AMOCO_SS 6 230 777420 G24-015-TAP 230 1 | Current Study | 25.97 | (519.00, 519.00) | 3276754.2179 | 6.6408 | 49343000 | 0.075707
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1909869.4557 | 2.2602 | 84500000 | 0.069395
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 1250860.136 | 0.63219 | 197860000 | 0.031244
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 1184548.6158 | 2.1451 | 55220000 | 0.10463
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1175398.5958 | 1.391 | 84500000 | 0.16499
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 1151828.6807 | 1.3631 | 84500000 | 0.08665
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1136435.81 | 0.57248 | 198511000 | 0.030602
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 988082.6192 | 0.79158 | 124824000 | 0.051787
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 908365.5113 | 0.55032 | 165062000 | 0.034625
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 697610.7216 | 2.6325 | 26500000 | 0.041374
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 689640.2729 | 0.84631 | 81488000 | 0.056194
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add 0.9 MVAR switched shunt at GEN-2024-157 138 kV | Current Study |  |  | 498793.4322 | 20.5054 | 2432500 | 1
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 461108.0113 | 1.0607 | 43472000 | 0.032327
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 323574.3298 | 1.7396 | 18600000 | 0.23112
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add 7 MVAR switched shunt at CL-AFTP4 138 kV | Current Study |  |  | 313769.7517 | 12.8991 | 2432500 | 1
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 293101.902 | 1.5758 | 18600000 | 0.15792
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 283357.6016 | 1.5234 | 18600000 | 0.15694
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 283248.0203 | 1.5228 | 18600000 | 0.24011
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 279424.3011 | 1.5023 | 18600000 | 0.15694
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528018 RED_BLUFF 3 115 528235 WOLFCAMP_TP3 115 1 | Current Study | 7.81 | (598.00, 598.00) | 271761.3403 | 3.4797 | 7810000 | 0.046652
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 258726.7915 | 1.391 | 18600000 | 0.16499
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 254480.955 | 1.3682 | 18600000 | 0.11683
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 239216.4179 | 1.2861 | 18600000 | 0.24763
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 199896.0598 | 1.0747 | 18600000 | 0.033049
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add 0.7 MVAR switched shunt at GEN-2024-161 138 kV | Current Study |  |  | 196883.6172 | 8.0939 | 2432500 | 0.038415
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 174971.2694 | 0.94071 | 18600000 | 0.16499
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 174971.2694 | 0.94071 | 18600000 | 0.16499
GEN-2024-365 | 05 SOUTHWEST | TBD | NRIS | Add 0.09 MVAR switched shunt at GRAY CO3 115 kV | Current Study |  |  | 173113.3868 | 7.8243 | 2212500 | 0.14205
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add 18 MVAR switched shunt at FALCNRD4 138 kV | Current Study |  |  | 166096.8543 | 6.8282 | 2432500 | 0.051121
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | Current Study | 0.78 | (598.00, 598.00) | 159842.9938 | 3.0205 | 5292000 | 0.042666
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | Current Study | 0.2 | (598.00, 598.00) | 135316.8201 | 3.0205 | 4480000 | 0.042666
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 126050.8544 | 0.5042 | 25000000 | 0.0085525
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 126050.8544 | 0.5042 | 25000000 | 0.0074532
GEN-2024-365 | 05 SOUTHWEST | TBD | NRIS | Add 16 MVAR switched shunt at UNDERWOOD 2 345 kV | Current Study |  |  | 102231.402 | 1.9289 | 5300000 | 0.1514
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 99327.3436 | 1.5151 | 6556000 | 0.10463
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add 0.7 MVAR switched shunt at ROSEVLT2 69 kV | Current Study |  |  | 94229.6645 | 6.8282 | 1380000 | 0.051121
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 88592.2829 | 0.54714 | 16192000 | 0.061347
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-161-TAP 138 kV | Current Study |  |  | 86481.1141 | 3.5552 | 2432500 | 0.038415
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 82254.7873 | 0.55064 | 14938000 | 0.05865
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 79627.9706 | 0.55064 | 14460953.1406 | 0.05865
GEN-2024-365 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 74495.9766 | 0.41158 | 18100000 | 0.0063055
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 52914.6044 | 0.44096 | 12000000 | 0.061347
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 33007.8362 | 1.4919 | 2212500 | 0.061347
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 528184 SENDERO +3 115 528187 SENDERO_345 345 M2 | Current Study |  | (435.00, 435.00) | 15404.5695 | 0.091694 | 16800000 | 0.00036253
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add 0.5 MVAR switched shunt at RKY_RDG4 138 kV | Current Study |  |  | 15071.9645 | 0.61961 | 2432500 | 0.038415
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 12731.3717 | 0.57543 | 2212500 | 0.061347
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1 | Current Study | 2.13 | (598.00, 598.00) | 12401.4026 | 0.58223 | 2130000 | 0.0063494
GEN-2024-365 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 9068.3027 | 0.65712 | 1380000 | 0.041595
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 9027.7462 | 0.54714 | 1650000 | 0.061347
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 7288.4973 | 0.13752 | 5300000 | 0.019694
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 6079.3785 | 0.27477 | 2212500 | 0.028534
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 5397.2525 | 0.39111 | 1380000 | 0.061347
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 3857.8986 | 0.27956 | 1380000 | 0.028534
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 1590.3467 | 0.11524 | 1380000 | 0.010211
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528184 SENDERO +3 115 528193 BLACKRIVER 3 115 1 | Current Study | 0.25 | (598.00, 598.00) | 1455.5637 | 0.58223 | 250000 | 0.0063494
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 747.967 | 0.054201 | 1380000 | 0.00038778
GEN-2024-365 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 166.9157 | 0.012095 | 1380000 | 0.0012616
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 19582831.0759 | 1.5238 | 1285130000 | 0.24011
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 19380947.4822 | 1.5241 | 1271630000 | 0.15694
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 18343064.1571 | 1.7083 | 1073760000 | 0.14631
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 16277772.5892 | 1.0747 | 1514620000 | 0.033049
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 10453665.238 | 1.114 | 938400000 | 0.094495
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 10081442.4412 | 1.391 | 724760000 | 0.16499
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 9371060.6043 | 0.99862 | 938400000 | 0.14991
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 6486852.3351 | 1.3435 | 482840000 | 0.17071
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 6421402.7642 | 1.3682 | 469340000 | 0.11683
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 5603862.7069 | 1.529 | 366500000 | 0.05025
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526460 AMOCO_SS 6 230 777420 G24-015-TAP 230 1 | Current Study | 25.97 | (519.00, 519.00) | 3276754.2179 | 6.6408 | 49343000 | 0.075707
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1909869.4557 | 2.2602 | 84500000 | 0.069395
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 1250860.136 | 0.63219 | 197860000 | 0.031244
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 1184548.6158 | 2.1451 | 55220000 | 0.10463
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1175398.5958 | 1.391 | 84500000 | 0.16499
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 1151828.6807 | 1.3631 | 84500000 | 0.08665
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1136435.81 | 0.57248 | 198511000 | 0.030602
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 988082.6192 | 0.79158 | 124824000 | 0.051787
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 908365.5113 | 0.55032 | 165062000 | 0.034625
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 697610.7216 | 2.6325 | 26500000 | 0.041374
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 689640.2729 | 0.84631 | 81488000 | 0.056194
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add 0.9 MVAR switched shunt at GEN-2024-157 138 kV | Current Study |  |  | 498793.4322 | 20.5054 | 2432500 | 1
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 461108.0113 | 1.0607 | 43472000 | 0.032327
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 323574.3298 | 1.7396 | 18600000 | 0.23112
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add 7 MVAR switched shunt at CL-AFTP4 138 kV | Current Study |  |  | 313769.7517 | 12.8991 | 2432500 | 1
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 293101.902 | 1.5758 | 18600000 | 0.15792
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 283357.6016 | 1.5234 | 18600000 | 0.15694
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 283248.0203 | 1.5228 | 18600000 | 0.24011
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 279424.3011 | 1.5023 | 18600000 | 0.15694
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528018 RED_BLUFF 3 115 528235 WOLFCAMP_TP3 115 1 | Current Study | 7.81 | (598.00, 598.00) | 271761.3403 | 3.4797 | 7810000 | 0.046652
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 258726.7915 | 1.391 | 18600000 | 0.16499
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 254480.955 | 1.3682 | 18600000 | 0.11683
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 239216.4179 | 1.2861 | 18600000 | 0.24763
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 199896.0598 | 1.0747 | 18600000 | 0.033049
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add 0.7 MVAR switched shunt at GEN-2024-161 138 kV | Current Study |  |  | 196883.6172 | 8.0939 | 2432500 | 0.038415
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 174971.2694 | 0.94071 | 18600000 | 0.16499
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 174971.2694 | 0.94071 | 18600000 | 0.16499
GEN-2024-366 | 05 SOUTHWEST | TBD | NRIS | Add 0.09 MVAR switched shunt at GRAY CO3 115 kV | Current Study |  |  | 173113.3868 | 7.8243 | 2212500 | 0.14205
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add 18 MVAR switched shunt at FALCNRD4 138 kV | Current Study |  |  | 166096.8543 | 6.8282 | 2432500 | 0.051121
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | Current Study | 0.78 | (598.00, 598.00) | 159842.9938 | 3.0205 | 5292000 | 0.042666
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | Current Study | 0.2 | (598.00, 598.00) | 135316.8201 | 3.0205 | 4480000 | 0.042666
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 126050.8544 | 0.5042 | 25000000 | 0.0085525
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 126050.8544 | 0.5042 | 25000000 | 0.0074532
GEN-2024-366 | 05 SOUTHWEST | TBD | NRIS | Add 16 MVAR switched shunt at UNDERWOOD 2 345 kV | Current Study |  |  | 102231.402 | 1.9289 | 5300000 | 0.1514
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 99327.3436 | 1.5151 | 6556000 | 0.10463
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add 0.7 MVAR switched shunt at ROSEVLT2 69 kV | Current Study |  |  | 94229.6645 | 6.8282 | 1380000 | 0.051121
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 88592.2829 | 0.54714 | 16192000 | 0.061347
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-161-TAP 138 kV | Current Study |  |  | 86481.1141 | 3.5552 | 2432500 | 0.038415
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 82254.7873 | 0.55064 | 14938000 | 0.05865
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 79627.9706 | 0.55064 | 14460953.1406 | 0.05865
GEN-2024-366 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 74495.9766 | 0.41158 | 18100000 | 0.0063055
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 52914.6044 | 0.44096 | 12000000 | 0.061347
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 33007.8362 | 1.4919 | 2212500 | 0.061347
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 528184 SENDERO +3 115 528187 SENDERO_345 345 M2 | Current Study |  | (435.00, 435.00) | 15404.5695 | 0.091694 | 16800000 | 0.00036253
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add 0.5 MVAR switched shunt at RKY_RDG4 138 kV | Current Study |  |  | 15071.9645 | 0.61961 | 2432500 | 0.038415
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 12731.3717 | 0.57543 | 2212500 | 0.061347
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1 | Current Study | 2.13 | (598.00, 598.00) | 12401.4026 | 0.58223 | 2130000 | 0.0063494
GEN-2024-366 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 9068.3027 | 0.65712 | 1380000 | 0.041595
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 9027.7462 | 0.54714 | 1650000 | 0.061347
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 7288.4973 | 0.13752 | 5300000 | 0.019694
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 6079.3785 | 0.27477 | 2212500 | 0.028534
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 5397.2525 | 0.39111 | 1380000 | 0.061347
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 3857.8986 | 0.27956 | 1380000 | 0.028534
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 1590.3467 | 0.11524 | 1380000 | 0.010211
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528184 SENDERO +3 115 528193 BLACKRIVER 3 115 1 | Current Study | 0.25 | (598.00, 598.00) | 1455.5637 | 0.58223 | 250000 | 0.0063494
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 747.967 | 0.054201 | 1380000 | 0.00038778
GEN-2024-366 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 166.9157 | 0.012095 | 1380000 | 0.0012616
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 15672037.1973 | 1.6672 | 940000000 | 0.018846
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511423 FLE TAP4 138 511467 L.E.S.-4 138 1 | Current Study | 19.98 | (265.00, 265.00) | 9614524.9631 | 40.1006 | 23976000 | 0.041591
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | Current Study | 17.69 | (265.00, 265.00) | 8463142.7064 | 39.8678 | 21228000 | 0.038078
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 532803 BURNS 7 345 1 | Current Study | 50.03 | (1793.00, 1793.00) | 5667531.6973 | 5.1492 | 110066000 | 0.042993
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511477 S.W.S.-4 138 511586 TONKAWA4 138 1 | Current Study | 11.5 | (265.00, 265.00) | 5533885.7395 | 40.1006 | 13800000 | 0.041591
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 764550 G20-087-TAP 345 1 | Current Study | 14.38 | (1793.00, 1793.00) | 5236288.1406 | 16.5517 | 31636000 | 0.45156
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532803 BURNS 7 345 1 | Current Study | 45.5 | (1793.00, 1793.00) | 5154361.2278 | 5.1492 | 100100000 | 0.042993
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511423 FLE TAP4 138 511586 TONKAWA4 138 1 | Current Study | 8.33 | (265.00, 265.00) | 4008458.1053 | 40.1006 | 9996000 | 0.041591
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2 | Current Study |  | (484.00, 515.00) | 3282403.395 | 18.1348 | 18100000 | 0.070324
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | Current Study | 8.91 | (2390.00, 2390.00) | 3202026.3355 | 16.3352 | 19602000 | 0.45156
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 2904628.3237 | 2.4766 | 117282000 | 0.041693
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 2822851.7908 | 1.8788 | 150244000 | 0.034062
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | Current Study | 13.6 | (1793.00, 1793.00) | 2622658.8627 | 8.7656 | 29920000 | 0.13241
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | Current Study | 5.97 | (2390.00, 2390.00) | 2145465.4571 | 16.3352 | 13134000 | 0.45156
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | Current Study | 11.1 | (395.00, 395.00) | 1976053.7047 | 14.8352 | 13320000 | 0.033539
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | Current Study | 3.9 | (265.00, 265.00) | 1865814.3898 | 39.8678 | 4680000 | 0.038078
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1677112.6925 | 0.76819 | 218320000 | 0.018963
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1634371.4275 | 1.6274 | 100427000 | 0.016721
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 1461112.1607 | 1.6246 | 89936000 | 0.015181
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1418683.6237 | 1.4858 | 95480000 | 0.048071
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 1387569.8539 | 2.5158 | 55154000 | 0.035492
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1382716.4754 | 0.96158 | 143796000 | 0.038422
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1319354.2987 | 0.66463 | 198511000 | 0.028422
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 1303741.4326 | 1.9754 | 66000000 | 0.036323
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 1258509.6662 | 1.4858 | 84700000 | 0.048071
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1175435.6717 | 0.94167 | 124824000 | 0.049285
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 1156067.5981 | 0.58429 | 197860000 | 0.023101
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 971120.9583 | 2.726 | 35625000 | 0.022744
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 915171.2667 | 1.9475 | 46992000 | 0.063101
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 831673.9325 | 0.50386 | 165062000 | 0.025362
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 820288.0918 | 1.2969 | 63250000 | 0.056336
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511477 S.W.S.-4 138 520814 ANADARK4 138 1 | Current Study | 7.37 | (395.00, 395.00) | 805602.064 | 9.109 | 8844000 | 0.021695
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 789568.5279 | 0.96894 | 81488000 | 0.051469
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 752721.4037 | 0.56619 | 132946000 | 0.014082
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 715268.622 | 0.76105 | 93984000 | 0.03778
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511425 TUTCONT4 138 514898 CIMARON4 138 1 | Current Study | 14.65 | (395.00, 395.00) | 704767.5611 | 4.0089 | 17580000 | 0.028022
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 664173.8431 | 2.5158 | 26400000 | 0.035492
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 532778.9425 | 1.5859 | 33594000 | 0.05177
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 524004.0387 | 2.0015 | 26180000 | 0.018093
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 776060 G23-204-TAP 345 1 | Current Study | 17.82 | (1793.00, 1793.00) | 506116.039 | 1.291 | 39204000 | 0.038904
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 443997.4838 | 1.7294 | 25674000 | 0.048568
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | Current Study | 0.93 | (211.00, 211.00) | 440940.5384 | 39.5108 | 1116000 | 0.042163
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 423984.3529 | 0.92343 | 45914000 | 0.037346
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 419854.2323 | 0.37223 | 112794000 | 0.025364
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 419290.4126 | 1.6573 | 25300000 | 0.027156
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 403956.7733 | 0.75562 | 53460000 | 0.02182
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 138 MVAR switched shunt at GEN-2024-016 345 kV | Current Study |  |  | 318934.5859 | 6.0176 | 5300000 | 0.030139
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 315654.0341 | 1.7626 | 17908000 | 0.050322
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 303522.7212 | 2.4637 | 12320000 | 0.042291
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | Current Study | 7.74 | (1793.00, 1793.00) | 295409.472 | 1.7348 | 17028000 | 0.038904
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 285689.8566 | 2.3807 | 12000000 | 0.042291
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 285689.8566 | 2.3807 | 12000000 | 0.042291
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 0.06 MVAR switched shunt at G24-125-TAP 345 kV | Current Study |  |  | 268465.8582 | 5.0654 | 5300000 | 0.028942
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515802 GRACMNT4 138 521089 WASHITA4 138 1 | Current Study | 5.87 | (265.00, 265.00) | 267854.3628 | 3.8026 | 7044000 | 0.008524
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CHILD4WT 138 kV | Current Study |  |  | 266181.3187 | 10.9427 | 2432500 | 0.45156
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 254709.1201 | 2.1226 | 12000000 | 0.042291
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 252230.7905 | 4.7591 | 5300000 | 0.037345
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 242586.371 | 1.6115 | 15053000 | 0.017052
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 231393.4729 | 0.92343 | 25058000 | 0.037346
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 227967.9561 | 9.3718 | 2432500 | 0.34004
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at GRANTTP3 115 kV | Current Study |  |  | 227028.6841 | 10.2612 | 2212500 | 0.045776
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at PNTPR-GOAB3 115 kV | Current Study |  |  | 227028.6841 | 10.2612 | 2212500 | 0.045776
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 210625.141 | 1.7552 | 12000000 | 0.033091
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 205690.6031 | 1.7141 | 12000000 | 0.048071
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 202433.8307 | 1.6869 | 12000000 | 0.068664
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | Current Study | 6.93 | (1793.00, 1793.00) | 196822.904 | 1.291 | 15246000 | 0.038904
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 195536.9911 | 1.6295 | 12000000 | 0.044113
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 193539.8711 | 1.6128 | 12000000 | 0.042291
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 193539.8711 | 1.6128 | 12000000 | 0.042291
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 185415.0242 | 1.5451 | 12000000 | 0.041693
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 183549.9791 | 1.5296 | 12000000 | 0.042291
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 181714.6782 | 1.5143 | 12000000 | 0.033091
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 180432.6473 | 1.5036 | 12000000 | 0.042291
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 175891.2149 | 3.3187 | 5300000 | 0.033091
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 172013.1823 | 1.4334 | 12000000 | 0.042291
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 171217.7551 | 3.2305 | 5300000 | 0.034315
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 168639.739 | 1.4053 | 12000000 | 0.015181
GEN-2024-367 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 166897.1689 | 0.92208 | 18100000 | 0.011301
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 160437.8007 | 1.337 | 12000000 | 0.051469
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 156315.9415 | 1.3026 | 12000000 | 0.044113
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511477 S.W.S.-4 138 521089 WASHITA4 138 1 | Current Study | 2.05 | (717.00, 717.00) | 139059.518 | 5.6528 | 2460000 | 0.028793
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 138816.9671 | 1.1568 | 12000000 | 0.031553
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2 | Current Study |  | (478.00, 478.00) | 118695.8349 | 0.65578 | 18100000 | 0.0043898
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511501 TUTTLE4 138 511575 LEONARD4 138 1 | Current Study | 2.12 | (395.00, 395.00) | 111155.2373 | 4.3693 | 2544000 | 0.028022
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 109895.2804 | 2.0735 | 5300000 | 0.041693
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 107406.6749 | 0.89506 | 12000000 | 0.031553
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 105443.6072 | 1.9895 | 5300000 | 0.041693
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 100996.3146 | 1.9056 | 5300000 | 0.044113
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514948 CEDARLN4 138 766111 G21-088-TAP 138 1 | Current Study | 2.86 | (395.00, 395.00) | 99307.041 | 2.8936 | 3432000 | 0.01984
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 98018.7691 | 0.65617 | 14938000 | 0.055912
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 97111.4875 | 1.4714 | 6600000 | 0.048071
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 96653.2524 | 0.82893 | 11660000 | 0.03778
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 94888.5277 | 0.65617 | 14460953.1406 | 0.055912
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 94864.803 | 1.7899 | 5300000 | 0.068664
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 90290.2307 | 1.7036 | 5300000 | 0.041924
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 82632.979 | 0.51033 | 16192000 | 0.045776
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 79012.8086 | 1.1972 | 6600000 | 0.031553
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 79012.8086 | 1.1972 | 6600000 | 0.031553
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 78926.9488 | 1.1959 | 6600000 | 0.03778
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 75085.5277 | 1.1377 | 6600000 | 0.031553
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 67403.5124 | 1.2718 | 5300000 | 0.028942
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 66001.575 | 1.2453 | 5300000 | 0.031553
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 63964.3202 | 1.2069 | 5300000 | 0.033091
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 62831.1263 | 1.1855 | 5300000 | 0.033091
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 61395.8571 | 2.524 | 2432500 | 0.041693
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 59256.675 | 1.1181 | 5300000 | 0.033091
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 58779.0646 | 1.109 | 5300000 | 0.041924
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 57840.8806 | 1.9475 | 2970000 | 0.063101
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | Current Study | 1.06 | (395.00, 395.00) | 55577.6187 | 4.3693 | 1272000 | 0.028022
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 55347.8203 | 2.5158 | 2200000 | 0.035492
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 52301.7004 | 1.4858 | 3520000 | 0.048071
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 52043.7076 | 0.98196 | 5300000 | 0.042291
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 48956.7932 | 1.5064 | 3250000 | 0.031553
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 48289.9479 | 1.4858 | 3250000 | 0.048071
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 43290.1471 | 1.332 | 3250000 | 0.048071
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 42845.0968 | 1.9475 | 2200000 | 0.063101
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 41927.9373 | 1.2901 | 3250000 | 0.031553
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 41558.0831 | 1.2787 | 3250000 | 0.031553
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 41555.5097 | 1.2786 | 3250000 | 0.031553
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 40472.6639 | 1.2453 | 3250000 | 0.031553
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 37946.0088 | 1.1676 | 3250000 | 0.031553
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 36176.9546 | 0.68258 | 5300000 | 0.0040591
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 34816.5906 | 1.0713 | 3250000 | 0.031553
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 34527.3354 | 0.65146 | 5300000 | 0.045776
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 33881.7381 | 1.0425 | 3250000 | 0.03778
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 32691.3711 | 2.4766 | 1320000 | 0.041693
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 30109.073 | 0.25091 | 12000000 | 0.027926
GEN-2024-367 | 04 SOUTHEAST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 27656.7467 | 2.0041 | 1380000 | 0.10149
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 25740.3023 | 1.1191 | 2300000 | 0.063101
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 25490.4378 | 1.0479 | 2432500 | 0.03778
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 25137.0606 | 1.0334 | 2432500 | 0.03778
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 21233.3271 | 1.5386 | 1380000 | 0.042994
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 20714.9574 | 1.5011 | 1380000 | 0.058501
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 19889.7382 | 0.37528 | 5300000 | 0.042994
GEN-2024-367 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 19701.8908 | 0.37173 | 5300000 | 0.050776
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 16618.3101 | 1.2042 | 1380000 | 0.03778
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514947 CANADN-4 138 766111 G21-088-TAP 138 1 | Current Study | 0.3 | (395.00, 395.00) | 10416.8225 | 2.8936 | 360000 | 0.01984
GEN-2024-367 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 8420.4802 | 0.51033 | 1650000 | 0.045776
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511458 ELKCTY-4 138 511485 CLINTJC4 138 1 | Current Study | 24.08 | (211.00, 211.00) | 28896000 | 100 | 28896000 | 0.029062
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 28396860.5371 | 1.8749 | 1514620000 | 0.046124
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 17857954.945 | 1.903 | 938400000 | 0.12914
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 16292784.1352 | 1.2678 | 1285130000 | 0.15981
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 16237124.7496 | 1.7303 | 938400000 | 0.2078
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 16171370.5924 | 1.2717 | 1271630000 | 0.10476
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | Current Study | 13.92 | (519.00, 519.00) | 13349130.0857 | 50.4731 | 26448000 | 0.33152
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 12282553.4327 | 1.6947 | 724760000 | 0.16081
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | Current Study | 11.15 | (519.00, 519.00) | 10806668.041 | 51.0109 | 21185000 | 0.33035
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 7915988.1691 | 1.6395 | 482840000 | 0.16666
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 7719443.5269 | 0.71892 | 1073760000 | 0.049259
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 7433699.5316 | 1.5839 | 469340000 | 0.1082
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Rebuild 3-winding transformer 512106 SHAM 2WT 69 512107 SHAM 3WT 115 512109 SR1TERT 14 1 | Current Study |  | (68.00, 68.00) | 4725000 | 100 | 4725000 | 0.033253
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 2902051.5397 | 8.1461 | 35625000 | 0.067967
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 1867122.4553 | 0.94366 | 197860000 | 0.03731
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1592295.9658 | 0.80212 | 198511000 | 0.034302
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 1475138.0888 | 1.7457 | 84500000 | 0.088778
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523095 HITCHLAND 6 230 778320 G24-045-TAP 230 1 | Current Study | 37.8 | (772.00, 772.00) | 1440705.6314 | 2.006 | 71820000 | 0.041508
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1432026.8297 | 1.6947 | 84500000 | 0.16081
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1427595.5439 | 1.1437 | 124824000 | 0.059858
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 1326866.7382 | 0.80386 | 165062000 | 0.040462
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 1172414.8257 | 8.3744 | 14000000 | 0.033984
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 983562.6785 | 1.207 | 81488000 | 0.064115
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 865903.3954 | 1.9919 | 43472000 | 0.048565
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523094 HITCHLD_TR21 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2 | Current Study |  | (560.00, 644.00) | 655983.8208 | 2.6239 | 25000000 | 0.023278
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523091 HITCHLD_TR01 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2 | Current Study |  | (560.00, 644.00) | 655983.8208 | 2.6239 | 25000000 | 0.02025
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 440573.0191 | 0.79785 | 55220000 | 0.031133
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 348722.1917 | 1.8749 | 18600000 | 0.046124
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 321473.9825 | 1.2859 | 25000000 | 0.015207
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 321473.9825 | 1.2859 | 25000000 | 0.017449
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 315215.3732 | 1.6947 | 18600000 | 0.16081
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 299613.1082 | 1.6108 | 18600000 | 0.12914
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 294598.3962 | 1.5839 | 18600000 | 0.1082
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 275469.5253 | 1.481 | 18600000 | 0.2078
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 275469.5253 | 1.481 | 18600000 | 0.2078
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 250927.1332 | 1.3491 | 18600000 | 0.2078
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 245752.5823 | 1.3213 | 18600000 | 0.16666
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 244196.2859 | 1.3129 | 18600000 | 0.1082
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 235449.8 | 0.27864 | 84500000 | 0.006844
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 233150.3106 | 1.2535 | 18600000 | 0.10476
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 225994.7856 | 1.215 | 18600000 | 0.12914
GEN-2024-368 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 142394.6292 | 0.78671 | 18100000 | 0.0096421
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 133674.2241 | 0.82556 | 16192000 | 0.074051
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 116296.4379 | 0.77853 | 14938000 | 0.066338
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 112582.4969 | 0.77853 | 14460953.1406 | 0.066338
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 82140.1493 | 1.5498 | 5300000 | 0.17756
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 64545.2108 | 4.6772 | 1380000 | 0.33152
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 49804.5725 | 2.2511 | 2212500 | 0.074052
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 44015.0055 | 3.1895 | 1380000 | 0.018256
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 36943.1419 | 0.5635 | 6556000 | 0.031133
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 36347.7128 | 0.3029 | 12000000 | 0.033712
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 29364.7042 | 2.1279 | 1380000 | 0.17756
GEN-2024-368 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 25615.3635 | 1.8562 | 1380000 | 0.093995
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 19526.5143 | 1.415 | 1380000 | 0.17756
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 19209.9997 | 0.86825 | 2212500 | 0.074052
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 13621.694 | 0.82556 | 1650000 | 0.074051
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 8978.2561 | 0.4058 | 2212500 | 0.033712
GEN-2024-368 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 5697.4906 | 0.41286 | 1380000 | 0.033712
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | Current Study | 300 | (1792.00, 1792.00) | 15481411.5342 | 1.647 | 940000000 | 0.018617
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 532803 BURNS 7 345 1 | Current Study | 50.03 | (1793.00, 1793.00) | 5644687.9434 | 5.1285 | 110066000 | 0.04282
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532803 BURNS 7 345 1 | Current Study | 45.5 | (1793.00, 1793.00) | 5133585.877 | 5.1285 | 100100000 | 0.04282
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511425 TUTCONT4 138 514898 CIMARON4 138 1 | Current Study | 14.65 | (395.00, 395.00) | 4472302.5836 | 25.4397 | 17580000 | 0.17782
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2 | Current Study |  | (478.00, 478.00) | 3466053.686 | 19.1495 | 18100000 | 0.12819
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520861 COLE 4 138 520868 CRINER 4 138 1 | Current Study | 10.06 | (211.00, 211.00) | 3261583.1793 | 27.0178 | 12072000 | 0.071819
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 2938020.0409 | 2.5051 | 117282000 | 0.042172
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 2840997.4692 | 1.8909 | 150244000 | 0.034281
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | Current Study | 11.1 | (395.00, 395.00) | 2634026.5937 | 19.775 | 13320000 | 0.044706
GEN-2024-369 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1 | Current Study | 5.63 | (525.00, 525.00) | 2442404.0302 | 36.1516 | 6756000 | 0.021807
GEN-2024-369 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | Current Study | 4.8 | (395.00, 395.00) | 2337258.2087 | 40.5774 | 5760000 | 0.026821
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515802 GRACMNT4 138 521089 WASHITA4 138 1 | Current Study | 5.87 | (265.00, 265.00) | 2247623.6711 | 31.9083 | 7044000 | 0.071527
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511477 S.W.S.-4 138 520814 ANADARK4 138 1 | Current Study | 7.37 | (395.00, 395.00) | 2174643.8061 | 24.5889 | 8844000 | 0.058563
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520868 CRINER 4 138 520888 PAYNESW4 138 1 | Current Study | 6.54 | (211.00, 211.00) | 2120353.2796 | 27.0178 | 7848000 | 0.071819
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 1695860.6089 | 0.77678 | 218320000 | 0.019175
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 1687830.9013 | 1.6807 | 100427000 | 0.017268
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 1687185.487 | 4.736 | 35625000 | 0.039515
GEN-2024-369 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 514853 DVISION4 138 514863 HAYMAKR4 138 1 | Current Study | 3.36 | (395.00, 395.00) | 1636080.7461 | 40.5774 | 4032000 | 0.026821
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 1517217.4416 | 2.7269 | 55638000 | 0.049202
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 1498187.3189 | 1.6658 | 89936000 | 0.015566
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 1446289.1466 | 1.5148 | 95480000 | 0.049006
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 1398063.563 | 2.5348 | 55154000 | 0.035761
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 1393788.747 | 0.96928 | 143796000 | 0.03873
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | Current Study | 30 | (1793.00, 1793.00) | 1333979.9668 | 2.0212 | 66000000 | 0.037165
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1296787.0148 | 0.65326 | 198511000 | 0.027936
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 1282998.4365 | 1.5148 | 84700000 | 0.049006
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 1149164.8089 | 2.563 | 44836000 | 0.048138
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1139587.3373 | 0.91296 | 124824000 | 0.047782
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 1103307.0383 | 0.55762 | 197860000 | 0.022047
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | Current Study | 13.6 | (1793.00, 1793.00) | 985787.743 | 3.2947 | 29920000 | 0.04977
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 912133.2605 | 1.941 | 46992000 | 0.062891
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 794166.429 | 0.48113 | 165062000 | 0.024218
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 762515.3273 | 0.93574 | 81488000 | 0.049706
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511477 S.W.S.-4 138 521089 WASHITA4 138 1 | Current Study | 2.05 | (717.00, 717.00) | 739820.5529 | 30.074 | 2460000 | 0.15319
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | Current Study | 39.66 | (1195.10, 1481.90) | 739354.0414 | 0.55613 | 132946000 | 0.013832
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 736691.8082 | 0.78385 | 93984000 | 0.038911
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511501 TUTTLE4 138 511575 LEONARD4 138 1 | Current Study | 2.12 | (395.00, 395.00) | 705367.1063 | 27.7267 | 2544000 | 0.17782
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 681614.7996 | 4.8687 | 14000000 | 0.019757
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 669196.7593 | 2.5348 | 26400000 | 0.035761
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520973 LEXNGTN4 138 520976 LIL AXE4 138 1 | Current Study | 9.71 | (265.00, 265.00) | 589225.338 | 5.0569 | 11652000 | 0.033638
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 580791.1048 | 0.91825 | 63250000 | 0.039888
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 560363.5149 | 1.668 | 33594000 | 0.05445
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 541414.3229 | 1.1792 | 45914000 | 0.047689
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 535043.4016 | 2.0437 | 26180000 | 0.018474
GEN-2024-369 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 514893 XEROX 4 138 514894 CZECHAL4 138 1 | Current Study | 1.17 | (472.00, 472.00) | 507568.866 | 36.1516 | 1404000 | 0.021807
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 764550 G20-087-TAP 345 1 | Current Study | 14.38 | (1793.00, 1793.00) | 464374.4061 | 1.4679 | 31636000 | 0.040046
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 424512.7365 | 1.6779 | 25300000 | 0.027495
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 407670.7875 | 0.76257 | 53460000 | 0.022021
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 388718.447 | 1.5141 | 25674000 | 0.042521
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 122 MVAR switched shunt at HOYT 7 345 kV | Current Study |  |  | 352994.9396 | 6.6603 | 5300000 | 0.039336
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | Current Study | 1.06 | (395.00, 395.00) | 352683.5532 | 27.7267 | 1272000 | 0.17782
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 322091.0996 | 6.0772 | 5300000 | 0.047689
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 138 MVAR switched shunt at GEN-2024-016 345 kV | Current Study |  |  | 315311.7541 | 5.9493 | 5300000 | 0.029797
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 306962.6849 | 2.4916 | 12320000 | 0.04277
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 295481.9903 | 1.1792 | 25058000 | 0.047689
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 288927.7763 | 2.4077 | 12000000 | 0.04277
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 288927.7763 | 2.4077 | 12000000 | 0.04277
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | Current Study | 8.91 | (2390.00, 2390.00) | 283968.1541 | 1.4487 | 19602000 | 0.040046
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 275893.7223 | 1.5406 | 17908000 | 0.043983
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 0.06 MVAR switched shunt at G24-125-TAP 345 kV | Current Study |  |  | 274456.7893 | 5.1784 | 5300000 | 0.029588
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 257595.9138 | 2.1466 | 12000000 | 0.04277
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 249909.2702 | 1.6602 | 15053000 | 0.017566
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514948 CEDARLN4 138 766111 G21-088-TAP 138 1 | Current Study | 2.86 | (395.00, 395.00) | 246855.6018 | 7.1928 | 3432000 | 0.049318
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 218096.8635 | 1.8175 | 12000000 | 0.049202
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 210224.5999 | 1.7519 | 12000000 | 0.033028
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 209693.0554 | 1.7474 | 12000000 | 0.049006
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 203327.4125 | 1.6944 | 12000000 | 0.068968
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 195733.3917 | 1.6311 | 12000000 | 0.04277
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 195733.3917 | 1.6311 | 12000000 | 0.04277
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | Current Study | 5.97 | (2390.00, 2390.00) | 190268.2245 | 1.4487 | 13134000 | 0.040046
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 187546.6045 | 1.5629 | 12000000 | 0.042172
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 185630.2773 | 1.5469 | 12000000 | 0.04277
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 182477.6147 | 1.5206 | 12000000 | 0.04277
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 181369.1154 | 1.5114 | 12000000 | 0.033028
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | Current Study |  |  | 175556.7265 | 3.3124 | 5300000 | 0.033028
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 174350.727 | 1.4529 | 12000000 | 0.049202
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 173962.7261 | 1.4497 | 12000000 | 0.04277
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 172918.9481 | 1.441 | 12000000 | 0.015566
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at CENTRTN5 161 kV | Current Study |  |  | 170870.0886 | 5.2575 | 3250000 | 0.026911
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | Current Study |  |  | 169755.7566 | 3.2029 | 5300000 | 0.034022
GEN-2024-369 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 158797.9411 | 0.87734 | 18100000 | 0.010753
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 154940.6553 | 1.2912 | 12000000 | 0.049706
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 145077.7441 | 5.9641 | 2432500 | 0.2164
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 141640.0321 | 1.1803 | 12000000 | 0.032195
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CHILD4WT 138 kV | Current Study |  |  | 127564.1224 | 5.2442 | 2432500 | 0.2164
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 112648.657 | 2.1254 | 5300000 | 0.049202
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 111158.6657 | 2.0973 | 5300000 | 0.042172
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 109590.9613 | 0.91326 | 12000000 | 0.032195
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 106655.8148 | 2.0124 | 5300000 | 0.042172
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 99548.1377 | 0.85376 | 11660000 | 0.038911
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 99001.1417 | 1.5 | 6600000 | 0.049006
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 96895.0949 | 0.64865 | 14938000 | 0.055271
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 95283.5545 | 1.7978 | 5300000 | 0.068968
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 93800.7382 | 0.64865 | 14460953.1406 | 0.055271
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 83800.9559 | 1.5812 | 5300000 | 0.038911
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 81290.8827 | 1.2317 | 6600000 | 0.038911
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 80619.6604 | 1.2215 | 6600000 | 0.032195
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 80619.6604 | 1.2215 | 6600000 | 0.032195
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 79232.4909 | 0.48933 | 16192000 | 0.043892
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 76612.512 | 1.1608 | 6600000 | 0.032195
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 68907.6508 | 1.3001 | 5300000 | 0.029588
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 67343.8226 | 1.2706 | 5300000 | 0.032195
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | Current Study |  |  | 63842.6807 | 1.2046 | 5300000 | 0.033028
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 62711.6417 | 1.1832 | 5300000 | 0.033028
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 62101.6801 | 2.553 | 2432500 | 0.042172
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | Current Study |  |  | 59143.9879 | 1.1159 | 5300000 | 0.033028
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 57648.8718 | 1.941 | 2970000 | 0.062891
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 55766.3966 | 2.5348 | 2200000 | 0.035761
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 54554.5378 | 1.0293 | 5300000 | 0.038911
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 53319.4155 | 1.5148 | 3520000 | 0.049006
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 52633.5547 | 0.99309 | 5300000 | 0.04277
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 49952.4079 | 1.537 | 3250000 | 0.032195
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 49229.6029 | 1.5148 | 3250000 | 0.049006
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 44132.513 | 1.3579 | 3250000 | 0.049006
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 42780.6089 | 1.3163 | 3250000 | 0.032195
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 42702.868 | 1.941 | 2200000 | 0.062891
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 42403.2332 | 1.3047 | 3250000 | 0.032195
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 42400.6074 | 1.3046 | 3250000 | 0.032195
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 41295.7403 | 1.2706 | 3250000 | 0.032195
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 38717.7015 | 1.1913 | 3250000 | 0.032195
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 37968.7303 | 0.71639 | 5300000 | 0.0042602
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 35524.6416 | 1.0931 | 3250000 | 0.032195
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 34896.527 | 1.0737 | 3250000 | 0.038911
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | Current Study |  |  | 33106.4821 | 0.62465 | 5300000 | 0.043893
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 33067.1924 | 2.5051 | 1320000 | 0.042172
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 29656.1417 | 0.24713 | 12000000 | 0.027506
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 26253.8996 | 1.0793 | 2432500 | 0.038911
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514947 CANADN-4 138 766111 G21-088-TAP 138 1 | Current Study | 0.3 | (395.00, 395.00) | 25893.9442 | 7.1928 | 360000 | 0.049318
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 25889.9385 | 1.0643 | 2432500 | 0.038911
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 25654.8558 | 1.1154 | 2300000 | 0.062892
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 21147.7439 | 1.5324 | 1380000 | 0.042821
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 19809.5706 | 0.37377 | 5300000 | 0.042821
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 17116.0436 | 1.2403 | 1380000 | 0.038911
GEN-2024-369 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 14348.7071 | 0.27073 | 5300000 | 0.03698
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 13262.8634 | 0.96108 | 1380000 | 0.037456
GEN-2024-369 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 8073.9631 | 0.48933 | 1650000 | 0.043892
GEN-2024-370 | 03 CENTRAL | TBD | ERIS | Rebuild line 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 | Current Study | 7.49 | (364.00, 364.00) | 8025000 | 71.4286 | 11235000 | 0.18905
GEN-2024-370 | 03 CENTRAL | TBD | ERIS | Rebuild line 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | Current Study | 17.54 | (1793.00, 1793.00) | 3446119.8336 | 8.9305 | 38588000 | 0.034329
GEN-2024-370 | 03 CENTRAL | TBD | ERIS | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | Current Study | 2.29 | (446.00, 446.00) | 2453571.4286 | 71.4286 | 3435000 | 0.81095
GEN-2024-370 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 2399481.5097 | 0.2557 | 938400000 | 0.030709
GEN-2024-370 | 03 CENTRAL | TBD | ERIS | Rebuild line 645458 S3458 3 345 778170 G24-040-TAP 345 1 | Current Study | 13.15 | (1793.00, 1793.00) | 1848034.1166 | 6.388 | 28930000 | 0.079244
GEN-2024-370 | 03 CENTRAL | TBD | ERIS | Rebuild line 640139 COOPER 3 345 778170 G24-040-TAP 345 1 | Current Study | 12.59 | (1793.00, 1793.00) | 1769334.5649 | 6.388 | 27698000 | 0.079244
GEN-2024-370 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 1604573.5772 | 0.8083 | 198511000 | 0.021858
GEN-2024-370 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 955028.7422 | 1.0162 | 93984000 | 0.050443
GEN-2024-370 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 931938.7353 | 0.6481 | 143796000 | 0.025896
GEN-2024-370 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 304930.5211 | 0.66413 | 45914000 | 0.026859
GEN-2024-370 | 03 CENTRAL | TBD | ERIS | Rebuild line 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 | Current Study | 3.23 | (1793.00, 1793.00) | 288292.4527 | 4.057 | 7106000 | 0.036585
GEN-2024-370 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 166418.7175 | 0.66413 | 25058000 | 0.026859
GEN-2024-370 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 129051.7034 | 1.1068 | 11660000 | 0.050443
GEN-2024-370 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 64172.8315 | 0.34502 | 18600000 | 0.048409
GEN-2024-370 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 64172.8315 | 0.34502 | 18600000 | 0.048409
GEN-2024-370 | 03 CENTRAL | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 41269.7045 | 0.27627 | 14938000 | 0.023541
GEN-2024-370 | 03 CENTRAL | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 39951.7514 | 0.27627 | 14460953.1406 | 0.023541
GEN-2024-370 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 37081.3814 | 0.19936 | 18600000 | 0.030709
GEN-2024-370 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 14981.391 | 0.90796 | 1650000 | 0.044034
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | Current Study | 314.6 | (5300.00, 5300.00) | 31264622.9274 | 2.0642 | 1514620000 | 0.050782
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | Current Study | 220.8 | (5300.00, 5300.00) | 28397124.1536 | 2.6446 | 1073760000 | 0.18121
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | Current Study | 262.9 | (5300.00, 5300.00) | 27438246.1193 | 2.1351 | 1285130000 | 0.26914
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | Current Study | 262.9 | (5300.00, 5300.00) | 27350114.9915 | 2.1508 | 1271630000 | 0.17718
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | Current Study | 192 | (5300.00, 5300.00) | 14774349.4265 | 1.5744 | 938400000 | 0.10684
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | Current Study | 140.8 | (5300.00, 5300.00) | 13880968.0615 | 1.9153 | 724760000 | 0.18174
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 13268892.3761 | 1.414 | 938400000 | 0.16982
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | Current Study | 92.2 | (5300.00, 5300.00) | 9993316.5702 | 2.0697 | 482840000 | 0.21039
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | Current Study | 92.2 | (5300.00, 5300.00) | 9841233.4624 | 2.0968 | 469340000 | 0.14324
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | Current Study | 115 | (1195.00, 1195.00) | 6786937.1125 | 1.8518 | 366500000 | 0.048687
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526460 AMOCO_SS 6 230 777420 G24-015-TAP 230 1 | Current Study | 25.97 | (519.00, 519.00) | 3033691.0088 | 6.1482 | 49343000 | 0.056073
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | Current Study |  | (1650.00, 1650.00) | 2020990.4674 | 2.3917 | 84500000 | 0.058746
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | Current Study |  | (1650.00, 1650.00) | 1618386.502 | 1.9153 | 84500000 | 0.18174
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | Current Study |  | (2300.00, 2300.00) | 1594536.9144 | 1.887 | 84500000 | 0.095964
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 1589629.8136 | 0.80341 | 197860000 | 0.031765
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 1531730.7713 | 1.2271 | 124824000 | 0.064225
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 1449754.2637 | 0.73031 | 198511000 | 0.031231
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | Current Study | 25.1 | (2390.00, 2390.00) | 1215482.5678 | 2.2012 | 55220000 | 0.085892
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 1141701.5876 | 0.69168 | 165062000 | 0.034816
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | Current Study |  | (522.00, 522.00) | 1066927.4525 | 4.0261 | 26500000 | 0.050621
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 1059736.5703 | 1.3005 | 81488000 | 0.069081
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | Current Study | 19.76 | (1793.00, 1793.00) | 814097.0411 | 1.8727 | 43472000 | 0.04566
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528013 PHANTOM 3 115 528228 WOOD_DRAW 3 115 1 | Current Study | 7.71 | (260.00, 260.00) | 658430.7424 | 8.54 | 7710000 | 0.009982
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528016 SAND_DUNES 3 115 528018 RED_BLUFF 3 115 1 | Current Study | 7.69 | (394.00, 394.00) | 634766.1219 | 8.2544 | 7690000 | 0.035192
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527956 SBCRDWRDLEA 115 528505 LEA_ROAD 3 115 1 | Current Study | 4 | (217.00, 217.00) | 440263.8214 | 11.0066 | 4000000 | 0.063636
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 435643.1155 | 2.3422 | 18600000 | 0.24894
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528018 RED_BLUFF 3 115 528235 WOLFCAMP_TP3 115 1 | Current Study | 7.81 | (598.00, 598.00) | 408278.5542 | 5.2276 | 7810000 | 0.056069
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 399870.1815 | 2.1498 | 18600000 | 0.17718
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | Current Study |  |  | 396869.5263 | 2.1337 | 18600000 | 0.26914
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | Current Study |  |  | 394319.5643 | 2.12 | 18600000 | 0.17718
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | Current Study |  |  | 390009.2521 | 2.0968 | 18600000 | 0.14324
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1 | Current Study | 3.54 | (217.00, 217.00) | 389633.4819 | 11.0066 | 3540000 | 0.063636
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | Current Study |  |  | 383939.1969 | 2.0642 | 18600000 | 0.050782
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | Current Study |  |  | 356236.5555 | 1.9153 | 18600000 | 0.18174
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1 | Current Study | 3.11 | (217.00, 217.00) | 342305.1211 | 11.0066 | 3110000 | 0.063636
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 699.00) | 328512.5035 | 1.3141 | 25000000 | 0.017831
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | Current Study |  | (615.00, 637.00) | 328512.5035 | 1.3141 | 25000000 | 0.015539
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 320526.7909 | 1.7233 | 18600000 | 0.26544
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | Current Study |  |  | 247877.6975 | 1.3327 | 18600000 | 0.10684
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 240914.9898 | 1.2952 | 18600000 | 0.18174
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 240914.9898 | 1.2952 | 18600000 | 0.18174
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | Current Study | 0.78 | (598.00, 598.00) | 236742.2214 | 4.4736 | 5292000 | 0.050553
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | Current Study | 0.2 | (598.00, 598.00) | 200416.6954 | 4.4736 | 4480000 | 0.050553
GEN-2024-371 | 05 SOUTHWEST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 163042.4167 | 0.90079 | 18100000 | 0.01104
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 112647.1117 | 0.6957 | 16192000 | 0.062403
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 104963.6994 | 0.70266 | 14938000 | 0.059873
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | Current Study | 2.98 | (2390.00, 2390.00) | 101921.2323 | 1.5546 | 6556000 | 0.085892
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 101611.6708 | 0.70266 | 14460953.1406 | 0.059873
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 88788.6413 | 1.6753 | 5300000 | 0.19193
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 33943.5976 | 2.4597 | 1380000 | 0.17434
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | Current Study |  |  | 32604.7363 | 0.27171 | 12000000 | 0.03024
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | Current Study |  |  | 31741.5078 | 2.3001 | 1380000 | 0.19193
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1 | Current Study | 2.13 | (598.00, 598.00) | 23766.3004 | 1.1158 | 2130000 | 0.0097345
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | Current Study |  |  | 21789.4438 | 0.98483 | 2212500 | 0.032397
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 21107.0066 | 1.5295 | 1380000 | 0.19193
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 16188.249 | 0.73167 | 2212500 | 0.062403
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 13988.1487 | 1.0136 | 1380000 | 0.0058017
GEN-2024-371 | 05 SOUTHWEST | TBD | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | Current Study |  |  | 12296.3905 | 0.89104 | 1380000 | 0.045121
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 11478.9856 | 0.6957 | 1650000 | 0.062403
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | Current Study |  |  | 8053.7027 | 0.36401 | 2212500 | 0.03024
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add 2-winding transformer 528184 SENDERO +3 115 528187 SENDERO_345 345 M2 | Current Study |  | (435.00, 435.00) | 6251.3598 | 0.03721 | 16800000 | 0.00011769
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | Current Study |  |  | 5110.7804 | 0.37035 | 1380000 | 0.03024
GEN-2024-371 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528184 SENDERO +3 115 528193 BLACKRIVER 3 115 1 | Current Study | 0.25 | (598.00, 598.00) | 2789.4719 | 1.1158 | 250000 | 0.0097345
GEN-2024-372 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 652305 SIOUXC29 13 652552 SIOUXCY2 230 652564 SIOUXCY3 345 M2 | Current Study |  | (600.00, 750.00) | 25000000 | 100 | 25000000 | 0.017042
GEN-2024-372 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659202 LO.KVA2_-BE9 13 M2 | Current Study |  | (500.00, 617.00) | 485750.1616 | 1.943 | 25000000 | 0.008555
GEN-2024-372 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659201 LO.KU1A_-BE9 13 M2 | Current Study |  | (600.00, 637.40) | 479074.4062 | 1.9163 | 25000000 | 0.0096993
GEN-2024-372 | 02 NEBRASKA | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 4172.8579 | 0.30238 | 1380000 | 0.037944
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 521098 WSBNKTP4 138 778530 G24-052-TAP 138 1 | Current Study | 9.45 | (472.00, 472.00) | 5689045.7374 | 50.168 | 11340000 | 0.65991
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505600 TUPELO 4 138 505602 S BROWN4 138 1 | Current Study | 36.9 | (281.00, 281.00) | 3899836.9963 | 8.8072 | 44280000 | 0.094881
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520918 FROGVIL4 138 520948 HUGO PP4 138 1 | Current Study | 6.55 | (717.00, 717.00) | 3613405.9237 | 45.9721 | 7860000 | 0.65991
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 520918 FROGVIL4 138 773820 G23-092-TAP 138 1 | Current Study | 6.3 | (717.00, 717.00) | 3475489.6671 | 45.9721 | 7560000 | 0.65991
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1 | Current Study | 56.1 | (1793.00, 1793.00) | 3420806.5142 | 2.7717 | 123420000 | 0.066255
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 521098 WSBNKTP4 138 773820 G23-092-TAP 138 1 | Current Study | 3.4 | (472.00, 472.00) | 2046852.4346 | 50.168 | 4080000 | 0.65991
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515150 CANEYCK4 138 515151 LTLCITY4 138 1 | Current Study | 11.79 | (265.00, 265.00) | 1824657.2602 | 12.8969 | 14148000 | 0.11595
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1 | Current Study | 30.63 | (1793.00, 1793.00) | 1802847.0377 | 2.6754 | 67386000 | 0.073009
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505598 ALLEN 4 138 505600 TUPELO 4 138 1 | Current Study | 19.4 | (211.00, 211.00) | 1726107.5969 | 7.4146 | 23280000 | 0.033638
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 521049 SCLMNJC4 138 784980 G24-267-TAP 138 1 | Current Study | 6.96 | (472.00, 472.00) | 1511457.8972 | 18.097 | 8352000 | 0.34009
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505596 EXPLOR 4 138 505598 ALLEN 4 138 1 | Current Study | 14.8 | (211.00, 211.00) | 1312946.8102 | 7.3927 | 17760000 | 0.033428
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 1198489.77 | 1.0625 | 112794000 | 0.15084
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | Current Study | 53.31 | (2390.00, 2390.00) | 1192170.4112 | 1.0165 | 117282000 | 0.03565
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 1172501.4202 | 0.7804 | 150244000 | 0.029475
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 1 | Current Study |  | (1868.00, 1868.00) | 995450.1194 | 1.6186 | 61500000 | 0.065705
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 2 | Current Study |  | (1868.00, 1868.00) | 995450.1194 | 1.6186 | 61500000 | 0.065705
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515151 LTLCITY4 138 515157 BROWN 4 138 1 | Current Study | 6.37 | (265.00, 265.00) | 985841.1151 | 12.8969 | 7644000 | 0.11595
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 776060 G23-204-TAP 345 1 | Current Study | 17.82 | (1793.00, 1793.00) | 934306.8208 | 2.3832 | 39204000 | 0.14962
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | Current Study | 28.75 | (1793.00, 1793.00) | 857468.9621 | 1.3557 | 63250000 | 0.12269
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | Current Study | 40.88 | (2390.00, 2390.00) | 720483.6212 | 0.80111 | 89936000 | 0.015596
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | Current Study | 67.2 | (1792.00, 1792.00) | 696700.378 | 0.31912 | 218320000 | 0.016412
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 691347.0148 | 0.72408 | 95480000 | 0.048803
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515044 SEMINOL4 138 515531 VANOSTP4 138 1 | Current Study | 21.55 | (395.00, 395.00) | 680488.6312 | 2.6314 | 25860000 | 0.03635
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 662186.7577 | 1.1902 | 55638000 | 0.044738
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | Current Study | 29.17 | (1713.00, 1792.00) | 655788.8728 | 0.653 | 100427000 | 0.013977
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 613291.7067 | 0.72408 | 84700000 | 0.048803
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 585987.9443 | 0.40751 | 143796000 | 0.033923
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 521049 SCLMNJC4 138 769060 G22-104-TAP 138 1 | Current Study | 2.27 | (472.00, 472.00) | 558211.7836 | 20.4924 | 2724000 | 0.34009
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | Current Study | 7.74 | (1793.00, 1793.00) | 545335.5819 | 3.2026 | 17028000 | 0.14962
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 545005.1602 | 0.98815 | 55154000 | 0.029043
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 484855.1528 | 0.24425 | 198511000 | 0.02176
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515178 PARKLN 4 138 515977 LKKONWA4 138 1 | Current Study | 13.56 | (472.00, 472.00) | 483593.9917 | 2.9719 | 16272000 | 0.059916
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | Current Study | 20.38 | (1793.00, 1793.00) | 480914.2769 | 1.0726 | 44836000 | 0.041969
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515117 ARBUCKL4 138 515531 VANOSTP4 138 1 | Current Study | 18.2 | (472.00, 472.00) | 468783.8568 | 2.1464 | 21840000 | 0.035275
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 764550 G20-087-TAP 345 1 | Current Study | 14.38 | (1793.00, 1793.00) | 443383.2291 | 1.4015 | 31636000 | 0.079657
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | Current Study | 60.6 | (956.00, 956.00) | 436953.9671 | 0.22084 | 197860000 | 0.01819
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 423275.6844 | 0.3391 | 124824000 | 0.036974
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 392121.3328 | 0.83444 | 46992000 | 0.056326
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | Current Study | 13.16 | (395.00, 395.00) | 389262.1095 | 2.4649 | 15792000 | 0.040574
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505602 S BROWN4 138 769060 G22-104-TAP 138 1 | Current Study | 1.62 | (717.00, 717.00) | 379453.6513 | 19.5192 | 1944000 | 0.34009
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | Current Study | 6.93 | (1793.00, 1793.00) | 363341.5414 | 2.3832 | 15246000 | 0.14962
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 361500.7489 | 0.38464 | 93984000 | 0.039779
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 507454 TURK 4 138 507456 TURK 3 115 507458 TURK1 1 13 M2 | Current Study |  | (257.00, 257.00) | 350833.5822 | 3.3734 | 10400000 | 0.020641
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | Current Study | 13.6 | (1793.00, 1793.00) | 327214.1507 | 1.0936 | 29920000 | 0.034417
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | Current Study | 50.02 | (1098.00, 1098.00) | 315753.0862 | 0.19129 | 165062000 | 0.02006
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | Current Study | 11.67 | (1793.00, 1793.00) | 315222.6048 | 1.2278 | 25674000 | 0.071837
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 295111.8297 | 0.87847 | 33594000 | 0.059741
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Current Study | 37.04 | (1793.00, 1793.00) | 281082.4195 | 0.34494 | 81488000 | 0.038173
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | Current Study | 8.91 | (2390.00, 2390.00) | 271131.9045 | 1.3832 | 19602000 | 0.079657
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 260872.0352 | 0.98815 | 26400000 | 0.029043
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 224183.7484 | 0.48827 | 45914000 | 0.041139
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | Current Study | 8.14 | (1793.00, 1793.00) | 223877.0791 | 1.2502 | 17908000 | 0.074356
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Current Study | 11.5 | (1793.00, 1793.00) | 199862.1259 | 0.78997 | 25300000 | 0.026968
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 191464.9634 | 1.5955 | 12000000 | 0.039553
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | Current Study | 5.97 | (2390.00, 2390.00) | 181667.505 | 1.3832 | 13134000 | 0.079657
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 | Current Study | 6.08 | (395.00, 395.00) | 179841.4609 | 2.4649 | 7296000 | 0.040574
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | Current Study | 24.3 | (1793.00, 1793.00) | 134764.7449 | 0.25209 | 53460000 | 0.015165
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1 | Current Study | 11.3 | (1793.00, 1793.00) | 127948.4874 | 0.51468 | 24860000 | 0.026458
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | Current Study | 5.6 | (2390.00, 2390.00) | 124875.9016 | 1.0136 | 12320000 | 0.036249
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 122350.4022 | 0.48827 | 25058000 | 0.041139
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | Current Study |  |  | 117539.1058 | 0.97949 | 12000000 | 0.036249
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | Current Study |  |  | 117539.1058 | 0.97949 | 12000000 | 0.036249
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | Current Study |  |  | 104792.9478 | 0.87327 | 12000000 | 0.036249
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 100236.2493 | 0.8353 | 12000000 | 0.048803
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | Current Study | 1.63 | (2390.00, 2390.00) | 96897.7678 | 0.64371 | 15053000 | 0.01419
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 95187.6836 | 0.79323 | 12000000 | 0.044738
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 504122 MCNAB 3 115 507456 TURK 3 115 1 | Current Study | 2.65 | (394.00, 394.00) | 89395.0955 | 3.3734 | 2650000 | 0.041282
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 84485.196 | 0.70404 | 12000000 | 0.027653
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 83723.5198 | 0.6977 | 12000000 | 0.059164
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | Current Study |  |  | 83157.2193 | 0.69298 | 12000000 | 0.015596
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 79626.5701 | 0.66355 | 12000000 | 0.036249
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 79626.5701 | 0.66355 | 12000000 | 0.036249
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 78198.5163 | 0.65165 | 12000000 | 0.040053
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 77133.0986 | 1.4553 | 5300000 | 0.039553
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 76287.0302 | 1.1559 | 6600000 | 0.040053
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 76101.432 | 0.63418 | 12000000 | 0.035651
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 76094.8212 | 0.63412 | 12000000 | 0.044738
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | Current Study |  |  | 75516.5083 | 0.6293 | 12000000 | 0.036249
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 74484.85 | 0.62071 | 12000000 | 0.035272
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 74233.9693 | 0.61862 | 12000000 | 0.036249
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 73021.3026 | 0.60851 | 12000000 | 0.048803
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 72888.7356 | 0.60741 | 12000000 | 0.027653
GEN-2024-373 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 69110.2238 | 0.38182 | 18100000 | 0.0097494
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 57631.0679 | 0.48026 | 12000000 | 0.035272
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | Current Study |  |  | 49165.1487 | 0.92764 | 5300000 | 0.044738
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 48849.0925 | 0.41895 | 11660000 | 0.039779
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 47323.9473 | 0.71703 | 6600000 | 0.048803
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 45749.9663 | 0.69318 | 6600000 | 0.040053
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 45105.2348 | 0.85104 | 5300000 | 0.035651
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | Current Study |  |  | 43278.0975 | 0.81657 | 5300000 | 0.035651
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 42395.8059 | 0.64236 | 6600000 | 0.035272
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 42395.8059 | 0.64236 | 6600000 | 0.035272
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | Current Study |  |  | 41121.7509 | 0.77588 | 5300000 | 0.039779
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | Current Study |  |  | 39890.0394 | 0.60439 | 6600000 | 0.039779
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 39234.6239 | 0.74028 | 5300000 | 0.059164
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 38201.3757 | 1.1754 | 3250000 | 0.040053
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 38201.3757 | 1.1754 | 3250000 | 0.040053
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 36142.2557 | 0.24195 | 14938000 | 0.04295
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | Current Study |  |  | 36140.3481 | 1.112 | 3250000 | 0.035272
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | Current Study |  |  | 36140.3481 | 1.112 | 3250000 | 0.035272
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 35414.3842 | 0.6682 | 5300000 | 0.035272
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 34988.0484 | 0.24195 | 14460953.1406 | 0.04295
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 32644.6457 | 1.4193 | 2300000 | 0.16672
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Current Study | 7.36 | (1793.00, 1793.00) | 31311.0922 | 0.19337 | 16192000 | 0.036136
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | Current Study |  |  | 29375.6826 | 0.90387 | 3250000 | 0.035272
GEN-2024-373 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 27429.0533 | 0.51753 | 5300000 | 0.14727
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 26770.3165 | 0.5051 | 5300000 | 0.039779
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 26361.7315 | 0.49739 | 5300000 | 0.023582
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 26268.6866 | 0.80827 | 3250000 | 0.035272
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 25637.1707 | 1.8578 | 1380000 | 0.15084
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 25487.4476 | 0.72408 | 3520000 | 0.048803
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | Current Study |  |  | 25199.2127 | 1.0359 | 2432500 | 0.035651
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 24782.9494 | 0.83444 | 2970000 | 0.056326
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 23659.4699 | 0.44641 | 5300000 | 0.040053
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 23532.4472 | 0.72408 | 3250000 | 0.048803
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 23120.6822 | 0.71141 | 3250000 | 0.040053
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CHILD4WT 138 kV | Current Study |  |  | 22538.9275 | 0.92657 | 2432500 | 0.079657
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 22519.4977 | 0.69291 | 3250000 | 0.040053
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | Current Study |  |  | 22497.2219 | 0.69222 | 3250000 | 0.035272
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 22298.7698 | 0.68612 | 3250000 | 0.035272
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | Current Study |  |  | 22297.3889 | 0.68607 | 3250000 | 0.035272
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 22018.4708 | 1.5955 | 1380000 | 0.039553
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 21739.3363 | 0.98815 | 2200000 | 0.029043
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 21716.3677 | 0.6682 | 3250000 | 0.035272
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 21095.966 | 0.64911 | 3250000 | 0.048803
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 18681.4954 | 0.57482 | 3250000 | 0.035272
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 18357.7403 | 0.83444 | 2200000 | 0.056326
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 17625.9453 | 0.33257 | 5300000 | 0.0041202
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 17123.9847 | 0.52689 | 3250000 | 0.039779
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 | Current Study | 0.55 | (395.00, 395.00) | 16268.5532 | 2.4649 | 660000 | 0.040574
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 14532.924 | 0.59745 | 2432500 | 0.045162
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 14497.2401 | 1.0505 | 1380000 | 0.040053
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Current Study | 0.6 | (2390.00, 2390.00) | 13417.7874 | 1.0165 | 1320000 | 0.03565
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | Current Study |  |  | 12882.9833 | 0.52962 | 2432500 | 0.039779
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 12704.3849 | 0.52228 | 2432500 | 0.039779
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | Current Study |  |  | 12325.5315 | 0.89315 | 1380000 | 0.035272
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 10140.3118 | 0.73481 | 1380000 | 0.035272
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 9376.2922 | 0.67944 | 1380000 | 0.039553
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | Current Study |  |  | 8398.9696 | 0.60862 | 1380000 | 0.039779
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | Current Study |  |  | 8049.2274 | 0.15187 | 5300000 | 0.036249
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 7983.7165 | 0.36085 | 2212500 | 0.030393
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 7740.5956 | 0.34986 | 2212500 | 0.030393
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 4499.6521 | 0.20337 | 2212500 | 0.036136
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | Current Study | 0.75 | (1793.00, 1793.00) | 3190.6684 | 0.19337 | 1650000 | 0.036136
GEN-2024-374 | 02 NEBRASKA | TBD | NRIS | Rebuild line 652424 BELFELD3 345 659183 CHARL_CK-BE3 345 1 | Current Study | 40.74 | (1793.00, 1793.00) | 8523024.3553 | 9.5093 | 89628000 | 0.08594
GEN-2024-374 | 02 NEBRASKA | TBD | NRIS | Rebuild line 652497 MAURINE4 230 785430 G24-282-TAP 230 1 | Current Study | 36.92 | (637.00, 637.00) | 5109036.8917 | 7.2832 | 70148000 | 0.047484
GEN-2024-374 | 02 NEBRASKA | TBD | NRIS | Add 0.6 MVAR switched shunt at BISON___-GE4 230 kV | Current Study |  |  | 794108.6038 | 20.761 | 3825000 | 0.035195
GEN-2024-374 | 02 NEBRASKA | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 35689.4659 | 2.5862 | 1380000 | 0.36058
GEN-2024-375 | 03 CENTRAL | TBD | ERIS | Rebuild 2-winding transformer 543063 SWAVRLY5 161 543094 SWAVRLY2 69 1 | Current Study |  | (87.00, 87.00) | 6075000 | 100 | 6075000 | 0.088589
GEN-2024-375 | 03 CENTRAL | TBD | ERIS | Rebuild line 543100 AMOCOPL2 69 543102 WHGNSVL2 69 1 | Current Study | 5.7 | (140.00, 140.00) | 4845000 | 100 | 4845000 | 0.088589
GEN-2024-375 | 03 CENTRAL | TBD | ERIS | Rebuild line 543094 SWAVRLY2 69 543658 DOVER_TAP2 69 1 | Current Study | 4.9 | (140.00, 140.00) | 4165000 | 100 | 4165000 | 0.088589
GEN-2024-375 | 03 CENTRAL | TBD | ERIS | Rebuild line 543098 CTY HIG2 69 543657 CORDERTP2 69 1 | Current Study | 2.7 | (140.00, 140.00) | 2295000 | 100 | 2295000 | 0.088589
GEN-2024-375 | 03 CENTRAL | TBD | ERIS | Rebuild line 543099 HIGNSVL2 69 543102 WHGNSVL2 69 1 | Current Study | 2.5 | (140.00, 140.00) | 2125000 | 100 | 2125000 | 0.088589
GEN-2024-375 | 03 CENTRAL | TBD | ERIS | Rebuild line 543096 MAYVWTP2 69 543100 AMOCOPL2 69 1 | Current Study | 1.07 | (106.00, 106.00) | 909500 | 100 | 909500 | 0.088589
GEN-2024-375 | 03 CENTRAL | TBD | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | Current Study | 192 | (5300.00, 5300.00) | 870479.7511 | 0.092762 | 938400000 | 0.027851
GEN-2024-375 | 03 CENTRAL | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | Current Study | 60.81 | (2010.00, 2010.00) | 450168.2982 | 0.22677 | 198511000 | 0.01533
GEN-2024-375 | 03 CENTRAL | TBD | ERIS | Rebuild line 543657 CORDERTP2 69 543658 DOVER_TAP2 69 1 | Current Study | 0.45 | (140.00, 140.00) | 382500 | 100 | 382500 | 0.088589
GEN-2024-375 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 323709.373 | 0.34443 | 93984000 | 0.042745
GEN-2024-375 | 03 CENTRAL | TBD | ERIS | Rebuild line 543098 CTY HIG2 69 543099 HIGNSVL2 69 1 | Current Study | 0.3 | (140.00, 140.00) | 255000 | 100 | 255000 | 0.088589
GEN-2024-375 | 03 CENTRAL | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 197541.69 | 0.13738 | 143796000 | 0.013723
GEN-2024-375 | 03 CENTRAL | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 81002.5536 | 0.17642 | 45914000 | 0.017837
GEN-2024-375 | 03 CENTRAL | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 44207.9102 | 0.17642 | 25058000 | 0.017837
GEN-2024-375 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 43742.3966 | 0.37515 | 11660000 | 0.042745
GEN-2024-375 | 03 CENTRAL | TBD | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 21372.8322 | 0.11491 | 18600000 | 0.040307
GEN-2024-375 | 03 CENTRAL | TBD | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | Current Study |  |  | 21372.8322 | 0.11491 | 18600000 | 0.040307
GEN-2024-375 | 03 CENTRAL | TBD | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | Current Study |  |  | 13452.3194 | 0.072324 | 18600000 | 0.027851
GEN-2024-375 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 0.75 | (2390.00, 2390.00) | 2939.1847 | 0.17813 | 1650000 | 0.021597
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509106 HEMPHIL4 138 509107 SIXMILE4 138 1 | Current Study | 9.32 | (211.00, 211.00) | 9680498.4305 | 86.5567 | 11184000 | 0.51824
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | Current Study | 45.24 | (0.00, 0.00) | 976755.0633 | 0.65011 | 150244000 | 0.020723
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | Current Study | 43.4 | (1793.00, 1793.00) | 625623.9058 | 0.65524 | 95480000 | 0.037274
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | Current Study | 38.5 | (1793.00, 1793.00) | 554988.9487 | 0.65524 | 84700000 | 0.037274
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | Current Study | 43.16 | (1310.00, 1570.00) | 506045.4623 | 0.35192 | 143796000 | 0.024725
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | Current Study | 60.81 | (2010.00, 2010.00) | 394447.5881 | 0.1987 | 198511000 | 0.014941
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV | Current Study |  |  | 385599.1821 | 27.942 | 1380000 | 0.51824
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Current Study | 21.36 | (1793.00, 1793.00) | 358745.1149 | 0.76342 | 46992000 | 0.043492
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | Current Study |  |  | 339996.1941 | 2.8333 | 12000000 | 0.059279
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | Current Study | 37.04 | (830.00, 830.00) | 325123.0902 | 0.26047 | 124824000 | 0.02397
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 294055.2514 | 0.2607 | 112794000 | 0.031235
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at PHILL 7 345 kV | Current Study |  |  | 293651.0286 | 5.5406 | 5300000 | 0.034756
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | Current Study |  |  | 196609.3467 | 1.6384 | 12000000 | 0.077734
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | Current Study |  |  | 179818.9471 | 1.4985 | 12000000 | 0.077734
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | Current Study |  |  | 175423.449 | 2.6579 | 6600000 | 0.077734
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 156660.0066 | 1.3055 | 12000000 | 0.077734
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | Current Study |  |  | 150488.3047 | 1.2541 | 12000000 | 0.077734
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | Current Study |  |  | 143838.5762 | 1.1987 | 12000000 | 0.059279
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | Current Study |  |  | 137808.7832 | 1.1484 | 12000000 | 0.077734
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | Current Study |  |  | 136970.0205 | 2.5843 | 5300000 | 0.059279
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | Current Study |  |  | 110705.4439 | 1.6774 | 6600000 | 0.077734
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | Current Study |  |  | 110705.4439 | 1.6774 | 6600000 | 0.077734
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | Current Study |  |  | 105202.9009 | 1.594 | 6600000 | 0.077734
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 99393.064 | 0.82828 | 12000000 | 0.059279
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | Current Study |  |  | 87844.776 | 2.7029 | 3250000 | 0.077734
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 87844.776 | 2.7029 | 3250000 | 0.077734
GEN-2024-376 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 79083.0185 | 0.43692 | 18100000 | 0.0094157
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 78882.0288 | 0.65735 | 12000000 | 0.03129
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | Current Study |  |  | 78515.8231 | 1.4814 | 5300000 | 0.059279
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | Current Study |  |  | 69640.1547 | 0.58033 | 12000000 | 0.019237
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | Current Study |  |  | 60857.3425 | 0.50714 | 12000000 | 0.024323
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | Current Study |  |  | 60852.0724 | 0.5071 | 12000000 | 0.02338
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | Current Study |  |  | 60852.0724 | 0.5071 | 12000000 | 0.02338
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | Current Study |  |  | 60081.3285 | 0.50068 | 12000000 | 0.019237
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | Current Study |  |  | 54405.3925 | 1.0265 | 5300000 | 0.077734
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | Current Study |  |  | 53166.44 | 1.6359 | 3250000 | 0.077734
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | Current Study |  |  | 51784.0052 | 1.5934 | 3250000 | 0.077734
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 50489.0425 | 2.282 | 2212500 | 0.16222
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 48951.5455 | 2.2125 | 2212500 | 0.16222
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | Current Study |  |  | 48781.7885 | 1.501 | 3250000 | 0.077734
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | Current Study |  |  | 42825.0863 | 0.64886 | 6600000 | 0.037274
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 39813.1682 | 1.225 | 3250000 | 0.077734
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | Current Study |  |  | 39099.5623 | 2.8333 | 1380000 | 0.059279
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | Current Study |  |  | 37710.7516 | 0.31426 | 12000000 | 0.015496
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 33336.674 | 2.4157 | 1380000 | 0.077734
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 32664.4578 | 0.61631 | 5300000 | 0.041571
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | Current Study | 6.79 | (2390.00, 2390.00) | 29439.578 | 0.19708 | 14938000 | 0.029527
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | Current Study |  |  | 28935.083 | 0.54594 | 5300000 | 0.024323
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | Current Study | 6.5732 | (2390.00, 2390.00) | 28499.4215 | 0.19708 | 14460953.1406 | 0.029527
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Current Study | 1.6 | (1793.00, 1793.00) | 23064.4758 | 0.65524 | 3520000 | 0.037274
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 22673.4974 | 0.76342 | 2970000 | 0.043492
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | Current Study |  |  | 21706.7315 | 0.40956 | 5300000 | 0.027223
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 21295.3301 | 0.65524 | 3250000 | 0.037274
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | Current Study |  |  | 20192.2134 | 1.4632 | 1380000 | 0.059279
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 17743.2112 | 0.54594 | 3250000 | 0.024323
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 16795.1833 | 0.76342 | 2200000 | 0.043492
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | Current Study |  |  | 16650.0627 | 1.2065 | 1380000 | 0.059279
GEN-2024-376 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 12940.4277 | 0.24416 | 5300000 | 0.05864
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | Current Study |  |  | 12562.7023 | 0.23703 | 5300000 | 0.0024784
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | Current Study |  |  | 10090.1048 | 0.4387 | 2300000 | 0.043492
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | Current Study |  |  | 9879.109 | 0.40613 | 2432500 | 0.02591
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 7489.2363 | 0.3385 | 2212500 | 0.050762
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | Current Study |  |  | 6402.0007 | 0.46391 | 1380000 | 0.03179
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509049 MURVAUL4 138 712002 TENASK4 138 P | Current Study | 10 | (265.00, 265.00) | 8563110.8999 | 71.3593 | 12000000 | 0.049175
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509048 MURVAULTP 138 509049 MURVAUL4 138 P | Current Study | 9 | (265.00, 265.00) | 7706799.8099 | 71.3593 | 10800000 | 0.049175
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | Current Study | 51.27 | (1793.00, 1793.00) | 5058239.1699 | 4.4845 | 112794000 | 0.056588
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | Current Study | 7.6 | (211.00, 211.00) | 2433913.7286 | 26.6877 | 9120000 | 0.037772
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | Current Study | 10.42 | (395.00, 395.00) | 2300151.1411 | 18.3953 | 12504000 | 0.011006
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507732 GENMOTR4 138 507759 SW SHV 4 138 1 | Current Study | 4.34 | (395.00, 395.00) | 1600707.9003 | 30.7356 | 5208000 | 0.01556
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1 | Current Study | 11.3 | (1793.00, 1793.00) | 1403998.9229 | 5.6476 | 24860000 | 0.025807
GEN-2024-377 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 914920.7398 | 5.0548 | 18100000 | 0.011473
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507727 FLOURNY4 138 507732 GENMOTR4 138 1 | Current Study | 1.56 | (395.00, 395.00) | 575369.66 | 30.7356 | 1872000 | 0.01556
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Add 10 MVAR switched shunt at G20-007-TAP 345 kV | Current Study |  |  | 528922.2008 | 9.9797 | 5300000 | 0.028992
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Add 38 MVAR switched shunt at FRNT2WD7 345 kV | Current Study |  |  | 457280.9812 | 8.6279 | 5300000 | 0.037633
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Add 19 MVAR switched shunt at RANCHRD7 345 kV | Current Study |  |  | 418660.8196 | 7.8993 | 5300000 | 0.037633
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 398684.8865 | 7.5224 | 5300000 | 0.11987
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | Current Study | 1.8 | (395.00, 395.00) | 397338.9687 | 18.3953 | 2160000 | 0.011006
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Add 0.42 MVAR switched shunt at TWNLKSW4 138 kV | Current Study |  |  | 281452.9561 | 11.5705 | 2432500 | 0.034172
GEN-2024-377 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 123851.6317 | 2.3368 | 5300000 | 0.05911
GEN-2024-379 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | Current Study | 21.32 | (1793.00, 1793.00) | 46904000 | 100 | 46904000 | 0.31191
GEN-2024-379 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508809 LONGWD 7 345 788340 G24-379-TAP 345 1 | Current Study | 19.1 | (1793.00, 1793.00) | 42020000 | 100 | 42020000 | 0.68809
GEN-2024-379 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 508808 LONGWD 4 138 508809 LONGWD 7 345 508819 LONGW1-1 13 M2 | Current Study |  | (580.00, 580.00) | 18100000 | 100 | 18100000 | 0.061204
GEN-2024-379 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | Current Study | 10.42 | (395.00, 395.00) | 6827318.9106 | 54.6011 | 12504000 | 0.032668
GEN-2024-379 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507774 NORAM 4 138 508808 LONGWD 4 138 1 | Current Study | 4.8 | (281.00, 281.00) | 5760000 | 100 | 5760000 | 0.027858
GEN-2024-379 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507732 GENMOTR4 138 507759 SW SHV 4 138 1 | Current Study | 4.34 | (395.00, 395.00) | 3064455.9122 | 58.8413 | 5208000 | 0.029788
GEN-2024-379 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1 | Current Study | 11.3 | (1793.00, 1793.00) | 1409779.2322 | 5.6709 | 24860000 | 0.025914
GEN-2024-379 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | Current Study | 1.8 | (395.00, 395.00) | 1179383.3051 | 54.6011 | 2160000 | 0.032668
GEN-2024-379 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507727 FLOURNY4 138 507732 GENMOTR4 138 1 | Current Study | 1.56 | (395.00, 395.00) | 1101509.4984 | 58.8413 | 1872000 | 0.029788
GEN-2024-379 | 04 SOUTHEAST | TBD | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | Current Study |  | (505.00, 505.00) | 869666.1585 | 4.8048 | 18100000 | 0.010905
GEN-2024-379 | 04 SOUTHEAST | TBD | ERIS | Add 38 MVAR switched shunt at FRNT2WD7 345 kV | Current Study |  |  | 425808.2573 | 8.0341 | 5300000 | 0.035043
GEN-2024-379 | 04 SOUTHEAST | TBD | ERIS | Add 19 MVAR switched shunt at RANCHRD7 345 kV | Current Study |  |  | 389846.1588 | 7.3556 | 5300000 | 0.035043
GEN-2024-379 | 04 SOUTHEAST | TBD | ERIS | Add 4 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 185211.0893 | 3.4945 | 5300000 | 0.055688
GEN-2024-379 | 04 SOUTHEAST | TBD | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | Current Study |  |  | 122366.1274 | 2.3088 | 5300000 | 0.058401
GEN-2024-003 | 04 SOUTHEAST | 171474 | ERIS | Fitzhugh 161kV GEN-2024-003 Interconnection (Non-Shared NU) (AECC) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-003 | 04 SOUTHEAST | 171473 | ERIS | Fitzhugh 161kV GEN-2024-003 Interconnection (TOIF) (AECC) | Interconnection |  |  | 1750000 | 100 | 1750000 | 1
GEN-2024-007 | 03 CENTRAL | 171475 | ERIS | Seward 115 kV Substation GEN-2024-007 Interconnection (TOIF) (MIDW) | Interconnection |  |  | 883537.2 | 100 | 883537.2 | 1
GEN-2024-007 | 03 CENTRAL | 171476 | ERIS | Seward 115 kV Substation GEN-2024-007 Interconnection (Non-Shared NU) (MIDW) | Interconnection |  |  | 3397809.87 | 100 | 3397809.87 | 1
GEN-2024-013 | 04 SOUTHEAST | 171478 | ERIS | Norman Hills 345 kV GEN-2024-013 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-013 | 04 SOUTHEAST | 171477 | ERIS | Norman Hills 345 kV GEN-2024-013 Interconnection (TOIF) (OGE) | Interconnection |  |  | 3500000 | 100 | 3500000 | 1
GEN-2024-015 | 05 SOUTHWEST | 171479 | ERIS | Sundown-Amaco-Yoakum 230 kV Substation GEN-2024-015 Interconnection (TOIF) (SPS) | Interconnection |  |  | 3766557 | 100 | 3766557 | 1
GEN-2024-015 | 05 SOUTHWEST | 171480 | ERIS | Sundown-Amaco-Yoakum 230 kV Substation GEN-2024-015 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 24794114 | 100 | 24794114 | 1
GEN-2024-016 | 03 CENTRAL | 171481 | ERIS | Post Rock - Macon 345 kV Line GEN-2024-016 Interconnection (TOIF) (ITCGP) | Interconnection |  |  | 1306433 | 100 | 1306433 | 1
GEN-2024-016 | 03 CENTRAL | 171482 | ERIS | Post Rock - Macon 345 kV Line GEN-2024-016 Interconnection (Non-Shared NU) (ITCGP) | Interconnection |  |  | 17836757 | 100 | 17836757 | 1
GEN-2024-017 | 02 NEBRASKA | 171483 | ERIS | Olive Creek 345 kV Substation GEN-2024-017 Interconnection (TOIF) (NPPD) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-017 | 02 NEBRASKA | 171484 | ERIS | Olive Creek 345 kV Substation GEN-2024-017 Interconnection (Non-Shared NU) (NPPD) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-018 | 02 NEBRASKA | 171485 | ERIS | New Beatrice Power Station 345 kV GEN-2024-018 Interconnection (TOIF) (NPPD) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-018 | 02 NEBRASKA | 171492 | ERIS | New Beatrice Power Station 345 kV GEN-2024-018/019/022/023 Interconnection (TOIF) (NPPD) | Interconnection |  |  | 750000 | 25 | 3000000 | 1
GEN-2024-018 | 02 NEBRASKA | 171492 | ERIS | New Beatrice Power Station 345 kV GEN-2024-018/019/022/023 Interconnection (Shared NU) (NPPD) | Interconnection |  |  | 1090909.09 | 16 | 7000000 | 1
GEN-2024-019 | 02 NEBRASKA | 171486 | ERIS | New Beatrice Power Station 345 kV Substation GEN-2024-019 Interconnection (TOIF) (NPPD) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-019 | 02 NEBRASKA | 171492 | ERIS | New Beatrice Power Station 345 kV GEN-2024-018/019/022/023 Interconnection (TOIF) (NPPD) | Interconnection |  |  | 750000 | 25 | 3000000 | 1
GEN-2024-019 | 02 NEBRASKA | 171492 | ERIS | New Beatrice Power Station 345 kV GEN-2024-018/019/022/023 Interconnection (Shared NU) (NPPD) | Interconnection |  |  | 1818181.82 | 26 | 7000000 | 1
GEN-2024-020 | 02 NEBRASKA | 171487 | ERIS | Olive Creek 345 kV Substation GEN-2024-020 Interconnection (TOIF) (NPPD) | Interconnection |  |  | 1000000 | 100 | 1000000 | 1
GEN-2024-020 | 02 NEBRASKA | 171488 | ERIS | Olive Creek 345 kV Substation GEN-2024-020 Interconnection (Non-Shared NU) (NPPD) | Interconnection |  |  | 5000000 | 100 | 5000000 | 1
GEN-2024-021 | 02 NEBRASKA | 171489 | ERIS | Olive Creek 345 kV Substation GEN-2024-021 Interconnection (TOIF) (NPPD) | Interconnection |  |  | 1000000 | 100 | 1000000 | 1
GEN-2024-021 | 02 NEBRASKA | 171490 | ERIS | Olive Creek 345 kV Substation GEN-2024-021 Interconnection (Non-Shared NU) (NPPD) | Interconnection |  |  | 5000000 | 100 | 5000000 | 1
GEN-2024-022 | 02 NEBRASKA | 171492 | ERIS | New Beatrice Power Station 345 kV GEN-2024-018/019/022/023 Interconnection (TOIF) (NPPD) | Interconnection |  |  | 750000 | 25 | 3000000 | 1
GEN-2024-022 | 02 NEBRASKA | 171491 | ERIS | New Beatrice Power Station 345 kV GEN-2024-022 Interconnection (TOIF) (NPPD) | Interconnection |  |  | 1000000 | 100 | 1000000 | 1
GEN-2024-022 | 02 NEBRASKA | 171492 | ERIS | New Beatrice Power Station 345 kV GEN-2024-018/019/022/023 Interconnection (Shared NU) (NPPD) | Interconnection |  |  | 2272727.27 | 32 | 7000000 | 1
GEN-2024-023 | 02 NEBRASKA | 171492 | ERIS | New Beatrice Power Station 345 kV GEN-2024-018/019/022/023 Interconnection (TOIF) (NPPD) | Interconnection |  |  | 750000 | 25 | 3000000 | 1
GEN-2024-023 | 02 NEBRASKA | 171493 | ERIS | New Beatrice Power Station 345 kV GEN-2024-023 Interconnection (TOIF) (NPPD) | Interconnection |  |  | 1000000 | 100 | 1000000 | 1
GEN-2024-023 | 02 NEBRASKA | 171492 | ERIS | New Beatrice Power Station 345 kV GEN-2024-018/019/022/023 Interconnection (Shared NU) (NPPD) | Interconnection |  |  | 1818181.82 | 26 | 7000000 | 1
GEN-2024-025 | 04 SOUTHEAST | 171495 | ERIS | Lydia 345 kV Substation GEN-2024-025 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 3900000 | 100 | 3900000 | 1
GEN-2024-025 | 04 SOUTHEAST | 171494 | ERIS | Lydia 345 kV Substation GEN-2024-025 Interconnection (TOIF) (AEP) | Interconnection |  |  | 5225000 | 100 | 5225000 | 1
GEN-2024-029 | 04 SOUTHEAST | 171497 | ERIS | Crescent 138 kV Substation GEN-2024-029 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 1500000 | 100 | 1500000 | 1
GEN-2024-029 | 04 SOUTHEAST | 171496 | ERIS | Crescent 138 kV Substation GEN-2024-029 Interconnection (TOIF) (OGE) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-030 | 03 CENTRAL | 171498 | ERIS | Santa Fe 115 kV Substation GEN-2024-030 Interconnection (TOIF) (SUNC) | Interconnection |  |  | 2250000 | 100 | 2250000 | 1
GEN-2024-030 | 03 CENTRAL | 171499 | ERIS | Santa Fe 115 kV Substation GEN-2024-030 Interconnection (Non-Shared NU) (SUNC) | Interconnection |  |  | 5250000 | 100 | 5250000 | 1
GEN-2024-032 | 03 CENTRAL | 171501 | ERIS | Hugoton 115 kV Substation GEN-2024-032 Interconnection (Non-Shared NU) (SUNC) | Interconnection |  |  | 1050000 | 100 | 1050000 | 1
GEN-2024-032 | 03 CENTRAL | 171500 | ERIS | Hugoton 115 kV Substation GEN-2024-032 Interconnection (TOIF) (SUNC) | Interconnection |  |  | 2450000 | 100 | 2450000 | 1
GEN-2024-034 | 01 NORTH | 171502 | ERIS | Forman 115 kV Substation GEN-2024-034 Interconnection (TOIF) (WAPA) | Interconnection |  |  | 410000 | 100 | 410000 | 1
GEN-2024-034 | 01 NORTH | 171503 | ERIS | Forman 115 kV Substation GEN-2024-034 Interconnection (Non-Shared NU) (WAPA) | Interconnection |  |  | 30940000 | 100 | 30940000 | 1
GEN-2024-035 | 01 NORTH | 171504 | ERIS | Groton 345 kV Substation GEN-2024-035 Interconnection (TOIF) (BEPC) | Interconnection |  |  | 2834775 | 100 | 2834775 | 1
GEN-2024-035 | 01 NORTH | 171505 | ERIS | Groton 345 kV Substation GEN-2024-035 Interconnection (Non-Shared NU) (BEPC) | Interconnection |  |  | 7125379 | 100 | 7125379 | 1
GEN-2024-038 | 02 NEBRASKA | 171506 | ERIS | Cooper - S12080 161 kV line GEN-2024-038 Interconnection (TOIF) (OPPD) | Interconnection |  |  | 476039 | 100 | 476039 | 1
GEN-2024-038 | 02 NEBRASKA | 171507 | ERIS | Cooper - S12080 161 kV line GEN-2024-038 Interconnection (Non-Shared NU) (OPPD) | Interconnection |  |  | 20250000 | 100 | 20250000 | 1
GEN-2024-039 | 02 NEBRASKA | 171508 | ERIS | Humboldt - S1280 161 kV line GEN-2024-039 Interconnection (TOIF) (OPPD) | Interconnection |  |  | 476039 | 100 | 476039 | 1
GEN-2024-039 | 02 NEBRASKA | 171509 | ERIS | Humboldt - S1280 161 kV line GEN-2024-039 Interconnection (Non-Shared NU) (OPPD) | Interconnection |  |  | 20250000 | 100 | 20250000 | 1
GEN-2024-040 | 02 NEBRASKA | 171510 | ERIS | S3458 to Cooper 345 kV line GEN-2024-040 Interconnection (TOIF) (OPPD) | Interconnection |  |  | 496523 | 100 | 496523 | 1
GEN-2024-040 | 02 NEBRASKA | 171511 | ERIS | S3458 to Cooper 345 kV line GEN-2024-040 Interconnection (Non-Shared NU) (OPPD) | Interconnection |  |  | 22250000 | 100 | 22250000 | 1
GEN-2024-041 | 05 SOUTHWEST | 171512 | ERIS | Tuco - Whirlwind 345 kV line GEN-2024-041 Interconnection (TOIF) (SPS) | Interconnection |  |  | 5024078.97 | 100 | 5024078.97 | 1
GEN-2024-041 | 05 SOUTHWEST | 171514 | ERIS | Tuco - Whirlwind 345 kV line GEN-2024-041/042 Interconnection (Shared NU) (SPS) | Interconnection |  |  | 13860161.15 | 50 | 27720322.3 | 1
GEN-2024-042 | 05 SOUTHWEST | 171513 | ERIS | Tuco - Whirlwind 345 kV line GEN-2024-042 Interconnection (TOIF) (SPS) | Interconnection |  |  | 5024078.97 | 100 | 5024078.97 | 1
GEN-2024-042 | 05 SOUTHWEST | 171514 | ERIS | Tuco - Whirlwind 345 kV line GEN-2024-041/042 Interconnection (Shared NU) (SPS) | Interconnection |  |  | 13860161.15 | 50 | 27720322.3 | 1
GEN-2024-043 | 05 SOUTHWEST | 171515 | ERIS | Crossroads - Tolk 345 kV Line GEN-2024-043 Interconnection (TOIF) (SPS) | Interconnection |  |  | 4774296.21 | 100 | 4774296.21 | 1
GEN-2024-043 | 05 SOUTHWEST | 171516 | ERIS | Crossroads - Tolk 345 kV Line GEN-2024-043 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 29754372.46 | 100 | 29754372.46 | 1
GEN-2024-044 | 04 SOUTHEAST | 171517 | ERIS | Hosston - Plain Dealing 69 kV Line GEN-2024-044 Interconnection (TOIF) (AEP) | Interconnection |  |  | 3475000 | 100 | 3475000 | 1
GEN-2024-044 | 04 SOUTHEAST | 171518 | ERIS | Hosston - Plain Dealing 69 kV Line GEN-2024-044 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 16475000 | 100 | 16475000 | 1
GEN-2024-045 | 05 SOUTHWEST | 171519 | ERIS | Hitchland - Moore 230kV line GEN-2024-045 Interconnection (TOIF) (SPS) | Interconnection |  |  | 3976274 | 100 | 3976274 | 1
GEN-2024-045 | 05 SOUTHWEST | 171521 | ERIS | Hitchland-Moore 230 kV line GEN-2024-045/046 Interconnection (Shared NU) (SPS) | Interconnection |  |  | 11513615.5 | 50 | 23027231 | 1
GEN-2024-046 | 05 SOUTHWEST | 171520 | ERIS | Hitchland-Moore 230 kV line GEN-2024-046 Interconnection (TOIF) (SPS) | Interconnection |  |  | 2961025.2 | 100 | 2961025.2 | 1
GEN-2024-046 | 05 SOUTHWEST | 171521 | ERIS | Hitchland-Moore 230 kV line GEN-2024-045/046 Interconnection (Shared NU) (SPS) | Interconnection |  |  | 11513615.5 | 50 | 23027231 | 1
GEN-2024-050 | 05 SOUTHWEST | 171523 | ERIS | Olson 230 kV Substation GEN-2024-050 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 1846031.59 | 100 | 1846031.59 | 1
GEN-2024-050 | 05 SOUTHWEST | 171522 | ERIS | Olson 230 kV Substation GEN-2024-050 Interconnection (TOIF) (SPS) | Interconnection |  |  | 3233717.92 | 100 | 3233717.92 | 1
GEN-2024-051 | 02 NEBRASKA | 171524 | ERIS | Waverly 115 kV Substation GEN-2024-051 Interconnection (TOIF) (LES) | Interconnection |  |  | 7533500 | 100 | 7533500 | 1
GEN-2024-051 | 02 NEBRASKA | 171525 | ERIS | Waverly 115 kV Substation GEN-2024-051 Interconnection (Non-Shared NU) (LES) | Interconnection |  |  | 7533500 | 100 | 7533500 | 1
GEN-2024-052 | 04 SOUTHEAST | 171526 | ERIS | Unger - West Bank Tap 138 kV Line GEN-2024-052 Interconnection (TOIF) (WFEC) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-052 | 04 SOUTHEAST | 171893 | ERIS | Unger - West Bank Tap 138 kV Line GEN-2024-052/373 Interconnection (Shared NU) (WFEC) | Interconnection |  |  | 0 |  | 0 | 1
GEN-2024-052 | 04 SOUTHEAST | 171526 | ERIS | Unger - West Bank Tap 138 kV Line GEN-2024-052 Interconnection (TOIF) (WFEC) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-052 | 04 SOUTHEAST | 171893 | ERIS | Unger - West Bank Tap 138 kV Line GEN-2024-052/373 Interconnection (Shared NU) (WFEC) | Interconnection |  |  | 1814814.8148 | 25.9259 | 7000000 | 1
GEN-2024-054 | 03 CENTRAL | 171903 | ERIS | Overton - Sedalia East 161 kV line GEN-2024-054 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-054 | 03 CENTRAL | 171902 | ERIS | Overton - Sedalia East 161 kV line GEN-2024-054 Interconnection (TOIF) (WERE) | Interconnection |  |  | 112911 | 100 | 112911 | 1
GEN-2024-055 | 03 CENTRAL | 171904 | ERIS | Butler - Nevada 161 kV line GEN-2024-055 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1495123 | 100 | 1495123 | 1
GEN-2024-055 | 03 CENTRAL | 171905 | ERIS | Butler - Nevada 161 kV line GEN-2024-055 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 15550547 | 100 | 15550547 | 1
GEN-2024-056 | 04 SOUTHEAST | 171527 | ERIS | Cow Creek - Morrison 138 kV line GEN-2024-056 Interconnection (TOIF) (OGE) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-056 | 04 SOUTHEAST | 171528 | ERIS | Cow Creek - Morrison 138 kV line GEN-2024-056 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 7000000 | 100 | 7000000 | 1
GEN-2024-058 | 04 SOUTHEAST | 171529 | ERIS | Farmland - Delaware 138 kV line GEN-2024-058 Interconnection (TOIF) (AEP) | Interconnection |  |  | 3325000 | 100 | 3325000 | 1
GEN-2024-058 | 04 SOUTHEAST | 171530 | ERIS | Farmland - Delaware 138 kV line GEN-2024-058 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 17175000 | 100 | 17175000 | 1
GEN-2024-061 | 03 CENTRAL | 171906 | ERIS | Creswell 138 kV Substation GEN-2024-061 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1040240 | 100 | 1040240 | 1
GEN-2024-061 | 03 CENTRAL | 171907 | ERIS | Creswell 138 kV Substation GEN-2024-061 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 14040446 | 100 | 14040446 | 1
GEN-2024-062 | 04 SOUTHEAST | 171531 | ERIS | Dover SW 138 kV Substation GEN-2024-062 Interconnection (TOIF) (WFEC) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-062 | 04 SOUTHEAST | 171532 | ERIS | Dover SW 138 kV Substation GEN-2024-062 Interconnection (Non-Shared NU) (WFEC) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-062 | 04 SOUTHEAST | 171531 | ERIS | Dover SW 138 kV Substation GEN-2024-062 Interconnection (TOIF) (WFEC) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-062 | 04 SOUTHEAST | 171532 | ERIS | Dover SW 138 kV Substation GEN-2024-062 Interconnection (Non-Shared NU) (WFEC) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-063 | 05 SOUTHWEST | 171533 | ERIS | Plant X 230 kV Substation GEN-2024-063 Interconnection (TOIF) (SPS) | Interconnection |  |  | 3382454.46 | 100 | 3382454.46 | 1
GEN-2024-063 | 05 SOUTHWEST | 171534 | ERIS | Plant X 230 kV Substation GEN-2024-063 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 7964621.39 | 100 | 7964621.39 | 1
GEN-2024-065 | 02 NEBRASKA | 171535 | ERIS | FREMONT7 115 kV Substation GEN-2024-065 Interconnection (TOIF) (NPPD) | Interconnection |  |  | 500000 | 100 | 500000 | 1
GEN-2024-065 | 02 NEBRASKA | 171536 | ERIS | FREMONT7 115 kV Substation GEN-2024-065 Interconnection (Non-Shared NU) (NPPD) | Interconnection |  |  | 9500000 | 100 | 9500000 | 1
GEN-2024-067 | 03 CENTRAL | 171537 | ERIS | Cirrus 345 kV Substation GEN-2024-067 Interconnection (TOIF) (ITCGP) | Interconnection |  |  | 1306438 | 100 | 1306438 | 1
GEN-2024-067 | 03 CENTRAL | 171538 | ERIS | Cirrus 345 kV Substation GEN-2024-067 Interconnection (Non-Shared NU) (ITCGP) | Interconnection |  |  | 4630435 | 100 | 4630435 | 1
GEN-2024-068 | 04 SOUTHEAST | 171539 | ERIS | Lydia - Welsh 345 kV Line GEN-2024-068 Interconnection (TOIF) (AEP) | Interconnection |  |  | 5225000 | 100 | 5225000 | 1
GEN-2024-068 | 04 SOUTHEAST | 171540 | ERIS | Lydia - Welsh 345 kV Line GEN-2024-068 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 28225000 | 100 | 28225000 | 1
GEN-2024-069 | 03 CENTRAL | 171908 | ERIS | Franklin 69 kV Substation GEN-2024-069 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1038346 | 100 | 1038346 | 1
GEN-2024-069 | 03 CENTRAL | 171909 | ERIS | Franklin 69 kV Substation GEN-2024-069 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 5700860 | 100 | 5700860 | 1
GEN-2024-071 | 04 SOUTHEAST | 171541 | ERIS | West Atlanta - Atlanta 69 kV Line GEN-2024-071 Interconnection (TOIF) (AEP) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-071 | 04 SOUTHEAST | 171542 | ERIS | West Atlanta - Atlanta 69 kV Line GEN-2024-071 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-072 | 03 CENTRAL | 171544 | ERIS | Beloit 115 kV Substation GEN-2024-072 Interconnection (Non-Shared NU) (SUNC) | Interconnection |  |  | 1500000 | 100 | 1500000 | 1
GEN-2024-072 | 03 CENTRAL | 171543 | ERIS | Beloit 115 kV Substation GEN-2024-072 Interconnection (TOIF) (SUNC) | Interconnection |  |  | 3500000 | 100 | 3500000 | 1
GEN-2024-073 | 05 SOUTHWEST | 171546 | ERIS | Crossroads - Hobbs 345 kV Substation GEN-2024-073 Interconnection (Non-Shared NU) (NEET) | Interconnection |  |  | 840255 | 100 | 840255 | 1
GEN-2024-073 | 05 SOUTHWEST | 171545 | ERIS | Crossroads - Hobbs 345 kV Substation GEN-2024-073 Interconnection (TOIF) (NEET) | Interconnection |  |  | 42764795 | 100 | 42764795 | 1
GEN-2024-074 | 03 CENTRAL | 171910 | ERIS | Duncan Road 161 kV Substation GEN-2024-074 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1061550 | 100 | 1061550 | 1
GEN-2024-074 | 03 CENTRAL | 171911 | ERIS | Duncan Road 161 kV Substation GEN-2024-074 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 1235193 | 100 | 1235193 | 1
GEN-2024-076 | 03 CENTRAL | 171912 | ERIS | Neosho - LaCygne 345 kV Line GEN-2024-076 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1958090 | 100 | 1958090 | 1
GEN-2024-076 | 03 CENTRAL | 171913 | ERIS | Neosho - LaCygne 345 kV Line GEN-2024-076 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 1958090 | 100 | 1958090 | 1
GEN-2024-077 | 05 SOUTHWEST | 171547 | ERIS | Pringle 230 kV Substation GEN-2024-077 Interconnection (TOIF) (SPS) | Interconnection |  |  | 3558255 | 100 | 3558255 | 1
GEN-2024-077 | 05 SOUTHWEST | 171548 | ERIS | Pringle 230 kV Substation GEN-2024-077 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 8790893 | 100 | 8790893 | 1
GEN-2024-078 | 05 SOUTHWEST | 171550 | ERIS | Pringle 230 kV Substation GEN-2024-078 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 2493980 | 100 | 2493980 | 1
GEN-2024-078 | 05 SOUTHWEST | 171549 | ERIS | Pringle 230 kV Substation GEN-2024-078 Interconnection (TOIF) (SPS) | Interconnection |  |  | 2770537 | 100 | 2770537 | 1
GEN-2024-079 | 05 SOUTHWEST | 171553 | ERIS | San Juan 230 kV Substation GEN-2024-079/080 Interconnection (Shared NU) (SPS) | Interconnection |  |  | 2017890.75 | 50 | 4035781.5 | 1
GEN-2024-079 | 05 SOUTHWEST | 171551 | ERIS | San Juan 230 kV Substation GEN-2024-079 Interconnection (TOIF) (SPS) | Interconnection |  |  | 3422577.15 | 100 | 3422577.15 | 1
GEN-2024-080 | 05 SOUTHWEST | 171553 | ERIS | San Juan 230 kV Substation GEN-2024-079/080 Interconnection (Shared NU) (SPS) | Interconnection |  |  | 2017890.75 | 50 | 4035781.5 | 1
GEN-2024-080 | 05 SOUTHWEST | 171552 | ERIS | San Juan 230 kV Substation GEN-2024-080 Interconnection (TOIF) (SPS) | Interconnection |  |  | 3422577.15 | 100 | 3422577.15 | 1
GEN-2024-081 | 01 NORTH | 171555 | ERIS | Springbrook - Tande 345 kV Line GEN-2024-081/082 Interconnection (Shared NU) (BEPC) | Interconnection |  |  | 1546743 | 50 | 3093486 | 1
GEN-2024-081 | 01 NORTH | 171554 | ERIS | Springbrook - Tande 345 kV Line GEN-2024-081 Interconnection (TOIF) (BEPC) | Interconnection |  |  | 3093490 | 100 | 3093490 | 1
GEN-2024-082 | 01 NORTH | 171555 | ERIS | Springbrook - Tande 345 kV Line GEN-2024-081/082 Interconnection (Shared NU) (BEPC) | Interconnection |  |  | 1546743 | 50 | 3093486 | 1
GEN-2024-082 | 01 NORTH | 171556 | ERIS | Springbrook - Tande 345 kV Line GEN-2024-082 Interconnection (TOIF) (BEPC) | Interconnection |  |  | 38027515 | 100 | 38027515 | 1
GEN-2024-083 | 04 SOUTHEAST | 171557 | ERIS | Hugo 345 kV Substation GEN-2024-083 Interconnection (TOIF) (ITCGP) | Interconnection |  |  | 1306432 | 100 | 1306432 | 1
GEN-2024-083 | 04 SOUTHEAST | 171558 | ERIS | Hugo 345 kV Substation GEN-2024-083 Interconnection (Non-Shared NU) (ITCGP) | Interconnection |  |  | 3834311 | 100 | 3834311 | 1
GEN-2024-084 | 03 CENTRAL | 171559 | ERIS | Reeds Spring - Aurora 161 kV Line GEN-2024-084 Interconnection (TOIF) (EMDE) | Interconnection |  |  | 3775786 | 100 | 3775786 | 1
GEN-2024-084 | 03 CENTRAL | 171560 | ERIS | Reeds Spring - Aurora 161 kV Line GEN-2024-084 Interconnection (Non-Shared NU) (EMDE) | Interconnection |  |  | 11956657 | 100 | 11956657 | 1
GEN-2024-085 | 03 CENTRAL | 171561 | ERIS | Otis 115 kV Substation GEN-2024-085 Interconnection (TOIF) (SUNC) | Interconnection |  |  | 4500000 | 100 | 4500000 | 1
GEN-2024-085 | 03 CENTRAL | 171562 | ERIS | Otis 115 kV Substation GEN-2024-085 Interconnection (Non-Shared NU) (SUNC) | Interconnection |  |  | 10500000 | 100 | 10500000 | 1
GEN-2024-088 | 03 CENTRAL | 171563 | ERIS | McCartney 161 kV Substation GEN-2024-088 Interconnection (TOIF) (CUS) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-088 | 03 CENTRAL | 171564 | ERIS | McCartney 161 kV Substation GEN-2024-088 Interconnection (Non-Shared NU) (CUS) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-088 | 03 CENTRAL | 171563 | ERIS | McCartney 161 kV Substation GEN-2024-088 Interconnection (TOIF) (CUS) | Interconnection |  |  | 2700000 | 100 | 2700000 | 1
GEN-2024-088 | 03 CENTRAL | 171564 | ERIS | McCartney 161 kV Substation GEN-2024-088 Interconnection (Non-Shared NU) (CUS) | Interconnection |  |  | 2930000 | 100 | 2930000 | 1
GEN-2024-089 | 05 SOUTHWEST | 171565 | ERIS | Pleasant Hills 230 kV Substation GEN-2024-089 Interconnection (TOIF) (SPS) | Interconnection |  |  | 3797868.29 | 100 | 3797868.29 | 1
GEN-2024-089 | 05 SOUTHWEST | 171566 | ERIS | Pleasant Hills 230 kV Substation GEN-2024-089 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 6566666.79 | 100 | 6566666.79 | 1
GEN-2024-090 | 03 CENTRAL | 171914 | ERIS | Smithville 161 kV Substation GEN-2024-090 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1061550 | 100 | 1061550 | 1
GEN-2024-090 | 03 CENTRAL | 171915 | ERIS | Smithville 161 kV Substation GEN-2024-090 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 3659394 | 100 | 3659394 | 1
GEN-2024-091 | 03 CENTRAL | 171567 | ERIS | 145 JOPLIN WEST 7TH 161 kV Substation GEN-2024-091 Interconnection (TOIF) (EDE) | Interconnection |  |  | 5035992 | 100 | 5035992 | 1
GEN-2024-091 | 03 CENTRAL | 171568 | ERIS | 145 JOPLIN WEST 7TH 161 kV Substation GEN-2024-091 Interconnection (Non-Shared NU) (EDE) | Interconnection |  |  | 12949695 | 100 | 12949695 | 1
GEN-2024-092 | 05 SOUTHWEST | 171569 | ERIS | Portales 115 kV Substation GEN-2024-092 Interconnection (TOIF) (SPS) | Interconnection |  |  | 3235767.6 | 100 | 3235767.6 | 1
GEN-2024-092 | 05 SOUTHWEST | 171570 | ERIS | Portales 115 kV Substation GEN-2024-092 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 4844709.15 | 100 | 4844709.15 | 1
GEN-2024-099 | 05 SOUTHWEST | 171572 | ERIS | Newhart 230 kV Substation GEN-2024-099 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 1603584.62 | 100 | 1603584.62 | 1
GEN-2024-099 | 05 SOUTHWEST | 171571 | ERIS | Newhart 230 kV Substation GEN-2024-099 Interconnection (TOIF) (SPS) | Interconnection |  |  | 3214046.86 | 100 | 3214046.86 | 1
GEN-2024-102 | 03 CENTRAL | 171573 | ERIS | Holcomb 345 kV Substation GEN-2024-102 Interconnection (TOIF) (SUNC) | Interconnection |  |  | 3000000 | 100 | 3000000 | 1
GEN-2024-102 | 03 CENTRAL | 171574 | ERIS | Holcomb 345 kV Substation GEN-2024-102 Interconnection (Non-Shared NU) (SUNC) | Interconnection |  |  | 7000000 | 100 | 7000000 | 1
GEN-2024-109 | 05 SOUTHWEST | 171575 | ERIS | Tolk - Crossroads 345 kV line GEN-2024-109 Interconnection (TOIF) (SPS) | Interconnection |  |  | 4671893.78 | 100 | 4671893.78 | 1
GEN-2024-109 | 05 SOUTHWEST | 171576 | ERIS | Tolk - Crossroads 345 kV line GEN-2024-109 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 27903630.08 | 100 | 27903630.08 | 1
GEN-2024-113 | 04 SOUTHEAST | 171577 | ERIS | Muskogee - Ft. Smith 345 kV Line GEN-2024-113 Interconnection (TOIF) (OGE) | Interconnection |  |  | 3000000 | 100 | 3000000 | 1
GEN-2024-113 | 04 SOUTHEAST | 171578 | ERIS | Muskogee - Ft. Smith 345 kV Line GEN-2024-113 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 18000000 | 100 | 18000000 | 1
GEN-2024-114 | 04 SOUTHEAST | 171579 | ERIS | Jonesboro - Independence County 161 kV Line GEN-2024-114 Interconnection (TOIF) (SWPA) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-114 | 04 SOUTHEAST | 171580 | ERIS | Jonesboro - Independence County 161 kV Line GEN-2024-114 Interconnection (Non-Shared NU) (SWPA) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-114 | 04 SOUTHEAST | 171579 | ERIS | Jonesboro - Independence County 161 kV Line GEN-2024-114 Interconnection (TOIF) (SWPA) | Interconnection |  |  | 800000 | 100 | 800000 | 1
GEN-2024-114 | 04 SOUTHEAST | 171580 | ERIS | Jonesboro - Independence County 161 kV Line GEN-2024-114 Interconnection (Non-Shared NU) (SWPA) | Interconnection |  |  | 8600000 | 100 | 8600000 | 1
GEN-2024-117 | 04 SOUTHEAST | 171581 | ERIS | Coffeyville Tap - North Bartlesville 138kV Line GEN-2024-117 Interconnection (TOIF) (AEP) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-117 | 04 SOUTHEAST | 171582 | ERIS | Coffeyville Tap - North Bartlesville 138kV Line GEN-2024-117 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 17175000 | 100 | 17175000 | 1
GEN-2024-118 | 04 SOUTHEAST | 171584 | ERIS | Lynn Lane West Tap 138 kV Substation GEN-2024-118 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 2800000 | 100 | 2800000 | 1
GEN-2024-118 | 04 SOUTHEAST | 171583 | ERIS | Lynn Lane West Tap 138 kV Substation GEN-2024-118 Interconnection (TOIF) (AEP) | Interconnection |  |  | 3325000 | 100 | 3325000 | 1
GEN-2024-119 | 04 SOUTHEAST | 171585 | ERIS | Lexington 138 kV Substation GEN-2024-119 Interconnection (TOIF) (WFEC) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-119 | 04 SOUTHEAST | 171586 | ERIS | Lexington 138 kV Substation GEN-2024-119 Interconnection (Non-Shared NU) (WFEC) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-119 | 04 SOUTHEAST | 171585 | ERIS | Lexington 138 kV Substation GEN-2024-119 Interconnection (TOIF) (WFEC) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-119 | 04 SOUTHEAST | 171586 | ERIS | Lexington 138 kV Substation GEN-2024-119 Interconnection (Non-Shared NU) (WFEC) | Interconnection |  |  | 7000000 | 100 | 7000000 | 1
GEN-2024-120 | 04 SOUTHEAST | 171588 | ERIS | JNS KAMO 138 kV Substation GEN-2024-120 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 1500000 | 100 | 1500000 | 1
GEN-2024-120 | 04 SOUTHEAST | 171587 | ERIS | JNS KAMO 138 kV Substation GEN-2024-120 Interconnection (TOIF) (OGE) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-121 | 03 CENTRAL | 171916 | ERIS | Jarbalo 115 kV Substation GEN-2024-121 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1038348 | 100 | 1038348 | 1
GEN-2024-121 | 03 CENTRAL | 171917 | ERIS | Jarbalo 115 kV Substation GEN-2024-121 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 33543364 | 100 | 33543364 | 1
GEN-2024-122 | 04 SOUTHEAST | 171589 | ERIS | Lieberman - IPC Jefferson 138 kV Line GEN-2024-122 Interconnection (TOIF) (AEP) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-122 | 04 SOUTHEAST | 171590 | ERIS | Lieberman - IPC Jefferson 138 kV Line GEN-2024-122 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-123 | 04 SOUTHEAST | 171591 | ERIS | Center - Tenaha 138 kV Line GEN-2024-123 Interconnection (TOIF) (AEP) | Interconnection |  |  | 3325000 | 100 | 3325000 | 1
GEN-2024-123 | 04 SOUTHEAST | 171592 | ERIS | Center - Tenaha 138 kV Line GEN-2024-123 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 17175000 | 100 | 17175000 | 1
GEN-2024-124 | 05 SOUTHWEST | 171593 | ERIS | Crossroads-Hobbs-Roadrunner 345 kV Line GEN-2024-124 Interconnection (TOIF) (NEET) | Interconnection |  |  | 840255 | 100 | 840255 | 1
GEN-2024-124 | 05 SOUTHWEST | 171594 | ERIS | Crossroads-Hobbs-Roadrunner 345 kV Line GEN-2024-124 Interconnection (Non-Shared NU) (NEET) | Interconnection |  |  | 28818600 | 100 | 28818600 | 1
GEN-2024-125 | 03 CENTRAL | 171918 | ERIS | Neosho Ridge - Caney River 345 kV Line GEN-2024-125 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1958092 | 100 | 1958092 | 1
GEN-2024-125 | 03 CENTRAL | 171919 | ERIS | Neosho Ridge - Caney River 345 kV Line GEN-2024-125 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 31994301 | 100 | 31994301 | 1
GEN-2024-128 | 04 SOUTHEAST | 171595 | ERIS | Gracemont - Lawton 345 kV Line GEN-2024-128 Interconnection (TOIF) (OGE) | Interconnection |  |  | 3000000 | 100 | 3000000 | 1
GEN-2024-128 | 04 SOUTHEAST | 171596 | ERIS | Gracemont - Lawton 345 kV Line GEN-2024-128 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 18000000 | 100 | 18000000 | 1
GEN-2024-129 | 03 CENTRAL | 171920 | ERIS | Caney River - Neosho 345 kV Line GEN-2024-129 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1958092 | 100 | 1958092 | 1
GEN-2024-129 | 03 CENTRAL | 171921 | ERIS | Caney River - Neosho 345 kV Line GEN-2024-129 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 31994301 | 100 | 31994301 | 1
GEN-2024-132 | 04 SOUTHEAST | 171597 | ERIS | Hugo - Sunnyside 345 kV Line GEN-2024-132 Interconnection (TOIF) (OGE) | Interconnection |  |  | 1500000 | 100 | 1500000 | 1
GEN-2024-132 | 04 SOUTHEAST | 171598 | ERIS | Hugo - Sunnyside 345 kV Line GEN-2024-132 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 3000000 | 100 | 3000000 | 1
GEN-2024-134 | 04 SOUTHEAST | 171599 | ERIS | Degrasse 345 kV Substation GEN-2024-134 Interconnection (TOIF) (OGE) | Interconnection |  |  | 3000000 | 100 | 3000000 | 1
GEN-2024-134 | 04 SOUTHEAST | 171600 | ERIS | Degrasse 345 kV Substation GEN-2024-134 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 5500000 | 100 | 5500000 | 1
GEN-2024-135 | 04 SOUTHEAST | 171601 | ERIS | Degrasse 345 kV Substation GEN-2024-135 Interconnection (TOIF) (OGE) | Interconnection |  |  | 3000000 | 100 | 3000000 | 1
GEN-2024-135 | 04 SOUTHEAST | 171602 | ERIS | Degrasse 345 kV Substation GEN-2024-135 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 5500000 | 100 | 5500000 | 1
GEN-2024-136 | 03 CENTRAL | 171603 | ERIS | Setab 345 kV Substation GEN-2024-136 Interconnection (TOIF) (SUNC) | Interconnection |  |  | 551624 | 100 | 551624 | 1
GEN-2024-136 | 03 CENTRAL | 171614 | ERIS | Setab 345 kV Substation GEN-2024-136/137/138/144 Interconnection (Shared NU) (SUNC) | Interconnection |  |  | 1655473.7577 | 31.0102 | 5338489 | 1
GEN-2024-137 | 03 CENTRAL | 171604 | ERIS | Setab 345 kV Substation GEN-2024-137 Interconnection (TOIF) (SUNC) | Interconnection |  |  | 551624 | 100 | 551624 | 1
GEN-2024-137 | 03 CENTRAL | 171614 | ERIS | Setab 345 kV Substation GEN-2024-136/137/138/144 Interconnection (Shared NU) (SUNC) | Interconnection |  |  | 1227119.9229 | 22.9863 | 5338489 | 1
GEN-2024-138 | 03 CENTRAL | 171605 | ERIS | Setab 345 kV Substation GEN-2024-138 Interconnection (TOIF) (SUNC) | Interconnection |  |  | 551624 | 100 | 551624 | 1
GEN-2024-138 | 03 CENTRAL | 171614 | ERIS | Setab 345 kV Substation GEN-2024-136/137/138/144 Interconnection (Shared NU) (SUNC) | Interconnection |  |  | 1227119.9229 | 22.9863 | 5338489 | 1
GEN-2024-139 | 03 CENTRAL | 171606 | ERIS | Wolf Creek - Blackberry 345 kV Line GEN-2024-139 Interconnection (TOIF) (NEET) | Interconnection |  |  | 840255 | 100 | 840255 | 1
GEN-2024-139 | 03 CENTRAL | 171607 | ERIS | Wolf Creek - Blackberry 345 kV Line GEN-2024-139 Interconnection (Non-Shared NU) (NEET) | Interconnection |  |  | 28818600 | 100 | 28818600 | 1
GEN-2024-140 | 02 NEBRASKA | 171608 | ERIS | Antelope - Hoskins 345 kV line GEN-2024-140 Interconnection (TOIF) (NPPD) | Interconnection |  |  | 1000000 | 100 | 1000000 | 1
GEN-2024-140 | 02 NEBRASKA | 171609 | ERIS | Antelope - Hoskins 345 kV line GEN-2024-140 Interconnection (Non-Shared NU) (NPPD) | Interconnection |  |  | 4000000 | 100 | 4000000 | 1
GEN-2024-141 | 01 NORTH | 171610 | ERIS | BASIN__-BE4 230 kV Substation GEN-2024-141 Interconnection (TOIF) (BEPC) | Interconnection |  |  | 2270573 | 100 | 2270573 | 1
GEN-2024-141 | 01 NORTH | 171611 | ERIS | BASIN__-BE4 230 kV Substation GEN-2024-141 Interconnection (Non-Shared NU) (BEPC) | Interconnection |  |  | 7362181 | 100 | 7362181 | 1
GEN-2024-142 | 03 CENTRAL | 171922 | ERIS | Reno - Summit 345 kV Line GEN-2024-142 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1958090 | 100 | 1958090 | 1
GEN-2024-142 | 03 CENTRAL | 171923 | ERIS | Reno - Summit 345 kV Line GEN-2024-142 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 33532966 | 100 | 33532966 | 1
GEN-2024-143 | 05 SOUTHWEST | 171616 | ERIS | XIT Interchange 230 kV Substation GEN-2024-143/145 Interconnection (Shared NU) (SPS) | Interconnection |  |  | 1236604.2333 | 50.638 | 2442046.04 | 1
GEN-2024-143 | 05 SOUTHWEST | 171612 | ERIS | XIT Interchange 230 kV Substation GEN-2024-143 Interconnection (TOIF) (SPS) | Interconnection |  |  | 4144145.19 | 100 | 4144145.19 | 1
GEN-2024-144 | 03 CENTRAL | 171613 | ERIS | Setab 345 kV Substation GEN-2024-144 Interconnection (TOIF) (SUNC) | Interconnection |  |  | 551624 | 100 | 551624 | 1
GEN-2024-144 | 03 CENTRAL | 171614 | ERIS | Setab 345 kV Substation GEN-2024-136/137/138/144 Interconnection (Shared NU) (SUNC) | Interconnection |  |  | 1228775.3966 | 23.0173 | 5338489 | 1
GEN-2024-145 | 05 SOUTHWEST | 171616 | ERIS | XIT Interchange 230 kV Substation GEN-2024-143/145 Interconnection (Shared NU) (SPS) | Interconnection |  |  | 1205441.8067 | 49.362 | 2442046.04 | 1
GEN-2024-145 | 05 SOUTHWEST | 171615 | ERIS | XIT Interchange 230 kV Substation GEN-2024-145 Interconnection (TOIF) (SPS) | Interconnection |  |  | 4144145.19 | 100 | 4144145.19 | 1
GEN-2024-153 | 05 SOUTHWEST | 171617 | ERIS | Bushland 230 kV Substation GEN-2024-153 Interconnection (TOIF) (SPS) | Interconnection |  |  | 4261023.01 | 100 | 4261023.01 | 1
GEN-2024-153 | 05 SOUTHWEST | 171618 | ERIS | Bushland 230 kV Substation GEN-2024-153 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 33296957.63 | 100 | 33296957.63 | 1
GEN-2024-154 | 04 SOUTHEAST | 171620 | ERIS | Chisholm 345 kV Substation GEN-2024-154 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 3900000 | 100 | 3900000 | 1
GEN-2024-154 | 04 SOUTHEAST | 171619 | ERIS | Chisholm 345 kV Substation GEN-2024-154 Interconnection (TOIF) (AEP) | Interconnection |  |  | 5225000 | 100 | 5225000 | 1
GEN-2024-157 | 04 SOUTHEAST | 171621 | ERIS | Hobart - Martha 138 kV Line GEN-2024-157 Interconnection (TOIF) (AEP) | Interconnection |  |  | 3325000 | 100 | 3325000 | 1
GEN-2024-157 | 04 SOUTHEAST | 171622 | ERIS | Hobart - Martha 138 kV Line GEN-2024-157 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 17175000 | 100 | 17175000 | 1
GEN-2024-158 | 04 SOUTHEAST | 171623 | ERIS | Altus Jct - Snyder 138 kV Line GEN-2024-158 Interconnection (TOIF) (AEP) | Interconnection |  |  | 3325000 | 100 | 3325000 | 1
GEN-2024-158 | 04 SOUTHEAST | 171624 | ERIS | Altus Jct - Snyder 138 kV Line GEN-2024-158 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 17175000 | 100 | 17175000 | 1
GEN-2024-159 | 05 SOUTHWEST | 171625 | ERIS | Oasis - San Juan Mesa Wind 230 kV Line GEN-2024-159 Interconnection (TOIF) (SPS) | Interconnection |  |  | 4119557 | 100 | 4119557 | 1
GEN-2024-159 | 05 SOUTHWEST | 171626 | ERIS | Oasis - San Juan Mesa Wind 230 kV Line GEN-2024-159 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 27237303 | 100 | 27237303 | 1
GEN-2024-161 | 04 SOUTHEAST | 171627 | ERIS | Hobart - Martha 138 kV Line GEN-2024-161 Interconnection (TOIF) (AEP) | Interconnection |  |  | 3525000 | 100 | 3525000 | 1
GEN-2024-161 | 04 SOUTHEAST | 171628 | ERIS | Hobart - Martha 138 kV Line GEN-2024-161 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 17175000 | 100 | 17175000 | 1
GEN-2024-162 | 02 NEBRASKA | 171629 | ERIS | Twin Church 230 kV Substation GEN-2024-162 Interconnection (TOIF) (NPPD) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-162 | 02 NEBRASKA | 171630 | ERIS | Twin Church 230 kV Substation GEN-2024-162 Interconnection (Non-Shared NU) (NPPD) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-164 | 04 SOUTHEAST | 171631 | ERIS | Arbuckle 138 kV Substation GEN-2024-164 Interconnection (TOIF) (OGE) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-164 | 04 SOUTHEAST | 171632 | ERIS | Arbuckle 138 kV Substation GEN-2024-164 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 27000000 | 100 | 27000000 | 1
GEN-2024-165 | 04 SOUTHEAST | 171633 | ERIS | Pittsburg - Johnston County 345 kV line GEN-2024-165 Interconnection (TOIF) (AEP) | Interconnection |  |  | 5425000 | 100 | 5425000 | 1
GEN-2024-165 | 04 SOUTHEAST | 171634 | ERIS | Pittsburg - Johnston County 345 kV line GEN-2024-165 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 28225000 | 100 | 28225000 | 1
GEN-2024-166 | 03 CENTRAL | 171924 | ERIS | Murray Gill 138 kV Substation GEN-2024-166 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1040242 | 100 | 1040242 | 1
GEN-2024-166 | 03 CENTRAL | 171925 | ERIS | Murray Gill 138 kV Substation GEN-2024-166 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 3654211 | 100 | 3654211 | 1
GEN-2024-167 | 03 CENTRAL | 171926 | ERIS | Orrick 161 kV Substation GEN-2024-167 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1495123 | 100 | 1495123 | 1
GEN-2024-167 | 03 CENTRAL | 171927 | ERIS | Orrick 161 kV Substation GEN-2024-167 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 16202977 | 100 | 16202977 | 1
GEN-2024-168 | 02 NEBRASKA | 171635 | ERIS | Geneva 115 kV Substation GEN-2024-168 Interconnection (TOIF) (NPPD) | Interconnection |  |  | 500000 | 100 | 500000 | 1
GEN-2024-168 | 02 NEBRASKA | 171636 | ERIS | Geneva 115 kV Substation GEN-2024-168 Interconnection (Non-Shared NU) (NPPD) | Interconnection |  |  | 13500000 | 100 | 13500000 | 1
GEN-2024-170 | 03 CENTRAL | 171928 | ERIS | Dogwood 345 kV Substation GEN-2024-170 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1958092 | 100 | 1958092 | 1
GEN-2024-170 | 03 CENTRAL | 171929 | ERIS | Dogwood 345 kV Substation GEN-2024-170 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 4228553 | 100 | 4228553 | 1
GEN-2024-171 | 04 SOUTHEAST | 171637 | ERIS | Tulsa North - GR Energy Center 345 kV Line GEN-2024-171 Interconnection (TOIF) (GRDA) | Interconnection |  |  | 3797463 | 100 | 3797463 | 1
GEN-2024-171 | 04 SOUTHEAST | 171638 | ERIS | Tulsa North - GR Energy Center 345 kV Line GEN-2024-171 Interconnection (Non-Shared NU) (GRDA) | Interconnection |  |  | 14597250 | 100 | 14597250 | 1
GEN-2024-173 | 02 NEBRASKA | 171639 | ERIS | Pawnee Lake 115 kV Substation GEN-2024-173 Interconnection (TOIF) (NPPD) | Interconnection |  |  | 500000 | 100 | 500000 | 1
GEN-2024-173 | 02 NEBRASKA | 171640 | ERIS | Pawnee Lake 115 kV Substation GEN-2024-173 Interconnection (Non-Shared NU) (NPPD) | Interconnection |  |  | 7500000 | 100 | 7500000 | 1
GEN-2024-175 | 03 CENTRAL | 171641 | ERIS | Summit 161 kV Substation GEN-2024-175 Interconnection (TOIF) (CUS) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-175 | 03 CENTRAL | 171642 | ERIS | Summit 161 kV Substation GEN-2024-175 Interconnection (Non-Shared NU) (CUS) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-175 | 03 CENTRAL | 171641 | ERIS | Summit 161 kV Substation GEN-2024-175 Interconnection (TOIF) (CUS) | Interconnection |  |  | 55000 | 100 | 55000 | 1
GEN-2024-175 | 03 CENTRAL | 171642 | ERIS | Summit 161 kV Substation GEN-2024-175 Interconnection (Non-Shared NU) (CUS) | Interconnection |  |  | 700000 | 100 | 700000 | 1
GEN-2024-176 | 03 CENTRAL | 171930 | ERIS | Reno County 115 kV Substation GEN-2024-176 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1040242 | 100 | 1040242 | 1
GEN-2024-176 | 03 CENTRAL | 171931 | ERIS | Reno County 115 kV Substation GEN-2024-176 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 4480714 | 100 | 4480714 | 1
GEN-2024-177 | 04 SOUTHEAST | 171644 | ERIS | Red Point 138 kV Substation GEN-2024-177 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 2800000 | 100 | 2800000 | 1
GEN-2024-177 | 04 SOUTHEAST | 171643 | ERIS | Red Point 138 kV Substation GEN-2024-177 Interconnection (TOIF) (AEP) | Interconnection |  |  | 3325000 | 100 | 3325000 | 1
GEN-2024-178 | 04 SOUTHEAST | 171645 | ERIS | Pirkey 138 kV Substation GEN-2024-178 Interconnection (TOIF) (AEP) | Interconnection |  |  | 3325000 | 100 | 3325000 | 1
GEN-2024-178 | 04 SOUTHEAST | 171646 | ERIS | Pirkey 138 kV Substation GEN-2024-178 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 6300000 | 100 | 6300000 | 1
GEN-2024-180 | 04 SOUTHEAST | 171647 | ERIS | Kerr Dam 161 kV Substation GEN-2024-180 Interconnection (TOIF) (GRDA) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-180 | 04 SOUTHEAST | 171648 | ERIS | Kerr Dam 161 kV Substation GEN-2024-180 Interconnection (Non-Shared NU) (GRDA) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-181 | 03 CENTRAL | 171649 | ERIS | Brookline 161 kV Substation GEN-2024-181 Interconnection (TOIF) (CUS) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-181 | 03 CENTRAL | 171650 | ERIS | Brookline 161 kV Substation GEN-2024-181 Interconnection (Non-Shared NU) (CUS) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-181 | 03 CENTRAL | 171649 | ERIS | Brookline 161 kV Substation GEN-2024-181 Interconnection (TOIF) (CUS) | Interconnection |  |  | 55000 | 100 | 55000 | 1
GEN-2024-181 | 03 CENTRAL | 171650 | ERIS | Brookline 161 kV Substation GEN-2024-181 Interconnection (Non-Shared NU) (CUS) | Interconnection |  |  | 1700000 | 100 | 1700000 | 1
GEN-2024-184 | 04 SOUTHEAST | 171651 | ERIS | Atoka to Lehigh 138 kV line GEN-2024-184 Interconnection (TOIF) (AEP) | Interconnection |  |  | 3325000 | 100 | 3325000 | 1
GEN-2024-184 | 04 SOUTHEAST | 171652 | ERIS | Atoka to Lehigh 138 kV line GEN-2024-184 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 17175000 | 100 | 17175000 | 1
GEN-2024-186 | 05 SOUTHWEST | 171653 | ERIS | Roswell Interchange 115 kV Substation GEN-2024-186 Interconnection (TOIF) (SPS) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-186 | 05 SOUTHWEST | 171654 | ERIS | Roswell Interchange 115 kV Substation GEN-2024-186 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 30757015 | 100 | 30757015 | 1
GEN-2024-187 | 04 SOUTHEAST | 171655 | ERIS | Civit 138 kV Substation GEN-2024-187 Interconnection (TOIF) (WFEC) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-187 | 04 SOUTHEAST | 171656 | ERIS | Civit 138 kV Substation GEN-2024-187 Interconnection (Non-Shared NU) (WFEC) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-187 | 04 SOUTHEAST | 171655 | ERIS | Civit 138 kV Substation GEN-2024-187 Interconnection (TOIF) (WFEC) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-187 | 04 SOUTHEAST | 171656 | ERIS | Civit 138 kV Substation GEN-2024-187 Interconnection (Non-Shared NU) (WFEC) | Interconnection |  |  | 7000000 | 100 | 7000000 | 1
GEN-2024-189 | 03 CENTRAL | 171657 | ERIS | ITC Great Plains Saddle 345 kV Substation GEN-2024-189 Interconnection (TOIF) (ITCGP) | Interconnection |  |  | 1306438 | 100 | 1306438 | 1
GEN-2024-189 | 03 CENTRAL | 171658 | ERIS | ITC Great Plains Saddle 345 kV Substation GEN-2024-189 Interconnection (Non-Shared NU) (ITCGP) | Interconnection |  |  | 4630438 | 100 | 4630438 | 1
GEN-2024-193 | 03 CENTRAL | 171659 | ERIS | Spearville - Holcomb 345 kV Line GEN-2024-193 Interconnection (TOIF) (SUNC) | Interconnection |  |  | 2619450 | 100 | 2619450 | 1
GEN-2024-193 | 03 CENTRAL | 171661 | ERIS | Spearville - Holcomb 345 kV Line GEN-2024-193/194 Interconnection (Shared NU) (SUNC) | Interconnection |  |  | 20432445.5 | 50 | 40864891 | 1
GEN-2024-194 | 03 CENTRAL | 171660 | ERIS | Spearville - Holcomb 345 kV Line GEN-2024-194 Interconnection (TOIF) (SUNC) | Interconnection |  |  | 2619450 | 100 | 2619450 | 1
GEN-2024-194 | 03 CENTRAL | 171661 | ERIS | Spearville - Holcomb 345 kV Line GEN-2024-193/194 Interconnection (Shared NU) (SUNC) | Interconnection |  |  | 20432445.5 | 50 | 40864891 | 1
GEN-2024-204 | 04 SOUTHEAST | 171663 | ERIS | Brown 138 kV Substation GEN-2024-204 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-204 | 04 SOUTHEAST | 171662 | ERIS | Brown 138 kV Substation GEN-2024-204 Interconnection (TOIF) (OGE) | Interconnection |  |  | 100000 | 100 | 100000 | 1
GEN-2024-205 | 03 CENTRAL | 171664 | ERIS | St. John 115 kV Substation GEN-2024-205 Interconnection (TOIF) (SUNC) | Interconnection |  |  | 1200000 | 100 | 1200000 | 1
GEN-2024-205 | 03 CENTRAL | 171665 | ERIS | St. John 115 kV Substation GEN-2024-205 Interconnection (Non-Shared NU) (SUNC) | Interconnection |  |  | 2800000 | 100 | 2800000 | 1
GEN-2024-206 | 03 CENTRAL | 171666 | ERIS | Blue Valley 161 kV Substation GEN-2024-206 Interconnection (TOIF) (INDN) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-206 | 03 CENTRAL | 171667 | ERIS | Blue Valley 161 kV Substation GEN-2024-206 Interconnection (Non-Shared NU) (INDN) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-207 | 03 CENTRAL | 171668 | ERIS | Blue Valley - Blumil 161 kV Line GEN-2024-207 Interconnection (TOIF) (INDN) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-207 | 03 CENTRAL | 171669 | ERIS | Blue Valley - Blumil 161 kV Line GEN-2024-207 Interconnection (Non-Shared NU) (INDN) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-209 | 03 CENTRAL | 171670 | ERIS | Elm Creek - North Manhattan 230 kV Line GEN-2024-209 Interconnection (TOIF) (SUNC) | Interconnection |  |  | 5400000 | 100 | 5400000 | 1
GEN-2024-209 | 03 CENTRAL | 171671 | ERIS | Elm Creek - North Manhattan 230 kV Line GEN-2024-209 Interconnection (Non-Shared NU) (SUNC) | Interconnection |  |  | 12600000 | 100 | 12600000 | 1
GEN-2024-210 | 03 CENTRAL | 171672 | ERIS | St. Francis Tap 115 kV Substation GEN-2024-210 Interconnection (TOIF) (SUNC) | Interconnection |  |  | 5100000 | 100 | 5100000 | 1
GEN-2024-210 | 03 CENTRAL | 171673 | ERIS | St. Francis Tap 115 kV Substation GEN-2024-210 Interconnection (Non-Shared NU) (SUNC) | Interconnection |  |  | 11900000 | 100 | 11900000 | 1
GEN-2024-211 | 02 NEBRASKA | 171674 | ERIS | Substation 3740 345 kV GEN-2024-211 Interconnection (TOIF) (OPPD) | Interconnection |  |  | 1900000 | 100 | 1900000 | 1
GEN-2024-211 | 02 NEBRASKA | 171675 | ERIS | Substation 3740 345 kV GEN-2024-211 Interconnection (Non-Shared NU) (OPPD) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-212 | 02 NEBRASKA | 171676 | ERIS | Substation 3740 345 kV GEN-2024-212 Interconnection (TOIF) (OPPD) | Interconnection |  |  | 1900000 | 100 | 1900000 | 1
GEN-2024-212 | 02 NEBRASKA | 171677 | ERIS | Substation 3740 345 kV GEN-2024-212 Interconnection (Non-Shared NU) (OPPD) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-213 | 02 NEBRASKA | 171678 | ERIS | Substation 3740 345 kV GEN-2024-213 Interconnection (TOIF) (OPPD) | Interconnection |  |  | 1900000 | 100 | 1900000 | 1
GEN-2024-213 | 02 NEBRASKA | 171679 | ERIS | Substation 3740 345 kV GEN-2024-213 Interconnection (Non-Shared NU) (OPPD) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-215 | 03 CENTRAL | 171680 | ERIS | Elm Creek 345 kV Substation GEN-2024-215 Interconnection (TOIF) (ITCGP) | Interconnection |  |  | 1306438 | 100 | 1306438 | 1
GEN-2024-215 | 03 CENTRAL | 171681 | ERIS | Elm Creek 345 kV Substation GEN-2024-215 Interconnection (Non-Shared NU) (ITCGP) | Interconnection |  |  | 1856969 | 100 | 1856969 | 1
GEN-2024-216 | 01 NORTH | 171682 | ERIS | Dawson County - Miles City 230 kV Line GEN-2024-216 Interconnection (TOIF) (WAPA) | Interconnection |  |  | 884136 | 100 | 884136 | 1
GEN-2024-216 | 01 NORTH | 171683 | ERIS | Dawson County - Miles City 230 kV Line GEN-2024-216 Interconnection (Non-Shared NU) (WAPA) | Interconnection |  |  | 9073864 | 100 | 9073864 | 1
GEN-2024-217 | 03 CENTRAL | 171932 | ERIS | Sibley - Hawthorne 345 kV line GEN-2024-217 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1958092 | 100 | 1958092 | 1
GEN-2024-217 | 03 CENTRAL | 171933 | ERIS | Sibley - Hawthorne 345 kV line GEN-2024-217 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 31935383 | 100 | 31935383 | 1
GEN-2024-218 | 03 CENTRAL | 171684 | ERIS | Cimarron River 115 kV Substation GEN-2024-218 Interconnection (TOIF) (SUNC) | Interconnection |  |  | 4500000 | 100 | 4500000 | 1
GEN-2024-218 | 03 CENTRAL | 171685 | ERIS | Cimarron River 115 kV Substation GEN-2024-218 Interconnection (Non-Shared NU) (SUNC) | Interconnection |  |  | 10500000 | 100 | 10500000 | 1
GEN-2024-219 | 04 SOUTHEAST | 171686 | ERIS | Chigley - Oaklawn 138 kV Line GEN-2024-219 Interconnection (TOIF) (OGE) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-219 | 04 SOUTHEAST | 171687 | ERIS | Chigley - Oaklawn 138 kV Line GEN-2024-219 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 7000000 | 100 | 7000000 | 1
GEN-2024-220 | 04 SOUTHEAST | 171688 | ERIS | Rodessa - Bloomberg 69 kV Line GEN-2024-220 Interconnection (TOIF) (AEP) | Interconnection |  |  | 3475000 | 100 | 3475000 | 1
GEN-2024-220 | 04 SOUTHEAST | 171689 | ERIS | Rodessa - Bloomberg 69 kV Line GEN-2024-220 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 16475000 | 100 | 16475000 | 1
GEN-2024-221 | 05 SOUTHWEST | 171690 | ERIS | 345 kV Crossroads - Eddy County 345 kV Line GEN-2024-221 Interconnection (TOIF) (SPS) | Interconnection |  |  | 4872126.25 | 100 | 4872126.25 | 1
GEN-2024-221 | 05 SOUTHWEST | 171691 | ERIS | 345 kV Crossroads - Eddy County 345 kV Line GEN-2024-221 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 45536712.63 | 100 | 45536712.63 | 1
GEN-2024-226 | 04 SOUTHEAST | 171694 | ERIS | John W Turk Jr Power Plant 345 kV Substation GEN-2024-226/227 Interconnection (Shared NU) (AEP) | Interconnection |  |  | 0 |  | 0 | 1
GEN-2024-226 | 04 SOUTHEAST | 171692 | ERIS | John W Turk Jr Power Plant 345 kV Substation GEN-2024-226 Interconnection (TOIF) (AEP) | Interconnection |  |  | 5425000 | 100 | 5425000 | 1
GEN-2024-227 | 04 SOUTHEAST | 171694 | ERIS | John W Turk Jr Power Plant 345 kV Substation GEN-2024-226/227 Interconnection (Shared NU) (AEP) | Interconnection |  |  | 0 |  | 0 | 1
GEN-2024-227 | 04 SOUTHEAST | 171693 | ERIS | John W Turk Jr Power Plant 345 kV Substation GEN-2024-227 Interconnection (TOIF) (AEP) | Interconnection |  |  | 5425000 | 100 | 5425000 | 1
GEN-2024-228 | 03 CENTRAL | 171695 | ERIS | Rice to Circle 230 kV Line GEN-2024-228 Interconnection (TOIF) (MIDW) | Interconnection |  |  | 1797541.2 | 100 | 1797541.2 | 1
GEN-2024-228 | 03 CENTRAL | 171696 | ERIS | Rice to Circle 230 kV Line GEN-2024-228 Interconnection (Non-Shared NU) (MIDW) | Interconnection |  |  | 11100578.58 | 100 | 11100578.58 | 1
GEN-2024-229 | 04 SOUTHEAST | 171697 | ERIS | Lawton East Side - Oklaunion North 345 kV GEN-2024-229 Interconnection (TOIF) (AEP) | Interconnection |  |  | 5425000 | 100 | 5425000 | 1
GEN-2024-229 | 04 SOUTHEAST | 171699 | ERIS | Lawton East Side - Oklaunion North 345 kV GEN-2024-229/230 Interconnection (Shared NU) (AEP) | Interconnection |  |  | 11290000 | 40 | 28225000 | 1
GEN-2024-230 | 04 SOUTHEAST | 171698 | ERIS | Lawton East Side - Oklaunion North 345 kV GEN-2024-230 Interconnection (TOIF) (AEP) | Interconnection |  |  | 5425000 | 100 | 5425000 | 1
GEN-2024-230 | 04 SOUTHEAST | 171699 | ERIS | Lawton East Side - Oklaunion North 345 kV GEN-2024-229/230 Interconnection (Shared NU) (AEP) | Interconnection |  |  | 16935000 | 60 | 28225000 | 1
GEN-2024-231 | 02 NEBRASKA | 171700 | ERIS | S1399 5 161 kV Substation GEN-2024-231 Interconnection (TOIF) (OPPD) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-231 | 02 NEBRASKA | 171701 | ERIS | S1399 5 161 kV Substation GEN-2024-231 Interconnection (Non-Shared NU) (OPPD) | Interconnection |  |  | 350000 | 100 | 350000 | 1
GEN-2024-232 | 04 SOUTHEAST | 171702 | ERIS | Crockett - Rocky Creek 345 kV line GEN-2024-232 Interconnection (TOIF) (AEP) | Interconnection |  |  | 5225000 | 100 | 5225000 | 1
GEN-2024-232 | 04 SOUTHEAST | 171703 | ERIS | Crockett - Rocky Creek 345 kV line GEN-2024-232 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 28225000 | 100 | 28225000 | 1
GEN-2024-234 | 02 NEBRASKA | 171704 | ERIS | Raun - Tekamah 161 kV line GEN-2024-234 Interconnection (TOIF) (OPPD) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-234 | 02 NEBRASKA | 171705 | ERIS | Raun - Tekamah 161 kV line GEN-2024-234 Interconnection (Non-Shared NU) (OPPD) | Interconnection |  |  | 350000 | 100 | 350000 | 1
GEN-2024-235 | 04 SOUTHEAST | 171706 | ERIS | Sooner - Wekiwa 345 kV line GEN-2024-235 Interconnection (TOIF) (AEP) | Interconnection |  |  | 5225000 | 100 | 5225000 | 1
GEN-2024-235 | 04 SOUTHEAST | 171707 | ERIS | Sooner - Wekiwa 345 kV line GEN-2024-235 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 28225000 | 100 | 28225000 | 1
GEN-2024-236 | 04 SOUTHEAST | 171708 | ERIS | Seminole - Muskogee 345 kV line GEN-2024-236 Interconnection (TOIF) (OGE) | Interconnection |  |  | 3000000 | 100 | 3000000 | 1
GEN-2024-236 | 04 SOUTHEAST | 171709 | ERIS | Seminole - Muskogee 345 kV line GEN-2024-236 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 18000000 | 100 | 18000000 | 1
GEN-2024-239 | 04 SOUTHEAST | 171710 | ERIS | Cimarron 345 kV Substation GEN-2024-239 Interconnection (TOIF) (OGE) | Interconnection |  |  | 2500000 | 100 | 2500000 | 1
GEN-2024-239 | 04 SOUTHEAST | 171711 | ERIS | Cimarron 345 kV Substation GEN-2024-239 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 3000000 | 100 | 3000000 | 1
GEN-2024-240 | 04 SOUTHEAST | 171712 | ERIS | Neosho - Delaware 345 kV line GEN-2024-240 Interconnection (TOIF) (AEP) | Interconnection |  |  | 5225000 | 100 | 5225000 | 1
GEN-2024-240 | 04 SOUTHEAST | 171713 | ERIS | Neosho - Delaware 345 kV line GEN-2024-240 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 28225000 | 100 | 28225000 | 1
GEN-2024-241 | 04 SOUTHEAST | 171715 | ERIS | Lydia 345 kV Substation GEN-2024-241 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-241 | 04 SOUTHEAST | 171714 | ERIS | Lydia 345 kV Substation GEN-2024-241 Interconnection (TOIF) (AEP) | Interconnection |  |  | 200000 | 100 | 200000 | 1
GEN-2024-242 | 04 SOUTHEAST | 171717 | ERIS | 515171 138 kV Substation GEN-2024-242 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 1500000 | 100 | 1500000 | 1
GEN-2024-242 | 04 SOUTHEAST | 171716 | ERIS | 515171 138 kV Substation GEN-2024-242 Interconnection (TOIF) (OGE) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-243 | 04 SOUTHEAST | 171718 | ERIS | Van Buren 161 kV Substation GEN-2024-243 Interconnection (TOIF) (SWPA) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-243 | 04 SOUTHEAST | 171719 | ERIS | Van Buren 161 kV Substation GEN-2024-243 Interconnection (Non-Shared NU) (SWPA) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-243 | 04 SOUTHEAST | 171718 | ERIS | Van Buren 161 kV Substation GEN-2024-243 Interconnection (TOIF) (SWPA) | Interconnection |  |  | 800000 | 100 | 800000 | 1
GEN-2024-243 | 04 SOUTHEAST | 171719 | ERIS | Van Buren 161 kV Substation GEN-2024-243 Interconnection (Non-Shared NU) (SWPA) | Interconnection |  |  | 4100000 | 100 | 4100000 | 1
GEN-2024-244 | 05 SOUTHWEST | 171720 | ERIS | Texas County Interchange 115 kV Substation GEN-2024-244 Interconnection (TOIF) (SPS) | Interconnection |  |  | 3442284.34 | 100 | 3442284.34 | 1
GEN-2024-244 | 05 SOUTHWEST | 171721 | ERIS | Texas County Interchange 115 kV Substation GEN-2024-244 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 6281531.43 | 100 | 6281531.43 | 1
GEN-2024-245 | 04 SOUTHEAST | 171723 | ERIS | Lincoln 138 kV Substation GEN-2024-245 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 1500000 | 100 | 1500000 | 1
GEN-2024-245 | 04 SOUTHEAST | 171722 | ERIS | Lincoln 138 kV Substation GEN-2024-245 Interconnection (TOIF) (OGE) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-246 | 05 SOUTHWEST | 171724 | ERIS | North Loving 115 kV Substation GEN-2024-246 Interconnection (TOIF) (SPS) | Interconnection |  |  | 3089885.6 | 100 | 3089885.6 | 1
GEN-2024-246 | 05 SOUTHWEST | 171725 | ERIS | North Loving 115 kV Substation GEN-2024-246 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 3275577.97 | 100 | 3275577.97 | 1
GEN-2024-247 | 04 SOUTHEAST | 171726 | ERIS | Stillwater Northtap 138 kV Substation GEN-2024-247 Interconnection (TOIF) (GRDA) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-247 | 04 SOUTHEAST | 171727 | ERIS | Stillwater Northtap 138 kV Substation GEN-2024-247 Interconnection (Non-Shared NU) (GRDA) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-247 | 04 SOUTHEAST | 171727 | ERIS | Stillwater Northtap 138 kV Substation GEN-2024-247 Interconnection (Non-Shared NU) (GRDA) | Interconnection |  |  | 195000 | 100 | 195000 | 1
GEN-2024-247 | 04 SOUTHEAST | 171726 | ERIS | Stillwater Northtap 138 kV Substation GEN-2024-247 Interconnection (TOIF) (GRDA) | Interconnection |  |  | 1751000 | 100 | 1751000 | 1
GEN-2024-249 | 03 CENTRAL | 171934 | ERIS | Jeffrey EC 345 kV Substation GEN-2024-249 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1742929 | 100 | 1742929 | 1
GEN-2024-249 | 03 CENTRAL | 171935 | ERIS | Jeffrey EC 345 kV Substation GEN-2024-249 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 5202083 | 100 | 5202083 | 1
GEN-2024-250 | 04 SOUTHEAST | 171729 | ERIS | Pittsburgh 345 kV Substation GEN-2024-250 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 3900000 | 100 | 3900000 | 1
GEN-2024-250 | 04 SOUTHEAST | 171728 | ERIS | Pittsburgh 345 kV Substation GEN-2024-250 Interconnection (TOIF) (AEP) | Interconnection |  |  | 5225000 | 100 | 5225000 | 1
GEN-2024-251 | 05 SOUTHWEST | 171730 | ERIS | Atoka 115 kV Substation GEN-2024-251 Interconnection (TOIF) (SPS) | Interconnection |  |  | 3015769.29 | 100 | 3015769.29 | 1
GEN-2024-251 | 05 SOUTHWEST | 171731 | ERIS | Atoka 115 kV Substation GEN-2024-251 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 5047349.56 | 100 | 5047349.56 | 1
GEN-2024-252 | 04 SOUTHEAST | 171732 | ERIS | Cimmaron 345 kV Substation GEN-2024-252 Interconnection (TOIF) (OGE) | Interconnection |  |  | 2500000 | 100 | 2500000 | 1
GEN-2024-252 | 04 SOUTHEAST | 171733 | ERIS | Cimmaron 345 kV Substation GEN-2024-252 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 3000000 | 100 | 3000000 | 1
GEN-2024-253 | 03 CENTRAL | 171936 | ERIS | Stranger Creek - 87th Street 345 kV line GEN-2024-253 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1958092 | 100 | 1958092 | 1
GEN-2024-253 | 03 CENTRAL | 171937 | ERIS | Stranger Creek - 87th Street 345 kV line GEN-2024-253 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 33058407 | 100 | 33058407 | 1
GEN-2024-254 | 04 SOUTHEAST | 171735 | ERIS | Mathewson 345 kV Substation GEN-2024-254 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-254 | 04 SOUTHEAST | 171734 | ERIS | Mathewson 345 kV Substation GEN-2024-254 Interconnection (TOIF) (OGE) | Interconnection |  |  | 3000000 | 100 | 3000000 | 1
GEN-2024-255 | 04 SOUTHEAST | 171736 | ERIS | Spring Creek 345 kV Substation GEN-2024-255 Interconnection (TOIF) (OGE) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-255 | 04 SOUTHEAST | 171737 | ERIS | Spring Creek 345 kV Substation GEN-2024-255 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 7500000 | 100 | 7500000 | 1
GEN-2024-257 | 03 CENTRAL | 171738 | ERIS | Skellyville 115 kV Tap Substation GEN-2024-257 Interconnection (TOIF) (SUNC) | Interconnection |  |  | 6300000 | 100 | 6300000 | 1
GEN-2024-257 | 03 CENTRAL | 171739 | ERIS | Skellyville 115 kV Tap Substation GEN-2024-257 Interconnection (Non-Shared NU) (SUNC) | Interconnection |  |  | 14700000 | 100 | 14700000 | 1
GEN-2024-258 | 03 CENTRAL | 171740 | ERIS | Wolf Creek - Blackberry 345 kV Line GEN-2024-258 Interconnection (TOIF) (NEET) | Interconnection |  |  | 840255 | 100 | 840255 | 1
GEN-2024-258 | 03 CENTRAL | 171741 | ERIS | Wolf Creek - Blackberry 345 kV Line GEN-2024-258 Interconnection (Non-Shared NU) (NEET) | Interconnection |  |  | 28818600 | 100 | 28818600 | 1
GEN-2024-259 | 03 CENTRAL | 171742 | ERIS | Asbury 161 kV Substation GEN-2024-259 Interconnection (TOIF) (EMDE) | Interconnection |  |  | 5877539 | 100 | 5877539 | 1
GEN-2024-259 | 03 CENTRAL | 171743 | ERIS | Asbury 161 kV Substation GEN-2024-259 Interconnection (Non-Shared NU) (EMDE) | Interconnection |  |  | 33306052 | 100 | 33306052 | 1
GEN-2024-260 | 03 CENTRAL | 171938 | ERIS | East Town 161 kV Substation GEN-2024-260 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1061551 | 100 | 1061551 | 1
GEN-2024-260 | 03 CENTRAL | 171939 | ERIS | East Town 161 kV Substation GEN-2024-260 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 1235193 | 100 | 1235193 | 1
GEN-2024-261 | 05 SOUTHWEST | 171744 | ERIS | Hobbs 115 kV Line GEN-2024-261 Interconnection (TOIF) (LCEC) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-261 | 05 SOUTHWEST | 171745 | ERIS | Hobbs 115 kV Line GEN-2024-261 Interconnection (Non-Shared NU) (LCEC) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-265 | 05 SOUTHWEST | 171746 | ERIS | Hobbs 115 kV Line GEN-2024-265 Interconnection (TOIF) (SPS) | Interconnection |  |  | 3262876.57 | 100 | 3262876.57 | 1
GEN-2024-265 | 05 SOUTHWEST | 171747 | ERIS | Hobbs 115 kV Line GEN-2024-265 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 15220699.21 | 100 | 15220699.21 | 1
GEN-2024-266 | 05 SOUTHWEST | 171748 | ERIS | Potter Co - Hitchland 345 kV Line GEN-2024-266 Interconnection (TOIF) (SPS) | Interconnection |  |  | 3261652.93 | 100 | 3261652.93 | 1
GEN-2024-266 | 05 SOUTHWEST | 171749 | ERIS | Potter Co - Hitchland 345 kV Line GEN-2024-266 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 27605699.58 | 100 | 27605699.58 | 1
GEN-2024-267 | 04 SOUTHEAST | 171750 | ERIS | Durantp4 - Sclmnjc4 138 kV Line GEN-2024-267 Interconnection (TOIF) (WFEC) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-267 | 04 SOUTHEAST | 171751 | ERIS | Durantp4 - Sclmnjc4 138 kV Line GEN-2024-267 Interconnection (Non-Shared NU) (WFEC) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-267 | 04 SOUTHEAST | 171750 | ERIS | Durantp4 - Sclmnjc4 138 kV Line GEN-2024-267 Interconnection (TOIF) (WFEC) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-267 | 04 SOUTHEAST | 171751 | ERIS | Durantp4 - Sclmnjc4 138 kV Line GEN-2024-267 Interconnection (Non-Shared NU) (WFEC) | Interconnection |  |  | 7000000 | 100 | 7000000 | 1
GEN-2024-268 | 04 SOUTHEAST | 171752 | ERIS | Muskogee - Fort Smith 345 kV Line GEN-2024-268 Interconnection (TOIF) (OGE) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-268 | 04 SOUTHEAST | 171753 | ERIS | Muskogee - Fort Smith 345 kV Line GEN-2024-268 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 3000000 | 100 | 3000000 | 1
GEN-2024-271 | 05 SOUTHWEST | 171754 | ERIS | Chaves County - San Juan Wind 230 kV Line GEN-2024-271 Interconnection (TOIF) (SPS) | Interconnection |  |  | 3858814.71 | 100 | 3858814.71 | 1
GEN-2024-271 | 05 SOUTHWEST | 171755 | ERIS | Chaves County - San Juan Wind 230 kV Line GEN-2024-271 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 26356389.29 | 100 | 26356389.29 | 1
GEN-2024-272 | 03 CENTRAL | 171756 | ERIS | Sawyer 115 kV Substation GEN-2024-272 Interconnection (TOIF) (KACY) | Interconnection |  |  | 5100000 | 100 | 5100000 | 1
GEN-2024-272 | 03 CENTRAL | 171757 | ERIS | Sawyer 115 kV Substation GEN-2024-272 Interconnection (Non-Shared NU) (KACY) | Interconnection |  |  | 11900000 | 100 | 11900000 | 1
GEN-2024-273 | 05 SOUTHWEST | 171758 | ERIS | Pearl 115 kV Substation GEN-2024-273 Interconnection (TOIF) (SPS) | Interconnection |  |  | 2622572 | 100 | 2622572 | 1
GEN-2024-273 | 05 SOUTHWEST | 171759 | ERIS | Pearl 115 kV Substation GEN-2024-273 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 10211151 | 100 | 10211151 | 1
GEN-2024-274 | 03 CENTRAL | 171760 | ERIS | Harper - Anthony 138 kV Line GEN-2024-274 Interconnection (TOIF) (SUNC) | Interconnection |  |  | 4500000 | 100 | 4500000 | 1
GEN-2024-274 | 03 CENTRAL | 171761 | ERIS | Harper - Anthony 138 kV Line GEN-2024-274 Interconnection (Non-Shared NU) (SUNC) | Interconnection |  |  | 10500000 | 100 | 10500000 | 1
GEN-2024-276 | 03 CENTRAL | 171940 | ERIS | Tecumseh Hill - Swissvale 230kV Line GEN-2024-276 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1958092 | 100 | 1958092 | 1
GEN-2024-276 | 03 CENTRAL | 171942 | ERIS | Tecumseh Hill - Swissvale 230kV Line GEN-2024-276/277 Interconnection (Shared NU) (WERE) | Interconnection |  |  | 16322218.5 | 50 | 32644437 | 1
GEN-2024-277 | 03 CENTRAL | 171941 | ERIS | Tecumseh Hill - Swissvale 230kV Line GEN-2024-277 Interconnection (TOIF) (WERE) | Interconnection |  |  | 112911 | 100 | 112911 | 1
GEN-2024-277 | 03 CENTRAL | 171942 | ERIS | Tecumseh Hill - Swissvale 230kV Line GEN-2024-276/277 Interconnection (Shared NU) (WERE) | Interconnection |  |  | 16322218.5 | 50 | 32644437 | 1
GEN-2024-278 | 05 SOUTHWEST | 171762 | ERIS | Eddy County - Crossroads 345 kV Line GEN-2024-278 Interconnection (TOIF) (SPS) | Interconnection |  |  | 3338843.04 | 100 | 3338843.04 | 1
GEN-2024-278 | 05 SOUTHWEST | 171763 | ERIS | Eddy County - Crossroads 345 kV Line GEN-2024-278 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 31250321.55 | 100 | 31250321.55 | 1
GEN-2024-280 | 05 SOUTHWEST | 171764 | ERIS | Andrews County 345 kV Substation GEN-2024-280 Interconnection (TOIF) (SPS) | Interconnection |  |  | 4502736.58 | 100 | 4502736.58 | 1
GEN-2024-280 | 05 SOUTHWEST | 171765 | ERIS | Andrews County 345 kV Substation GEN-2024-280 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 8636936.73 | 100 | 8636936.73 | 1
GEN-2024-281 | 05 SOUTHWEST | 171766 | ERIS | Jal - Teague 115 kV Line GEN-2024-281 Interconnection (TOIF) (SPS) | Interconnection |  |  | 2804642.69 | 100 | 2804642.69 | 1
GEN-2024-281 | 05 SOUTHWEST | 171767 | ERIS | Jal - Teague 115 kV Line GEN-2024-281 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 22838049.8 | 100 | 22838049.8 | 1
GEN-2024-282 | 01 NORTH | 171768 | ERIS | Maurine - New Underwood 230 kV Line GEN-2024-282 Interconnection (TOIF) (WAPA) | Interconnection |  |  | 620000 | 100 | 620000 | 1
GEN-2024-282 | 01 NORTH | 171770 | ERIS | Maurine - New Underwood 230 kV Line GEN-2024-282/283 Interconnection (Shared NU) (WAPA) | Interconnection |  |  | 13115000 | 50 | 26230000 | 1
GEN-2024-283 | 01 NORTH | 171769 | ERIS | Maurine - New Underwood 230 kV Line GEN-2024-283 Interconnection (TOIF) (WAPA) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-283 | 01 NORTH | 171770 | ERIS | Maurine - New Underwood 230 kV Line GEN-2024-282/283 Interconnection (Shared NU) (WAPA) | Interconnection |  |  | 13115000 | 50 | 26230000 | 1
GEN-2024-284 | 01 NORTH | 171771 | ERIS | Antelope Valley - Broadland 345 kV Line GEN-2024-284 Interconnection (TOIF) (BEPC) | Interconnection |  |  | 4791248 | 100 | 4791248 | 1
GEN-2024-284 | 01 NORTH | 171772 | ERIS | Antelope Valley - Broadland 345 kV Line GEN-2024-284 Interconnection (Non-Shared NU) (BEPC) | Interconnection |  |  | 30292999 | 100 | 30292999 | 1
GEN-2024-285 | 01 NORTH | 171773 | ERIS | Crocker 345 kV Substation GEN-2024-285 Interconnection (TOIF) (BEPC) | Interconnection |  |  | 1799526 | 100 | 1799526 | 1
GEN-2024-285 | 01 NORTH | 171774 | ERIS | Crocker 345 kV Substation GEN-2024-285 Interconnection (Non-Shared NU) (BEPC) | Interconnection |  |  | 4745484 | 100 | 4745484 | 1
GEN-2024-286 | 04 SOUTHEAST | 171775 | ERIS | AES 5 161 kV Substation GEN-2024-286 Interconnection (TOIF) (OGE) | Interconnection |  |  | 5000000 | 100 | 5000000 | 1
GEN-2024-286 | 04 SOUTHEAST | 171776 | ERIS | AES 5 161 kV Substation GEN-2024-286 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 12000000 | 100 | 12000000 | 1
GEN-2024-287 | 03 CENTRAL | 171777 | ERIS | Wolf Creek - Blackberry 345 kV Line GEN-2024-287 Interconnection (TOIF) (NEET) | Interconnection |  |  | 840255 | 100 | 840255 | 1
GEN-2024-287 | 03 CENTRAL | 171778 | ERIS | Wolf Creek - Blackberry 345 kV Line GEN-2024-287 Interconnection (Non-Shared NU) (NEET) | Interconnection |  |  | 28818600 | 100 | 28818600 | 1
GEN-2024-288 | 03 CENTRAL | 171779 | ERIS | Elm Creek - Tobias 345 kV Line GEN-2024-288 Interconnection (TOIF) (SUNC) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-288 | 03 CENTRAL | 171780 | ERIS | Elm Creek - Tobias 345 kV Line GEN-2024-288 Interconnection (Non-Shared NU) (SUNC) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-289 | 03 CENTRAL | 171943 | ERIS | Archie - Clinton 161 kV Line GEN-2024-289 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1495125 | 100 | 1495125 | 1
GEN-2024-289 | 03 CENTRAL | 171944 | ERIS | Archie - Clinton 161 kV Line GEN-2024-289 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 7763701 | 100 | 7763701 | 1
GEN-2024-291 | 04 SOUTHEAST | 171781 | ERIS | Muskogee - Pittsburg 345 kV Line GEN-2024-291 Interconnection (TOIF) (OGE) | Interconnection |  |  | 3000000 | 100 | 3000000 | 1
GEN-2024-291 | 04 SOUTHEAST | 171782 | ERIS | Muskogee - Pittsburg 345 kV Line GEN-2024-291 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 5000000 | 100 | 5000000 | 1
GEN-2024-293 | 04 SOUTHEAST | 171783 | ERIS | Muskoge7 345 kV Substation GEN-2024-293 Interconnection (TOIF) (OGE) | Interconnection |  |  | 3000000 | 100 | 3000000 | 1
GEN-2024-293 | 04 SOUTHEAST | 171784 | ERIS | Muskoge7 345 kV Substation GEN-2024-293 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 5000000 | 100 | 5000000 | 1
GEN-2024-294 | 04 SOUTHEAST | 171785 | ERIS | Tulsa North - Igloo Valley 345 kV line GEN-2024-294 Interconnection (TOIF) (GRDA) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-294 | 04 SOUTHEAST | 171786 | ERIS | Tulsa North - Igloo Valley 345 kV line GEN-2024-294 Interconnection (Non-Shared NU) (GRDA) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-294 | 04 SOUTHEAST | 171786 | ERIS | Tulsa North - Igloo Valley 345 kV line GEN-2024-294 Interconnection (Non-Shared NU) (GRDA) | Interconnection |  |  | 130000 | 100 | 130000 | 1
GEN-2024-295 | 05 SOUTHWEST | 171788 | ERIS | S Loving 115 kV Substation GEN-2024-295 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 2172444.84 | 100 | 2172444.84 | 1
GEN-2024-295 | 05 SOUTHWEST | 171787 | ERIS | S Loving 115 kV Substation GEN-2024-295 Interconnection (TOIF) (SPS) | Interconnection |  |  | 3362273.9 | 100 | 3362273.9 | 1
GEN-2024-296 | 04 SOUTHEAST | 171789 | ERIS | Muskogee - Pittsburg 345 kV Line GEN-2024-296 Interconnection (TOIF) (OGE) | Interconnection |  |  | 3000000 | 100 | 3000000 | 1
GEN-2024-296 | 04 SOUTHEAST | 171792 | ERIS | Muskogee - Pittsburg 345 kV Line GEN-2024-296/297/298 Interconnection (Shared NU) (OGE) | Interconnection |  |  | 6000000 | 33.3333 | 18000000 | 1
GEN-2024-297 | 04 SOUTHEAST | 171790 | ERIS | Muskogee - Pittsburg 345 kV Line GEN-2024-297 Interconnection (TOIF) (OGE) | Interconnection |  |  | 3000000 | 100 | 3000000 | 1
GEN-2024-297 | 04 SOUTHEAST | 171792 | ERIS | Muskogee - Pittsburg 345 kV Line GEN-2024-296/297/298 Interconnection (Shared NU) (OGE) | Interconnection |  |  | 6000000 | 33.3333 | 18000000 | 1
GEN-2024-298 | 04 SOUTHEAST | 171791 | ERIS | Muskogee - Pittsburg 345 kV Line GEN-2024-298 Interconnection (TOIF) (OGE) | Interconnection |  |  | 3000000 | 100 | 3000000 | 1
GEN-2024-298 | 04 SOUTHEAST | 171792 | ERIS | Muskogee - Pittsburg 345 kV Line GEN-2024-296/297/298 Interconnection (Shared NU) (OGE) | Interconnection |  |  | 6000000 | 33.3333 | 18000000 | 1
GEN-2024-299 | 04 SOUTHEAST | 171793 | ERIS | AES 5 345 kV Substation GEN-2024-299 Interconnection (TOIF) (OGE) | Interconnection |  |  | 8000000 | 100 | 8000000 | 1
GEN-2024-299 | 04 SOUTHEAST | 171794 | ERIS | AES 5 345 kV Substation GEN-2024-299 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 20000000 | 100 | 20000000 | 1
GEN-2024-303 | 05 SOUTHWEST | 171795 | ERIS | Crossroads 345 kV Substation GEN-2024-303 Interconnection (TOIF) (SPS) | Interconnection |  |  | 4502736.58 | 100 | 4502736.58 | 1
GEN-2024-303 | 05 SOUTHWEST | 171796 | ERIS | Crossroads 345 kV Substation GEN-2024-303 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 8636936.73 | 100 | 8636936.73 | 1
GEN-2024-304 | 05 SOUTHWEST | 171797 | ERIS | Crossroads 345 kV Substation GEN-2024-304 Interconnection (TOIF) (SPS) | Interconnection |  |  | 4502736.58 | 100 | 4502736.58 | 1
GEN-2024-304 | 05 SOUTHWEST | 171798 | ERIS | Crossroads 345 kV Substation GEN-2024-304 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 8636936.73 | 100 | 8636936.73 | 1
GEN-2024-305 | 04 SOUTHEAST | 171799 | ERIS | Superior - Jefferson 69 kV Line GEN-2024-305 Interconnection (TOIF) (AEP) | Interconnection |  |  | 3275000 | 100 | 3275000 | 1
GEN-2024-305 | 04 SOUTHEAST | 171800 | ERIS | Superior - Jefferson 69 kV Line GEN-2024-305 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 16475000 | 100 | 16475000 | 1
GEN-2024-306 | 05 SOUTHWEST | 171801 | ERIS | Taylor Switching Station 115 kV Substation GEN-2024-306 Interconnection (TOIF) (SPS) | Interconnection |  |  | 2907181.63 | 100 | 2907181.63 | 1
GEN-2024-306 | 05 SOUTHWEST | 171802 | ERIS | Taylor Switching Station 115 kV Substation GEN-2024-306 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 21550441.87 | 100 | 21550441.87 | 1
GEN-2024-308 | 04 SOUTHEAST | 171803 | ERIS | Okeene - Mooreland 138 kV line GEN-2024-308 Interconnection (TOIF) (WFEC) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-308 | 04 SOUTHEAST | 171804 | ERIS | Okeene - Mooreland 138 kV line GEN-2024-308 Interconnection (Non-Shared NU) (WFEC) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-308 | 04 SOUTHEAST | 171803 | ERIS | Okeene - Mooreland 138 kV line GEN-2024-308 Interconnection (TOIF) (WFEC) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-308 | 04 SOUTHEAST | 171804 | ERIS | Okeene - Mooreland 138 kV line GEN-2024-308 Interconnection (Non-Shared NU) (WFEC) | Interconnection |  |  | 7000000 | 100 | 7000000 | 1
GEN-2024-310 | 05 SOUTHWEST | 171807 | ERIS | Eddy - Chaves 230 kV line GEN-2024-310/311 Interconnection (Shared NU) (SPS) | Interconnection |  |  | 0 |  | 0 | 1
GEN-2024-310 | 05 SOUTHWEST | 171805 | ERIS | Eddy - Chaves 230 kV line GEN-2024-310 Interconnection (TOIF) (SPS) | Interconnection |  |  | 4549755.92 | 100 | 4549755.92 | 1
GEN-2024-311 | 05 SOUTHWEST | 171807 | ERIS | Eddy - Chaves 230 kV line GEN-2024-310/311 Interconnection (Shared NU) (SPS) | Interconnection |  |  | 0 |  | 0 | 1
GEN-2024-311 | 05 SOUTHWEST | 171806 | ERIS | Eddy - Chaves 230 kV line GEN-2024-311 Interconnection (TOIF) (SPS) | Interconnection |  |  | 4549755.92 | 100 | 4549755.92 | 1
GEN-2024-312 | 04 SOUTHEAST | 171808 | ERIS | Clarksville Ozark 161 kV line GEN-2024-312 Interconnection (TOIF) (SWPA) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-312 | 04 SOUTHEAST | 171809 | ERIS | Clarksville Ozark 161 kV line GEN-2024-312 Interconnection (Non-Shared NU) (SWPA) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-312 | 04 SOUTHEAST | 171808 | ERIS | Clarksville Ozark 161 kV line GEN-2024-312 Interconnection (TOIF) (SWPA) | Interconnection |  |  | 800000 | 100 | 800000 | 1
GEN-2024-312 | 04 SOUTHEAST | 171809 | ERIS | Clarksville Ozark 161 kV line GEN-2024-312 Interconnection (Non-Shared NU) (SWPA) | Interconnection |  |  | 8600000 | 100 | 8600000 | 1
GEN-2024-316 | 04 SOUTHEAST | 171810 | ERIS | Pittsburg - Valliant 345 kV Line GEN-2024-316 Interconnection (TOIF) (AEP) | Interconnection |  |  | 5225000 | 100 | 5225000 | 1
GEN-2024-316 | 04 SOUTHEAST | 171811 | ERIS | Pittsburg - Valliant 345 kV Line GEN-2024-316 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 28225000 | 100 | 28225000 | 1
GEN-2024-317 | 05 SOUTHWEST | 171812 | ERIS | Dragon 345 kV Substation GEN-2024-317 Interconnection (TOIF) (SPS) | Interconnection |  |  | 2882135.29 | 100 | 2882135.29 | 1
GEN-2024-317 | 05 SOUTHWEST | 171813 | ERIS | Dragon 345 kV Substation GEN-2024-317 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 6564758.74 | 100 | 6564758.74 | 1
GEN-2024-318 | 04 SOUTHEAST | 171814 | ERIS | Tulsa North - American Airlines 138 kV Line GEN-2024-318 Interconnection (TOIF) (AEP) | Interconnection |  |  | 3325000 | 100 | 3325000 | 1
GEN-2024-318 | 04 SOUTHEAST | 171815 | ERIS | Tulsa North - American Airlines 138 kV Line GEN-2024-318 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 17175000 | 100 | 17175000 | 1
GEN-2024-319 | 03 CENTRAL | 171816 | ERIS | Metro 5 161 kV Substation GEN-2024-319 Interconnection (TOIF) (KACY) | Interconnection |  |  | 200000 | 100 | 200000 | 1
GEN-2024-319 | 03 CENTRAL | 171817 | ERIS | Metro 5 161 kV Substation GEN-2024-319 Interconnection (Non-Shared NU) (KACY) | Interconnection |  |  | 2757867 | 100 | 2757867 | 1
GEN-2024-320 | 03 CENTRAL | 171945 | ERIS | Jaggard 115 kV Substation GEN-2024-320 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1040242 | 100 | 1040242 | 1
GEN-2024-320 | 03 CENTRAL | 171946 | ERIS | Jaggard 115 kV Substation GEN-2024-320 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 16424539 | 100 | 16424539 | 1
GEN-2024-321 | 04 SOUTHEAST | 171818 | ERIS | Seminole 345 kV Substation GEN-2024-321 Interconnection (TOIF) (OGE) | Interconnection |  |  | 3000000 | 100 | 3000000 | 1
GEN-2024-321 | 04 SOUTHEAST | 171819 | ERIS | Seminole 345 kV Substation GEN-2024-321 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 5000000 | 100 | 5000000 | 1
GEN-2024-322 | 03 CENTRAL | 171820 | ERIS | Redlin - Beach3 115 kV line GEN-2024-322 Interconnection (TOIF) (MIDW) | Interconnection |  |  | 1222480.35 | 100 | 1222480.35 | 1
GEN-2024-322 | 03 CENTRAL | 171821 | ERIS | Redlin - Beach3 115 kV line GEN-2024-322 Interconnection (Non-Shared NU) (MIDW) | Interconnection |  |  | 7964021.52 | 100 | 7964021.52 | 1
GEN-2024-323 | 04 SOUTHEAST | 171822 | ERIS | ITC Hugo 7 345 kV Substation GEN-2024-323 Interconnection (TOIF) (ITCGP) | Interconnection |  |  | 1306438 | 100 | 1306438 | 1
GEN-2024-323 | 04 SOUTHEAST | 171823 | ERIS | ITC Hugo 7 345 kV Substation GEN-2024-323 Interconnection (Non-Shared NU) (ITCGP) | Interconnection |  |  | 4630437 | 100 | 4630437 | 1
GEN-2024-324 | 05 SOUTHWEST | 171825 | ERIS | Samson - Chaves 115 kV Line GEN-2024-324 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-324 | 05 SOUTHWEST | 171824 | ERIS | Samson - Chaves 115 kV Line GEN-2024-324 Interconnection (TOIF) (SPS) | Interconnection |  |  | 3134444.66 | 100 | 3134444.66 | 1
GEN-2024-325 | 05 SOUTHWEST | 171826 | ERIS | Sierra 115 kV Substation GEN-2024-325 Interconnection (TOIF) (SPS) | Interconnection |  |  | 2416023.14 | 100 | 2416023.14 | 1
GEN-2024-325 | 05 SOUTHWEST | 171827 | ERIS | Sierra 115 kV Substation GEN-2024-325 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 8107736.66 | 100 | 8107736.66 | 1
GEN-2024-326 | 01 NORTH | 171828 | ERIS | Belfield 230 kV Substation GEN-2024-326 Interconnection (TOIF) (WAPA) | Interconnection |  |  | 680000 | 100 | 680000 | 1
GEN-2024-326 | 01 NORTH | 171829 | ERIS | Belfield 230 kV Substation GEN-2024-326 Interconnection (Non-Shared NU) (WAPA) | Interconnection |  |  | 8970000 | 100 | 8970000 | 1
GEN-2024-327 | 01 NORTH | 171830 | ERIS | Berthold 115 kV Substation GEN-2024-327 Interconnection (TOIF) (CPEC) | Interconnection |  |  | 214000 | 100 | 214000 | 1
GEN-2024-327 | 01 NORTH | 171831 | ERIS | Berthold 115 kV Substation GEN-2024-327 Interconnection (Non-Shared NU) (CPEC) | Interconnection |  |  | 1395000 | 100 | 1395000 | 1
GEN-2024-328 | 01 NORTH | 171832 | ERIS | Little Missouri 230 kV Substation GEN-2024-328 Interconnection (TOIF) (BEPC) | Interconnection |  |  | 2270573 | 100 | 2270573 | 1
GEN-2024-328 | 01 NORTH | 171833 | ERIS | Little Missouri 230 kV Substation GEN-2024-328 Interconnection (Non-Shared NU) (BEPC) | Interconnection |  |  | 7362181 | 100 | 7362181 | 1
GEN-2024-329 | 01 NORTH | 171835 | ERIS | Pleasant Valley 115 kV Substation GEN-2024-329 Interconnection (Non-Shared NU) (MWEC) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-329 | 01 NORTH | 171834 | ERIS | Pleasant Valley 115 kV Substation GEN-2024-329 Interconnection (TOIF) (MWEC) | Interconnection |  |  | 1200000 | 100 | 1200000 | 1
GEN-2024-330 | 03 CENTRAL | 171947 | ERIS | Butler 138 kV Substation GEN-2024-330 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1040242 | 100 | 1040242 | 1
GEN-2024-330 | 03 CENTRAL | 171948 | ERIS | Butler 138 kV Substation GEN-2024-330 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 24263481 | 100 | 24263481 | 1
GEN-2024-331 | 01 NORTH | 171836 | ERIS | Round Up 345 kV Substation GEN-2024-331 Interconnection (TOIF) (BEPC) | Interconnection |  |  | 2804764 | 100 | 2804764 | 1
GEN-2024-331 | 01 NORTH | 171837 | ERIS | Round Up 345 kV Substation GEN-2024-331 Interconnection (Non-Shared NU) (BEPC) | Interconnection |  |  | 5716377 | 100 | 5716377 | 1
GEN-2024-332 | 04 SOUTHEAST | 171838 | ERIS | Discovery 138 kV Substation GEN-2024-332 Interconnection (TOIF) (OGE) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-332 | 04 SOUTHEAST | 171839 | ERIS | Discovery 138 kV Substation GEN-2024-332 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 3000000 | 100 | 3000000 | 1
GEN-2024-333 | 04 SOUTHEAST | 171840 | ERIS | Kelley Avenue 138 kV GEN-2024-333 Interconnection (TOIF) (OGE) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-333 | 04 SOUTHEAST | 171841 | ERIS | Kelley Avenue 138 kV GEN-2024-333 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 4500000 | 100 | 4500000 | 1
GEN-2024-334 | 04 SOUTHEAST | 171843 | ERIS | OMPA 345 kV Switchyard GEN-2024-334 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-334 | 04 SOUTHEAST | 171842 | ERIS | OMPA 345 kV Switchyard GEN-2024-334 Interconnection (TOIF) (OGE) | Interconnection |  |  | 100000 | 100 | 100000 | 1
GEN-2024-336 | 05 SOUTHWEST | 171844 | ERIS | Ink Basin 230 kV Substation GEN-2024-336 Interconnection (TOIF) (SPS) | Interconnection |  |  | 3955290.56 | 100 | 3955290.56 | 1
GEN-2024-336 | 05 SOUTHWEST | 171845 | ERIS | Ink Basin 230 kV Substation GEN-2024-336 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 6052126.09 | 100 | 6052126.09 | 1
GEN-2024-337 | 04 SOUTHEAST | 171846 | ERIS | Sunnyside - Pooleville 138 kV line GEN-2024-337 Interconnection (TOIF) (OGE) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-337 | 04 SOUTHEAST | 171847 | ERIS | Sunnyside - Pooleville 138 kV line GEN-2024-337 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 7000000 | 100 | 7000000 | 1
GEN-2024-338 | 04 SOUTHEAST | 171848 | ERIS | Pittsburg - Johnston County 345 kV line GEN-2024-338 Interconnection (TOIF) (AEP) | Interconnection |  |  | 5225000 | 100 | 5225000 | 1
GEN-2024-338 | 04 SOUTHEAST | 171849 | ERIS | Pittsburg - Johnston County 345 kV line GEN-2024-338 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 28225000 | 100 | 28225000 | 1
GEN-2024-339 | 03 CENTRAL | 171949 | ERIS | Stranger Creek 115 kV Substation GEN-2024-339 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1040242 | 100 | 1040242 | 1
GEN-2024-339 | 03 CENTRAL | 171950 | ERIS | Stranger Creek 115 kV Substation GEN-2024-339 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 1289137 | 100 | 1289137 | 1
GEN-2024-340 | 04 SOUTHEAST | 171850 | ERIS | Riverside – Redbud 345 kV line GEN-2024-340 Interconnection (TOIF) (AEP) | Interconnection |  |  | 5225000 | 100 | 5225000 | 1
GEN-2024-340 | 04 SOUTHEAST | 171851 | ERIS | Riverside – Redbud 345 kV line GEN-2024-340 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 28225000 | 100 | 28225000 | 1
GEN-2024-341 | 04 SOUTHEAST | 171852 | ERIS | Pittsburgh 345 kV Substation GEN-2024-341 Interconnection (TOIF) (AEP) | Interconnection |  |  | 5225000 | 100 | 5225000 | 1
GEN-2024-341 | 04 SOUTHEAST | 171853 | ERIS | Pittsburgh 345 kV Substation GEN-2024-341 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 9250000 | 100 | 9250000 | 1
GEN-2024-343 | 04 SOUTHEAST | 171854 | ERIS | LeBrock 345 kV Substation GEN-2024-343 Interconnection (TOIF) (AEP) | Interconnection |  |  | 9700000 | 100 | 9700000 | 1
GEN-2024-343 | 04 SOUTHEAST | 171855 | ERIS | LeBrock 345 kV Substation GEN-2024-343 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 59500000 | 100 | 59500000 | 1
GEN-2024-344 | 04 SOUTHEAST | 171856 | ERIS | Riverside - Redbud Switch 345 kV Line GEN-2024-344 Interconnection (TOIF) (AEP) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-344 | 04 SOUTHEAST | 171857 | ERIS | Riverside - Redbud Switch 345 kV Line GEN-2024-344 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 500000 | 100 | 500000 | 1
GEN-2024-344 | 04 SOUTHEAST | 171858 | ERIS | Riverside - Redbud Switch 345 kV Line GEN-2024-344 Interconnection (TOIF) (OGE) | Interconnection |  |  | 3000000 | 100 | 3000000 | 1
GEN-2024-344 | 04 SOUTHEAST | 171859 | ERIS | Riverside - Redbud Switch 345 kV Line GEN-2024-344 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 18000000 | 100 | 18000000 | 1
GEN-2024-345 | 04 SOUTHEAST | 171861 | ERIS | Delaware 345 kV Substation GEN-2024-345 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 3900000 | 100 | 3900000 | 1
GEN-2024-345 | 04 SOUTHEAST | 171860 | ERIS | Delaware 345 kV Substation GEN-2024-345 Interconnection (TOIF) (AEP) | Interconnection |  |  | 5225000 | 100 | 5225000 | 1
GEN-2024-346 | 04 SOUTHEAST | 171862 | ERIS | Coffeyville Tap - North Barlettsville 138 kV Line GEN-2024-346 Interconnection (TOIF) (AEP) | Interconnection |  |  | 3325000 | 100 | 3325000 | 1
GEN-2024-346 | 04 SOUTHEAST | 171863 | ERIS | Coffeyville Tap - North Barlettsville 138 kV Line GEN-2024-346 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 17175000 | 100 | 17175000 | 1
GEN-2024-351 | 05 SOUTHWEST | 171864 | ERIS | Cooper Ranch 115 kV Substation GEN-2024-351 Interconnection (TOIF) (SPS) | Interconnection |  |  | 2804642.69 | 100 | 2804642.69 | 1
GEN-2024-351 | 05 SOUTHWEST | 171865 | ERIS | Cooper Ranch 115 kV Substation GEN-2024-351 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 17105898.86 | 100 | 17105898.86 | 1
GEN-2024-352 | 03 CENTRAL | 171951 | ERIS | Sibley 345 kV Substation GEN-2024-352 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1958092 | 100 | 1958092 | 1
GEN-2024-352 | 03 CENTRAL | 171952 | ERIS | Sibley 345 kV Substation GEN-2024-352 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 42429444 | 100 | 42429444 | 1
GEN-2024-355 | 05 SOUTHWEST | 171866 | ERIS | Lubbock South 230 kV Substation GEN-2024-355 Interconnection (TOIF) (SPS) | Interconnection |  |  | 2653967 | 100 | 2653967 | 1
GEN-2024-355 | 05 SOUTHWEST | 171867 | ERIS | Lubbock South 230 kV Substation GEN-2024-355 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 16784151 | 100 | 16784151 | 1
GEN-2024-359 | 01 NORTH | 171868 | ERIS | Belfield 345 kV Substation GEN-2024-359 Interconnection (TOIF) (WAPA) | Interconnection |  |  | 709995 | 100 | 709995 | 1
GEN-2024-359 | 01 NORTH | 171869 | ERIS | Belfield 345 kV Substation GEN-2024-359 Interconnection (Non-Shared NU) (WAPA) | Interconnection |  |  | 3640000 | 100 | 3640000 | 1
GEN-2024-360 | 04 SOUTHEAST | 171870 | ERIS | Seminole - Maud 138 kV Line GEN-2024-360 Interconnection (TOIF) (OGE) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-360 | 04 SOUTHEAST | 171871 | ERIS | Seminole - Maud 138 kV Line GEN-2024-360 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 3000000 | 100 | 3000000 | 1
GEN-2024-361 | 04 SOUTHEAST | 171872 | ERIS | Spring Valley - Warwick 138 kV line GEN-2024-361 Interconnection (TOIF) (OGE) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-361 | 04 SOUTHEAST | 171873 | ERIS | Spring Valley - Warwick 138 kV line GEN-2024-361 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 7000000 | 100 | 7000000 | 1
GEN-2024-362 | 04 SOUTHEAST | 171875 | ERIS | Leonard 138 kV Substation GEN-2024-362 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 2800000 | 100 | 2800000 | 1
GEN-2024-362 | 04 SOUTHEAST | 171874 | ERIS | Leonard 138 kV SubstationGEN-2024-362 Interconnection (TOIF) (AEP) | Interconnection |  |  | 3525000 | 100 | 3525000 | 1
GEN-2024-364 | 05 SOUTHWEST | 171877 | ERIS | Bushland 230 kV Substation GEN-2024-364 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 1716577.16 | 100 | 1716577.16 | 1
GEN-2024-364 | 05 SOUTHWEST | 171876 | ERIS | Bushland 230 kV Substation GEN-2024-364 Interconnection (TOIF) (SPS) | Interconnection |  |  | 3852000.39 | 100 | 3852000.39 | 1
GEN-2024-365 | 05 SOUTHWEST | 171878 | ERIS | Hobbs - Yoakum 345 kV Line GEN-2024-365 Interconnection (TOIF) (SPS) | Interconnection |  |  | 4701870.35 | 100 | 4701870.35 | 1
GEN-2024-365 | 05 SOUTHWEST | 171881 | ERIS | Hobbs - Yoakum 345 kV Line GEN-2024-365/366 Interconnection (Shared NU) (SPS) | Interconnection |  |  | 13895283.3 | 50 | 27790566.6 | 1
GEN-2024-365 | 05 SOUTHWEST | 171879 | ERIS | Hobbs - Yoakum 345 kV Line GEN-2024-365 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 27790566.6 | 100 | 27790566.6 | 1
GEN-2024-366 | 05 SOUTHWEST | 171880 | ERIS | Hobbs - Yoakum 345 kV Line GEN-2024-366 Interconnection (TOIF) (SPS) | Interconnection |  |  | 4701870.35 | 100 | 4701870.35 | 1
GEN-2024-366 | 05 SOUTHWEST | 171881 | ERIS | Hobbs - Yoakum 345 kV Line GEN-2024-365/366 Interconnection (Shared NU) (SPS) | Interconnection |  |  | 13895283.3 | 50 | 27790566.6 | 1
GEN-2024-367 | 04 SOUTHEAST | 171882 | ERIS | Lawton East Side 345 kV Substation GEN-2024-367 Interconnection (TOIF) (AEP) | Interconnection |  |  | 5225000 | 100 | 5225000 | 1
GEN-2024-367 | 04 SOUTHEAST | 171883 | ERIS | Lawton East Side 345 kV Substation GEN-2024-367 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 20900000 | 100 | 20900000 | 1
GEN-2024-368 | 05 SOUTHWEST | 171884 | ERIS | Bowers 115 kV Substation GEN-2024-368 Interconnection (TOIF) (SPS) | Interconnection |  |  | 2944531.47 | 100 | 2944531.47 | 1
GEN-2024-368 | 05 SOUTHWEST | 171885 | ERIS | Bowers 115 kV Substation GEN-2024-368 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 3298358.56 | 100 | 3298358.56 | 1
GEN-2024-369 | 04 SOUTHEAST | 171887 | ERIS | Cornville 138 kV Substation GEN-2024-369 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 2800000 | 100 | 2800000 | 1
GEN-2024-369 | 04 SOUTHEAST | 171886 | ERIS | Cornville 138 kV Substation GEN-2024-369 Interconnection (TOIF) (AEP) | Interconnection |  |  | 3525000 | 100 | 3525000 | 1
GEN-2024-370 | 03 CENTRAL | 171953 | ERIS | Smithville 161 kV Substation GEN-2024-370 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1061551 | 100 | 1061551 | 1
GEN-2024-370 | 03 CENTRAL | 171954 | ERIS | Smithville 161 kV Substation GEN-2024-370 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 3659394 | 100 | 3659394 | 1
GEN-2024-371 | 05 SOUTHWEST | 171888 | ERIS | Maddox 115 kV Substation GEN-2024-371 Interconnection (TOIF) (SPS) | Interconnection |  |  | 3539457.82 | 100 | 3539457.82 | 1
GEN-2024-371 | 05 SOUTHWEST | 171889 | ERIS | Maddox 115 kV Substation GEN-2024-371 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 44215863.76 | 100 | 44215863.76 | 1
GEN-2024-372 | 02 NEBRASKA | 171890 | ERIS | S1252 161 kV Substation GEN-2024-372 Interconnection (TOIF) (OPPD) | Interconnection |  |  | 476039 | 100 | 476039 | 1
GEN-2024-372 | 02 NEBRASKA | 171891 | ERIS | S1252 161 kV Substation GEN-2024-372 Interconnection (Non-Shared NU) (OPPD) | Interconnection |  |  | 1500000 | 100 | 1500000 | 1
GEN-2024-373 | 04 SOUTHEAST | 171892 | ERIS | Unger - West Bank Tap 138 kV Line GEN-2024-373 Interconnection (TOIF) (WFEC) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-373 | 04 SOUTHEAST | 171893 | ERIS | Unger - West Bank Tap 138 kV Line GEN-2024-052/373 Interconnection (Shared NU) (WFEC) | Interconnection |  |  | 0 |  | 0 | 1
GEN-2024-373 | 04 SOUTHEAST | 171892 | ERIS | Unger - West Bank Tap 138 kV Line GEN-2024-373 Interconnection (TOIF) (WFEC) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-373 | 04 SOUTHEAST | 171893 | ERIS | Unger - West Bank Tap 138 kV Line GEN-2024-052/373 Interconnection (Shared NU) (WFEC) | Interconnection |  |  | 5185185.1852 | 74.0741 | 7000000 | 1
GEN-2024-374 | 02 NEBRASKA | 171894 | ERIS | Stegall 345 kV Substation GEN-2024-374 Interconnection (TOIF) (BEPC) | Interconnection |  |  | 2834775 | 100 | 2834775 | 1
GEN-2024-374 | 02 NEBRASKA | 171895 | ERIS | Stegall 345 kV Substation GEN-2024-374 Interconnection (Non-Shared NU) (BEPC) | Interconnection |  |  | 7125379 | 100 | 7125379 | 1
GEN-2024-375 | 03 CENTRAL | 171955 | ERIS | West Southwest 161 kV Substation GEN-2024-375 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1495125 | 100 | 1495125 | 1
GEN-2024-375 | 03 CENTRAL | 171956 | ERIS | West Southwest 161 kV Substation GEN-2024-375 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 15638683 | 100 | 15638683 | 1
GEN-2024-376 | 04 SOUTHEAST | 171896 | ERIS | Hemphill 138 kV Substation GEN-2024-376 Interconnection (TOIF) (ETEC) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-376 | 04 SOUTHEAST | 171897 | ERIS | Hemphill 138 kV Substation GEN-2024-376 Interconnection (Non-Shared NU) (ETEC) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-377 | 04 SOUTHEAST | 171898 | ERIS | Pirkey 345 kV Substation GEN-2024-377 Interconnection (TOIF) (AEP) | Interconnection |  |  | 5225000 | 100 | 5225000 | 1
GEN-2024-377 | 04 SOUTHEAST | 171899 | ERIS | Pirkey 345 kV Substation GEN-2024-377 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 12750000 | 100 | 12750000 | 1
GEN-2024-379 | 04 SOUTHEAST | 171900 | ERIS | Longwood - El Dorado 345 kV Line GEN-2024-379 Interconnection (TOIF) (AEP) | Interconnection |  |  | 5225000 | 100 | 5225000 | 1
GEN-2024-379 | 04 SOUTHEAST | 171901 | ERIS | Longwood - El Dorado 345 kV Line GEN-2024-379 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 28225000 | 100 | 28225000 | 1
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild the 3COUCH% to 3LEWISVILLE# 115kV Line 1 | JTIQ Expanded Scope Analysis | 9.07 | (239,239) | 5442000 | 60 | 9070000 | 0.06137
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild the 3COUCH% to 3LEWISVILLE# 115kV Line 1 | JTIQ Expanded Scope Analysis | 9.07 | (239,239) | 3628000 | 40 | 9070000 | 0.06137
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild the 3COUCH% to 3MCNEIL! 115kV Line 1 | JTIQ Expanded Scope Analysis | 14.43 | (239,239) | 8658000 | 60 | 14430000 | 0.08298
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild the 3COUCH% to 3MCNEIL! 115kV Line 1 | JTIQ Expanded Scope Analysis | 14.43 | (239,239) | 5772000 | 40 | 14430000 | 0.08298
GEN-2024-226 | 04 SOUTHEAST | TBD | ERIS | Rebuild the 3LEWISVILLE# to 3PATMOS.W# 115kV Line 1 | JTIQ Expanded Scope Analysis | 10.38 | (239,239) | 6228000 | 60 | 10380000 | 0.06137
GEN-2024-227 | 04 SOUTHEAST | TBD | ERIS | Rebuild the 3LEWISVILLE# to 3PATMOS.W# 115kV Line 1 | JTIQ Expanded Scope Analysis | 10.38 | (239,239) | 4152000 | 40 | 10380000 | 0.06137
GEN-2024-379 | 04 SOUTHEAST | TBD | ERIS | Rebuild the 3MINDEN_LA! to 3SAREPTA! 115kV Line 1 | JTIQ Expanded Scope Analysis | 21.84 | (239,239) | 21840000 | 100 | 21840000 | 0.03164
GEN-2024-114 | 04 SOUTHEAST | TBD | ERIS | Rebuild the 5EVERTON RD to 5ST JOE 161kV Line 1 | JTIQ Expanded Scope Analysis | 13.58 | (557,557) | 20370000 | 100 | 20370000 | 0.03806
GEN-2024-114 | 04 SOUTHEAST | TBD | ERIS | Rebuild the 5HARRISON.E! to 5EVERTON RD 161kV Line 1 | JTIQ Expanded Scope Analysis | 8.3 | (557,557) | 12450000 | 100 | 12450000 | 0.03806
GEN-2024-114 | 04 SOUTHEAST | TBD | ERIS | Rebuild the 5JONESBORO! to 5JONSBORO.N# 161kV Line 1 | JTIQ Expanded Scope Analysis | 7.05 | (557,557) | 10575000 | 100 | 10575000 | 0.14516
GEN-2024-114 | 04 SOUTHEAST | TBD | ERIS | Rebuild the 5JONSBORO.N# to 5PARGOULD.S# 161kV Line 1 | JTIQ Expanded Scope Analysis | 6.22 | (557,557) | 9330000 | 100 | 9330000 | 0.14516
GEN-2024-114 | 04 SOUTHEAST | TBD | ERIS | Rebuild the 5PARAGOULD% to 5PARGOULD.S# 161kV Line 1 | JTIQ Expanded Scope Analysis | 7.67 | (557,557) | 11505000 | 100 | 11505000 | 0.14516
GEN-2024-114 | 04 SOUTHEAST | TBD | ERIS | Rebuild the 5ST JOE to 5HILLTOP% 161kV Line 1 | JTIQ Expanded Scope Analysis | 3.9 | (557,557) | 5850000 | 100 | 5850000 | 0.03806
GEN-2024-327 | 01 NORTH | TBD | ERIS | Rebuild the SOURIS 7 to MALLARD7 115kV Line 1 | JTIQ Expanded Scope Analysis | 5.3 | (239,239) | 5300000 | 100 | 5300000 | 0.12295

## Upgrade Summary
Upgrade Type | Study Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade length (miles) | Upgrade Rating (MVA) | Transmission Owner(s) | Estimated Lead Time | Total Upgrade Cost
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2 | TBD | 314.6 | (5300.00, 5300.00) | AEPW/OKGE |  | 1514620000
Current Study | Steady State | 05 SOUTHWEST / 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add line 526001 CRWFSHDRW9 765 514812 MINCO 9 765 1 | TBD | 262.9 | (5300.00, 5300.00) | OKGE/SPS |  | 1285130000
Current Study | Steady State | 04 SOUTHEAST / 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2 | TBD | 262.9 | (5300.00, 5300.00) | OKGE/SPS |  | 1271630000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add line 528014 PHANTOM 9 765 526001 CRDRW9 765 2 | TBD | 220.8 | (5300.00, 5300.00) | SPS |  | 1073760000
Current Study | Steady State | 03 CENTRAL / 01 NORTH | DISIS-2024-001 | ERIS | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2 | TBD | 300 | (1792.00, 1792.00) | SUNC/WAPA |  | 940000000
Current Study | Steady State | 04 SOUTHEAST / 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add line 515378 WWARD9 765 523966 POTTER_CO 9 765 1 | TBD | 192 | (5300.00, 5300.00) | OKGE/SPS |  | 938400000
Current Study | Steady State | 04 SOUTHEAST / 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2 | TBD | 192 | (5300.00, 5300.00) | OKGE/SPS |  | 938400000
Current Study | Steady State | 04 SOUTHEAST / 03 CENTRAL | DISIS-2024-001 | ERIS | Add line 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TBD | 140.8 | (5300.00, 5300.00) | OKGE/WERE |  | 724760000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Add line 659131 LARAMIE_-MB3 345 800120 UNDERWOOD 2 345 P2 | TBD | 206.4 | (1792.00, 1792.00) | WAPA |  | 649840000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Add line 652424 BELFELD3 345 800121 MAURINE 2 345 P2 | TBD | 154.2 | (1792.00, 1792.00) | WAPA |  | 488020000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add line 515049 SEMINOLE9 765 514812 MINCO 9 765 1 | TBD | 92.2 | (5300.00, 5300.00) | OKGE |  | 482840000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2 | TBD | 92.2 | (5300.00, 5300.00) | OKGE |  | 469340000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2 | TBD | 115 | (1195.00, 1195.00) | SPS |  | 366500000
Current Study | Steady State | 02 NEBRASKA / 03 CENTRAL | DISIS-2024-001 | ERIS | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2 | TBD | 67.2 | (1792.00, 1792.00) | NPPD/SUNC |  | 218320000
Current Study | Steady State | 04 SOUTHEAST / 03 CENTRAL | DISIS-2024-001 | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2 | TBD | 60.81 | (2010.00, 2010.00) | OKGE/SUNC |  | 198511000
Current Study | Steady State | 04 SOUTHEAST / 03 CENTRAL | DISIS-2024-001 | ERIS | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 YY | TBD | 60.81 | (2010.00, 2010.00) | OKGE/SUNC |  | 198511000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2 | TBD | 60.6 | (956.00, 956.00) | SPS |  | 197860000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 523097 HITCHLAND 7 345 784950 G24-266_TAP 345 1 | TBD | 84.86 | (1793.00, 1793.00) | SPS |  | 186692000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TBD | 75.83 | (1793.00, 1793.00) | NPPD |  | 166826000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2 | TBD | 50.02 | (1098.00, 1098.00) | SPS |  | 165062000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 521157 HUGO 7 345 560088 BISON 7 345 1 | TBD | 74.88 | (1793.00, 1793.00) | OKGE/WFEC |  | 164736000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 640404 WAYSIDE 4 230 652484 NUNDRWD4 230 1 | TBD | 80.12 | (519.00, 519.00) | WAPA |  | 152228000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2 | TBD | 45.24 | (0.00, 0.00) | WERE |  | 150244000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2 | TBD | 43.16 | (1310.00, 1570.00) | WERE |  | 143796000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Add line 652424 BELFELD3 345 659183 CHARL_CK-BE3 345 P2 | TBD | 40.74 | (531.00, 531.00) | WAPA |  | 136294000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 652403 DAWSONC4 230 652411 MI CTYE4 230 1 | TBD | 70.4 | (386.00, 386.00) | WAPA |  | 133760000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2 | TBD | 39.66 | (1195.10, 1481.90) | SUNC |  | 132946000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2 | TBD | 37.04 | (830.00, 830.00) | WERE |  | 124824000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1 | TBD | 56.1 | (1793.00, 1793.00) | AEPW |  | 123420000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TBD | 53.31 | (2390.00, 2390.00) | KCPL/WERE |  | 117282000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | TBD | 51.27 | (1793.00, 1793.00) | AEPW/OKGE |  | 112794000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1 | TBD | 59.17 | (637.00, 637.00) | SPS |  | 112423000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add line 523869 CHAN+TASCOS6 230 523959 POTTER_CO 6 230 P2 | TBD | 41.65 | (496.00, 546.00) | SPS |  | 111325000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 532768 EMPEC 7 345 532803 BURNS 7 345 1 | TBD | 50.03 | (1793.00, 1793.00) | WERE |  | 110066000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3 | TBD | 39.39 | (478.00, 544.00) | SPS |  | 105675000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | TBD | 54.58 | (637.00, 637.00) | SPS |  | 103702000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2 | TBD | 29.17 | (1713.00, 1792.00) | KCPL |  | 100427000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 532796 WICHITA7 345 532803 BURNS 7 345 1 | TBD | 45.5 | (1793.00, 1793.00) | WERE |  | 100100000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1 | TBD | 52.45 | (1046.00, 1046.00) | SPS |  | 99655000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Rebuild line 645456 S3456 3 345 645458 S3458 3 345 1 | TBD | 44.95 | (1793.00, 1793.00) | OPPD |  | 98890000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | TBD | 44.59 | (1793.00, 1793.00) | AEPW/OKGE |  | 98098000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 652529 WATERTN3 345 659165 CROCKER_-BE3 345 1 | TBD | 44.23 | (1793.00, 1793.00) | WAPA |  | 97306000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TBD | 43.4 | (1793.00, 1793.00) | KCPL/WERE |  | 95480000
Current Study | Steady State | 03 CENTRAL / 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | TBD | 42.72 | (1793.00, 1793.00) | AEPW/WERE |  | 93984000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 524885 SN_JUAN_SS 6 230 785100 G24-271-TAP 230 1 | TBD | 49.09 | (637.00, 637.00) | SPS |  | 93271000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TBD | 40.88 | (2390.00, 2390.00) | KCPL |  | 89936000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Rebuild line 652424 BELFELD3 345 659183 CHARL_CK-BE3 345 1 | TBD | 40.74 | (1793.00, 1793.00) | WAPA |  | 89628000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add line 523221 XIT_INTG 6 230 523869 CHAN+TASCOS6 230 P2 | TBD | 32.28 | (495.00, 545.00) | SPS |  | 87900000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | TBD | 38.5 | (1793.00, 1793.00) | WERE |  | 84700000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 2-winding transformer 532798 VIOLA 7 345 532828 VIOLA9 765 M2 | TBD |  | (2300.00, 2300.00) | WERE |  | 84500000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 2-winding transformer 532828 VIOLA9 765 532798 VIOLA 7 345 1 | TBD |  | (1650.00, 1650.00) | WERE |  | 84500000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 2-winding transformer 514812 MINCO 9 765 514801 MINCO 7 345 1 | TBD |  | (1650.00, 1650.00) | OKGE |  | 84500000
Current Study | Steady State | 02 NEBRASKA / 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TBD | 38.26 | (1793.00, 1793.00) | NPPD/SUNC |  | 84172000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TBD | 37.4 | (1793.00, 1793.00) | SUNC |  | 82280000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | TBD | 37.04 | (1793.00, 1793.00) | WERE |  | 81488000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | TBD | 36.8 | (1793.00, 1793.00) | WAPA |  | 80960000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 532913 KELLY 5 161 532920 TECHILL5 161 1 | TBD | 52.64 | (160.00, 160.00) | WERE |  | 78960000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1 | TBD | 40.93 | (519.00, 519.00) | WAPA |  | 77767000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 530582 S HAYS6 230 539679 GRTBEND6 230 1 | TBD | 39.2 | (386.00, 386.00) | MIDW/SUNC |  | 74480000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 652497 MAURINE4 230 659351 BISON___-GE4 230 1 | TBD | 38.56 | (386.00, 386.00) | WAPA |  | 73264000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 523095 HITCHLAND 6 230 778320 G24-045-TAP 230 1 | TBD | 37.8 | (772.00, 772.00) | SPS |  | 71820000
Current Study | Steady State | OTHER / 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 338110 5HILLTOP% 161 505507 SWPINEY5 161 1 | TBD | 47.56 | (246.00, 246.00) | EES-EAI/SWPA |  | 71340000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Rebuild line 652497 MAURINE4 230 785430 G24-282-TAP 230 1 | TBD | 36.92 | (637.00, 637.00) | WAPA |  | 70148000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1 | TBD | 30.63 | (1793.00, 1793.00) | AEPW |  | 67386000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 | TBD | 30.44 | (1793.00, 1793.00) | WERE |  | 66968000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 652884 NUNDRWD-LNX3 230 785430 G24-282-TAP 230 1 | TBD | 35.21 | (519.00, 519.00) | WAPA |  | 66899000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 525481 PLANT_X 6 230 525520 OLSON 6 230 1 | TBD | 34.94 | (519.00, 519.00) | SPS |  | 66386000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | TBD | 30 | (1793.00, 1793.00) | WERE |  | 66000000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Rebuild line 652216 WATFORD4 230 659302 CHARL_CK-BE4 230 1 | TBD | 34.26 | (637.00, 637.00) | WAPA |  | 65094000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 516210 RAVEN 7 345 785850 G24-296-TAP 345 1 | TBD | 28.75 | (1793.00, 1793.00) | OKGE |  | 63250000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 1 | TBD |  | (1868.00, 1868.00) | OKGE |  | 61500000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild 2-winding transformer 515045 SEMINOL7 345 515049 SEMINOLE9 765 2 | TBD |  | (1868.00, 1868.00) | OKGE |  | 61500000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 652403 DAWSONC4 230 652616 MINGUSVILLE4 230 1 | TBD | 30.68 | (386.00, 386.00) | WAPA |  | 58292000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 514909 REDBUD 7 345 787290 G24-344-TAP 345 1 | TBD | 26.49 | (1793.00, 1793.00) | OKGE |  | 58278000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | TBD | 26.47 | (1793.00, 1793.00) | NPPD |  | 58234000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TBD | 25.29 | (2390.00, 2390.00) | WERE |  | 55638000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 525832 TUCO_INT 7 345 526000 CRWFSHDRW7 345 2 | TBD | 25.1 | (2390.00, 2390.00) | SPS |  | 55220000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TBD | 25.07 | (1793.00, 1793.00) | WERE |  | 55154000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1 | TBD | 24.3 | (1793.00, 1793.00) | WERE |  | 53460000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 652404 DAWSONC7 115 661056 LEWIS 7 115 1 | TBD | 51.58 | (176.00, 176.00) | WAPA |  | 51580000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 524875 OASIS 6 230 787680 G24-357-TAP 230 1 | TBD | 26.02 | (901.00, 901.00) | SPS |  | 49438000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 526460 AMOCO_SS 6 230 777420 G24-015-TAP 230 1 | TBD | 25.97 | (519.00, 519.00) | SPS |  | 49343000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 523309 MOORE_CNTY 6 230 778320 G24-045-TAP 230 1 | TBD | 24.89 | (772.00, 772.00) | SPS |  | 47291000
Current Study | Steady State | 05 SOUTHWEST / 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 523106 TXPHSF 3 115 539672 E-LIBER3 115 1 | TBD | 47.28 | (260.00, 260.00) | SPS/SUNC |  | 47280000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TBD | 21.36 | (1793.00, 1793.00) | AEPW/GRDA |  | 46992000
Current Study | Steady State | OTHER / 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | TBD | 21.32 | (1793.00, 1793.00) | AEPW/EES |  | 46904000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TBD | 21.05 | (1793.00, 1793.00) | SUNC |  | 46310000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 659265 LITTL_MS-BE4 230 659266 RHAME___-BE4 230 1 | TBD | 24.19 | (519.00, 519.00) | WAPA |  | 45961000
Current Study | Steady State | 04 SOUTHEAST / 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TBD | 20.87 | (1793.00, 1793.00) | OKGE/WERE |  | 45914000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 527799 EDDY_NORTH 6 230 528095 7-RIVERS 6 230 1 | TBD | 24.1 | (386.00, 386.00) | SPS |  | 45790000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 512110 LAKEP4WT 138 521043 RUSSELL4 138 1 | TBD | 37.45 | (134.00, 134.00) | AEPW/WFEC |  | 44940000
Current Study | Steady State | 02 NEBRASKA / 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | TBD | 23.61 | (386.00, 386.00) | NPPD/WAPA |  | 44859000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 514715 WOODRNG7 345 515476 HUNTERS7 345 1 | TBD | 20.38 | (1793.00, 1793.00) | OKGE |  | 44836000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 527597 TWEEDY 3 115 527798 EDDY_NTH 3 115 1 | TBD | 44.83 | (394.00, 394.00) | SPS |  | 44830000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1 | TBD | 20.15 | (1793.00, 1793.00) | OPPD |  | 44330000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 505600 TUPELO 4 138 505602 S BROWN4 138 1 | TBD | 36.9 | (281.00, 281.00) | SWPA |  | 44280000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | TBD | 19.87 | (1793.00, 1793.00) | LES/NPPD |  | 43714000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 532791 BENTON 7 345 532796 WICHITA7 345 1 | TBD | 19.76 | (1793.00, 1793.00) | WERE |  | 43472000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 652425 BELFELD4 230 659247 MEDORA__-UM4 230 1 | TBD | 22.59 | (519.00, 519.00) | WAPA |  | 42921000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 652568 GROTONSOUTH7 115 655481 REDFELD-ER7 115 1 | TBD | 42.57 | (176.00, 176.00) | WAPA |  | 42570000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TBD | 19.2 | (2390.00, 2390.00) | SUNC |  | 42240000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 512101 CHILD4WT 138 512110 LAKEP4WT 138 1 | TBD | 35.14 | (134.00, 134.00) | AEPW |  | 42168000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508809 LONGWD 7 345 788340 G24-379-TAP 345 1 | TBD | 19.1 | (1793.00, 1793.00) | AEPW |  | 42020000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 532871 CIRCLE 6 230 532872 EMCPHER6 230 1 | TBD | 21.74 | (386.00, 386.00) | WERE |  | 41306000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add line 532871 CIRCLE 6 230 783810 G24-228-TAP 230 P2 | TBD | 13.42 | (328.00, 398.00) | WERE |  | 40750000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 520848 CDRDLTP4 138 521016 OKEENE 4 138 1 | TBD | 33.95 | (211.00, 211.00) | WFEC |  | 40740000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 659070 W.BANK.S-BE3 345 779400 G24-081-TAP 345 1 | TBD | 18.38 | (1793.00, 1793.00) | WAPA |  | 40436000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 523961 POTTER_CO 7 345 784950 G24-266_TAP 345 1 | TBD | 18.24 | (1793.00, 1793.00) | SPS |  | 40128000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508359 WELSH 7 345 776060 G23-204-TAP 345 1 | TBD | 17.82 | (1793.00, 1793.00) | AEPW |  | 39204000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 528095 7-RIVERS 6 230 528179 PECOS 6 230 1 | TBD | 20.61 | (386.00, 386.00) | SPS |  | 39159000
Current Study | Steady State | OTHER / 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | TBD | 17.54 | (1793.00, 1793.00) | MEC/NPPD |  | 38588000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 524885 SN_JUAN_SS 6 230 787680 G24-357-TAP 230 1 | TBD | 20.18 | (901.00, 901.00) | SPS |  | 38342000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | TBD | 16.71 | (1793.00, 1793.00) | LES/NPPD |  | 36762000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 541207 ARCHIE 5 161 785640 G24-289-TAP 161 1 | TBD | 24.2 | (364.00, 364.00) | KCPL |  | 36300000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1 | TBD | 18.95 | (901.00, 901.00) | SPS |  | 36005000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | TBD | 18.75 | (519.00, 519.00) | AEPW |  | 35625000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TBD | 16.04 | (2390.00, 2390.00) | SUNC |  | 35288000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | TBD | 15.27 | (1793.00, 1793.00) | AEPW |  | 33594000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | TBD | 32.97 | (217.00, 217.00) | WAPA |  | 32970000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 520882 DOVERSW4 138 521016 OKEENE 4 138 1 | TBD | 27.24 | (211.00, 211.00) | WFEC |  | 32688000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 511409 TREASILD7 345 764550 G20-087-TAP 345 1 | TBD | 14.38 | (1793.00, 1793.00) | AEPW |  | 31636000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 652515 HURON 7 115 655481 REDFELD-ER7 115 1 | TBD | 30.85 | (176.00, 176.00) | WAPA |  | 30850000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 652522 SUMMIT-7 115 652531 WATERTN7 115 1 | TBD | 30.78 | (176.00, 176.00) | WAPA |  | 30780000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 539663 GLENELD3 115 539693 SMITH-C3 115 1 | TBD | 30.72 | (176.00, 176.00) | SUNC |  | 30720000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 539642 ELLSWTP3 115 539678 GRTBEND3 115 1 | TBD | 30.21 | (115.00, 115.00) | SUNC |  | 30210000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TBD | 13.6 | (1793.00, 1793.00) | AEPW |  | 29920000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 645458 S3458 3 345 778170 G24-040-TAP 345 1 | TBD | 13.15 | (1793.00, 1793.00) | OPPD |  | 28930000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 511458 ELKCTY-4 138 511485 CLINTJC4 138 1 | TBD | 24.08 | (211.00, 211.00) | AEPW |  | 28896000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TBD | 13 | (2390.00, 2390.00) | SUNC |  | 28600000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 547473 RDS295 5 161 779490 G24-084-TAP 161 1 | TBD | 18.76 | (246.00, 246.00) | EMDE |  | 28140000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 532856 SWISVAL6 230 785250 G24-276-TAP 230 1 | TBD | 14.81 | (386.00, 386.00) | WERE |  | 28139000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Rebuild line 640100 CAMBRIG7 115 640269 MCCOOK 7 115 1 | TBD | 28.11 | (176.00, 176.00) | NPPD |  | 28110000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 640139 COOPER 3 345 778170 G24-040-TAP 345 1 | TBD | 12.59 | (1793.00, 1793.00) | NPPD/OPPD |  | 27698000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 533008 TV1MNDV4 138 533020 NEOSHOS4 138 1 | TBD | 22.77 | (265.00, 265.00) | WERE |  | 27324000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | TBD | 27.23 | (297.00, 297.00) | SUNC |  | 27230000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add line 505418 JONESBO5 161 774620 G23-132-TAP 161 P2 | TBD | 9.8 | (237.00, 237.00) | SWPA |  | 26780000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | TBD | 17.69 | (160.00, 160.00) | LES/OPPD |  | 26535000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 530618 HUNTSVL3 115 530624 ST JOHN3 115 1 | TBD | 26.5 | (297.00, 297.00) | MIDW |  | 26500000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild 2-winding transformer and add 2-winding transformer 528013 PHANTOM 3 115 528015 PHANTOM 7 345 4 | TBD |  | (522.00, 522.00) | SPS |  | 26500000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | TBD | 13.92 | (519.00, 519.00) | SPS |  | 26448000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | TBD | 12 | (1793.00, 1793.00) | WERE |  | 26400000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | TBD | 11.9 | (1793.00, 1793.00) | KCPL |  | 26180000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 533001 ALTOONA4 138 533006 TAYLOR 4 138 1 | TBD | 21.66 | (265.00, 265.00) | WERE |  | 25992000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 515044 SEMINOL4 138 515531 VANOSTP4 138 1 | TBD | 21.55 | (395.00, 395.00) | OKGE |  | 25860000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 652512 GROTON 7 115 660001 ABR SIEBRCHT 115 1 | TBD | 25.8 | (260.00, 260.00) | WAPA |  | 25800000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 516091 OKTAHA 7 345 516374 KEEFTON7 345 1 | TBD | 11.67 | (1793.00, 1793.00) | OKGE |  | 25674000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TBD | 11.5 | (1793.00, 1793.00) | KCPL |  | 25300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | TBD | 11.39 | (1793.00, 1793.00) | WERE |  | 25058000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Add 3-winding transformer 652220 BELFELD29 13 652424 BELFELD3 345 652425 BELFELD4 230 M2 | TBD |  | (250.00, 312.00) | WAPA |  | 25000000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Add 3-winding transformer 652221 BELFELD9 13 652424 BELFELD3 345 652425 BELFELD4 230 M2 | TBD |  | (312.00, 390.00) | WAPA |  | 25000000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Add 3-winding transformer 652237 WATERT19 13 652529 WATERTN3 345 652530 WATERTN4 230 M2 | TBD |  | (400.00, 478.00) | WAPA |  | 25000000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Add 3-winding transformer 652305 SIOUXC29 13 652552 SIOUXCY2 230 652564 SIOUXCY3 345 M2 | TBD |  | (600.00, 750.00) | WAPA |  | 25000000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659201 LO.KU1A_-BE9 13 M2 | TBD |  | (600.00, 637.40) | WAPA |  | 25000000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Add 3-winding transformer 659105 LELAND_O-BE3 345 659106 LELAND_O-BE4 230 659202 LO.KVA2_-BE9 13 M2 | TBD |  | (500.00, 617.00) | WAPA |  | 25000000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Add 3-winding transformer 659120 BROADLND-BE3 345 659204 BD.KU2A_-BE9 13 659205 BROADLND-BE4 230 M2 | TBD |  | (471.00, 478.00) | WAPA |  | 25000000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2 | TBD |  | (600.00, 637.00) | WAPA |  | 25000000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 3-winding transformer 523091 HITCHLD_TR01 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2 | TBD |  | (560.00, 644.00) | SPS |  | 25000000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 3-winding transformer 523094 HITCHLD_TR21 13 523095 HITCHLAND 6 230 523097 HITCHLAND 7 345 M2 | TBD |  | (560.00, 644.00) | SPS |  | 25000000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 3-winding transformer 525824 TUCO_TR1 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | TBD |  | (615.00, 699.00) | SPS |  | 25000000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 3-winding transformer 525825 TUCO_TR2 1 13 525830 TUCO_INT 6 230 525832 TUCO_INT 7 345 M2 | TBD |  | (615.00, 637.00) | SPS |  | 25000000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 3-winding transformer 527796 EDDY_TR 1 13 527799 EDDY_NORTH 6 230 527802 EDDY_CNTY 7 345 M2 | TBD |  | (516.00, 558.00) | SPS |  | 25000000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1 | TBD | 11.3 | (1793.00, 1793.00) | OKGE |  | 24860000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 511564 MARTHA 4 138 781800 G24-161-TAP 138 1 | TBD | 20.7 | (395.00, 395.00) | AEPW |  | 24840000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Rebuild line 640194 GOSPER 7 115 640242 JOHN.2 7 115 1 | TBD | 24.13 | (176.00, 176.00) | NPPD |  | 24130000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 511423 FLE TAP4 138 511467 L.E.S.-4 138 1 | TBD | 19.98 | (265.00, 265.00) | AEPW |  | 23976000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 505507 SWPINEY5 161 505508 DARDANE5 161 1 | TBD | 15.98 | (246.00, 246.00) | SWPA |  | 23970000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 505598 ALLEN 4 138 505600 TUPELO 4 138 1 | TBD | 19.4 | (211.00, 211.00) | SWPA |  | 23280000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 539656 CLIFTON3 115 539657 CONCORD3 115 1 | TBD | 23.19 | (176.00, 176.00) | SUNC |  | 23190000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 539650 BELOIT 3 115 539657 CONCORD3 115 1 | TBD | 22.17 | (176.00, 176.00) | SUNC |  | 22170000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild 3-winding transformer and add 3-winding transformer 523265 PRINGLE_TR 1 13 523266 PRINGLE 3 115 523267 PRINGLE 6 230 1 | TBD |  | (312.00, 312.00) | SPS |  | 21900000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild 3-winding transformer and add 3-winding transformer 524263 BSHLND_TR1 1 13 524266 BUSHLAND 3 115 524267 BUSHLAND 6 230 1 | TBD |  | (323.00, 323.00) | SPS |  | 21900000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 515117 ARBUCKL4 138 515531 VANOSTP4 138 1 | TBD | 18.2 | (472.00, 472.00) | OKGE |  | 21840000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | TBD | 21.31 | (217.00, 217.00) | WAPA |  | 21310000
Current Study | Steady State | 04 SOUTHEAST / 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TBD | 17.69 | (265.00, 265.00) | AEPW/OMPA |  | 21228000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | TBD | 11.15 | (519.00, 519.00) | AEPW |  | 21185000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Rebuild line 640326 REDWILO7 115 640365 STOCKVL7 115 1 | TBD | 21.09 | (176.00, 176.00) | NPPD |  | 21090000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 524623 DEAFSMITH 6 230 525520 OLSON 6 230 1 | TBD | 11 | (519.00, 519.00) | SPS |  | 20900000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 539678 GRTBEND3 115 539684 OTISSUB3 115 1 | TBD | 20.83 | (176.00, 176.00) | SUNC |  | 20830000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 512631 MIAMI 5 161 512632 AFTON 5 161 1 | TBD | 13.5 | (309.00, 309.00) | GRDA |  | 20250000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 523266 PRINGLE 3 115 523377 RIVERVIEW 3 115 1 | TBD | 20.25 | (260.00, 260.00) | SPS |  | 20250000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 2 | TBD | 20.02 | (260.00, 260.00) | SPS |  | 20020000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TBD | 9 | (1793.00, 1793.00) | WAPA |  | 19800000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 532996 TIOGA 4 138 533001 ALTOONA4 138 1 | TBD | 16.38 | (134.00, 134.00) | WERE |  | 19656000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 511409 TREASILD7 345 780810 G24-128-TAP 345 1 | TBD | 8.91 | (2390.00, 2390.00) | AEPW/OKGE |  | 19602000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 505592 WELEETK4 138 505595 GREASYC4 138 1 | TBD | 16.28 | (211.00, 211.00) | SWPA |  | 19536000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 512632 AFTON 5 161 512669 KETCHUM5 161 1 | TBD | 12.8 | (309.00, 309.00) | GRDA |  | 19200000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 539649 SAWYER 3 115 539760 BARBER 3 115 1 | TBD | 19 | (598.00, 598.00) | SUNC |  | 19000000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 520826 BENNGTN4 138 520884 DURANTP4 138 1 | TBD | 15.8 | (395.00, 395.00) | WFEC |  | 18960000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 515097 WLNUTCK4 138 515100 PAOLI- 4 138 1 | TBD | 15.55 | (265.00, 265.00) | OKGE |  | 18660000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 150 MVAR switched shunt at VIOLA9 765 kV | TBD |  |  | WERE |  | 18600000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV | TBD |  |  | OKGE |  | 18600000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 150 MVAR switched shunt at MINCO 9 765 kV | TBD |  |  | OKGE |  | 18600000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 375 MVAR switched shunt at WWARD9 765 kV | TBD |  |  | OKGE |  | 18600000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 560 MVAR switched shunt at WWRDEHV9 765 kV | TBD |  |  | OKGE |  | 18600000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 641.25 MVAR switched shunt at WWARD9 765 kV | TBD |  |  | OKGE |  | 18600000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 880 MVAR switched shunt at SWSHRV9 765 kV | TBD |  |  | AEPW |  | 18600000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 960 MVAR switched shunt at MINCO 9 765 kV | TBD |  |  | OKGE |  | 18600000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 225 MVAR switched shunt at POTTER_CO 9 765 kV | TBD |  |  | SPS |  | 18600000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV | TBD |  |  | SPS |  | 18600000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV | TBD |  |  | SPS |  | 18600000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1 | TBD | 8.4 | (1793.00, 1793.00) | OKGE |  | 18480000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 547476 ASB349 5 161 547477 CJ 366 5 161 1 | TBD | 12.3 | (551.00, 551.00) | EMDE |  | 18450000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1 | TBD | 9.6 | (901.00, 901.00) | SPS |  | 18240000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | TBD | 18.19 | (329.00, 329.00) | SUNC |  | 18190000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2 | TBD |  | (505.00, 505.00) | AEPW |  | 18100000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 3-winding transformer 508808 LONGWD 4 138 508809 LONGWD 7 345 508819 LONGW1-1 13 M2 | TBD |  | (580.00, 580.00) | AEPW |  | 18100000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2 | TBD |  | (484.00, 515.00) | AEPW |  | 18100000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 3-winding transformer 514808 JOHNCO 4 138 514809 JOHNCO 7 345 514810 JOHNCO11 13 M2 | TBD |  | (478.00, 478.00) | OKGE |  | 18100000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Add 3-winding transformer 514898 CIMARON4 138 514901 CIMARON7 345 515715 CIMARO21 13 M2 | TBD |  | (478.00, 478.00) | OKGE |  | 18100000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 3-winding transformer 515375 WWRDEHV7 345 515376 WWRDEHV4 138 515795 WWDEHV21 13 M2 | TBD |  | (478.00, 478.00) | OKGE |  | 18100000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 3-winding transformer 515375 WWRDEHV7 345 515376 WWRDEHV4 138 515799 WWDEHV31 13 M2 | TBD |  | (478.00, 478.00) | OKGE |  | 18100000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2 | TBD |  | (478.00, 478.00) | OKGE |  | 18100000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2 | TBD |  | (478.00, 478.00) | WFEC |  | 18100000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 547476 ASB349 5 161 547491 PUR421 5 161 1 | TBD | 11.94 | (551.00, 551.00) | EMDE |  | 17910000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 516091 OKTAHA 7 345 516210 RAVEN 7 345 1 | TBD | 8.14 | (1793.00, 1793.00) | OKGE |  | 17908000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 505596 EXPLOR 4 138 505598 ALLEN 4 138 1 | TBD | 14.8 | (211.00, 211.00) | SWPA |  | 17760000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 1 | TBD | 17.76 | (260.00, 260.00) | SPS |  | 17760000
Current Study | Steady State | OTHER / 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | TBD | 11.77 | (446.00, 446.00) | AECI/KCPL |  | 17655000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 511425 TUTCONT4 138 514898 CIMARON4 138 1 | TBD | 14.65 | (395.00, 395.00) | AEPW/OKGE |  | 17580000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | TBD | 7.74 | (1793.00, 1793.00) | AEPW |  | 17028000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 640140 COOPER 5 161 778110 G24-038-TAP 161 1 | TBD | 11.26 | (446.00, 446.00) | NPPD/OPPD |  | 16890000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Add 2-winding transformer 655943 W.BANK.S-MW7 115 659070 W.BANK.S-BE3 345 M2 | TBD |  | (435.00, 435.00) | WAPA |  | 16800000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Add 3-winding transformer 659160 GROTON__-BE3 345 659161 GRT.KU2A-BE9 13 659187 GROTON__-BE7 115 M2 | TBD |  | (400.00, 400.00) | WAPA |  | 16800000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2 | TBD |  | (336.00, 336.00) | NPPD |  | 16800000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2 | TBD |  | (417.00, 417.00) | NPPD |  | 16800000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2 | TBD |  | (417.00, 417.00) | NPPD |  | 16800000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 3-winding transformer 531259 SETAB 1 13 531464 SETAB 3 115 531465 SETAB 7 345 M2 | TBD |  | (280.00, 308.00) | SUNC |  | 16800000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 3-winding transformer 531448 HOLCOMB3 115 531449 HOLCOMB7 345 531450 HOLCTER1 13 M2 | TBD |  | (336.00, 358.50) | SUNC |  | 16800000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2 | TBD |  | (350.00, 385.00) | SUNC |  | 16800000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 2-winding transformer 528184 SENDERO +3 115 528187 SENDERO_345 345 M2 | TBD |  | (435.00, 435.00) | SPS |  | 16800000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 533210 ENEMEHA3 115 533212 KINGFISH3 115 1 | TBD | 16.47 | (115.00, 115.00) | WERE |  | 16470000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 511446 CL-AFTP4 138 511458 ELKCTY-4 138 1 | TBD | 13.67 | (395.00, 395.00) | AEPW |  | 16404000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 514827 CTNWOOD4 138 515377 CRESENT4 138 1 | TBD | 13.6 | (472.00, 472.00) | OKGE |  | 16320000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 515178 PARKLN 4 138 515977 LKKONWA4 138 1 | TBD | 13.56 | (472.00, 472.00) | OKGE |  | 16272000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 515134 PRARPNT4 138 515570 MAYSVLT4 138 1 | TBD | 13.55 | (211.00, 211.00) | OKGE |  | 16260000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TBD | 7.36 | (1793.00, 1793.00) | SPS |  | 16192000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Rebuild line 640082 BEVERLY7 115 640326 REDWILO7 115 1 | TBD | 16.08 | (176.00, 176.00) | NPPD |  | 16080000
Current Study | Steady State | 04 SOUTHEAST / 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 521042 RUSSELL2 69 529342 OMMANGM2 69 1 | TBD | 18.66 | (69.00, 69.00) | OMPA/WFEC |  | 15861000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | TBD | 13.16 | (395.00, 395.00) | OKGE |  | 15792000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 521056 STRATFD4 138 782580 G24-187-TAP 138 1 | TBD | 12.99 | (211.00, 211.00) | WFEC |  | 15588000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 520939 HLDTNTP4 138 520981 LOCO 4 138 1 | TBD | 12.85 | (211.00, 211.00) | WFEC |  | 15420000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | TBD | 6.93 | (1793.00, 1793.00) | AEPW |  | 15246000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 515133 BLUERIV4 138 515178 PARKLN 4 138 1 | TBD | 12.7 | (395.00, 395.00) | OKGE |  | 15240000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add line 542981 LACYGNE7 345 765571 G21-029-TAP 345 M2 | TBD | 1.63 | (2390.00, 2390.00) | KCPL |  | 15053000
Current Study | Steady State | OTHER / 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | TBD | 14.95 | (329.00, 329.00) | AEPW/EES-EAI |  | 14950000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TBD | 6.79 | (2390.00, 2390.00) | SUNC |  | 14938000
Current Study | Steady State | 04 SOUTHEAST / 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 512631 MIAMI 5 161 547487 HOC404 5 161 1 | TBD | 9.9 | (246.00, 246.00) | EMDE/GRDA |  | 14850000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 531357 RULETON3 115 531368 LAWNRID3 115 1 | TBD | 14.78 | (176.00, 176.00) | SUNC |  | 14780000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Rebuild line 652296 WARD 4 230 652426 BISMARK4 230 1 | TBD | 7.74 | (519.00, 519.00) | WAPA |  | 14706000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 511440 ALTUSJT4 138 521043 RUSSELL4 138 1 | TBD | 12.25 | (211.00, 211.00) | AEPW/WFEC |  | 14700000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | TBD | 14.69 | (260.00, 260.00) | SUNC |  | 14690000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 510379 DELWARE4 138 763113 G18-079-TAP 138 1 | TBD | 12.23 | (395.00, 395.00) | AEPW |  | 14676000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 539668 HARPER 4 138 539881 SPRVLSTR 138 1 | TBD | 12.1 | (281.00, 281.00) | SUNC |  | 14520000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 514785 WOODWRD4 138 515785 WINDFRM4 138 1 | TBD | 12.07 | (395.00, 395.00) | OKGE |  | 14484000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TBD | 6.5732 | (2390.00, 2390.00) | SUNC |  | 14460953.1406
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 520888 PAYNESW4 138 521023 PAOLI 4 138 1 | TBD | 12 | (265.00, 265.00) | WFEC |  | 14400000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 514710 WAUKOMI4 138 514774 HENESEY4 138 1 | TBD | 11.86 | (395.00, 395.00) | OKGE |  | 14232000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 515150 CANEYCK4 138 515151 LTLCITY4 138 1 | TBD | 11.79 | (265.00, 265.00) | OKGE |  | 14148000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | TBD |  | (339.00, 330.00) | AEPW |  | 14000000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 774620 G23-132-TAP 161 780390 G24-114-TAP 161 1 | TBD | 9.3 | (364.00, 364.00) | SWPA |  | 13950000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 511477 S.W.S.-4 138 511586 TONKAWA4 138 1 | TBD | 11.5 | (265.00, 265.00) | AEPW |  | 13800000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 3-winding transformer 523092 HITCHLD_TR11 13 523093 HITCHLAND 3 115 523095 HITCHLAND 6 230 M2 | TBD |  | (250.00, 288.00) | SPS |  | 13800000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 3-winding transformer 523093 HITCHLAND 3 115 523095 HITCHLAND 6 230 523098 HITCHLD_TR41 13 M2 | TBD |  | (250.00, 288.00) | SPS |  | 13800000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 3-winding transformer 524872 OASIS_TR1 1 13 524874 OASIS 3 115 524875 OASIS 6 230 M2 | TBD |  | (239.00, 239.00) | SPS |  | 13800000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 510880 COALGTP4 138 510881 ALLENGT4 138 1 | TBD | 11.48 | (211.00, 211.00) | AEPW |  | 13776000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 533002 DEARING4 138 533004 MONTGOM4 138 1 | TBD | 11.45 | (265.00, 265.00) | WERE |  | 13740000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 509752 INOLATP4 138 509790 CATOOSA4 138 1 | TBD | 11.41 | (395.00, 395.00) | AEPW |  | 13692000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 515100 PAOLI- 4 138 515124 MAYSVIL4 138 1 | TBD | 11.4 | (211.00, 211.00) | OKGE |  | 13680000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add line 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 P2 | TBD | 2.51 | (478.00, 478.00) | SPS |  | 13475000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Rebuild line 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 | TBD | 13.41 | (217.00, 217.00) | WAPA |  | 13410000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 520854 CIVIT 4 138 521023 PAOLI 4 138 1 | TBD | 11.15 | (211.00, 211.00) | WFEC |  | 13380000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 539650 BELOIT 3 115 539663 GLENELD3 115 1 | TBD | 13.33 | (176.00, 176.00) | SUNC |  | 13330000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | TBD | 11.1 | (395.00, 395.00) | WFEC |  | 13320000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 520842 CANADNS4 138 520976 LIL AXE4 138 1 | TBD | 11.08 | (265.00, 265.00) | WFEC |  | 13296000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TBD | 5.97 | (2390.00, 2390.00) | OKGE |  | 13134000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | TBD | 13.1 | (297.00, 297.00) | SUNC |  | 13100000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 539009 CONWAY 4 138 539881 SPRVLSTR 138 1 | TBD | 10.66 | (281.00, 281.00) | SUNC |  | 12792000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 515129 RATLIFF4 138 515134 PRARPNT4 138 1 | TBD | 10.62 | (265.00, 265.00) | OKGE |  | 12744000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 539753 PRATTENERGY3 115 539756 SKLYVL_GOAB3 115 1 | TBD | 12.52 | (260.00, 260.00) | SUNC |  | 12520000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | TBD | 10.42 | (395.00, 395.00) | AEPW |  | 12504000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 530618 HUNTSVL3 115 530724 CENTENNIAL3 115 1 | TBD | 12.45 | (297.00, 297.00) | MIDW |  | 12450000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 515117 ARBUCKL4 138 515133 BLUERIV4 138 1 | TBD | 10.35 | (395.00, 395.00) | OKGE |  | 12420000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 3-winding transformer 512623 CATSAGD4 138 512638 CATSAGR5 161 512833 CATTER1 1 13 M2 | TBD |  | (150.00, 188.00) | GRDA |  | 12400000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 3-winding transformer 512636 CATSAGR4 138 512638 CATSAGR5 161 512834 CATTER2 1 13 M2 | TBD |  | (150.00, 188.00) | GRDA |  | 12400000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 520425 PIC4 138 520848 CDRDLTP4 138 1 | TBD | 10.31 | (211.00, 211.00) | WFEC |  | 12372000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 532797 WOLFCRK7 345 532799 WAVERLY7 345 1 | TBD | 5.6 | (2390.00, 2390.00) | WERE |  | 12320000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Rebuild line 640080 BELDEN 7 115 640212 HARTGTN7 115 1 | TBD | 12.27 | (176.00, 176.00) | NPPD |  | 12270000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 531405 WALKMYR3 115 531481 HUGOTON3 115 1 | TBD | 12.27 | (598.00, 598.00) | SUNC |  | 12270000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 520861 COLE 4 138 520868 CRINER 4 138 1 | TBD | 10.06 | (211.00, 211.00) | WFEC |  | 12072000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Rebuild line 647101 AUBRNT 8 69 647975 S975 8 69 1 | TBD | 14.17 | (106.00, 106.00) | OPPD |  | 12044500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 533002 DEARING4 138 533003 LIBERTY4 138 1 | TBD | 10.03 | (395.00, 395.00) | WERE |  | 12036000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Add 525 MVAR SVC at SD.LS-LR-MB3 345 kV | TBD |  |  | WAPA |  | 12000000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Add 78 MVAR SVC at STEGALL_-MB3 345 kV | TBD |  |  | WAPA |  | 12000000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2 | TBD |  | (110.00, 120.00) | LES |  | 12000000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 646263 S1263 5 161 646280 S1280 5 161 1 | TBD | 8 | (309.00, 309.00) | OPPD |  | 12000000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 111 MVAR SVC at GEARY 7 345 kV | TBD |  |  | WERE |  | 12000000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 114 MVAR SVC at SWISVAL7 345 kV | TBD |  |  | WERE |  | 12000000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 12 MVAR SVC at NRSS7 345 kV | TBD |  |  | WERE |  | 12000000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 129 MVAR SVC at MONETT345 345 kV | TBD |  |  | SPRM |  | 12000000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 130 MVAR SVC at W.GRDNR7 345 kV | TBD |  |  | KCPL |  | 12000000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 141 MVAR SVC at G23-220-TAP 345 kV | TBD |  |  | WERE |  | 12000000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 141 MVAR SVC at WICHITA7 345 kV | TBD |  |  | WERE |  | 12000000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 15 MVAR SVC at GEN-2021-076 345 kV | TBD |  |  | MIDW |  | 12000000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 160 MVAR SVC at BUFFALO7 345 kV | TBD |  |  | WERE |  | 12000000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 160 MVAR SVC at NEOSHO 7 345 kV | TBD |  |  | WERE |  | 12000000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 165 MVAR SVC at G21-096-TAP 345 kV | TBD |  |  | WERE |  | 12000000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 174 MVAR SVC at LANG 7 345 kV | TBD |  |  | WERE |  | 12000000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 210 MVAR SVC at POSTROCK7 345 kV | TBD |  |  | MIDW |  | 12000000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 213 MVAR SVC at SUMMIT 7 345 kV | TBD |  |  | WERE |  | 12000000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 26 MVAR SVC at CANEYRV7 345 kV | TBD |  |  | WERE |  | 12000000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 260 MVAR SVC at G24-076-TAP 345 kV | TBD |  |  | WERE |  | 12000000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 3-winding transformer 532913 KELLY 5 161 532942 KELLY 1 13 533217 KELLY 3 115 M2 | TBD |  | (144.00, 144.00) | WERE |  | 12000000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 415 MVAR SVC at G16-111-TAP 345 kV | TBD |  |  | WERE |  | 12000000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 43 MVAR SVC at G23-221-TAP 345 kV | TBD |  |  | WERE |  | 12000000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 44 MVAR SVC at G15052_1 345 kV | TBD |  |  | WERE |  | 12000000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 44 MVAR SVC at G15052_T 345 kV | TBD |  |  | WERE |  | 12000000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 47 MVAR SVC at MORRIS 7 345 kV | TBD |  |  | WERE |  | 12000000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 88 MVAR SVC at BURNS 7 345 kV | TBD |  |  | WERE |  | 12000000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 531391 PIONEER3 115 531483 GRANTTP3 115 1 | TBD | 12 | (329.00, 329.00) | SUNC |  | 12000000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 68 MVAR SVC at TONTITN7 345 kV | TBD |  |  | AEPW |  | 12000000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 509049 MURVAUL4 138 712002 TENASK4 138 P | TBD | 10 | (265.00, 265.00) | AEPW |  | 12000000
Current Study | Steady State | OTHER / 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 337505 3EMMET 115 507448 NHOPE 3 115 1 | TBD | 12 | (329.00, 329.00) | AEPW/EES-EAI |  | 12000000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 531419 DOBSON 3 115 531493 GANO 3 115 1 | TBD | 11.92 | (260.00, 260.00) | SUNC |  | 11920000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 531432 PILE 3 115 531433 SCOTCTY3 115 1 | TBD | 11.88 | (260.00, 260.00) | SUNC |  | 11880000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 547485 CAR395 5 161 547491 PUR421 5 161 1 | TBD | 7.89 | (551.00, 551.00) | EMDE |  | 11835000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 539652 CMRIVTP3 115 539672 E-LIBER3 115 1 | TBD | 11.74 | (176.00, 176.00) | SUNC |  | 11740000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 655943 W.BANK.S-MW7 115 655945 WHEELS_T-MW7 115 1 | TBD | 11.73 | (394.00, 394.00) | WAPA |  | 11730000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | TBD | 5.3 | (1793.00, 1793.00) | AEPW |  | 11660000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 520973 LEXNGTN4 138 520976 LIL AXE4 138 1 | TBD | 9.71 | (265.00, 265.00) | WFEC |  | 11652000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 512710 KINZEGR4 138 512731 NORTHTP4 138 1 | TBD | 9.7 | (395.00, 395.00) | GRDA |  | 11640000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Rebuild line 640066 AXTELL 7 115 640275 MINDEN 7 115 1 | TBD | 11.61 | (217.00, 217.00) | NPPD |  | 11610000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 527891 HOBBS_INT 3 115 784800 G24-261-TAP 115 1 | TBD | 11.57 | (217.00, 217.00) | SPS |  | 11570000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 523216 RB-HOGUE 3 115 523246 DALHART 3 115 1 | TBD | 11.44 | (115.00, 115.00) | SPS |  | 11440000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 521098 WSBNKTP4 138 778530 G24-052-TAP 138 1 | TBD | 9.45 | (472.00, 472.00) | WFEC |  | 11340000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 | TBD | 7.49 | (364.00, 364.00) | KCPL |  | 11235000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 640316 PAWNEEL7 115 640340 SEWARD 7 115 1 | TBD | 11.21 | (217.00, 217.00) | NPPD |  | 11210000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 509106 HEMPHIL4 138 509107 SIXMILE4 138 1 | TBD | 9.32 | (211.00, 211.00) | AEPW |  | 11184000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 530724 CENTENNIAL3 115 533412 ARKVALJ3 115 1 | TBD | 10.96 | (297.00, 297.00) | MIDW/WERE |  | 10960000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 520603 NKNGFSH4 138 520882 DOVERSW4 138 1 | TBD | 9.13 | (211.00, 211.00) | WFEC |  | 10956000
Current Study | Steady State | 04 SOUTHEAST / 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 | TBD | 9.08 | (395.00, 395.00) | OKGE/WERE |  | 10896000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 528547 S_JAL 3 115 785400 G24-281-TAP 115 1 | TBD | 10.82 | (260.00, 260.00) | SPS |  | 10820000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 509048 MURVAULTP 138 509049 MURVAUL4 138 P | TBD | 9 | (265.00, 265.00) | AEPW |  | 10800000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Rebuild line 640261 LOWELL 7 115 640275 MINDEN 7 115 1 | TBD | 10.75 | (176.00, 176.00) | NPPD |  | 10750000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | TBD | 10.74 | (394.00, 394.00) | NPPD |  | 10740000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 539638 FLATRDG4 138 539674 BARBER 4 138 1 | TBD | 8.92 | (472.00, 472.00) | SUNC |  | 10704000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 520425 PIC4 138 786210 G24-308-TAP 138 1 | TBD | 8.91 | (211.00, 211.00) | WFEC |  | 10692000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | TBD | 10.55 | (297.00, 297.00) | LES/NPPD |  | 10550000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Add 3-winding transformer 505487 CRG X1 1 13 505488 CARTHAG5 161 505490 CARTHG 2 69 M2 | TBD |  | (84.00, 84.00) | SWPA |  | 10475000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Add 3-winding transformer 505488 CARTHAG5 161 505489 CRG X2 1 13 505490 CARTHG 2 69 M2 | TBD |  | (84.00, 84.00) | SWPA |  | 10475000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 3-winding transformer 539674 BARBER 4 138 539760 BARBER 3 115 539917 BARBER-1 13 M2 | TBD |  | (324.00, 324.00) | SUNC |  | 10400000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 3-winding transformer 507454 TURK 4 138 507456 TURK 3 115 507458 TURK1 1 13 M2 | TBD |  | (257.00, 257.00) | AEPW |  | 10400000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1 | TBD | 6.85 | (837.00, 837.00) | INDN/KCPL |  | 10275000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 533003 LIBERTY4 138 533008 TV1MNDV4 138 1 | TBD | 8.36 | (265.00, 265.00) | WERE |  | 10032000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 511423 FLE TAP4 138 511586 TONKAWA4 138 1 | TBD | 8.33 | (265.00, 265.00) | AEPW |  | 9996000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 507449 NWHOPE 3 115 507452 HOPESWI3 115 1 | TBD | 9.8 | (329.00, 329.00) | AEPW |  | 9800000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | TBD | 6.5 | (837.00, 837.00) | INDN/KCPL |  | 9750000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 539010 SADLHRN3 115 539648 PRICHRD3 115 1 | TBD | 9.47 | (598.00, 598.00) | SUNC |  | 9470000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 539010 SADLHRN3 115 539696 ST-JOHN3 115 1 | TBD | 9.4 | (598.00, 598.00) | SUNC |  | 9400000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 510895 LEHIGH-4 138 782490 G24-184-TAP 138 1 | TBD | 7.71 | (211.00, 211.00) | AEPW |  | 9252000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | TBD | 7.6 | (211.00, 211.00) | AEPW |  | 9120000
Current Study | Steady State | OTHER / 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | TBD | 6.07 | (364.00, 364.00) | AECI/INDN |  | 9105000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 511435 SNYDER-4 138 765230 G20-012-TAP 138 1 | TBD | 7.51 | (395.00, 395.00) | AEPW |  | 9012000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 655942 N.TWELVE-MW7 115 655959 EPPING -MW7 115 1 | TBD | 9 | (260.00, 260.00) | WAPA |  | 9000000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 3-winding transformer 511419 SNYDRTER 13 511435 SNYDER-4 138 511475 SNYDER-2 69 M2 | TBD |  | (75.00, 75.00) | AEPW |  | 9000000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 520847 TWNLKJT4 138 521073 TWNLKSW4 138 1 | TBD | 7.45 | (211.00, 211.00) | WFEC |  | 8940000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 511477 S.W.S.-4 138 520814 ANADARK4 138 1 | TBD | 7.37 | (395.00, 395.00) | AEPW/WFEC |  | 8844000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | TBD | 10.34 | (69.00, 69.00) | AEPW |  | 8789000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 521014 OILCRTP4 138 521056 STRATFD4 138 1 | TBD | 7.3 | (211.00, 211.00) | WFEC |  | 8760000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 533210 ENEMEHA3 115 533217 KELLY 3 115 1 | TBD | 8.7 | (115.00, 115.00) | WERE |  | 8700000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 515129 RATLIFF4 138 515561 CARTRCO4 138 1 | TBD | 7.22 | (265.00, 265.00) | OKGE |  | 8664000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Rebuild line 640100 CAMBRIG7 115 640194 GOSPER 7 115 1 | TBD | 8.61 | (176.00, 176.00) | NPPD |  | 8610000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Add 314 MVAR SVC at MAURINE4 230 kV | TBD |  |  | WAPA |  | 8600000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 80 MVAR SVC at AUBURN 6 230 kV | TBD |  |  | WERE |  | 8600000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 520969 LASALLE4 138 520971 LATTAJT4 138 1 | TBD | 7.1 | (211.00, 211.00) | WFEC |  | 8520000
Current Study | Steady State | OTHER / 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 300141 4STILWTR 138 512731 NORTHTP4 138 1 | TBD | 6.97 | (395.00, 395.00) | AECI/GRDA |  | 8364000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 521049 SCLMNJC4 138 784980 G24-267-TAP 138 1 | TBD | 6.96 | (472.00, 472.00) | WFEC |  | 8352000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 531432 PILE 3 115 531493 GANO 3 115 1 | TBD | 8.34 | (260.00, 260.00) | SUNC |  | 8340000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 505595 GREASYC4 138 505596 EXPLOR 4 138 1 | TBD | 6.91 | (211.00, 211.00) | SWPA |  | 8292000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Add 3-winding transformer 640173 FREMONT7 115 643058 FREMONT T1 9 13 647976 S976 8 69 M2 | TBD |  | (63.00, 63.00) | NPPD |  | 8125000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Add 3-winding transformer 640173 FREMONT7 115 643059 FREMONT T4 9 13 647976 S976 8 69 M2 | TBD |  | (56.00, 56.00) | NPPD |  | 8125000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 514710 WAUKOMI4 138 514711 WAUKOTP4 138 1 | TBD | 6.7 | (395.00, 395.00) | OKGE |  | 8040000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 512734 FARML 4 138 778710 G24-058-TAP 138 1 | TBD | 6.69 | (395.00, 395.00) | AEPW/GRDA |  | 8028000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508813 PLAINDL2 69 778290 G24-044-TAP 69 1 | TBD | 9.39 | (69.00, 69.00) | AEPW |  | 7981500
Current Study | Steady State | OTHER / 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | TBD | 4.2 | (519.00, 519.00) | WAPA/XEL |  | 7980000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 520918 FROGVIL4 138 520948 HUGO PP4 138 1 | TBD | 6.55 | (717.00, 717.00) | WFEC |  | 7860000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 520868 CRINER 4 138 520888 PAYNESW4 138 1 | TBD | 6.54 | (211.00, 211.00) | WFEC |  | 7848000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 528018 RED_BLUFF 3 115 528235 WOLFCAMP_TP3 115 1 | TBD | 7.81 | (598.00, 598.00) | SPS |  | 7810000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 524863 FE-CHZPLT 3 115 524874 OASIS 3 115 1 | TBD | 7.8 | (176.00, 176.00) | SPS |  | 7800000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 547469 RIV4525 161 547729 BAX488 5 161 1 | TBD | 5.19 | (364.00, 364.00) | EMDE |  | 7785000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 527482 CHAVES_CNTY3 115 527546 SAMSON 3 115 1 | TBD | 7.78 | (217.00, 217.00) | SPS |  | 7780000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 521096 WOODWRD2 69 521197 CRTSJCT2 69 1 | TBD | 9.13 | (106.00, 106.00) | WFEC |  | 7760500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 520893 EL RENO4 138 520899 SCOTTSW4 138 1 | TBD | 6.45 | (265.00, 265.00) | WFEC |  | 7740000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 528013 PHANTOM 3 115 528228 WOOD_DRAW 3 115 1 | TBD | 7.71 | (260.00, 260.00) | SPS |  | 7710000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 528016 SAND_DUNES 3 115 528018 RED_BLUFF 3 115 1 | TBD | 7.69 | (394.00, 394.00) | SPS |  | 7690000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 515151 LTLCITY4 138 515157 BROWN 4 138 1 | TBD | 6.37 | (265.00, 265.00) | OKGE |  | 7644000
Current Study | Steady State | 04 SOUTHEAST / 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 511564 MARTHA 4 138 529302 OMALTUS4 138 1 | TBD | 6.37 | (395.00, 395.00) | AEPW/OMPA |  | 7644000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 781680 GEN-2024-157 138 781800 G24-161-TAP 138 1 | TBD | 6.36 | (211.00, 211.00) | AEPW |  | 7632000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 524764 NORRIS_TP 3 115 524863 FE-CHZPLT 3 115 1 | TBD | 7.62 | (176.00, 176.00) | SPS |  | 7620000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 524662 PARMER_CO 3 115 524668 DS-#20 +3 115 1 | TBD | 7.6 | (176.00, 176.00) | SPS |  | 7600000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 520918 FROGVIL4 138 773820 G23-092-TAP 138 1 | TBD | 6.3 | (717.00, 717.00) | WFEC |  | 7560000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | NRIS | Rebuild line 533044 GILL E 4 138 533051 INTERST4 138 1 | TBD | 6.25 | (211.00, 211.00) | WERE |  | 7500000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Rebuild line 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 | TBD | 7.43 | (217.00, 217.00) | WAPA |  | 7430000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 547468 AUR124 5 161 779490 G24-084-TAP 161 1 | TBD | 4.95 | (246.00, 246.00) | EMDE |  | 7425000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 510422 COFFEYT4 138 787350 G24-346-TAP 138 1 | TBD | 6.1 | (525.00, 525.00) | AEPW |  | 7320000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | TBD | 8.6 | (69.00, 69.00) | AEPW |  | 7310000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 | TBD | 6.08 | (395.00, 395.00) | OKGE |  | 7296000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 530565 SEWARD 2 69 530569 GB STH 2 69 1 | TBD | 8.56 | (69.00, 69.00) | MIDW |  | 7276000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 539666 GBENDTP3 115 539678 GRTBEND3 115 1 | TBD | 7.21 | (176.00, 176.00) | SUNC |  | 7210000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 512654 PENSA 5 161 512669 KETCHUM5 161 1 | TBD | 4.8 | (364.00, 364.00) | GRDA |  | 7200000
Current Study | Steady State | OTHER / 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 | TBD | 3.23 | (1793.00, 1793.00) | AECI/GRDA |  | 7106000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 515802 GRACMNT4 138 521089 WASHITA4 138 1 | TBD | 5.87 | (265.00, 265.00) | OKGE/WFEC |  | 7044000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add line and rebuild line 524243 OUTPOST 3 115 524266 BUSHLAND 3 115 M2 | TBD | 1.93 | (598.00, 598.00) | SPS |  | 6902000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 520400 NOBLE4 138 520975 LIDDELL4 138 1 | TBD | 5.73 | (265.00, 265.00) | WFEC |  | 6876000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 647963 S963 8 69 647977 S977 8 69 1 | TBD | 8.02 | (106.00, 106.00) | OPPD |  | 6817000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1 | TBD | 6.81 | (260.00, 260.00) | SPS |  | 6810000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 761278 G17-108-TAP 161 785640 G24-289-TAP 161 1 | TBD | 4.53 | (364.00, 364.00) | KCPL |  | 6795000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1 | TBD | 5.63 | (525.00, 525.00) | OKGE |  | 6756000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TBD | 4.5 | (837.00, 837.00) | INDN/KCPL |  | 6750000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 533075 VIOLA 4 138 539009 CONWAY 4 138 1 | TBD | 5.62 | (281.00, 281.00) | SUNC/WERE |  | 6744000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 16 MVAR SVC at CPK446 5 161 kV | TBD |  |  | EMDE |  | 6600000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 32 MVAR SVC at SIBLEYRD5 161 kV | TBD |  |  | EMDE |  | 6600000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 40 MVAR SVC at HOC404 5 161 kV | TBD |  |  | EMDE |  | 6600000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 42 MVAR SVC at NEVADA 5 161 kV | TBD |  |  | KCPL |  | 6600000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 176 MVAR SVC at BULL SH5 161 kV | TBD |  |  | SWPA |  | 6600000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 28 MVAR SVC at MIAMI 5 161 kV | TBD |  |  | GRDA |  | 6600000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 38 MVAR SVC at WROGERS 5 161 kV | TBD |  |  | AEPW |  | 6600000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TBD | 2.98 | (2390.00, 2390.00) | SPS |  | 6556000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | TBD | 4.34 | (837.00, 837.00) | INDN |  | 6510000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 507452 HOPESWI3 115 507453 HOPE 3 115 1 | TBD | 6.38 | (260.00, 260.00) | AEPW |  | 6380000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 646280 S1280 5 161 778110 G24-038-TAP 161 1 | TBD | 4.25 | (309.00, 309.00) | OPPD |  | 6375000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Rebuild line 509817 T.NO.--4 138 509900 46ST-TP-4 138 1 | TBD | 5.18 | (211.00, 211.00) | AEPW |  | 6216000
Current Study | Steady State | 04 SOUTHEAST / 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1 | TBD | 4.14 | (551.00, 551.00) | EMDE/SWPA |  | 6210000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Rebuild line 515055 MAUD 4 138 787770 G24-360-TAP 138 1 | TBD | 5.11 | (395.00, 395.00) | OKGE |  | 6132000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Rebuild 3-winding transformer 640234 HUMBOLT5 161 647975 S975 8 69 648275 S975T4 9 13 1 | TBD |  | (102.00, 102.00) | OPPD |  | 6075000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild 3-winding transformer 646263 S1263 5 161 647111 W BROCK8 69 648263 S1263T19 13 1 | TBD |  | (121.00, 121.00) | OPPD |  | 6075000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild 2-winding transformer 543063 SWAVRLY5 161 543094 SWAVRLY2 69 1 | TBD |  | (87.00, 87.00) | KCPL |  | 6075000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | TBD |  | (180.00, 180.00) | INDN |  | 6075000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | TBD |  | (185.00, 185.00) | INDN |  | 6075000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild 2-winding transformer 548814 SUB M-161 161 548815 SUB M 69 1 | TBD |  | (139.00, 139.00) | INDN |  | 6075000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild 3-winding transformer 515336 VBI 2 69 515339 VBI 5 161 515769 VBI 1 13 2 | TBD |  | (83.00, 83.00) | OKGE |  | 6075000
Current Study | Steady State | 04 SOUTHEAST / 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 510422 COFFEYT4 138 533002 DEARING4 138 1 | TBD | 5.02 | (717.00, 717.00) | AEPW/WERE |  | 6024000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add line and rebuild line 531405 WALKMYR3 115 531510 HARBNGR3 115 M2 | TBD | 1.28 | (598.00, 598.00) | SUNC |  | 5992000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 533413 CIRCLE 3 115 533416 RENO 3 115 2 | TBD | 5.95 | (217.00, 217.00) | WERE |  | 5950000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Rebuild line 640250 KEARNEY7 115 640383 TOWER 7 115 1 | TBD | 5.92 | (176.00, 176.00) | NPPD |  | 5920000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 510880 COALGTP4 138 510895 LEHIGH-4 138 1 | TBD | 4.81 | (211.00, 211.00) | AEPW |  | 5772000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 507774 NORAM 4 138 508808 LONGWD 4 138 1 | TBD | 4.8 | (281.00, 281.00) | AEPW |  | 5760000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Rebuild line 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | TBD | 4.8 | (395.00, 395.00) | OKGE |  | 5760000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1 | TBD | 5.46 | (217.00, 217.00) | LES/NPPD |  | 5460000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 520971 LATTAJT4 138 521014 OILCRTP4 138 1 | TBD | 4.55 | (211.00, 211.00) | WFEC |  | 5460000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild 3-winding transformer 515113 CHIGLEY2 69 515114 CHIGLEY4 138 515712 CHIGLEY1 13 3 | TBD |  | (71.00, 71.00) | OKGE |  | 5400000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild 3-winding transformer 520995 MOORLND2 69 520999 MOORLND4 138 521180 MLNDTERT 2 1 | TBD |  | (86.00, 86.00) | WFEC |  | 5400000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild 3-winding transformer 521015 OKEENE 2 69 521016 OKEENE 4 138 521173 OKENTERT 13 1 | TBD |  | (103.00, 103.00) | WFEC |  | 5400000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild 3-winding transformer 521042 RUSSELL2 69 521043 RUSSELL4 138 521175 RSLTERT 13 1 | TBD |  | (81.00, 81.00) | WFEC |  | 5400000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Add 16 MVAR switched shunt at UNDERWOOD 2 345 kV | TBD |  |  | WAPA |  | 5300000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Add 25 MVAR switched shunt at BELFELD3 345 kV | TBD |  |  | WAPA |  | 5300000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Add 256 MVAR switched shunt at SD.LS-KS-MB3 345 kV | TBD |  |  | WAPA |  | 5300000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Add 203 MVAR switched shunt at REDWILO3 345 kV | TBD |  |  | NPPD |  | 5300000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Add 31 MVAR switched shunt at G24-016-TAP 345 kV | TBD |  |  | NPPD |  | 5300000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Add 50 MVAR switched shunt at MACON 3 345 kV | TBD |  |  | NPPD |  | 5300000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Add 62 MVAR switched shunt at AXTELL 3 345 kV | TBD |  |  | NPPD |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 0.02 MVAR switched shunt at PHILL 7 345 kV | TBD |  |  | KCPL |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 0.06 MVAR switched shunt at G24-125-TAP 345 kV | TBD |  |  | WERE |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 0.21 MVAR switched shunt at G22-013-TAP 345 kV | TBD |  |  | WERE |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 0.4 MVAR switched shunt at HI_BNKS2_WF7 345 kV | TBD |  |  | WERE |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 0.8 MVAR switched shunt at HARBNGR7 345 kV | TBD |  |  | SUNC |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 1 MVAR switched shunt at HI_BNKS1_WF7 345 kV | TBD |  |  | WERE |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 10 MVAR switched shunt at G20-007-TAP 345 kV | TBD |  |  | KCPL |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 122 MVAR switched shunt at HOYT 7 345 kV | TBD |  |  | WERE |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 135 MVAR switched shunt at G22-015-TAP 345 kV | TBD |  |  | SUNC |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 138 MVAR switched shunt at GEN-2024-016 345 kV | TBD |  |  | MIDW |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 15 MVAR switched shunt at GEN-2022-075 345 kV | TBD |  |  | MIDW |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 20 MVAR switched shunt at MINGO 7 345 kV | TBD |  |  | SUNC |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 204 MVAR switched shunt at LACYGNE11_7 345 kV | TBD |  |  | KCPL |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 220 MVAR SVC at NEOSHO 4 138 kV | TBD |  |  | WERE |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 248 MVAR switched shunt at GEN-2022-015 345 kV | TBD |  |  | SUNC |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 27 MVAR switched shunt at G18-128-TAP 345 kV | TBD |  |  | WERE |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 27 MVAR switched shunt at G22-075-TAP 345 kV | TBD |  |  | MIDW |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 32 MVAR SVC at LIBERTY4 138 kV | TBD |  |  | WERE |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 32 MVAR SVC at MONTGOM4 138 kV | TBD |  |  | WERE |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 34 MVAR switched shunt at OUTLAW_WF7 345 kV | TBD |  |  | KCPL |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 36 MVAR SVC at TIOGA 4 138 kV | TBD |  |  | WERE |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 36 MVAR switched shunt at JEC N 7 345 kV | TBD |  |  | WERE |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 48 MVAR switched shunt at ELKRVR17 345 kV | TBD |  |  | WERE |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 54 MVAR SVC at WHARV4 138 kV | TBD |  |  | WERE |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 7 MVAR switched shunt at G19-030-TAP 345 kV | TBD |  |  | SUNC |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | NRIS | Add 7 MVAR switched shunt at GEN-2020-007 345 kV | TBD |  |  | KCPL |  | 5300000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Add 0.8 MVAR switched shunt at G17-140-BUS 345 kV | TBD |  |  | AEPW |  | 5300000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 16 MVAR SVC at GROVE 4 138 kV | TBD |  |  | AEPW |  | 5300000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 19 MVAR switched shunt at RANCHRD7 345 kV | TBD |  |  | OKGE |  | 5300000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 24 MVAR SVC at JAY 4 138 kV | TBD |  |  | AEPW |  | 5300000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 37 MVAR switched shunt at CHAMSPR7 345 kV | TBD |  |  | AEPW |  | 5300000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 38 MVAR switched shunt at FRNT2WD7 345 kV | TBD |  |  | OKGE |  | 5300000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 4 MVAR switched shunt at GEN-2017-140 345 kV | TBD |  |  | AEPW |  | 5300000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 66 MVAR switched shunt at GEN-2021-021 345 kV | TBD |  |  | SPS |  | 5300000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add line and rebuild line 528020 BOPCO_PKRLK3 115 528235 WOLFCAMP_TP3 115 M2 | TBD | 0.78 | (598.00, 598.00) | SPS |  | 5292000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 515376 WWRDEHV4 138 515425 WWDPST 4 138 1 | TBD | 4.4 | (472.00, 472.00) | OKGE |  | 5280000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 520405 KGFSJCT4 138 520603 NKNGFSH4 138 1 | TBD | 4.35 | (211.00, 211.00) | WFEC |  | 5220000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 507732 GENMOTR4 138 507759 SW SHV 4 138 1 | TBD | 4.34 | (395.00, 395.00) | AEPW |  | 5208000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 533412 ARKVALJ3 115 533413 CIRCLE 3 115 1 | TBD | 5.2 | (297.00, 297.00) | WERE |  | 5200000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 647401 NCU903 8 69 647977 S977 8 69 1 | TBD | 6.05 | (106.00, 106.00) | OPPD |  | 5142500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508803 GILLIAM2 69 508815 SUPEROR2 69 1 | TBD | 6 | (69.00, 69.00) | AEPW |  | 5100000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Rebuild line 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 | TBD | 5 | (217.00, 217.00) | WAPA |  | 5000000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 530569 GB STH 2 69 530596 WPRTTS 2 69 1 | TBD | 5.86 | (69.00, 69.00) | MIDW |  | 4981000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 547477 CJ 366 5 161 547490 FIR417 5 161 1 | TBD | 3.26 | (551.00, 551.00) | EMDE |  | 4890000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1 | TBD | 4.86 | (217.00, 217.00) | SPS |  | 4860000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 543100 AMOCOPL2 69 543102 WHGNSVL2 69 1 | TBD | 5.7 | (140.00, 140.00) | KCPL |  | 4845000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add phase shifting xfmr 514785 WOODWRD4 138 515425 WWDPST 4 138 M2 | TBD |  | (421.00, 421.00) | OKGE |  | 4750000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild 3-winding transformer 530565 SEWARD 2 69 530631 SWRD1 1 12 530679 SEWRDMW3 115 1 | TBD |  | (87.00, 87.00) | MIDW |  | 4725000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild 3-winding transformer 512106 SHAM 2WT 69 512107 SHAM 3WT 115 512109 SR1TERT 14 1 | TBD |  | (68.00, 68.00) | AEPW |  | 4725000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | NRIS | Rebuild 2-winding transformer 528334 LE-NRTH_INT3 115 528618 LE-LOVINTON2 69 1 | TBD |  | (124.00, 124.00) | SPS |  | 4725000
Current Study | Steady State | 04 SOUTHEAST / 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | TBD | 3.9 | (265.00, 265.00) | AEPW/OMPA |  | 4680000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | TBD | 3.89 | (395.00, 395.00) | OKGE |  | 4668000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 539648 PRICHRD3 115 539753 PRATTENERGY3 115 1 | TBD | 4.57 | (260.00, 260.00) | SUNC |  | 4570000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 529298 OMPVET-4 138 529345 OMPARK-4 138 1 | TBD | 3.79 | (395.00, 395.00) | OMPA |  | 4548000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add line and rebuild line 528013 PHANTOM 3 115 528020 BOPCO_PKRLK3 115 M2 | TBD | 0.2 | (598.00, 598.00) | SPS |  | 4480000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Add line and rebuild line 652568 GROTONSOUTH7 115 659187 GROTON__-BE7 115 M2 | TBD | 0.1 | (598.00, 598.00) | WAPA |  | 4340000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add phase shifting xfmr 523084 SOONER 3 115 523106 TXPHSF 3 115 M2 | TBD |  | (120.00, 120.00) | SPS |  | 4300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 547467 ORO110 5 161 547490 FIR417 5 161 1 | TBD | 2.86 | (551.00, 551.00) | EMDE |  | 4290000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 | TBD | 3.49 | (395.00, 395.00) | OKGE |  | 4188000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 543094 SWAVRLY2 69 543658 DOVER_TAP2 69 1 | TBD | 4.9 | (140.00, 140.00) | KCPL |  | 4165000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 539652 CMRIVTP3 115 539654 CIM-PLT3 115 1 | TBD | 4.08 | (217.00, 217.00) | SUNC |  | 4080000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 521098 WSBNKTP4 138 773820 G23-092-TAP 138 1 | TBD | 3.4 | (472.00, 472.00) | WFEC |  | 4080000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Rebuild line 514853 DVISION4 138 514863 HAYMAKR4 138 1 | TBD | 3.36 | (395.00, 395.00) | OKGE |  | 4032000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 527956 SBCRDWRDLEA 115 528505 LEA_ROAD 3 115 1 | TBD | 4 | (217.00, 217.00) | SPS |  | 4000000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508812 OILCITY2 69 508815 SUPEROR2 69 1 | TBD | 4.66 | (106.00, 106.00) | AEPW |  | 3961000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 520535 BULFTTP4 138 520882 DOVERSW4 138 1 | TBD | 3.3 | (472.00, 472.00) | WFEC |  | 3960000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 547487 HOC404 5 161 547729 BAX488 5 161 1 | TBD | 2.6 | (364.00, 364.00) | EMDE |  | 3900000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 511440 ALTUSJT4 138 781710 G24-158-TAP 138 1 | TBD | 3.23 | (395.00, 395.00) | AEPW |  | 3876000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Rebuild line 514889 WRAIRPT4 138 514925 PENN 4 138 1 | TBD | 3.22 | (281.00, 281.00) | OKGE |  | 3864000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Add 0.6 MVAR switched shunt at BISON___-GE4 230 kV | TBD |  |  | WAPA |  | 3825000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Add 0.7 MVAR switched shunt at STEGALL_-MB4 230 kV | TBD |  |  | WAPA |  | 3825000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Add 18 MVAR switched shunt at CHARL_CK-BE4 230 kV | TBD |  |  | WAPA |  | 3825000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Add 24 MVAR switched shunt at DH_CS_EA-TS4 230 kV | TBD |  |  | WAPA |  | 3825000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Add 60 MVAR switched shunt at WAYSIDE 4 230 kV | TBD |  |  | WAPA |  | 3825000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Add 13 MVAR switched shunt at HASTING4 230 kV | TBD |  |  | NPPD |  | 3825000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 13 MVAR switched shunt at TECHILL6 230 kV | TBD |  |  | WERE |  | 3825000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | NRIS | Add 110 MVAR switched shunt at SEMINOLE 6 230 kV | TBD |  |  | SPS |  | 3825000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 12 MVAR switched shunt at OCHILTREE 6 230 kV | TBD |  |  | SPS |  | 3825000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 18 MVAR switched shunt at DEAFSMITH 6 230 kV | TBD |  |  | SPS |  | 3825000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 2 MVAR switched shunt at GEN-2024-080 230 kV | TBD |  |  | SPS |  | 3825000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 46 MVAR switched shunt at STLN-DEMARC6 230 kV | TBD |  |  | SPS |  | 3825000
Current Study | Steady State | 01 NORTH / OTHER | DISIS-2024-001 | ERIS | Rebuild line 652200 GLENDIVE7 115 661032 GLENDCT7 115 1 | TBD | 3.8 | (176.00, 176.00) | MDU/WAPA |  | 3800000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 515377 CRESENT4 138 521073 TWNLKSW4 138 1 | TBD | 3.13 | (395.00, 395.00) | OKGE/WFEC |  | 3756000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 515124 MAYSVIL4 138 515570 MAYSVLT4 138 1 | TBD | 3.01 | (211.00, 211.00) | OKGE |  | 3612000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 520533 KGFSHSW4 138 520600 EKFSHTP4 138 1 | TBD | 2.98 | (211.00, 211.00) | WFEC |  | 3576000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1 | TBD | 3.54 | (217.00, 217.00) | SPS |  | 3540000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TBD | 1.6 | (1793.00, 1793.00) | WERE |  | 3520000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | TBD | 2.29 | (446.00, 446.00) | KCPL |  | 3435000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 514948 CEDARLN4 138 766111 G21-088-TAP 138 1 | TBD | 2.86 | (395.00, 395.00) | OKGE |  | 3432000
Current Study | Steady State | 04 SOUTHEAST / 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 511440 ALTUSJT4 138 529345 OMPARK-4 138 1 | TBD | 2.86 | (281.00, 281.00) | AEPW/OMPA |  | 3432000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 524243 OUTPOST 3 115 524560 ARNOT 3 115 1 | TBD | 3.43 | (598.00, 598.00) | SPS |  | 3430000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 520884 DURANTP4 138 784980 G24-267-TAP 138 1 | TBD | 2.79 | (395.00, 395.00) | WFEC |  | 3348000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 527522 ROSWELL_CTY3 115 527534 SW4J795_W 3 115 1 | TBD | 3.33 | (217.00, 217.00) | SPS |  | 3330000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 504122 MCNAB 3 115 507453 HOPE 3 115 1 | TBD | 3.32 | (394.00, 394.00) | AEPW |  | 3320000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 533680 CHRYJCT2 69 533697 LIBERT-2 69 1 | TBD | 3.84 | (106.00, 106.00) | WERE |  | 3264000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 0.02 MVAR switched shunt at BRN412 5 161 kV | TBD |  |  | EMDE |  | 3250000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 0.05 MVAR switched shunt at MON383 5 161 kV | TBD |  |  | EMDE |  | 3250000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 0.23 MVAR switched shunt at RDS295 5 161 kV | TBD |  |  | EMDE |  | 3250000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 0.7 MVAR switched shunt at G24-084-TAP 161 kV | TBD |  |  | EMDE |  | 3250000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 12 MVAR switched shunt at NOL435 5 161 kV | TBD |  |  | EMDE |  | 3250000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 22 MVAR switched shunt at BAX488 5 161 kV | TBD |  |  | EMDE |  | 3250000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 26 MVAR switched shunt at CNTRVIL5 161 kV | TBD |  |  | KCPL |  | 3250000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 28 MVAR switched shunt at AUR124 5 161 kV | TBD |  |  | EMDE |  | 3250000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 34 MVAR switched shunt at NEO184 5 161 kV | TBD |  |  | EMDE |  | 3250000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 4 MVAR switched shunt at OZK457 5 161 kV | TBD |  |  | EMDE |  | 3250000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 40 MVAR switched shunt at DAD368 5 161 kV | TBD |  |  | EMDE |  | 3250000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 8 MVAR switched shunt at SWAVRLY5 161 kV | TBD |  |  | KCPL |  | 3250000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 0.02 MVAR switched shunt at AVOCA 5 161 kV | TBD |  |  | AEPW |  | 3250000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 0.03 MVAR switched shunt at CENTRTN5 161 kV | TBD |  |  | AEPW |  | 3250000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 0.05 MVAR switched shunt at SWPINEY5 161 kV | TBD |  |  | SWPA |  | 3250000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 0.16 MVAR switched shunt at INDEPCO5 161 kV | TBD |  |  | SWPA |  | 3250000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 22 MVAR switched shunt at WASHBURN5 161 kV | TBD |  |  | SWPA |  | 3250000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 4 MVAR switched shunt at NEO SPA5 161 kV | TBD |  |  | SWPA |  | 3250000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 548802 SUB H 69 548806 BLUVLY 69 1 | TBD | 3.8 | (106.00, 106.00) | INDN |  | 3230000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 524300 HILLSIDE 3 115 524560 ARNOT 3 115 1 | TBD | 3.17 | (598.00, 598.00) | SPS |  | 3170000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 528505 LEA_ROAD 3 115 528552 OIL_CENTER 3 115 1 | TBD | 3.11 | (217.00, 217.00) | SPS |  | 3110000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 547554 BAX492 2 69 547601 HOC404 2 69 1 | TBD | 3.59 | (106.00, 106.00) | EMDE |  | 3051500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 514774 HENESEY4 138 520535 BULFTTP4 138 1 | TBD | 2.53 | (395.00, 395.00) | OKGE/WFEC |  | 3036000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 514782 WODWRD 2 69 521096 WOODWRD2 69 1 | TBD | 3.5 | (140.00, 140.00) | OKGE/WFEC |  | 2975000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | TBD | 1.35 | (1793.00, 1793.00) | GRDA |  | 2970000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 530679 SEWRDMW3 115 539692 SEWARD 3 115 1 | TBD | 2.91 | (115.00, 115.00) | MIDW/SUNC |  | 2910000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508805 LIEBERM2 69 508812 OILCITY2 69 1 | TBD | 3.4 | (106.00, 106.00) | AEPW |  | 2890000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 531433 SCOTCTY3 115 531464 SETAB 3 115 1 | TBD | 2.77 | (394.00, 394.00) | SUNC |  | 2770000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 652200 GLENDIVE7 115 652404 DAWSONC7 115 1 | TBD | 2.73 | (176.00, 176.00) | WAPA |  | 2730000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 521049 SCLMNJC4 138 769060 G22-104-TAP 138 1 | TBD | 2.27 | (472.00, 472.00) | WFEC |  | 2724000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 504122 MCNAB 3 115 507456 TURK 3 115 1 | TBD | 2.65 | (394.00, 394.00) | AEPW |  | 2650000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 655945 WHEELS_T-MW7 115 655959 EPPING -MW7 115 1 | TBD | 2.6 | (260.00, 260.00) | WAPA |  | 2600000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | TBD | 2.6 | (260.00, 260.00) | SPS |  | 2600000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 529298 OMPVET-4 138 529302 OMALTUS4 138 1 | TBD | 2.13 | (395.00, 395.00) | OMPA |  | 2556000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 511501 TUTTLE4 138 511575 LEONARD4 138 1 | TBD | 2.12 | (395.00, 395.00) | AEPW |  | 2544000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1 | TBD | 2.49 | (394.00, 394.00) | SPS |  | 2490000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 511477 S.W.S.-4 138 521089 WASHITA4 138 1 | TBD | 2.05 | (717.00, 717.00) | AEPW/WFEC |  | 2460000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 520405 KGFSJCT4 138 520600 EKFSHTP4 138 1 | TBD | 2.03 | (211.00, 211.00) | WFEC |  | 2436000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 0.02 MVAR switched shunt at BEECRK4 138 kV | TBD |  |  | WERE |  | 2432500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 13 MVAR switched shunt at TAYLOR 4 138 kV | TBD |  |  | WERE |  | 2432500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 42 MVAR switched shunt at TV1MNDV4 138 kV | TBD |  |  | WERE |  | 2432500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 0.02 MVAR switched shunt at WELL 4WT 138 kV | TBD |  |  | AEPW |  | 2432500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Add 0.24 MVAR switched shunt at CASHION4 138 kV | TBD |  |  | WFEC |  | 2432500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Add 0.3 MVAR switched shunt at TWNLKJT4 138 kV | TBD |  |  | WFEC |  | 2432500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Add 0.33 MVAR switched shunt at TWNLAKE4 138 kV | TBD |  |  | WFEC |  | 2432500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 0.4 MVAR switched shunt at CRESENT4 138 kV | TBD |  |  | OKGE |  | 2432500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 0.4 MVAR switched shunt at GEN-2024-029 138 kV | TBD |  |  | OKGE |  | 2432500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 0.42 MVAR switched shunt at TWNLKSW4 138 kV | TBD |  |  | WFEC |  | 2432500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Add 0.5 MVAR switched shunt at FOURCTP4 138 kV | TBD |  |  | WFEC |  | 2432500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 0.5 MVAR switched shunt at RKY_RDG4 138 kV | TBD |  |  | AEPW |  | 2432500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Add 0.6 MVAR switched shunt at DOVER 4 138 kV | TBD |  |  | WFEC |  | 2432500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 0.7 MVAR switched shunt at G24-161-TAP 138 kV | TBD |  |  | AEPW |  | 2432500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 0.7 MVAR switched shunt at GEN-2024-157 138 kV | TBD |  |  | AEPW |  | 2432500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 0.7 MVAR switched shunt at GEN-2024-161 138 kV | TBD |  |  | AEPW |  | 2432500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 0.9 MVAR switched shunt at GEN-2024-157 138 kV | TBD |  |  | AEPW |  | 2432500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 1.2 MVAR switched shunt at LAKEP4WT 138 kV | TBD |  |  | AEPW |  | 2432500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Add 1.2 MVAR switched shunt at PINE ST4 138 kV | TBD |  |  | OKGE |  | 2432500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 10 MVAR switched shunt at CUSTER 4 138 kV | TBD |  |  | WFEC |  | 2432500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 16 MVAR switched shunt at CHILD4WT 138 kV | TBD |  |  | AEPW |  | 2432500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 16 MVAR switched shunt at NINMLTP4 138 kV | TBD |  |  | WFEC |  | 2432500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 18 MVAR switched shunt at FALCNRD4 138 kV | TBD |  |  | AEPW |  | 2432500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 2 MVAR switched shunt at G15048_1 138 kV | TBD |  |  | OKGE |  | 2432500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 21 MVAR switched shunt at WELLGS4 138 kV | TBD |  |  | AEPW |  | 2432500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Add 5 MVAR switched shunt at CTNWOOD4 138 kV | TBD |  |  | OKGE |  | 2432500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 5 MVAR switched shunt at SLKHILLS 4 138 kV | TBD |  |  | WFEC |  | 2432500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 6 MVAR switched shunt at REDHLSW4 138 kV | TBD |  |  | WFEC |  | 2432500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 6.3 MVAR switched shunt at HOLLIS 4 138 kV | TBD |  |  | AEPW |  | 2432500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 7 MVAR switched shunt at CL-AFTP4 138 kV | TBD |  |  | AEPW |  | 2432500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 8 MVAR switched shunt at ELLIS 4 138 kV | TBD |  |  | AEPW |  | 2432500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Rebuild line 514925 PENN 4 138 514926 SANTAFE4 138 1 | TBD | 2.02 | (265.00, 265.00) | OKGE |  | 2424000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508830 BALDWIN2 69 508842 WOODLWN2 69 1 | TBD | 2.73 | (69.00, 69.00) | AEPW |  | 2320500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 9 MVAR SVC at NEO184 2 69 kV | TBD |  |  | EMDE |  | 2300000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 30 MVAR SVC at ELDORDO2 69 kV | TBD |  |  | WFEC |  | 2300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 543098 CTY HIG2 69 543657 CORDERTP2 69 1 | TBD | 2.7 | (140.00, 140.00) | KCPL |  | 2295000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Rebuild line 514992 TURNER 4 138 516097 NORMHLL4 138 1 | TBD | 1.89 | (395.00, 395.00) | OKGE |  | 2268000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 533004 MONTGOM4 138 533006 TAYLOR 4 138 1 | TBD | 1.88 | (265.00, 265.00) | WERE |  | 2256000
Current Study | Steady State | OTHER / 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 338758 5HEBER.N# 161 505422 GREERSF5 161 1 | TBD | 1.4851 | (309.00, 309.00) | EES-EAI/SWPA |  | 2227580.5943
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | TBD |  |  | WAPA |  | 2212500
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Add 0.4 MVAR switched shunt at SHINDLER-ER7 115 kV | TBD |  |  | WAPA |  | 2212500
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Add 0.4 MVAR switched shunt at SNDCRKTP-MK7 115 kV | TBD |  |  | WAPA |  | 2212500
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Add 0.8 MVAR switched shunt at FARGO 7 115 kV | TBD |  |  | WAPA |  | 2212500
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Add 10 MVAR switched shunt at REDFIELD 115 kV | TBD |  |  | WAPA |  | 2212500
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Add 24 MVAR switched shunt at DAYTON__-ER7 115 kV | TBD |  |  | WAPA |  | 2212500
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Add 4.4 MVAR switched shunt at DESMET-ER7 115 kV | TBD |  |  | WAPA |  | 2212500
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Add 5 MVAR switched shunt at L11_____-MK7 115 kV | TBD |  |  | WAPA |  | 2212500
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Add 5 MVAR switched shunt at MOORHED7 115 kV | TBD |  |  | WAPA |  | 2212500
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Add 54 MVAR switched shunt at REDFELD-ER7 115 kV | TBD |  |  | WAPA |  | 2212500
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Add 0.7 MVAR switched shunt at SCOTBLF 7 115 kV | TBD |  |  | NPPD |  | 2212500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | NRIS | Add 0.09 MVAR switched shunt at GRAY CO3 115 kV | TBD |  |  | SUNC |  | 2212500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 1.1 MVAR switched shunt at SHARNSP3 115 kV | TBD |  |  | SUNC |  | 2212500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 12 MVAR switched shunt at BEELER 3 115 kV | TBD |  |  | SUNC |  | 2212500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 2.3 MVAR switched shunt at GRANT 3 115 kV | TBD |  |  | SUNC |  | 2212500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 20 MVAR switched shunt at MED-LDG3 115 kV | TBD |  |  | SUNC |  | 2212500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 21 MVAR switched shunt at GRANTTP3 115 kV | TBD |  |  | SUNC |  | 2212500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 21 MVAR switched shunt at LARNED3 115 kV | TBD |  |  | MIDW |  | 2212500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 21 MVAR switched shunt at RUSLSOL3 115 kV | TBD |  |  | SUNC |  | 2212500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 24 MVAR switched shunt at NESSCTY3 115 kV | TBD |  |  | SUNC |  | 2212500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 25 MVAR switched shunt at HIGHPT 3 115 kV | TBD |  |  | SUNC |  | 2212500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 30 MVAR switched shunt at GOVE 3 115 kV | TBD |  |  | SUNC |  | 2212500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 32 MVAR switched shunt at BARBER 3 115 kV | TBD |  |  | SUNC |  | 2212500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 40 MVAR switched shunt at PNTPR-GOAB3 115 kV | TBD |  |  | SUNC |  | 2212500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 40 MVAR switched shunt at SEGNTP 3 115 kV | TBD |  |  | MIDW |  | 2212500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 45 MVAR switched shunt at HUNTSVL3 115 kV | TBD |  |  | MIDW |  | 2212500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 6 MVAR switched shunt at CLIFTON3 115 kV | TBD |  |  | SUNC |  | 2212500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 63 MVAR switched shunt at SADLHRN3 115 kV | TBD |  |  | SUNC |  | 2212500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 8 MVAR switched shunt at IRS7 115 KV 115 kV | TBD |  |  | SUNC |  | 2212500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 8 MVAR switched shunt at RANSOM 3 115 kV | TBD |  |  | SUNC |  | 2212500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | NRIS | Add 8.4 MVAR switched shunt at MANTERT3 115 kV | TBD |  |  | SUNC |  | 2212500
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 12 MVAR switched shunt at NP-OCHILTRE3 115 kV | TBD |  |  | SPS |  | 2212500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TBD | 1 | (1793.00, 1793.00) | WERE |  | 2200000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | TBD | 1 | (1793.00, 1793.00) | GRDA |  | 2200000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | TBD | 1.8 | (395.00, 395.00) | AEPW |  | 2160000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | TBD | 1.8 | (395.00, 395.00) | AEPW |  | 2160000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1 | TBD | 2.13 | (598.00, 598.00) | SPS |  | 2130000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 543099 HIGNSVL2 69 543102 WHGNSVL2 69 1 | TBD | 2.5 | (140.00, 140.00) | KCPL |  | 2125000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 524300 HILLSIDE 3 115 524306 COULTER 3 115 1 | TBD | 2.11 | (598.00, 598.00) | SPS |  | 2110000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | TBD | 1.04 | (772.00, 772.00) | WAPA |  | 1976000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 509752 INOLATP4 138 510442 GUAVA 4 138 1 | TBD | 1.63 | (395.00, 395.00) | AEPW |  | 1956000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 505602 S BROWN4 138 769060 G22-104-TAP 138 1 | TBD | 1.62 | (717.00, 717.00) | SWPA/WFEC |  | 1944000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 659106 LELAND_O-BE4 230 659199 BASIN___-BE4 230 1 | TBD | 1 | (637.00, 637.00) | WAPA |  | 1900000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 507727 FLOURNY4 138 507732 GENMOTR4 138 1 | TBD | 1.56 | (395.00, 395.00) | AEPW |  | 1872000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | TBD | 1.46 | (395.00, 395.00) | OKGE |  | 1752000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Rebuild line 514959 FOSTER 4 138 515387 NEWDOMI4 138 1 | TBD | 1.44 | (281.00, 281.00) | OKGE |  | 1728000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | TBD | 0.75 | (2390.00, 2390.00) | NPPD |  | 1650000
Current Study | Steady State | 05 SOUTHWEST / 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | TBD | 0.75 | (1793.00, 1793.00) | SPS/SUNC |  | 1650000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Rebuild line 514893 XEROX 4 138 514896 MORGAN 4 138 1 | TBD | 1.37 | (472.00, 472.00) | OKGE |  | 1644000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 515105 WYNWOD 2 69 515113 CHIGLEY2 69 1 | TBD | 1.87 | (106.00, 106.00) | OKGE |  | 1589500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508089 WATLANT2 69 779100 G24-071-TAP 69 1 | TBD | 1.78 | (106.00, 106.00) | AEPW |  | 1513000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 533763 HUDSON-2 69 533770 PITTSBG2 69 1 | TBD | 1.75 | (69.00, 69.00) | WERE |  | 1487500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 520999 MOORLND4 138 786210 G24-308-TAP 138 1 | TBD | 1.19 | (395.00, 395.00) | WFEC |  | 1428000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Rebuild line 514893 XEROX 4 138 514894 CZECHAL4 138 1 | TBD | 1.17 | (472.00, 472.00) | OKGE |  | 1404000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Add 0.5 MVAR switched shunt at ORLAND-ER8 69 kV | TBD |  |  | WAPA |  | 1380000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Add 14.4 MVAR switched shunt at SW145-ER8 69 kV | TBD |  |  | WAPA |  | 1380000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Add 4 MVAR switched shunt at MOS-RDFL-ER8 69 kV | TBD |  |  | WAPA |  | 1380000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Add 5.5 MVAR switched shunt at LOOMIS-ER8 69 kV | TBD |  |  | WAPA |  | 1380000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 0.03 MVAR switched shunt at COL318_2 69 kV | TBD |  |  | EMDE |  | 1380000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 0.04 MVAR switched shunt at ELLIS 2 69 kV | TBD |  |  | SUNC |  | 1380000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 1.1 MVAR switched shunt at LIN314 2 69 kV | TBD |  |  | EMDE |  | 1380000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 1.1 MVAR switched shunt at ROC296 2 69 kV | TBD |  |  | EMDE |  | 1380000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 2.3 MVAR switched shunt at MON152 2 69 kV | TBD |  |  | EMDE |  | 1380000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 6.8 MVAR switched shunt at RANSOM 2 69 kV | TBD |  |  | SUNC |  | 1380000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 7 MVAR switched shunt at NEOSHON2 69 kV | TBD |  |  | WERE |  | 1380000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 0.04 MVAR switched shunt at SSLINC2 69 kV | TBD |  |  | GRDA |  | 1380000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 0.12 MVAR switched shunt at AFTN-EX2 69 kV | TBD |  |  | AEPW |  | 1380000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Add 0.12 MVAR switched shunt at LACEY 2 69 kV | TBD |  |  | WFEC |  | 1380000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Add 0.2 MVAR switched shunt at REDWING2 69 kV | TBD |  |  | OKGE |  | 1380000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Add 0.21 MVAR switched shunt at TURCRK 2 69 kV | TBD |  |  | OKGE |  | 1380000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Add 0.23 MVAR switched shunt at DOVERSW2 69 kV | TBD |  |  | WFEC |  | 1380000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 0.3 MVAR switched shunt at ROSVTAP2 69 kV | TBD |  |  | AEPW |  | 1380000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 0.7 MVAR switched shunt at ROSEVLT2 69 kV | TBD |  |  | WFEC |  | 1380000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 12 MVAR switched shunt at TXPLSTP2 69 kV | TBD |  |  | OKGE |  | 1380000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 12 MVAR switched shunt at WILDHRS2 69 kV | TBD |  |  | OKGE |  | 1380000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 15 MVAR switched shunt at SALISAWK 2 69 kV | TBD |  |  | GRDA |  | 1380000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 2 MVAR switched shunt at BIGPINEY2 69 kV | TBD |  |  | SWPA |  | 1380000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV | TBD |  |  | AEPW |  | 1380000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 30 MVAR switched shunt at NIXA NE2 69 kV | TBD |  |  | SWPA |  | 1380000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 4.8 MVAR switched shunt at COWSKIN2 69 kV | TBD |  |  | GRDA |  | 1380000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 6.3 MVAR switched shunt at GB-SHAMROCK 69 kV | TBD |  |  | AEPW |  | 1380000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 8 MVAR switched shunt at KANSAS 2 69 kV | TBD |  |  | GRDA |  | 1380000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | NRIS | Add 0.05 MVAR switched shunt at NP-VALERO_P2 69 kV | TBD |  |  | SPS |  | 1380000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | NRIS | Add 0.08 MVAR switched shunt at NP-SUB_A 2 69 kV | TBD |  |  | SPS |  | 1380000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 0.1 MVAR switched shunt at NP-LIPS_SHA2 69 kV | TBD |  |  | SPS |  | 1380000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | TBD |  |  | SPS |  | 1380000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 0.12 MVAR switched shunt at NP-BOOKER 2 69 kV | TBD |  |  | SPS |  | 1380000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 0.12 MVAR switched shunt at NP-ROGERS 2 69 kV | TBD |  |  | SPS |  | 1380000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 0.25 MVAR switched shunt at NP-PERYTN_G2 69 kV | TBD |  |  | SPS |  | 1380000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 1.6 MVAR switched shunt at NP-VALERO-G2 69 kV | TBD |  |  | SPS |  | 1380000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 2 MVAR switched shunt at POWELL CNR 2 69 kV | TBD |  |  | SPS |  | 1380000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 5 MVAR switched shunt at COLE 2 69 kV | TBD |  |  | SPS |  | 1380000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 7 MVAR switched shunt at NP-HARBOUR 2 69 kV | TBD |  |  | SPS |  | 1380000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 9.3 MVAR switched shunt at LE-LEWIS 2 69 kV | TBD |  |  | SPS |  | 1380000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TBD | 0.6 | (2390.00, 2390.00) | KCPL |  | 1320000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | TBD | 1.06 | (395.00, 395.00) | AEPW |  | 1272000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 524648 CARGILL 3 115 524655 FRIONA 3 115 1 | TBD | 1.27 | (115.00, 115.00) | SPS |  | 1270000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 507448 NHOPE 3 115 507449 NWHOPE 3 115 1 | TBD | 1.2 | (329.00, 329.00) | AEPW |  | 1200000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 511463 HOB-JCT4 138 781680 GEN-2024-157 138 1 | TBD | 1 | (395.00, 395.00) | AEPW |  | 1200000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | TBD | 0.93 | (211.00, 211.00) | AEPW |  | 1116000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 524281 34TH_ST_TP 3 115 524325 WESTERN 3 115 1 | TBD | 1.11 | (217.00, 217.00) | SPS |  | 1110000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508055 BLOOMBG2 69 783570 G24-220-TAP 69 1 | TBD | 1.23 | (69.00, 69.00) | AEPW |  | 1045500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 520995 MOORLND2 69 521197 CRTSJCT2 69 1 | TBD | 1.16 | (106.00, 106.00) | WFEC |  | 986000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 524281 34TH_ST_TP 3 115 524306 COULTER 3 115 1 | TBD | 0.96 | (217.00, 217.00) | SPS |  | 960000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 543096 MAYVWTP2 69 543100 AMOCOPL2 69 1 | TBD | 1.07 | (106.00, 106.00) | KCPL |  | 909500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 530570 GT BND 2 69 530596 WPRTTS 2 69 1 | TBD | 1.05 | (69.00, 69.00) | MIDW |  | 892500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 530605 REDLIN 3 115 786630 G24-322-TAP 115 1 | TBD | 0.86 | (115.00, 115.00) | MIDW |  | 860000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Rebuild line 647111 W BROCK8 69 647963 S963 8 69 1 | TBD | 1.01 | (106.00, 106.00) | OPPD |  | 858500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | TBD | 0.64 | (717.00, 717.00) | WFEC |  | 768000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | TBD | 0.58 | (395.00, 395.00) | OKGE |  | 696000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 | TBD | 0.55 | (395.00, 395.00) | OKGE |  | 660000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 533683 COFFSUB2 69 533685 CRA S 2 69 1 | TBD | 0.58 | (140.00, 140.00) | WERE |  | 493000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1 | TBD | 0.47 | (260.00, 260.00) | SPS |  | 470000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 505600 TUPELO 4 138 510881 ALLENGT4 138 1 | TBD | 0.38 | (211.00, 211.00) | AEPW/SWPA |  | 456000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 543657 CORDERTP2 69 543658 DOVER_TAP2 69 1 | TBD | 0.45 | (140.00, 140.00) | KCPL |  | 382500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 514947 CANADN-4 138 766111 G21-088-TAP 138 1 | TBD | 0.3 | (395.00, 395.00) | OKGE |  | 360000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 510887 ATOKA--4 138 782490 G24-184-TAP 138 1 | TBD | 0.28 | (211.00, 211.00) | AEPW |  | 336000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 515785 WINDFRM4 138 520999 MOORLND4 138 1 | TBD | 0.28 | (395.00, 395.00) | OKGE/WFEC |  | 336000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | TBD | 0.2 | (837.00, 837.00) | INDN |  | 300000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 652484 NUNDRWD4 230 652884 NUNDRWD-LNX3 230 Z | TBD | 0.14514 | (519.00, 519.00) | WAPA |  | 275765.6361
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 543098 CTY HIG2 69 543099 HIGNSVL2 69 1 | TBD | 0.3 | (140.00, 140.00) | KCPL |  | 255000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 652512 GROTON 7 115 652568 GROTONSOUTH7 115 Z | TBD | 0.25 | (598.00, 598.00) | WAPA |  | 250000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 528184 SENDERO +3 115 528193 BLACKRIVER 3 115 1 | TBD | 0.25 | (598.00, 598.00) | SPS |  | 250000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1 | TBD | 0.28 | (69.00, 69.00) | AEPW |  | 238000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | TBD | 0 | (880.00, 880.00) | WAPA |  | 220000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 514959 FOSTER 4 138 514962 DISCVRY4 138 1 | TBD | 0.18 | (281.00, 281.00) | OKGE |  | 216000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 520400 NOBLE4 138 520842 CANADNS4 138 1 | TBD | 0.18 | (265.00, 265.00) | WFEC |  | 216000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Rebuild line 652515 HURON 7 115 660009 HUR B TAP 115 1 | TBD | 0.2 | (176.00, 176.00) | WAPA |  | 200000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | TBD | 0.09 | (386.00, 386.00) | WERE |  | 171000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 520854 CIVIT 4 138 782580 G24-187-TAP 138 1 | TBD | 0.12 | (265.00, 265.00) | WFEC |  | 144000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | TBD | 0 | (424.00, 424.00) | AEPW/GRDA |  | 120000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | TBD | 0 | (275.00, 275.00) | AEPW/GRDA |  | 120000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 530624 ST JOHN3 115 539696 ST-JOHN3 115 Z1 | TBD | 0.1 | (326.00, 326.00) | MIDW/SUNC |  | 100000
Current Study | Steady State | OTHER / 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 620263 FORMN 7 115 652438 FORMAN 7 115 1 | TBD | 0.1 | (176.00, 176.00) | OTP/WAPA |  | 100000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1 | TBD | 0.06 | (140.00, 140.00) | OPPD |  | 51000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 652391 WILLISTON27 115 652421 WILISTN7 115 Z1 | TBD | 0.035484 | (217.00, 217.00) | WAPA |  | 35483.8712
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | LeBrock 345 kV Substation GEN-2024-343 Interconnection (Non-Shared NU) (AEP) | 171855 | - | - | AEP | 42 | 59500000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | 345 kV Crossroads - Eddy County 345 kV Line GEN-2024-221 Interconnection (Non-Shared NU) (SPS) | 171691 | - | - | SPS | 0 | 45536712.63
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Maddox 115 kV Substation GEN-2024-371 Interconnection (Non-Shared NU) (SPS) | 171889 | - | - | SPS | 0 | 44215863.76
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Crossroads - Hobbs 345 kV Substation GEN-2024-073 Interconnection (TOIF) (NEET) | 171545 | - | - | NEET | 0 | 42764795
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Sibley 345 kV Substation GEN-2024-352 Interconnection (Non-Shared NU) (WERE) | 171952 | - | - | WERE | 60 | 42429444
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Spearville - Holcomb 345 kV Line GEN-2024-193/194 Interconnection (Shared NU) (SUNC) | 171661 | - | - | SEPC | 60 | 40864891
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Springbrook - Tande 345 kV Line GEN-2024-082 Interconnection (TOIF) (BEPC) | 171556 | - | - | BEPC | 60 | 38027515
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Jarbalo 115 kV Substation GEN-2024-121 Interconnection (Non-Shared NU) (WERE) | 171917 | - | - | WERE | 42 | 33543364
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Reno - Summit 345 kV Line GEN-2024-142 Interconnection (Non-Shared NU) (WERE) | 171923 | - | - | WERE | 60 | 33532966
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Asbury 161 kV Substation GEN-2024-259 Interconnection (Non-Shared NU) (EMDE) | 171743 | - | - | EDE | 42 | 33306052
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Bushland 230 kV Substation GEN-2024-153 Interconnection (Non-Shared NU) (SPS) | 171618 | - | - | SPS | 0 | 33296957.63
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Stranger Creek - 87th Street 345 kV line GEN-2024-253 Interconnection (Non-Shared NU) (WERE) | 171937 | - | - | WERE | 60 | 33058407
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Tecumseh Hill - Swissvale 230kV Line GEN-2024-276/277 Interconnection (Shared NU) (WERE) | 171942 | - | - | WERE | 60 | 32644437
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Neosho Ridge - Caney River 345 kV Line GEN-2024-125 Interconnection (Non-Shared NU) (WERE) | 171919 | - | - | WERE | 60 | 31994301
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Caney River - Neosho 345 kV Line GEN-2024-129 Interconnection (Non-Shared NU) (WERE) | 171921 | - | - | WERE | 60 | 31994301
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Sibley - Hawthorne 345 kV line GEN-2024-217 Interconnection (Non-Shared NU) (WERE) | 171933 | - | - | WERE | 60 | 31935383
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Eddy County - Crossroads 345 kV Line GEN-2024-278 Interconnection (Non-Shared NU) (SPS) | 171763 | - | - | SPS | 0 | 31250321.55
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Forman 115 kV Substation GEN-2024-034 Interconnection (Non-Shared NU) (WAPA) | 171503 | - | - | WAPA | 72 | 30940000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Roswell Interchange 115 kV Substation GEN-2024-186 Interconnection (Non-Shared NU) (SPS) | 171654 | - | - | SPS | 0 | 30757015
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Antelope Valley - Broadland 345 kV Line GEN-2024-284 Interconnection (Non-Shared NU) (BEPC) | 171772 | - | - | BEPC | 60 | 30292999
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Crossroads - Tolk 345 kV Line GEN-2024-043 Interconnection (Non-Shared NU) (SPS) | 171516 | - | - | SPS | 0 | 29754372.46
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Wolf Creek - Blackberry 345 kV Line GEN-2024-139 Interconnection (Non-Shared NU) (NEET) | 171607 | - | - | NEET | 0 | 28818600
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Wolf Creek - Blackberry 345 kV Line GEN-2024-258 Interconnection (Non-Shared NU) (NEET) | 171741 | - | - | NEET | 0 | 28818600
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Wolf Creek - Blackberry 345 kV Line GEN-2024-287 Interconnection (Non-Shared NU) (NEET) | 171778 | - | - | NEET | 0 | 28818600
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Crossroads-Hobbs-Roadrunner 345 kV Line GEN-2024-124 Interconnection (Non-Shared NU) (NEET) | 171594 | - | - | NEET | 0 | 28818600
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Lydia - Welsh 345 kV Line GEN-2024-068 Interconnection (Non-Shared NU) (AEP) | 171540 | - | - | AEP | 42 | 28225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Pittsburg - Johnston County 345 kV line GEN-2024-165 Interconnection (Non-Shared NU) (AEP) | 171634 | - | - | AEP | 42 | 28225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Crockett - Rocky Creek 345 kV line GEN-2024-232 Interconnection (Non-Shared NU) (AEP) | 171703 | - | - | AEP | 42 | 28225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Sooner - Wekiwa 345 kV line GEN-2024-235 Interconnection (Non-Shared NU) (AEP) | 171707 | - | - | AEP | 42 | 28225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Neosho - Delaware 345 kV line GEN-2024-240 Interconnection (Non-Shared NU) (AEP) | 171713 | - | - | AEP | 42 | 28225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Pittsburg - Valliant 345 kV Line GEN-2024-316 Interconnection (Non-Shared NU) (AEP) | 171811 | - | - | AEP | 42 | 28225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Pittsburg - Johnston County 345 kV line GEN-2024-338 Interconnection (Non-Shared NU) (AEP) | 171849 | - | - | AEP | 42 | 28225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Riverside – Redbud 345 kV line GEN-2024-340 Interconnection (Non-Shared NU) (AEP) | 171851 | - | - | AEP | 42 | 28225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Longwood - El Dorado 345 kV Line GEN-2024-379 Interconnection (Non-Shared NU) (AEP) | 171901 | - | - | AEP | 42 | 28225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Lawton East Side - Oklaunion North 345 kV GEN-2024-229/230 Interconnection (Shared NU) (AEP) | 171699 | - | - | AEP | 42 | 28225000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Tolk - Crossroads 345 kV line GEN-2024-109 Interconnection (Non-Shared NU) (SPS) | 171576 | - | - | SPS | 0 | 27903630.08
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Hobbs - Yoakum 345 kV Line GEN-2024-365 Interconnection (Non-Shared NU) (SPS) | 171879 | - | - | SPS | 0 | 27790566.6
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Hobbs - Yoakum 345 kV Line GEN-2024-365/366 Interconnection (Shared NU) (SPS) | 171881 | - | - | SPS | 0 | 27790566.6
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Tuco - Whirlwind 345 kV line GEN-2024-041/042 Interconnection (Shared NU) (SPS) | 171514 | - | - | SPS | 0 | 27720322.3
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Potter Co - Hitchland 345 kV Line GEN-2024-266 Interconnection (Non-Shared NU) (SPS) | 171749 | - | - | SPS | 0 | 27605699.58
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Oasis - San Juan Mesa Wind 230 kV Line GEN-2024-159 Interconnection (Non-Shared NU) (SPS) | 171626 | - | - | SPS | 0 | 27237303
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Arbuckle 138 kV Substation GEN-2024-164 Interconnection (Non-Shared NU) (OGE) | 171632 | - | - | OGE | 36 | 27000000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Chaves County - San Juan Wind 230 kV Line GEN-2024-271 Interconnection (Non-Shared NU) (SPS) | 171755 | - | - | SPS | 0 | 26356389.29
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Maurine - New Underwood 230 kV Line GEN-2024-282/283 Interconnection (Shared NU) (WAPA) | 171770 | - | - | WAPA | 84 | 26230000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Sundown-Amaco-Yoakum 230 kV Substation GEN-2024-015 Interconnection (Non-Shared NU) (SPS) | 171480 | - | - | SPS | 0 | 24794114
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Butler 138 kV Substation GEN-2024-330 Interconnection (Non-Shared NU) (WERE) | 171948 | - | - | WERE | 48 | 24263481
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Hitchland-Moore 230 kV line GEN-2024-045/046 Interconnection (Shared NU) (SPS) | 171521 | - | - | SPS | 0 | 23027231
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Jal - Teague 115 kV Line GEN-2024-281 Interconnection (Non-Shared NU) (SPS) | 171767 | - | - | SPS | 0 | 22838049.8
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | S3458 to Cooper 345 kV line GEN-2024-040 Interconnection (Non-Shared NU) (OPPD) | 171511 | - | - | OPPD | 40 | 22250000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Taylor Switching Station 115 kV Substation GEN-2024-306 Interconnection (Non-Shared NU) (SPS) | 171802 | - | - | SPS | 0 | 21550441.87
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Lawton East Side 345 kV Substation GEN-2024-367 Interconnection (Non-Shared NU) (AEP) | 171883 | - | - | AEP | 36 | 20900000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Cooper - S12080 161 kV line GEN-2024-038 Interconnection (Non-Shared NU) (OPPD) | 171507 | - | - | OPPD | 40 | 20250000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Humboldt - S1280 161 kV line GEN-2024-039 Interconnection (Non-Shared NU) (OPPD) | 171509 | - | - | OPPD | 40 | 20250000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | AES 5 345 kV Substation GEN-2024-299 Interconnection (Non-Shared NU) (OGE) | 171794 | - | - | OGE | 48 | 20000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Muskogee - Ft. Smith 345 kV Line GEN-2024-113 Interconnection (Non-Shared NU) (OGE) | 171578 | - | - | OGE | 36 | 18000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Gracemont - Lawton 345 kV Line GEN-2024-128 Interconnection (Non-Shared NU) (OGE) | 171596 | - | - | OGE | 36 | 18000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Seminole - Muskogee 345 kV line GEN-2024-236 Interconnection (Non-Shared NU) (OGE) | 171709 | - | - | OGE | 36 | 18000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Riverside - Redbud Switch 345 kV Line GEN-2024-344 Interconnection (Non-Shared NU) (OGE) | 171859 | - | - | OGE | 36 | 18000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Muskogee - Pittsburg 345 kV Line GEN-2024-296/297/298 Interconnection (Shared NU) (OGE) | 171792 | - | - | OGE | 36 | 18000000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Post Rock - Macon 345 kV Line GEN-2024-016 Interconnection (Non-Shared NU) (ITCGP) | 171482 | - | - | ITCGP | 34 | 17836757
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Farmland - Delaware 138 kV line GEN-2024-058 Interconnection (Non-Shared NU) (AEP) | 171530 | - | - | AEP | 36 | 17175000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Coffeyville Tap - North Bartlesville 138kV Line GEN-2024-117 Interconnection (Non-Shared NU) (AEP) | 171582 | - | - | AEP | 36 | 17175000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Center - Tenaha 138 kV Line GEN-2024-123 Interconnection (Non-Shared NU) (AEP) | 171592 | - | - | AEP | 36 | 17175000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Hobart - Martha 138 kV Line GEN-2024-157 Interconnection (Non-Shared NU) (AEP) | 171622 | - | - | AEP | 36 | 17175000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Altus Jct - Snyder 138 kV Line GEN-2024-158 Interconnection (Non-Shared NU) (AEP) | 171624 | - | - | AEP | 36 | 17175000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Hobart - Martha 138 kV Line GEN-2024-161 Interconnection (Non-Shared NU) (AEP) | 171628 | - | - | AEP | 36 | 17175000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Atoka to Lehigh 138 kV line GEN-2024-184 Interconnection (Non-Shared NU) (AEP) | 171652 | - | - | AEP | 36 | 17175000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Tulsa North - American Airlines 138 kV Line GEN-2024-318 Interconnection (Non-Shared NU) (AEP) | 171815 | - | - | AEP | 36 | 17175000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Coffeyville Tap - North Barlettsville 138 kV Line GEN-2024-346 Interconnection (Non-Shared NU) (AEP) | 171863 | - | - | AEP | 36 | 17175000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Cooper Ranch 115 kV Substation GEN-2024-351 Interconnection (Non-Shared NU) (SPS) | 171865 | - | - | SPS | 0 | 17105898.86
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Lubbock South 230 kV Substation GEN-2024-355 Interconnection (Non-Shared NU) (SPS) | 171867 | - | - | SPS | 0 | 16784151
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Hosston - Plain Dealing 69 kV Line GEN-2024-044 Interconnection (Non-Shared NU) (AEP) | 171518 | - | - | AEP | 36 | 16475000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rodessa - Bloomberg 69 kV Line GEN-2024-220 Interconnection (Non-Shared NU) (AEP) | 171689 | - | - | AEP | 36 | 16475000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Superior - Jefferson 69 kV Line GEN-2024-305 Interconnection (Non-Shared NU) (AEP) | 171800 | - | - | AEP | 36 | 16475000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Jaggard 115 kV Substation GEN-2024-320 Interconnection (Non-Shared NU) (WERE) | 171946 | - | - | WERE | 48 | 16424539
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Orrick 161 kV Substation GEN-2024-167 Interconnection (Non-Shared NU) (WERE) | 171927 | - | - | WERE | 48 | 16202977
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | West Southwest 161 kV Substation GEN-2024-375 Interconnection (Non-Shared NU) (WERE) | 171956 | - | - | WERE | 48 | 15638683
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Butler - Nevada 161 kV line GEN-2024-055 Interconnection (Non-Shared NU) (WERE) | 171905 | - | - | WERE | 48 | 15550547
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Twin Church 230 kV Substation GEN-2024-162 Interconnection (Non-Shared NU) (NPPD) | 171630 | - | - | NPPD | 48 | 0
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Hobbs 115 kV Line GEN-2024-265 Interconnection (Non-Shared NU) (SPS) | 171747 | - | - | SPS | 0 | 15220699.21
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Skellyville 115 kV Tap Substation GEN-2024-257 Interconnection (Non-Shared NU) (SUNC) | 171739 | - | - | SEPC | 40 | 14700000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Tulsa North - GR Energy Center 345 kV Line GEN-2024-171 Interconnection (Non-Shared NU) (GRDA) | 171638 | - | - | GRDA | 36 | 14597250
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Creswell 138 kV Substation GEN-2024-061 Interconnection (Non-Shared NU) (WERE) | 171907 | - | - | WERE | 48 | 14040446
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Geneva 115 kV Substation GEN-2024-168 Interconnection (Non-Shared NU) (NPPD) | 171636 | - | - | NPPD | 48 | 13500000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | 145 JOPLIN WEST 7TH 161 kV Substation GEN-2024-091 Interconnection (Non-Shared NU) (EDE) | 171568 | - | - | EDE | 42 | 12949695
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Pirkey 345 kV Substation GEN-2024-377 Interconnection (Non-Shared NU) (AEP) | 171899 | - | - | AEP | 36 | 12750000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Elm Creek - North Manhattan 230 kV Line GEN-2024-209 Interconnection (Non-Shared NU) (SUNC) | 171671 | - | - | SEPC | 48 | 12600000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | AES 5 161 kV Substation GEN-2024-286 Interconnection (Non-Shared NU) (OGE) | 171776 | - | - | OGE | 0 | 12000000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Reeds Spring - Aurora 161 kV Line GEN-2024-084 Interconnection (Non-Shared NU) (EMDE) | 171560 | - | - | EDE | 42 | 11956657
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | St. Francis Tap 115 kV Substation GEN-2024-210 Interconnection (Non-Shared NU) (SUNC) | 171673 | - | - | SEPC | 40 | 11900000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Sawyer 115 kV Substation GEN-2024-272 Interconnection (Non-Shared NU) (KACY) | 171757 | - | - | KACY | 40 | 11900000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rice to Circle 230 kV Line GEN-2024-228 Interconnection (Non-Shared NU) (MIDW) | 171696 | - | - | MIDW | 36 | 11100578.58
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Otis 115 kV Substation GEN-2024-085 Interconnection (Non-Shared NU) (SUNC) | 171562 | - | - | SEPC | 40 | 10500000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Cimarron River 115 kV Substation GEN-2024-218 Interconnection (Non-Shared NU) (SUNC) | 171685 | - | - | SEPC | 40 | 10500000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Harper - Anthony 138 kV Line GEN-2024-274 Interconnection (Non-Shared NU) (SUNC) | 171761 | - | - | SEPC | 40 | 10500000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Pearl 115 kV Substation GEN-2024-273 Interconnection (Non-Shared NU) (SPS) | 171759 | - | - | SPS | 0 | 10211151
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | New Beatrice Power Station 345 kV GEN-2024-018/019/022/023 Interconnection (Shared NU) (NPPD) | 171492 | - | - | NPPD | 60 | 10000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | LeBrock 345 kV Substation GEN-2024-343 Interconnection (TOIF) (AEP) | 171854 | - | - | AEP | 42 | 9700000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | FREMONT7 115 kV Substation GEN-2024-065 Interconnection (Non-Shared NU) (NPPD) | 171536 | - | - | NPPD | 48 | 9500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Pittsburgh 345 kV Substation GEN-2024-341 Interconnection (Non-Shared NU) (AEP) | 171853 | - | - | AEP | 36 | 9250000
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Dawson County - Miles City 230 kV Line GEN-2024-216 Interconnection (Non-Shared NU) (WAPA) | 171683 | - | - | WAPA | 74 | 9073864
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Belfield 230 kV Substation GEN-2024-326 Interconnection (Non-Shared NU) (WAPA) | 171829 | - | - | WAPA | 72 | 8970000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Pringle 230 kV Substation GEN-2024-077 Interconnection (Non-Shared NU) (SPS) | 171548 | - | - | SPS | 0 | 8790893
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Andrews County 345 kV Substation GEN-2024-280 Interconnection (Non-Shared NU) (SPS) | 171765 | - | - | SPS | 0 | 8636936.73
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Crossroads 345 kV Substation GEN-2024-303 Interconnection (Non-Shared NU) (SPS) | 171796 | - | - | SPS | 0 | 8636936.73
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Crossroads 345 kV Substation GEN-2024-304 Interconnection (Non-Shared NU) (SPS) | 171798 | - | - | SPS | 0 | 8636936.73
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Jonesboro - Independence County 161 kV Line GEN-2024-114 Interconnection (Non-Shared NU) (SWPA) | 171580 | - | - | SWPA | 48 | 8600000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Clarksville Ozark 161 kV line GEN-2024-312 Interconnection (Non-Shared NU) (SWPA) | 171809 | - | - | SWPA | 48 | 8600000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Sierra 115 kV Substation GEN-2024-325 Interconnection (Non-Shared NU) (SPS) | 171827 | - | - | SPS | 0 | 8107736.66
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | AES 5 345 kV Substation GEN-2024-299 Interconnection (TOIF) (OGE) | 171793 | - | - | OGE | 48 | 8000000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Plant X 230 kV Substation GEN-2024-063 Interconnection (Non-Shared NU) (SPS) | 171534 | - | - | SPS | 0 | 7964621.39
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Redlin - Beach3 115 kV line GEN-2024-322 Interconnection (Non-Shared NU) (MIDW) | 171821 | - | - | MIDW | 36 | 7964021.52
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Archie - Clinton 161 kV Line GEN-2024-289 Interconnection (Non-Shared NU) (WERE) | 171944 | - | - | WERE | 48 | 7763701
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Waverly 115 kV Substation GEN-2024-051 Interconnection (Non-Shared NU) (LES) | 171525 | - | - | LES | 0 | 7533500
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Waverly 115 kV Substation GEN-2024-051 Interconnection (TOIF) (LES) | 171524 | - | - | LES | 9 | 7533500
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Pawnee Lake 115 kV Substation GEN-2024-173 Interconnection (Non-Shared NU) (NPPD) | 171640 | - | - | NPPD | 48 | 7500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Spring Creek 345 kV Substation GEN-2024-255 Interconnection (Non-Shared NU) (OGE) | 171737 | - | - | OGE | 36 | 7500000
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | BASIN__-BE4 230 kV Substation GEN-2024-141 Interconnection (Non-Shared NU) (BEPC) | 171611 | - | - | BEPC | 60 | 7362181
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Little Missouri 230 kV Substation GEN-2024-328 Interconnection (Non-Shared NU) (BEPC) | 171833 | - | - | BEPC | 60 | 7362181
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Groton 345 kV Substation GEN-2024-035 Interconnection (Non-Shared NU) (BEPC) | 171505 | - | - | BEPC | 60 | 7125379
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Stegall 345 kV Substation GEN-2024-374 Interconnection (Non-Shared NU) (BEPC) | 171895 | - | - | BEPC | 60 | 7125379
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Holcomb 345 kV Substation GEN-2024-102 Interconnection (Non-Shared NU) (SUNC) | 171574 | - | - | SEPC | 52 | 7000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Lexington 138 kV Substation GEN-2024-119 Interconnection (Non-Shared NU) (WFEC) | 171586 | - | - | WFEC | 60 | 7000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Civit 138 kV Substation GEN-2024-187 Interconnection (Non-Shared NU) (WFEC) | 171656 | - | - | WFEC | 60 | 7000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Durantp4 - Sclmnjc4 138 kV Line GEN-2024-267 Interconnection (Non-Shared NU) (WFEC) | 171751 | - | - | WFEC | 60 | 7000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Okeene - Mooreland 138 kV line GEN-2024-308 Interconnection (Non-Shared NU) (WFEC) | 171804 | - | - | WFEC | 60 | 7000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Unger - West Bank Tap 138 kV Line GEN-2024-052/373 Interconnection (Shared NU) (WFEC) | 171893 | - | - | WFEC | 60 | 7000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Cow Creek - Morrison 138 kV line GEN-2024-056 Interconnection (Non-Shared NU) (OGE) | 171528 | - | - | OGE | 36 | 7000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Chigley - Oaklawn 138 kV Line GEN-2024-219 Interconnection (Non-Shared NU) (OGE) | 171687 | - | - | OGE | 36 | 7000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Sunnyside - Pooleville 138 kV line GEN-2024-337 Interconnection (Non-Shared NU) (OGE) | 171847 | - | - | OGE | 36 | 7000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Spring Valley - Warwick 138 kV line GEN-2024-361 Interconnection (Non-Shared NU) (OGE) | 171873 | - | - | OGE | 36 | 7000000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Pleasant Hills 230 kV Substation GEN-2024-089 Interconnection (Non-Shared NU) (SPS) | 171566 | - | - | SPS | 0 | 6566666.79
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Dragon 345 kV Substation GEN-2024-317 Interconnection (Non-Shared NU) (SPS) | 171813 | - | - | SPS | 0 | 6564758.74
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Skellyville 115 kV Tap Substation GEN-2024-257 Interconnection (TOIF) (SUNC) | 171738 | - | - | SEPC | 40 | 6300000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Pirkey 138 kV Substation GEN-2024-178 Interconnection (Non-Shared NU) (AEP) | 171646 | - | - | AEP | 30 | 6300000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Texas County Interchange 115 kV Substation GEN-2024-244 Interconnection (Non-Shared NU) (SPS) | 171721 | - | - | SPS | 0 | 6281531.43
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Ink Basin 230 kV Substation GEN-2024-336 Interconnection (Non-Shared NU) (SPS) | 171845 | - | - | SPS | 0 | 6052126.09
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Asbury 161 kV Substation GEN-2024-259 Interconnection (TOIF) (EMDE) | 171742 | - | - | EDE | 42 | 5877539
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Round Up 345 kV Substation GEN-2024-331 Interconnection (Non-Shared NU) (BEPC) | 171837 | - | - | BEPC | 60 | 5716377
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Franklin 69 kV Substation GEN-2024-069 Interconnection (Non-Shared NU) (WERE) | 171909 | - | - | WERE | 48 | 5700860
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Degrasse 345 kV Substation GEN-2024-134 Interconnection (Non-Shared NU) (OGE) | 171600 | - | - | OGE | 36 | 5500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Degrasse 345 kV Substation GEN-2024-135 Interconnection (Non-Shared NU) (OGE) | 171602 | - | - | OGE | 36 | 5500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Pittsburg - Johnston County 345 kV line GEN-2024-165 Interconnection (TOIF) (AEP) | 171633 | - | - | AEP | 42 | 5425000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | John W Turk Jr Power Plant 345 kV Substation GEN-2024-226 Interconnection (TOIF) (AEP) | 171692 | - | - | AEP | 36 | 5425000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | John W Turk Jr Power Plant 345 kV Substation GEN-2024-227 Interconnection (TOIF) (AEP) | 171693 | - | - | AEP | 36 | 5425000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Lawton East Side - Oklaunion North 345 kV GEN-2024-229 Interconnection (TOIF) (AEP) | 171697 | - | - | AEP | 42 | 5425000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Lawton East Side - Oklaunion North 345 kV GEN-2024-230 Interconnection (TOIF) (AEP) | 171698 | - | - | AEP | 42 | 5425000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Elm Creek - North Manhattan 230 kV Line GEN-2024-209 Interconnection (TOIF) (SUNC) | 171670 | - | - | SEPC | 48 | 5400000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Setab 345 kV Substation GEN-2024-136/137/138/144 Interconnection (Shared NU) (SUNC) | 171614 | - | - | SEPC | 52 | 5338489
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Santa Fe 115 kV Substation GEN-2024-030 Interconnection (Non-Shared NU) (SUNC) | 171499 | - | - | SEPC | 40 | 5250000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Lydia 345 kV Substation GEN-2024-025 Interconnection (TOIF) (AEP) | 171494 | - | - | AEP | 36 | 5225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Lydia - Welsh 345 kV Line GEN-2024-068 Interconnection (TOIF) (AEP) | 171539 | - | - | AEP | 42 | 5225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Chisholm 345 kV Substation GEN-2024-154 Interconnection (TOIF) (AEP) | 171619 | - | - | AEP | 36 | 5225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Crockett - Rocky Creek 345 kV line GEN-2024-232 Interconnection (TOIF) (AEP) | 171702 | - | - | AEP | 42 | 5225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Sooner - Wekiwa 345 kV line GEN-2024-235 Interconnection (TOIF) (AEP) | 171706 | - | - | AEP | 42 | 5225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Neosho - Delaware 345 kV line GEN-2024-240 Interconnection (TOIF) (AEP) | 171712 | - | - | AEP | 42 | 5225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Pittsburgh 345 kV Substation GEN-2024-250 Interconnection (TOIF) (AEP) | 171728 | - | - | AEP | 36 | 5225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Pittsburg - Valliant 345 kV Line GEN-2024-316 Interconnection (TOIF) (AEP) | 171810 | - | - | AEP | 42 | 5225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Pittsburg - Johnston County 345 kV line GEN-2024-338 Interconnection (TOIF) (AEP) | 171848 | - | - | AEP | 42 | 5225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Riverside – Redbud 345 kV line GEN-2024-340 Interconnection (TOIF) (AEP) | 171850 | - | - | AEP | 42 | 5225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Pittsburgh 345 kV Substation GEN-2024-341 Interconnection (TOIF) (AEP) | 171852 | - | - | AEP | 36 | 5225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Delaware 345 kV Substation GEN-2024-345 Interconnection (TOIF) (AEP) | 171860 | - | - | AEP | 36 | 5225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Lawton East Side 345 kV Substation GEN-2024-367 Interconnection (TOIF) (AEP) | 171882 | - | - | AEP | 36 | 5225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Pirkey 345 kV Substation GEN-2024-377 Interconnection (TOIF) (AEP) | 171898 | - | - | AEP | 36 | 5225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Longwood - El Dorado 345 kV Line GEN-2024-379 Interconnection (TOIF) (AEP) | 171900 | - | - | AEP | 42 | 5225000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Jeffrey EC 345 kV Substation GEN-2024-249 Interconnection (Non-Shared NU) (WERE) | 171935 | - | - | WERE | 60 | 5202083
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | St. Francis Tap 115 kV Substation GEN-2024-210 Interconnection (TOIF) (SUNC) | 171672 | - | - | SEPC | 40 | 5100000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Sawyer 115 kV Substation GEN-2024-272 Interconnection (TOIF) (KACY) | 171756 | - | - | KACY | 40 | 5100000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Atoka 115 kV Substation GEN-2024-251 Interconnection (Non-Shared NU) (SPS) | 171731 | - | - | SPS | 0 | 5047349.56
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | 145 JOPLIN WEST 7TH 161 kV Substation GEN-2024-091 Interconnection (TOIF) (EDE) | 171567 | - | - | EDE | 42 | 5035992
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Tuco - Whirlwind 345 kV line GEN-2024-041 Interconnection (TOIF) (SPS) | 171512 | - | - | SPS | 0 | 5024078.97
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Tuco - Whirlwind 345 kV line GEN-2024-042 Interconnection (TOIF) (SPS) | 171513 | - | - | SPS | 0 | 5024078.97
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Olive Creek 345 kV Substation GEN-2024-020 Interconnection (Non-Shared NU) (NPPD) | 171488 | - | - | NPPD | 60 | 5000000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Olive Creek 345 kV Substation GEN-2024-021 Interconnection (Non-Shared NU) (NPPD) | 171490 | - | - | NPPD | 60 | 5000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | AES 5 161 kV Substation GEN-2024-286 Interconnection (TOIF) (OGE) | 171775 | - | - | OGE | 48 | 5000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Muskogee - Pittsburg 345 kV Line GEN-2024-291 Interconnection (Non-Shared NU) (OGE) | 171782 | - | - | OGE | 36 | 5000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Muskoge7 345 kV Substation GEN-2024-293 Interconnection (Non-Shared NU) (OGE) | 171784 | - | - | OGE | 36 | 5000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Seminole 345 kV Substation GEN-2024-321 Interconnection (Non-Shared NU) (OGE) | 171819 | - | - | OGE | 36 | 5000000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | 345 kV Crossroads - Eddy County 345 kV Line GEN-2024-221 Interconnection (TOIF) (SPS) | 171690 | - | - | SPS | 0 | 4872126.25
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Portales 115 kV Substation GEN-2024-092 Interconnection (Non-Shared NU) (SPS) | 171570 | - | - | SPS | 0 | 4844709.15
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Antelope Valley - Broadland 345 kV Line GEN-2024-284 Interconnection (TOIF) (BEPC) | 171771 | - | - | BEPC | 60 | 4791248
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Crossroads - Tolk 345 kV Line GEN-2024-043 Interconnection (TOIF) (SPS) | 171515 | - | - | SPS | 0 | 4774296.21
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Crocker 345 kV Substation GEN-2024-285 Interconnection (Non-Shared NU) (BEPC) | 171774 | - | - | BEPC | 60 | 4745484
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Hobbs - Yoakum 345 kV Line GEN-2024-365 Interconnection (TOIF) (SPS) | 171878 | - | - | SPS | 0 | 4701870.35
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Hobbs - Yoakum 345 kV Line GEN-2024-366 Interconnection (TOIF) (SPS) | 171880 | - | - | SPS | 0 | 4701870.35
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Tolk - Crossroads 345 kV line GEN-2024-109 Interconnection (TOIF) (SPS) | 171575 | - | - | SPS | 0 | 4671893.78
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | ITC Great Plains Saddle 345 kV Substation GEN-2024-189 Interconnection (Non-Shared NU) (ITCGP) | 171658 | - | - | ITCGP | 30 | 4630438
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | ITC Hugo 7 345 kV Substation GEN-2024-323 Interconnection (Non-Shared NU) (ITCGP) | 171823 | - | - | ITCGP | 30 | 4630437
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Cirrus 345 kV Substation GEN-2024-067 Interconnection (Non-Shared NU) (ITCGP) | 171538 | - | - | ITCGP | 30 | 4630435
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Eddy - Chaves 230 kV line GEN-2024-310 Interconnection (TOIF) (SPS) | 171805 | - | - | SPS | 0 | 4549755.92
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Eddy - Chaves 230 kV line GEN-2024-311 Interconnection (TOIF) (SPS) | 171806 | - | - | SPS | 0 | 4549755.92
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Andrews County 345 kV Substation GEN-2024-280 Interconnection (TOIF) (SPS) | 171764 | - | - | SPS | 0 | 4502736.58
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Crossroads 345 kV Substation GEN-2024-303 Interconnection (TOIF) (SPS) | 171795 | - | - | SPS | 0 | 4502736.58
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Crossroads 345 kV Substation GEN-2024-304 Interconnection (TOIF) (SPS) | 171797 | - | - | SPS | 0 | 4502736.58
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Otis 115 kV Substation GEN-2024-085 Interconnection (TOIF) (SUNC) | 171561 | - | - | SEPC | 40 | 4500000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Cimarron River 115 kV Substation GEN-2024-218 Interconnection (TOIF) (SUNC) | 171684 | - | - | SEPC | 40 | 4500000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Harper - Anthony 138 kV Line GEN-2024-274 Interconnection (TOIF) (SUNC) | 171760 | - | - | SEPC | 40 | 4500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Kelley Avenue 138 kV GEN-2024-333 Interconnection (Non-Shared NU) (OGE) | 171841 | - | - | OGE | 36 | 4500000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Reno County 115 kV Substation GEN-2024-176 Interconnection (Non-Shared NU) (WERE) | 171931 | - | - | WERE | 48 | 4480714
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Bushland 230 kV Substation GEN-2024-153 Interconnection (TOIF) (SPS) | 171617 | - | - | SPS | 0 | 4261023.01
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Dogwood 345 kV Substation GEN-2024-170 Interconnection (Non-Shared NU) (WERE) | 171929 | - | - | WERE | 60 | 4228553
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | XIT Interchange 230 kV Substation GEN-2024-143 Interconnection (TOIF) (SPS) | 171612 | - | - | SPS | 0 | 4144145.19
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | XIT Interchange 230 kV Substation GEN-2024-145 Interconnection (TOIF) (SPS) | 171615 | - | - | SPS | 0 | 4144145.19
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Oasis - San Juan Mesa Wind 230 kV Line GEN-2024-159 Interconnection (TOIF) (SPS) | 171625 | - | - | SPS | 0 | 4119557
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Van Buren 161 kV Substation GEN-2024-243 Interconnection (Non-Shared NU) (SWPA) | 171719 | - | - | SWPA | 48 | 4100000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | San Juan 230 kV Substation GEN-2024-079/080 Interconnection (Shared NU) (SPS) | 171553 | - | - | SPS | 0 | 4035781.5
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Antelope - Hoskins 345 kV line GEN-2024-140 Interconnection (Non-Shared NU) (NPPD) | 171609 | - | - | NPPD | 60 | 4000000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Hitchland - Moore 230kV line GEN-2024-045 Interconnection (TOIF) (SPS) | 171519 | - | - | SPS | 0 | 3976274
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Ink Basin 230 kV Substation GEN-2024-336 Interconnection (TOIF) (SPS) | 171844 | - | - | SPS | 0 | 3955290.56
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Lydia 345 kV Substation GEN-2024-025 Interconnection (Non-Shared NU) (AEP) | 171495 | - | - | AEP | 36 | 3900000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Chisholm 345 kV Substation GEN-2024-154 Interconnection (Non-Shared NU) (AEP) | 171620 | - | - | AEP | 36 | 3900000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Pittsburgh 345 kV Substation GEN-2024-250 Interconnection (Non-Shared NU) (AEP) | 171729 | - | - | AEP | 36 | 3900000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Delaware 345 kV Substation GEN-2024-345 Interconnection (Non-Shared NU) (AEP) | 171861 | - | - | AEP | 36 | 3900000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Chaves County - San Juan Wind 230 kV Line GEN-2024-271 Interconnection (TOIF) (SPS) | 171754 | - | - | SPS | 0 | 3858814.71
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Bushland 230 kV Substation GEN-2024-364 Interconnection (TOIF) (SPS) | 171876 | - | - | SPS | 0 | 3852000.39
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Hugo 345 kV Substation GEN-2024-083 Interconnection (Non-Shared NU) (ITCGP) | 171558 | - | - | ITCGP | 30 | 3834311
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Pleasant Hills 230 kV Substation GEN-2024-089 Interconnection (TOIF) (SPS) | 171565 | - | - | SPS | 0 | 3797868.29
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Tulsa North - GR Energy Center 345 kV Line GEN-2024-171 Interconnection (TOIF) (GRDA) | 171637 | - | - | GRDA | 36 | 3797463
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Reeds Spring - Aurora 161 kV Line GEN-2024-084 Interconnection (TOIF) (EMDE) | 171559 | - | - | EDE | 42 | 3775786
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Sundown-Amaco-Yoakum 230 kV Substation GEN-2024-015 Interconnection (TOIF) (SPS) | 171479 | - | - | SPS | 0 | 3766557
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Smithville 161 kV Substation GEN-2024-090 Interconnection (Non-Shared NU) (WERE) | 171915 | - | - | WERE | 42 | 3659394
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Smithville 161 kV Substation GEN-2024-370 Interconnection (Non-Shared NU) (WERE) | 171954 | - | - | WERE | 42 | 3659394
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Murray Gill 138 kV Substation GEN-2024-166 Interconnection (Non-Shared NU) (WERE) | 171925 | - | - | WERE | 48 | 3654211
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Belfield 345 kV Substation GEN-2024-359 Interconnection (Non-Shared NU) (WAPA) | 171869 | - | - | WAPA | 72 | 3640000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Pringle 230 kV Substation GEN-2024-077 Interconnection (TOIF) (SPS) | 171547 | - | - | SPS | 0 | 3558255
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Maddox 115 kV Substation GEN-2024-371 Interconnection (TOIF) (SPS) | 171888 | - | - | SPS | 0 | 3539457.82
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Hobart - Martha 138 kV Line GEN-2024-161 Interconnection (TOIF) (AEP) | 171627 | - | - | AEP | 36 | 3525000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Leonard 138 kV SubstationGEN-2024-362 Interconnection (TOIF) (AEP) | 171874 | - | - | AEP | 30 | 3525000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Cornville 138 kV Substation GEN-2024-369 Interconnection (TOIF) (AEP) | 171886 | - | - | AEP | 30 | 3525000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Beloit 115 kV Substation GEN-2024-072 Interconnection (TOIF) (SUNC) | 171543 | - | - | SEPC | 40 | 3500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Norman Hills 345 kV GEN-2024-013 Interconnection (TOIF) (OGE) | 171477 | - | - | OGE | 36 | 3500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Hosston - Plain Dealing 69 kV Line GEN-2024-044 Interconnection (TOIF) (AEP) | 171517 | - | - | AEP | 36 | 3475000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rodessa - Bloomberg 69 kV Line GEN-2024-220 Interconnection (TOIF) (AEP) | 171688 | - | - | AEP | 36 | 3475000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Texas County Interchange 115 kV Substation GEN-2024-244 Interconnection (TOIF) (SPS) | 171720 | - | - | SPS | 0 | 3442284.34
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | San Juan 230 kV Substation GEN-2024-079 Interconnection (TOIF) (SPS) | 171551 | - | - | SPS | 0 | 3422577.15
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | San Juan 230 kV Substation GEN-2024-080 Interconnection (TOIF) (SPS) | 171552 | - | - | SPS | 0 | 3422577.15
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Seward 115 kV Substation GEN-2024-007 Interconnection (Non-Shared NU) (MIDW) | 171476 | - | - | MIDW | 36 | 3397809.87
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Plant X 230 kV Substation GEN-2024-063 Interconnection (TOIF) (SPS) | 171533 | - | - | SPS | 0 | 3382454.46
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | S Loving 115 kV Substation GEN-2024-295 Interconnection (TOIF) (SPS) | 171787 | - | - | SPS | 0 | 3362273.9
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Eddy County - Crossroads 345 kV Line GEN-2024-278 Interconnection (TOIF) (SPS) | 171762 | - | - | SPS | 0 | 3338843.04
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Farmland - Delaware 138 kV line GEN-2024-058 Interconnection (TOIF) (AEP) | 171529 | - | - | AEP | 36 | 3325000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Lynn Lane West Tap 138 kV Substation GEN-2024-118 Interconnection (TOIF) (AEP) | 171583 | - | - | AEP | 30 | 3325000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Center - Tenaha 138 kV Line GEN-2024-123 Interconnection (TOIF) (AEP) | 171591 | - | - | AEP | 36 | 3325000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Hobart - Martha 138 kV Line GEN-2024-157 Interconnection (TOIF) (AEP) | 171621 | - | - | AEP | 36 | 3325000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Altus Jct - Snyder 138 kV Line GEN-2024-158 Interconnection (TOIF) (AEP) | 171623 | - | - | AEP | 36 | 3325000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Red Point 138 kV Substation GEN-2024-177 Interconnection (TOIF) (AEP) | 171643 | - | - | AEP | 30 | 3325000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Pirkey 138 kV Substation GEN-2024-178 Interconnection (TOIF) (AEP) | 171645 | - | - | AEP | 30 | 3325000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Atoka to Lehigh 138 kV line GEN-2024-184 Interconnection (TOIF) (AEP) | 171651 | - | - | AEP | 36 | 3325000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Tulsa North - American Airlines 138 kV Line GEN-2024-318 Interconnection (TOIF) (AEP) | 171814 | - | - | AEP | 36 | 3325000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Coffeyville Tap - North Barlettsville 138 kV Line GEN-2024-346 Interconnection (TOIF) (AEP) | 171862 | - | - | AEP | 36 | 3325000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Bowers 115 kV Substation GEN-2024-368 Interconnection (Non-Shared NU) (SPS) | 171885 | - | - | SPS | 0 | 3298358.56
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | North Loving 115 kV Substation GEN-2024-246 Interconnection (Non-Shared NU) (SPS) | 171725 | - | - | SPS | 0 | 3275577.97
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Superior - Jefferson 69 kV Line GEN-2024-305 Interconnection (TOIF) (AEP) | 171799 | - | - | AEP | 36 | 3275000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Hobbs 115 kV Line GEN-2024-265 Interconnection (TOIF) (SPS) | 171746 | - | - | SPS | 0 | 3262876.57
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Potter Co - Hitchland 345 kV Line GEN-2024-266 Interconnection (TOIF) (SPS) | 171748 | - | - | SPS | 0 | 3261652.93
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Portales 115 kV Substation GEN-2024-092 Interconnection (TOIF) (SPS) | 171569 | - | - | SPS | 0 | 3235767.6
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Olson 230 kV Substation GEN-2024-050 Interconnection (TOIF) (SPS) | 171522 | - | - | SPS | 0 | 3233717.92
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Newhart 230 kV Substation GEN-2024-099 Interconnection (TOIF) (SPS) | 171571 | - | - | SPS | 0 | 3214046.86
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Samson - Chaves 115 kV Line GEN-2024-324 Interconnection (TOIF) (SPS) | 171824 | - | - | SPS | 0 | 3134444.66
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Springbrook - Tande 345 kV Line GEN-2024-081 Interconnection (TOIF) (BEPC) | 171554 | - | - | BEPC | 60 | 3093490
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Springbrook - Tande 345 kV Line GEN-2024-081/082 Interconnection (Shared NU) (BEPC) | 171555 | - | - | BEPC | 60 | 3093486
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | North Loving 115 kV Substation GEN-2024-246 Interconnection (TOIF) (SPS) | 171724 | - | - | SPS | 0 | 3089885.6
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Atoka 115 kV Substation GEN-2024-251 Interconnection (TOIF) (SPS) | 171730 | - | - | SPS | 0 | 3015769.29
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Holcomb 345 kV Substation GEN-2024-102 Interconnection (TOIF) (SUNC) | 171573 | - | - | SEPC | 52 | 3000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Muskogee - Ft. Smith 345 kV Line GEN-2024-113 Interconnection (TOIF) (OGE) | 171577 | - | - | OGE | 36 | 3000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Gracemont - Lawton 345 kV Line GEN-2024-128 Interconnection (TOIF) (OGE) | 171595 | - | - | OGE | 36 | 3000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Hugo - Sunnyside 345 kV Line GEN-2024-132 Interconnection (Non-Shared NU) (OGE) | 171598 | - | - | OGE | 36 | 3000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Degrasse 345 kV Substation GEN-2024-134 Interconnection (TOIF) (OGE) | 171599 | - | - | OGE | 0 | 3000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Degrasse 345 kV Substation GEN-2024-135 Interconnection (TOIF) (OGE) | 171601 | - | - | OGE | 36 | 3000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Seminole - Muskogee 345 kV line GEN-2024-236 Interconnection (TOIF) (OGE) | 171708 | - | - | OGE | 36 | 3000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Cimarron 345 kV Substation GEN-2024-239 Interconnection (Non-Shared NU) (OGE) | 171711 | - | - | OGE | 48 | 3000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Cimmaron 345 kV Substation GEN-2024-252 Interconnection (Non-Shared NU) (OGE) | 171733 | - | - | OGE | 48 | 3000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Mathewson 345 kV Substation GEN-2024-254 Interconnection (TOIF) (OGE) | 171734 | - | - | OGE | 36 | 3000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Muskogee - Fort Smith 345 kV Line GEN-2024-268 Interconnection (Non-Shared NU) (OGE) | 171753 | - | - | OGE | 36 | 3000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Muskogee - Pittsburg 345 kV Line GEN-2024-291 Interconnection (TOIF) (OGE) | 171781 | - | - | OGE | 36 | 3000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Muskoge7 345 kV Substation GEN-2024-293 Interconnection (TOIF) (OGE) | 171783 | - | - | OGE | 36 | 3000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Muskogee - Pittsburg 345 kV Line GEN-2024-296 Interconnection (TOIF) (OGE) | 171789 | - | - | OGE | 36 | 3000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Muskogee - Pittsburg 345 kV Line GEN-2024-297 Interconnection (TOIF) (OGE) | 171790 | - | - | OGE | 36 | 3000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Muskogee - Pittsburg 345 kV Line GEN-2024-298 Interconnection (TOIF) (OGE) | 171791 | - | - | OGE | 36 | 3000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Seminole 345 kV Substation GEN-2024-321 Interconnection (TOIF) (OGE) | 171818 | - | - | OGE | 36 | 3000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Discovery 138 kV Substation GEN-2024-332 Interconnection (Non-Shared NU) (OGE) | 171839 | - | - | OGE | 36 | 3000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Riverside - Redbud Switch 345 kV Line GEN-2024-344 Interconnection (TOIF) (OGE) | 171858 | - | - | OGE | 36 | 3000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Seminole - Maud 138 kV Line GEN-2024-360 Interconnection (Non-Shared NU) (OGE) | 171871 | - | - | OGE | 36 | 3000000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Hitchland-Moore 230 kV line GEN-2024-046 Interconnection (TOIF) (SPS) | 171520 | - | - | SPS | 0 | 2961025.2
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Bowers 115 kV Substation GEN-2024-368 Interconnection (TOIF) (SPS) | 171884 | - | - | SPS | 0 | 2944531.47
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | McCartney 161 kV Substation GEN-2024-088 Interconnection (Non-Shared NU) (CUS) | 171564 | - | - | CUS | 26 | 2930000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Taylor Switching Station 115 kV Substation GEN-2024-306 Interconnection (TOIF) (SPS) | 171801 | - | - | SPS | 0 | 2907181.63
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Dragon 345 kV Substation GEN-2024-317 Interconnection (TOIF) (SPS) | 171812 | - | - | SPS | 0 | 2882135.29
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Groton 345 kV Substation GEN-2024-035 Interconnection (TOIF) (BEPC) | 171504 | - | - | BEPC | 60 | 2834775
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Stegall 345 kV Substation GEN-2024-374 Interconnection (TOIF) (BEPC) | 171894 | - | - | BEPC | 60 | 2834775
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Round Up 345 kV Substation GEN-2024-331 Interconnection (TOIF) (BEPC) | 171836 | - | - | BEPC | 60 | 2804764
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Jal - Teague 115 kV Line GEN-2024-281 Interconnection (TOIF) (SPS) | 171766 | - | - | SPS | 0 | 2804642.69
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Cooper Ranch 115 kV Substation GEN-2024-351 Interconnection (TOIF) (SPS) | 171864 | - | - | SPS | 0 | 2804642.69
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | St. John 115 kV Substation GEN-2024-205 Interconnection (Non-Shared NU) (SUNC) | 171665 | - | - | SEPC | 40 | 2800000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Lynn Lane West Tap 138 kV Substation GEN-2024-118 Interconnection (Non-Shared NU) (AEP) | 171584 | - | - | AEP | 30 | 2800000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Red Point 138 kV Substation GEN-2024-177 Interconnection (Non-Shared NU) (AEP) | 171644 | - | - | AEP | 30 | 2800000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Leonard 138 kV Substation GEN-2024-362 Interconnection (Non-Shared NU) (AEP) | 171875 | - | - | AEP | 30 | 2800000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Cornville 138 kV Substation GEN-2024-369 Interconnection (Non-Shared NU) (AEP) | 171887 | - | - | AEP | 30 | 2800000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Pringle 230 kV Substation GEN-2024-078 Interconnection (TOIF) (SPS) | 171549 | - | - | SPS | 0 | 2770537
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Metro 5 161 kV Substation GEN-2024-319 Interconnection (Non-Shared NU) (KACY) | 171817 | - | - | KACY | 25 | 2757867
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | McCartney 161 kV Substation GEN-2024-088 Interconnection (TOIF) (CUS) | 171563 | - | - | CUS | 26 | 2700000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Lubbock South 230 kV Substation GEN-2024-355 Interconnection (TOIF) (SPS) | 171866 | - | - | SPS | 0 | 2653967
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Pearl 115 kV Substation GEN-2024-273 Interconnection (TOIF) (SPS) | 171758 | - | - | SPS | 0 | 2622572
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Spearville - Holcomb 345 kV Line GEN-2024-193 Interconnection (TOIF) (SUNC) | 171659 | - | - | SEPC | 60 | 2619450
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Spearville - Holcomb 345 kV Line GEN-2024-194 Interconnection (TOIF) (SUNC) | 171660 | - | - | SEPC | 60 | 2619450
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Cimarron 345 kV Substation GEN-2024-239 Interconnection (TOIF) (OGE) | 171710 | - | - | OGE | 48 | 2500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Cimmaron 345 kV Substation GEN-2024-252 Interconnection (TOIF) (OGE) | 171732 | - | - | OGE | 48 | 2500000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Pringle 230 kV Substation GEN-2024-078 Interconnection (Non-Shared NU) (SPS) | 171550 | - | - | SPS | 0 | 2493980
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Hugoton 115 kV Substation GEN-2024-032 Interconnection (TOIF) (SUNC) | 171500 | - | - | SEPC | 40 | 2450000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | XIT Interchange 230 kV Substation GEN-2024-143/145 Interconnection (Shared NU) (SPS) | 171616 | - | - | SPS | 0 | 2442046.04
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Sierra 115 kV Substation GEN-2024-325 Interconnection (TOIF) (SPS) | 171826 | - | - | SPS | 0 | 2416023.14
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | BASIN__-BE4 230 kV Substation GEN-2024-141 Interconnection (TOIF) (BEPC) | 171610 | - | - | BEPC | 60 | 2270573
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Little Missouri 230 kV Substation GEN-2024-328 Interconnection (TOIF) (BEPC) | 171832 | - | - | BEPC | 60 | 2270573
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Santa Fe 115 kV Substation GEN-2024-030 Interconnection (TOIF) (SUNC) | 171498 | - | - | SEPC | 40 | 2250000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | S Loving 115 kV Substation GEN-2024-295 Interconnection (Non-Shared NU) (SPS) | 171788 | - | - | SPS | 0 | 2172444.84
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Substation 3740 345 kV GEN-2024-211 Interconnection (Non-Shared NU) (OPPD) | 171675 | - | - | OPPD | 40 | 2000000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Substation 3740 345 kV GEN-2024-212 Interconnection (Non-Shared NU) (OPPD) | 171677 | - | - | OPPD | 40 | 2000000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Substation 3740 345 kV GEN-2024-213 Interconnection (Non-Shared NU) (OPPD) | 171679 | - | - | OPPD | 40 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Unger - West Bank Tap 138 kV Line GEN-2024-052 Interconnection (TOIF) (WFEC) | 171526 | - | - | WFEC | 60 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Dover SW 138 kV Substation GEN-2024-062 Interconnection (TOIF) (WFEC) | 171531 | - | - | WFEC | 60 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Lexington 138 kV Substation GEN-2024-119 Interconnection (TOIF) (WFEC) | 171585 | - | - | WFEC | 60 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Civit 138 kV Substation GEN-2024-187 Interconnection (TOIF) (WFEC) | 171655 | - | - | WFEC | 60 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Durantp4 - Sclmnjc4 138 kV Line GEN-2024-267 Interconnection (TOIF) (WFEC) | 171750 | - | - | WFEC | 60 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Okeene - Mooreland 138 kV line GEN-2024-308 Interconnection (TOIF) (WFEC) | 171803 | - | - | WFEC | 60 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Unger - West Bank Tap 138 kV Line GEN-2024-373 Interconnection (TOIF) (WFEC) | 171892 | - | - | WFEC | 60 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Norman Hills 345 kV GEN-2024-013 Interconnection (Non-Shared NU) (OGE) | 171478 | - | - | OGE | 36 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Crescent 138 kV Substation GEN-2024-029 Interconnection (TOIF) (OGE) | 171496 | - | - | OGE | 36 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Cow Creek - Morrison 138 kV line GEN-2024-056 Interconnection (TOIF) (OGE) | 171527 | - | - | OGE | 36 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | JNS KAMO 138 kV Substation GEN-2024-120 Interconnection (TOIF) (OGE) | 171587 | - | - | OGE | 36 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Arbuckle 138 kV Substation GEN-2024-164 Interconnection (TOIF) (OGE) | 171631 | - | - | OGE | 36 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Chigley - Oaklawn 138 kV Line GEN-2024-219 Interconnection (TOIF) (OGE) | 171686 | - | - | OGE | 36 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | 515171 138 kV Substation GEN-2024-242 Interconnection (TOIF) (OGE) | 171716 | - | - | OGE | 36 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Lincoln 138 kV Substation GEN-2024-245 Interconnection (TOIF) (OGE) | 171722 | - | - | OGE | 36 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Mathewson 345 kV Substation GEN-2024-254 Interconnection (Non-Shared NU) (OGE) | 171735 | - | - | OGE | 36 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Spring Creek 345 kV Substation GEN-2024-255 Interconnection (TOIF) (OGE) | 171736 | - | - | OGE | 36 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Muskogee - Fort Smith 345 kV Line GEN-2024-268 Interconnection (TOIF) (OGE) | 171752 | - | - | OGE | 36 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Discovery 138 kV Substation GEN-2024-332 Interconnection (TOIF) (OGE) | 171838 | - | - | OGE | 36 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Kelley Avenue 138 kV GEN-2024-333 Interconnection (TOIF) (OGE) | 171840 | - | - | OGE | 36 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Sunnyside - Pooleville 138 kV line GEN-2024-337 Interconnection (TOIF) (OGE) | 171846 | - | - | OGE | 36 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Seminole - Maud 138 kV Line GEN-2024-360 Interconnection (TOIF) (OGE) | 171870 | - | - | OGE | 36 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Spring Valley - Warwick 138 kV line GEN-2024-361 Interconnection (TOIF) (OGE) | 171872 | - | - | OGE | 36 | 2000000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Neosho Ridge - Caney River 345 kV Line GEN-2024-125 Interconnection (TOIF) (WERE) | 171918 | - | - | WERE | 60 | 1958092
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Caney River - Neosho 345 kV Line GEN-2024-129 Interconnection (TOIF) (WERE) | 171920 | - | - | WERE | 60 | 1958092
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Dogwood 345 kV Substation GEN-2024-170 Interconnection (TOIF) (WERE) | 171928 | - | - | WERE | 60 | 1958092
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Sibley - Hawthorne 345 kV line GEN-2024-217 Interconnection (TOIF) (WERE) | 171932 | - | - | WERE | 60 | 1958092
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Stranger Creek - 87th Street 345 kV line GEN-2024-253 Interconnection (TOIF) (WERE) | 171936 | - | - | WERE | 60 | 1958092
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Tecumseh Hill - Swissvale 230kV Line GEN-2024-276 Interconnection (TOIF) (WERE) | 171940 | - | - | WERE | 60 | 1958092
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Sibley 345 kV Substation GEN-2024-352 Interconnection (TOIF) (WERE) | 171951 | - | - | WERE | 60 | 1958092
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Neosho - LaCygne 345 kV Line GEN-2024-076 Interconnection (Non-Shared NU) (WERE) | 171913 | - | - | WERE | 60 | 1958090
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Neosho - LaCygne 345 kV Line GEN-2024-076 Interconnection (TOIF) (WERE) | 171912 | - | - | WERE | 60 | 1958090
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Reno - Summit 345 kV Line GEN-2024-142 Interconnection (TOIF) (WERE) | 171922 | - | - | WERE | 60 | 1958090
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Substation 3740 345 kV GEN-2024-211 Interconnection (TOIF) (OPPD) | 171674 | - | - | OPPD | 36 | 1900000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Substation 3740 345 kV GEN-2024-212 Interconnection (TOIF) (OPPD) | 171676 | - | - | OPPD | 36 | 1900000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Substation 3740 345 kV GEN-2024-213 Interconnection (TOIF) (OPPD) | 171678 | - | - | OPPD | 36 | 1900000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Elm Creek 345 kV Substation GEN-2024-215 Interconnection (Non-Shared NU) (ITCGP) | 171681 | - | - | ITCGP | 30 | 1856969
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Olson 230 kV Substation GEN-2024-050 Interconnection (Non-Shared NU) (SPS) | 171523 | - | - | SPS | 0 | 1846031.59
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Crocker 345 kV Substation GEN-2024-285 Interconnection (TOIF) (BEPC) | 171773 | - | - | BEPC | 60 | 1799526
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rice to Circle 230 kV Line GEN-2024-228 Interconnection (TOIF) (MIDW) | 171695 | - | - | MIDW | 36 | 1797541.2
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Stillwater Northtap 138 kV Substation GEN-2024-247 Interconnection (TOIF) (GRDA) | 171726 | - | - | GRDA | 24 | 1751000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Fitzhugh 161kV GEN-2024-003 Interconnection (TOIF) (AECC) | 171473 | - | - | AECC | 0 | 1750000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Jeffrey EC 345 kV Substation GEN-2024-249 Interconnection (TOIF) (WERE) | 171934 | - | - | WERE | 60 | 1742929
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Bushland 230 kV Substation GEN-2024-364 Interconnection (Non-Shared NU) (SPS) | 171877 | - | - | SPS | 0 | 1716577.16
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Brookline 161 kV Substation GEN-2024-181 Interconnection (Non-Shared NU) (CUS) | 171650 | - | - | CUS | 30 | 1700000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Newhart 230 kV Substation GEN-2024-099 Interconnection (Non-Shared NU) (SPS) | 171572 | - | - | SPS | 0 | 1603584.62
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | S1252 161 kV Substation GEN-2024-372 Interconnection (Non-Shared NU) (OPPD) | 171891 | - | - | OPPD | 40 | 1500000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Beloit 115 kV Substation GEN-2024-072 Interconnection (Non-Shared NU) (SUNC) | 171544 | - | - | SEPC | 40 | 1500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Crescent 138 kV Substation GEN-2024-029 Interconnection (Non-Shared NU) (OGE) | 171497 | - | - | OGE | 36 | 1500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | JNS KAMO 138 kV Substation GEN-2024-120 Interconnection (Non-Shared NU) (OGE) | 171588 | - | - | OGE | 36 | 1500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Hugo - Sunnyside 345 kV Line GEN-2024-132 Interconnection (TOIF) (OGE) | 171597 | - | - | OGE | 36 | 1500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | 515171 138 kV Substation GEN-2024-242 Interconnection (Non-Shared NU) (OGE) | 171717 | - | - | OGE | 36 | 1500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Lincoln 138 kV Substation GEN-2024-245 Interconnection (Non-Shared NU) (OGE) | 171723 | - | - | OGE | 36 | 1500000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Archie - Clinton 161 kV Line GEN-2024-289 Interconnection (TOIF) (WERE) | 171943 | - | - | WERE | 48 | 1495125
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | West Southwest 161 kV Substation GEN-2024-375 Interconnection (TOIF) (WERE) | 171955 | - | - | WERE | 48 | 1495125
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Butler - Nevada 161 kV line GEN-2024-055 Interconnection (TOIF) (WERE) | 171904 | - | - | WERE | 48 | 1495123
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Orrick 161 kV Substation GEN-2024-167 Interconnection (TOIF) (WERE) | 171926 | - | - | WERE | 48 | 1495123
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Berthold 115 kV Substation GEN-2024-327 Interconnection (Non-Shared NU) (CPEC) | 171831 | - | - | CPEC | 24 | 1395000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Cirrus 345 kV Substation GEN-2024-067 Interconnection (TOIF) (ITCGP) | 171537 | - | - | ITCGP | 30 | 1306438
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | ITC Great Plains Saddle 345 kV Substation GEN-2024-189 Interconnection (TOIF) (ITCGP) | 171657 | - | - | ITCGP | 30 | 1306438
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Elm Creek 345 kV Substation GEN-2024-215 Interconnection (TOIF) (ITCGP) | 171680 | - | - | ITCGP | 30 | 1306438
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | ITC Hugo 7 345 kV Substation GEN-2024-323 Interconnection (TOIF) (ITCGP) | 171822 | - | - | ITCGP | 30 | 1306438
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Post Rock - Macon 345 kV Line GEN-2024-016 Interconnection (TOIF) (ITCGP) | 171481 | - | - | ITCGP | 0 | 1306433
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Hugo 345 kV Substation GEN-2024-083 Interconnection (TOIF) (ITCGP) | 171557 | - | - | ITCGP | 30 | 1306432
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Stranger Creek 115 kV Substation GEN-2024-339 Interconnection (Non-Shared NU) (WERE) | 171950 | - | - | WERE | 48 | 1289137
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Duncan Road 161 kV Substation GEN-2024-074 Interconnection (Non-Shared NU) (WERE) | 171911 | - | - | WERE | 42 | 1235193
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | East Town 161 kV Substation GEN-2024-260 Interconnection (Non-Shared NU) (WERE) | 171939 | - | - | WERE | 42 | 1235193
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Redlin - Beach3 115 kV line GEN-2024-322 Interconnection (TOIF) (MIDW) | 171820 | - | - | MIDW | 36 | 1222480.35
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Pleasant Valley 115 kV Substation GEN-2024-329 Interconnection (TOIF) (MWEC) | 171834 | - | - | MWE | 0 | 1200000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | St. John 115 kV Substation GEN-2024-205 Interconnection (TOIF) (SUNC) | 171664 | - | - | SEPC | 40 | 1200000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | East Town 161 kV Substation GEN-2024-260 Interconnection (TOIF) (WERE) | 171938 | - | - | WERE | 42 | 1061551
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Smithville 161 kV Substation GEN-2024-370 Interconnection (TOIF) (WERE) | 171953 | - | - | WERE | 42 | 1061551
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Duncan Road 161 kV Substation GEN-2024-074 Interconnection (TOIF) (WERE) | 171910 | - | - | WERE | 42 | 1061550
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Smithville 161 kV Substation GEN-2024-090 Interconnection (TOIF) (WERE) | 171914 | - | - | WERE | 42 | 1061550
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Hugoton 115 kV Substation GEN-2024-032 Interconnection (Non-Shared NU) (SUNC) | 171501 | - | - | SEPC | 40 | 1050000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Murray Gill 138 kV Substation GEN-2024-166 Interconnection (TOIF) (WERE) | 171924 | - | - | WERE | 48 | 1040242
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Reno County 115 kV Substation GEN-2024-176 Interconnection (TOIF) (WERE) | 171930 | - | - | WERE | 48 | 1040242
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Jaggard 115 kV Substation GEN-2024-320 Interconnection (TOIF) (WERE) | 171945 | - | - | WERE | 48 | 1040242
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Butler 138 kV Substation GEN-2024-330 Interconnection (TOIF) (WERE) | 171947 | - | - | WERE | 48 | 1040242
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Stranger Creek 115 kV Substation GEN-2024-339 Interconnection (TOIF) (WERE) | 171949 | - | - | WERE | 48 | 1040242
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Creswell 138 kV Substation GEN-2024-061 Interconnection (TOIF) (WERE) | 171906 | - | - | WERE | 48 | 1040240
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Jarbalo 115 kV Substation GEN-2024-121 Interconnection (TOIF) (WERE) | 171916 | - | - | WERE | 42 | 1038348
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Franklin 69 kV Substation GEN-2024-069 Interconnection (TOIF) (WERE) | 171908 | - | - | WERE | 48 | 1038346
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Olive Creek 345 kV Substation GEN-2024-020 Interconnection (TOIF) (NPPD) | 171487 | - | - | NPPD | 60 | 1000000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Olive Creek 345 kV Substation GEN-2024-021 Interconnection (TOIF) (NPPD) | 171489 | - | - | NPPD | 60 | 1000000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | New Beatrice Power Station 345 kV GEN-2024-022 Interconnection (TOIF) (NPPD) | 171491 | - | - | NPPD | 60 | 1000000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | New Beatrice Power Station 345 kV GEN-2024-023 Interconnection (TOIF) (NPPD) | 171493 | - | - | NPPD | 60 | 1000000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Antelope - Hoskins 345 kV line GEN-2024-140 Interconnection (TOIF) (NPPD) | 171608 | - | - | NPPD | 60 | 1000000
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Dawson County - Miles City 230 kV Line GEN-2024-216 Interconnection (TOIF) (WAPA) | 171682 | - | - | WAPA | 74 | 884136
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Seward 115 kV Substation GEN-2024-007 Interconnection (TOIF) (MIDW) | 171475 | - | - | MIDW | 36 | 883537.2
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Wolf Creek - Blackberry 345 kV Line GEN-2024-139 Interconnection (TOIF) (NEET) | 171606 | - | - | NEET | 0 | 840255
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Wolf Creek - Blackberry 345 kV Line GEN-2024-258 Interconnection (TOIF) (NEET) | 171740 | - | - | NEET | 0 | 840255
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Wolf Creek - Blackberry 345 kV Line GEN-2024-287 Interconnection (TOIF) (NEET) | 171777 | - | - | NEET | 0 | 840255
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Crossroads - Hobbs 345 kV Substation GEN-2024-073 Interconnection (Non-Shared NU) (NEET) | 171546 | - | - | NEET | 0 | 840255
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Crossroads-Hobbs-Roadrunner 345 kV Line GEN-2024-124 Interconnection (TOIF) (NEET) | 171593 | - | - | NEET | 0 | 840255
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Jonesboro - Independence County 161 kV Line GEN-2024-114 Interconnection (TOIF) (SWPA) | 171579 | - | - | SWPA | 48 | 800000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Van Buren 161 kV Substation GEN-2024-243 Interconnection (TOIF) (SWPA) | 171718 | - | - | SWPA | 48 | 800000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Clarksville Ozark 161 kV line GEN-2024-312 Interconnection (TOIF) (SWPA) | 171808 | - | - | SWPA | 48 | 800000
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Belfield 345 kV Substation GEN-2024-359 Interconnection (TOIF) (WAPA) | 171868 | - | - | WAPA | 72 | 709995
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Summit 161 kV Substation GEN-2024-175 Interconnection (Non-Shared NU) (CUS) | 171642 | - | - | CUS | 24 | 700000
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Belfield 230 kV Substation GEN-2024-326 Interconnection (TOIF) (WAPA) | 171828 | - | - | WAPA | 72 | 680000
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Maurine - New Underwood 230 kV Line GEN-2024-282 Interconnection (TOIF) (WAPA) | 171768 | - | - | WAPA | 84 | 620000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Setab 345 kV Substation GEN-2024-136 Interconnection (TOIF) (SUNC) | 171603 | - | - | SEPC | 52 | 551624
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Setab 345 kV Substation GEN-2024-137 Interconnection (TOIF) (SUNC) | 171604 | - | - | SEPC | 52 | 551624
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Setab 345 kV Substation GEN-2024-138 Interconnection (TOIF) (SUNC) | 171605 | - | - | SEPC | 52 | 551624
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Setab 345 kV Substation GEN-2024-144 Interconnection (TOIF) (SUNC) | 171613 | - | - | SEPC | 52 | 551624
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | FREMONT7 115 kV Substation GEN-2024-065 Interconnection (TOIF) (NPPD) | 171535 | - | - | NPPD | 48 | 500000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Twin Church 230 kV Substation GEN-2024-162 Interconnection (TOIF) (NPPD) | 171629 | - | - | NPPD | 48 | 0
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Geneva 115 kV Substation GEN-2024-168 Interconnection (TOIF) (NPPD) | 171635 | - | - | NPPD | 48 | 500000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Pawnee Lake 115 kV Substation GEN-2024-173 Interconnection (TOIF) (NPPD) | 171639 | - | - | NPPD | 48 | 500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Riverside - Redbud Switch 345 kV Line GEN-2024-344 Interconnection (Non-Shared NU) (AEP) | 171857 | - | - | AEP | 24 | 500000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | S3458 to Cooper 345 kV line GEN-2024-040 Interconnection (TOIF) (OPPD) | 171510 | - | - | OPPD | 30 | 496523
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Cooper - S12080 161 kV line GEN-2024-038 Interconnection (TOIF) (OPPD) | 171506 | - | - | OPPD | 30 | 476039
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Humboldt - S1280 161 kV line GEN-2024-039 Interconnection (TOIF) (OPPD) | 171508 | - | - | OPPD | 30 | 476039
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | S1252 161 kV Substation GEN-2024-372 Interconnection (TOIF) (OPPD) | 171890 | - | - | OPPD | 30 | 476039
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Forman 115 kV Substation GEN-2024-034 Interconnection (TOIF) (WAPA) | 171502 | - | - | WAPA | 72 | 410000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | S1399 5 161 kV Substation GEN-2024-231 Interconnection (Non-Shared NU) (OPPD) | 171701 | - | - | OPPD | 18 | 350000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Raun - Tekamah 161 kV line GEN-2024-234 Interconnection (Non-Shared NU) (OPPD) | 171705 | - | - | OPPD | 18 | 350000
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Berthold 115 kV Substation GEN-2024-327 Interconnection (TOIF) (CPEC) | 171830 | - | - | CPEC | 24 | 214000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Metro 5 161 kV Substation GEN-2024-319 Interconnection (TOIF) (KACY) | 171816 | - | - | KACY | 0 | 200000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Lydia 345 kV Substation GEN-2024-241 Interconnection (TOIF) (AEP) | 171714 | - | - | AEP | 18 | 200000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Stillwater Northtap 138 kV Substation GEN-2024-247 Interconnection (Non-Shared NU) (GRDA) | 171727 | - | - | GRDA | 24 | 195000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Tulsa North - Igloo Valley 345 kV line GEN-2024-294 Interconnection (Non-Shared NU) (GRDA) | 171786 | - | - | GRDA | 36 | 130000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Overton - Sedalia East 161 kV line GEN-2024-054 Interconnection (TOIF) (WERE) | 171902 | - | - | WERE | 36 | 112911
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Tecumseh Hill - Swissvale 230kV Line GEN-2024-277 Interconnection (TOIF) (WERE) | 171941 | - | - | WERE | 60 | 112911
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Brown 138 kV Substation GEN-2024-204 Interconnection (TOIF) (OGE) | 171662 | - | - | OGE | 9 | 100000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | OMPA 345 kV Switchyard GEN-2024-334 Interconnection (TOIF) (OGE) | 171842 | - | - | OGE | 9 | 100000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Summit 161 kV Substation GEN-2024-175 Interconnection (TOIF) (CUS) | 171641 | - | - | CUS | 18 | 55000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Brookline 161 kV Substation GEN-2024-181 Interconnection (TOIF) (CUS) | 171649 | - | - | CUS | 18 | 55000
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Maurine - New Underwood 230 kV Line GEN-2024-283 Interconnection (TOIF) (WAPA) | 171769 | - | - | WAPA | 84 | 0
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Pleasant Valley 115 kV Substation GEN-2024-329 Interconnection (Non-Shared NU) (MWEC) | 171835 | - | - | MWE | 0 | 0
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Olive Creek 345 kV Substation GEN-2024-017 Interconnection (Non-Shared NU) (NPPD) | 171484 | - | - | NPPD | 60 | 0
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Olive Creek 345 kV Substation GEN-2024-017 Interconnection (TOIF) (NPPD) | 171483 | - | - | NPPD | 60 | 0
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | New Beatrice Power Station 345 kV GEN-2024-018 Interconnection (TOIF) (NPPD) | 171485 | - | - | NPPD | 60 | 0
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | New Beatrice Power Station 345 kV Substation GEN-2024-019 Interconnection (TOIF) (NPPD) | 171486 | - | - | NPPD | 60 | 0
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | S1399 5 161 kV Substation GEN-2024-231 Interconnection (TOIF) (OPPD) | 171700 | - | - | OPPD | 0 | 0
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Raun - Tekamah 161 kV line GEN-2024-234 Interconnection (TOIF) (OPPD) | 171704 | - | - | OPPD | 0 | 0
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Overton - Sedalia East 161 kV line GEN-2024-054 Interconnection (Non-Shared NU) (WERE) | 171903 | - | - | WERE | 36 | 0
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Blue Valley 161 kV Substation GEN-2024-206 Interconnection (Non-Shared NU) (INDN) | 171667 | - | - | INDN | 0 | 0
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Blue Valley 161 kV Substation GEN-2024-206 Interconnection (TOIF) (INDN) | 171666 | - | - | INDN | 0 | 0
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Blue Valley - Blumil 161 kV Line GEN-2024-207 Interconnection (Non-Shared NU) (INDN) | 171669 | - | - | INDN | 0 | 0
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Blue Valley - Blumil 161 kV Line GEN-2024-207 Interconnection (TOIF) (INDN) | 171668 | - | - | INDN | 0 | 0
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Elm Creek - Tobias 345 kV Line GEN-2024-288 Interconnection (Non-Shared NU) (SUNC) | 171780 | - | - | SEPC | 0 | 0
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Elm Creek - Tobias 345 kV Line GEN-2024-288 Interconnection (TOIF) (SUNC) | 171779 | - | - | SEPC | 0 | 0
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Fitzhugh 161kV GEN-2024-003 Interconnection (Non-Shared NU) (AECC) | 171474 | - | - | AECC | 0 | 0
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | West Atlanta - Atlanta 69 kV Line GEN-2024-071 Interconnection (Non-Shared NU) (AEP) | 171542 | - | - | AEP | NA | 0
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | West Atlanta - Atlanta 69 kV Line GEN-2024-071 Interconnection (TOIF) (AEP) | 171541 | - | - | AEP | NA | 0
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Coffeyville Tap - North Bartlesville 138kV Line GEN-2024-117 Interconnection (TOIF) (AEP) | 171581 | - | - | AEP | NA | 0
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Lieberman - IPC Jefferson 138 kV Line GEN-2024-122 Interconnection (Non-Shared NU) (AEP) | 171590 | - | - | AEP | NA | 0
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Lieberman - IPC Jefferson 138 kV Line GEN-2024-122 Interconnection (TOIF) (AEP) | 171589 | - | - | AEP | NA | 0
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Kerr Dam 161 kV Substation GEN-2024-180 Interconnection (Non-Shared NU) (GRDA) | 171648 | - | - | GRDA | 0 | 0
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Kerr Dam 161 kV Substation GEN-2024-180 Interconnection (TOIF) (GRDA) | 171647 | - | - | GRDA | 0 | 0
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Brown 138 kV Substation GEN-2024-204 Interconnection (Non-Shared NU) (OGE) | 171663 | - | - | OGE | 0 | 0
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Lydia 345 kV Substation GEN-2024-241 Interconnection (Non-Shared NU) (AEP) | 171715 | - | - | AEP | 0 | 0
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Tulsa North - Igloo Valley 345 kV line GEN-2024-294 Interconnection (TOIF) (GRDA) | 171785 | - | - | GRDA | 0 | 0
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | OMPA 345 kV Switchyard GEN-2024-334 Interconnection (Non-Shared NU) (OGE) | 171843 | - | - | OGE | 0 | 0
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Riverside - Redbud Switch 345 kV Line GEN-2024-344 Interconnection (TOIF) (AEP) | 171856 | - | - | AEP | 0 | 0
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Hemphill 138 kV Substation GEN-2024-376 Interconnection (Non-Shared NU) (ETEC) | 171897 | - | - | ETEC | 0 | 0
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Hemphill 138 kV Substation GEN-2024-376 Interconnection (TOIF) (ETEC) | 171896 | - | - | ETEC | 0 | 0
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | John W Turk Jr Power Plant 345 kV Substation GEN-2024-226/227 Interconnection (Shared NU) (AEP) | 171694 | - | - | AEP | 36 | 0
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Roswell Interchange 115 kV Substation GEN-2024-186 Interconnection (TOIF) (SPS) | 171653 | - | - | SPS | 0 | 0
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Hobbs 115 kV Line GEN-2024-261 Interconnection (Non-Shared NU) (LCEC) | 171745 | - | - | LEA | 0 | 0
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Hobbs 115 kV Line GEN-2024-261 Interconnection (TOIF) (LCEC) | 171744 | - | - | LEA | 0 | 0
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Samson - Chaves 115 kV Line GEN-2024-324 Interconnection (Non-Shared NU) (SPS) | 171825 | - | - | SPS | 0 | 0
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Eddy - Chaves 230 kV line GEN-2024-310/311 Interconnection (Shared NU) (SPS) | 171807 | - | - | SPS | 0 | 0
JTIQ Expanded Scope Analysis | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild the 3MINDEN_LA! to 3SAREPTA! 115kV Line 1 | TBD | 21.84 | (239,239) | EES |  | 21840000
JTIQ Expanded Scope Analysis | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild the 5EVERTON RD to 5ST JOE 161kV Line 1 | TBD | 13.58 | (557,557) | EES-EAI |  | 20370000
JTIQ Expanded Scope Analysis | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild the 3COUCH% to 3MCNEIL! 115kV Line 1 | TBD | 14.43 | (239,239) | EES-EAI |  | 14430000
JTIQ Expanded Scope Analysis | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild the 5HARRISON.E! to 5EVERTON RD 161kV Line 1 | TBD | 8.3 | (557,557) | EES-EAI |  | 12450000
JTIQ Expanded Scope Analysis | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild the 5PARAGOULD% to 5PARGOULD.S# 161kV Line 1 | TBD | 7.67 | (557,557) | EES-EAI |  | 11505000
JTIQ Expanded Scope Analysis | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild the 5JONESBORO! to 5JONSBORO.N# 161kV Line 1 | TBD | 7.05 | (557,557) | EES-EAI |  | 10575000
JTIQ Expanded Scope Analysis | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild the 3LEWISVILLE# to 3PATMOS.W# 115kV Line 1 | TBD | 10.38 | (239,239) | EES-EAI |  | 10380000
JTIQ Expanded Scope Analysis | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild the 5JONSBORO.N# to 5PARGOULD.S# 161kV Line 1 | TBD | 6.22 | (557,557) | EES-EAI |  | 9330000
JTIQ Expanded Scope Analysis | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild the 3COUCH% to 3LEWISVILLE# 115kV Line 1 | TBD | 9.07 | (239,239) | EES-EAI |  | 9070000
JTIQ Expanded Scope Analysis | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild the 5ST JOE to 5HILLTOP% 161kV Line 1 | TBD | 3.9 | (557,557) | EES-EAI |  | 5850000
JTIQ Expanded Scope Analysis | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild the SOURIS 7 to MALLARD7 115kV Line 1 | TBD | 5.3 | (239,239) | XEL |  | 5300000

## All Thermal
SOLUTIONTYPE | Group | Scenario | Season | Mitigation Iteration | Source | Direction | MONTCOMMONNAME | Rating Type | Rating (MVA) | TDF | TC Loading % | CONTNAME | Constraint Violation Criteria | Upgrade Name
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.42125 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.054371 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.068658 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.25485 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.42125 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.042657 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.063989 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.23165 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.20777 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.20777 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.20777 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.20777 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.058558 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.10855 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.10855 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.041146 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.16589 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.24882 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.032916 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.030034 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.093389 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.04415 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-024 |  | Non-Converged |  |  | 0.033141 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.10567 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.11075 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.10011 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.04415 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.049494 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.065855 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.11809 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.12174 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-121 |  | Non-Converged |  |  | 0.030587 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.11509 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.11509 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.11509 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.041965 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.11509 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.048685 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.25423 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.20312 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.20312 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.091836 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.044993 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.10729 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.049774 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.062631 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.067304 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.087853 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-260 |  | Non-Converged |  |  | 0.033054 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.085771 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-276 |  | Non-Converged |  |  | 0.031225 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-277 |  | Non-Converged |  |  | 0.031225 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.050053 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.12106 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-339 |  | Non-Converged |  |  | 0.031051 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.057622 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.039802 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.35036 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.22111 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.055688 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-125 |  | Non-Converged |  |  | 0.034907 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-139 |  | Non-Converged |  |  | 0.034288 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.11512 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.046661 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.097733 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.060881 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.23361 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.37968 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.09778 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.053623 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-258 |  | Non-Converged |  |  | 0.030939 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.049827 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.041794 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-276 |  | Non-Converged |  |  | 0.035327 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-277 |  | Non-Converged |  |  | 0.035327 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.42164 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.0353 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.044464 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.043479 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.060084 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.10366 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.036544 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.052017 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.21871 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.18833 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.18833 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.18833 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.18833 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.050175 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.096476 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.096476 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.031848 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.13022 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.07972 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.037681 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.040881 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.64134 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.64134 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.64134 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.64134 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.34658 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.12694 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.037681 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.040881 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.64134 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.64134 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.64134 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.64134 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.34658 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.12694 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.87069 |  | Single 532871 CIRCLE6 230 783810 G24-228-TAP 230 1 | TDF Impact | Add line 532871 CIRCLE 6 230 783810 G24-228-TAP 230 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.074529 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.04295 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.091542 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.074529 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.10737 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.075552 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.075552 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.075552 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.075552 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.04456 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.059218 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.059218 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.037092 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.065714 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.049038 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.045471 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.096904 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.55707 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.049124 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.049038 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.11271 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.049056 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.030792 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.030792 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.030792 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.030792 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.030851 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.040413 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.091834 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.096043 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.096043 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.080633 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.035418 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.058629 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.058449 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.072905 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.068864 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.041876 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.14641 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-024 |  | Non-Converged |  |  | 0.13733 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-054 |  | Non-Converged |  |  | 0.045603 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-055 |  | Non-Converged |  |  | 0.049478 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.036426 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-069 |  | Non-Converged |  |  | 0.041253 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-074 |  | Non-Converged |  |  | 0.068992 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-076 |  | Non-Converged |  |  | 0.048113 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-084 |  | Non-Converged |  |  | 0.035243 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-090 |  | Non-Converged |  |  | 0.085131 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-091 |  | Non-Converged |  |  | 0.037846 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-121 |  | Non-Converged |  |  | 0.090251 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-125 |  | Non-Converged |  |  | 0.041248 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-139 |  | Non-Converged |  |  | 0.049627 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.038111 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.037835 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-167 |  | Non-Converged |  |  | 0.073644 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-170 |  | Non-Converged |  |  | 0.07416 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-175 |  | Non-Converged |  |  | 0.034338 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.036828 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-181 |  | Non-Converged |  |  | 0.034761 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.041325 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-217 |  | Non-Converged |  |  | 0.099583 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.033623 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-253 |  | Non-Converged |  |  | 0.089963 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-258 |  | Non-Converged |  |  | 0.046536 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-259 |  | Non-Converged |  |  | 0.039429 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-260 |  | Non-Converged |  |  | 0.13695 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.033342 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-276 |  | Non-Converged |  |  | 0.075228 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-277 |  | Non-Converged |  |  | 0.075228 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-287 |  | Non-Converged |  |  | 0.043938 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-289 |  | Non-Converged |  |  | 0.051613 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-319 |  | Non-Converged |  |  | 0.074005 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-320 |  | Non-Converged |  |  | 0.083338 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.040678 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-339 |  | Non-Converged |  |  | 0.095614 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-352 |  | Non-Converged |  |  | 0.11056 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-370 |  | Non-Converged |  |  | 0.085131 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-375 |  | Non-Converged |  |  | 0.042508 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.04415 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-024 |  | Non-Converged |  |  | 0.033141 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.10567 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.11075 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.10011 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.04415 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.049494 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.065855 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.11809 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.12174 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-121 |  | Non-Converged |  |  | 0.030587 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.11509 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.11509 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.11509 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.041965 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.11509 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.048685 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.25423 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.20312 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.20312 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.091836 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.044993 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.10729 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.049774 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.062631 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.067304 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.087853 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-260 |  | Non-Converged |  |  | 0.033054 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.085771 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-276 |  | Non-Converged |  |  | 0.031225 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-277 |  | Non-Converged |  |  | 0.031225 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.050053 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.12106 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-339 |  | Non-Converged |  |  | 0.031051 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.043479 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.060084 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.35698 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.036544 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.052017 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.446 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.3777 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.3777 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.3777 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.3777 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.050175 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.096476 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.096476 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.031848 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.24302 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.07972 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.095676 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.057829 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.1432 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.095676 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.16358 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.15121 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.15121 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.15121 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.15121 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.14317 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.24931 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.24931 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.10963 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.037086 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.1053 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.055986 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.13829 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.1053 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.15618 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 1 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 1 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 1 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 1 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.053788 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.076425 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.076425 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.091295 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.070588 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.057829 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.074787 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.070588 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.081764 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.050625 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.050625 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.050625 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.050625 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.14317 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.15578 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.15578 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.080563 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.037086 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.10466 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.055055 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.048283 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.13236 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.10466 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.051544 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.13409 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.22557 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.22557 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.22557 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.22557 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.056216 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.074649 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.074649 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.040856 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.27152 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.09003 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.039778 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.039214 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.11228 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.1053 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.055986 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.13829 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.1053 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.15618 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 1 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 1 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 1 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 1 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.053788 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.076425 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.076425 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.091295 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.049038 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.045471 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.096904 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.55707 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.049124 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.049038 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.11271 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.049056 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.030792 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.030792 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.030792 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.030792 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.030851 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.040413 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.091834 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.096043 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.096043 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.080633 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.035418 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.058629 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.058449 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.072905 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.068864 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.041876 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.14641 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.04415 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-024 |  | Non-Converged |  |  | 0.033141 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.10567 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.11075 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.10011 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.04415 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.049494 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.065855 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.11809 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.12174 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-121 |  | Non-Converged |  |  | 0.030587 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.11509 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.11509 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.11509 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.041965 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.11509 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.048685 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.25423 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.20312 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.20312 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.091836 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.044993 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.10729 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.049774 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.062631 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.067304 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.087853 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-260 |  | Non-Converged |  |  | 0.033054 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.085771 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-276 |  | Non-Converged |  |  | 0.031225 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-277 |  | Non-Converged |  |  | 0.031225 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.050053 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.12106 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-339 |  | Non-Converged |  |  | 0.031051 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.62195 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.054371 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.068658 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.25485 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.62195 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.042657 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.063989 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.23165 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.20777 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.20777 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.20777 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.20777 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.058558 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.10855 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.10855 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.041146 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.16589 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.34872 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.032916 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.030034 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.093389 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.043479 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.060084 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.10366 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.036544 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.052017 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.21871 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.18833 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.18833 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.18833 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.18833 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.050175 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.096476 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.096476 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.031848 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.13022 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.07972 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.1053 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.055986 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.13829 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.1053 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.15618 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 1 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 1 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 1 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 1 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.053788 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.076425 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.076425 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.091295 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.049038 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.045471 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.096904 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.55707 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.049124 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.049038 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.11271 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.049056 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.030792 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.030792 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.030792 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.030792 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.030851 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.040413 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.091834 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.096043 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.096043 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.080633 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.035418 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.058629 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.058449 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.072905 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.068864 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.041876 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.14641 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.060084 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.040881 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.64134 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.64134 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.64134 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.64134 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.34658 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.12694 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.1053 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.055986 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.13829 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.1053 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.15618 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.27434 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.27434 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.27434 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.27434 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.053788 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.076425 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.076425 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.091295 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.10466 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.055055 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.048283 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None